## Heat demand
Heat demand Pivdennodonbaska 3
[9 empty] | Flare |  |  |  |  | Total
Monat | Heat amount Gcal | Heat amount MWh | heat capacity needed MW | firing capacity kW | methane amount needed m3 CH4 | methane amount t CH4 | ERU t CO2 eq |  | firing capacity kW | maximum monthly firing amount | weighted amount (8,000 h) | methane amount needed m3 CH4 | methane amount t CH4 | methane amount needed m3 CH4 | % Boiler | % flare
January | 11282 | 13166.094 | 17.6964 | 24076.6842 | 1484442.888 | 1064.3474 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 1825341.607 | 81.32% | 18.68%
February | 9265 | 10812.255 | 16.0897 | 21890.7009 | 1219053.6569 | 874.063 |  |  | 5000 | 3360000 | 3068493.1507 | 307908.5204 | 220.7708 | 1526962.1773 | 79.84% | 20.16%
March | 7450 | 8694.15 | 11.6857 | 15898.8918 | 980242.8218 | 702.8353 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 1321141.5408 | 74.2% | 25.8%
April | 3024 | 3529.008 | 4.9014 | 6668.5714 | 397886.4823 | 285.2851 |  |  | 5000 | 3600000 | 3287671.2329 | 329901.9861 | 236.5401 | 727788.4684 | 54.67% | 45.33%
May | 882 | 1029.294 | 1.3835 | 1882.2581 | 112265.9776 | 80.4948 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 453164.6966 | 24.77% | 75.23%
June | 882 | 1029.294 | 1.4296 | 1945 | 112265.9776 | 80.4948 |  |  | 5000 | 3600000 | 3287671.2329 | 329901.9861 | 236.5401 | 442167.9637 | 25.39% | 74.61%
July | 882 | 1029.294 | 1.3835 | 1882.2581 | 112265.9776 | 80.4948 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 453164.6966 | 24.77% | 75.23%
August | 882 | 1029.294 | 1.3835 | 1882.2581 | 112265.9776 | 80.4948 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 453164.6966 | 24.77% | 75.23%
September | 882 | 1029.294 | 1.4296 | 1945 | 112265.9776 | 80.4948 |  |  | 5000 | 3600000 | 3287671.2329 | 329901.9861 | 236.5401 | 442167.9637 | 25.39% | 74.61%
October | 3024 | 3529.008 | 4.7433 | 6453.4562 | 397886.4823 | 285.2851 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 738785.2013 | 53.86% | 46.14%
November | 7213 | 8417.571 | 11.6911 | 15906.2188 | 949059.2582 | 680.4766 |  |  | 5000 | 3600000 | 3287671.2329 | 329901.9861 | 236.5401 | 1278961.2444 | 74.21% | 25.79%
December | 9809 | 11447.103 | 15.3859 | 20933.1852 | 1290631.1194 | 925.3841 |  |  | 5000 | 3720000 | 3397260.274 | 340898.719 | 244.4248 | 1631529.8384 | 79.11% | 20.89%
Summe | 55477 | 64741.659 | 7.4336 | 10113.7069 | 7280532.5969 | 5220.1419 | 95267.5892 | CH4-destruction | 5000 | 43800000 | 40000000 | 4013807.4978 | 2877.9049 | 11294340.0947 | 51.86% | 48.14%
[7 empty] | 30001.3729 | coal displacement |  |  |  |  | 2590.1144
total | [6 empty] | 125268.962 | total ERU per year
winter boiler | 51067 | 59595.189 | 11.7419 | 15975.3869 | 6719202.709 | 4817.6766
summer boiler | 4410 | 5146.47 | 1.4019 | 1907.3548 | 561329.8879 | 402.4742
Note on B4: Adam Hadulla: coal mine statistic data!
Note on C4: Adam Hadulla: 1 Gcal/h=1.167 MWh
Note on D4: Adam Hadulla: 31 days=744 h 30 days=720 h 28 days=672 h
Note on E4: Adam Hadulla: calculated using the measured efficiency of the boiler of 73,5 %
Note on F4: Adam Hadulla: heating value of methane 9.9656 kWh/m³
Note on G4: Adam Hadulla: heating value methane: 13.899 MWh/kg
Note on N4: Adam Hadulla: heating value of methane 9.9656 kWh/m³
Note on O4: Adam Hadulla: heating value methane: 13.899 MWh/kg
Note on O18: Adam Hadulla: reduction due to flaring tool - 90% efficiency

## Calculation
Operating Company | Eco-Alliance
Project name | Pivdennodonbaska No3
Actual state of the project: | PDD 2nd Version - TÜV Süd
Concession
Project type | fuel switch for a coal fired steam boiler + single flare
Adress: | 85670 Vugledar Donbas Oblast Ukraine
Coal mine: | Active Coal Mine Pivdennodonbaska No3
active / abandoned | active | active
CMM source | central suction system | central suction system |  | central suction system
Utilisation | heat generation | heat generation | heat generation | flare | sum
Manufacturer | russian boiler | russian boiler | total | A-TEC / Pro2
type | KVGM-20 | KVG-7,4 | for both boilers | KGU 5/8
Installed Capacity: | winter boiler 20 Gkal | summer boiler 7.4 Gkal |  | single flare 5.0 MW
firing capacity: (MW) | 23.34 | 8.64 |  | 5 | 36.98
power generation:(MW) | 0 | 0 |  | 0 | 0
heat generation: (MWh) | 59595.189 | 5146.47 | 64741.659 | 0 | 64741.659
number of modules: | 1 | 1 |  | 1
operation time methane destruction (h) |  |  |  | 8000
operation time heat production (h) | Oct-Apr | May-Sept |  | 0
operation time power production (h) | 0 | 0 |  | 0
efficiency heat production | 89% | 92% |  | 0%
efficiency power production | 0% | 0% |  | 0%
Project emissions PEy (tCO2eq) | 13757 | 1149 | 14906 | 13166 | 28072 | 7018 | 25%
project emissions due to own consumption PEME (tCO2eq) | 0 | 0 | 0 | 0 | 0
project emissions from methane destroyed PEMD (tCO2eq) | 13248.6105 | 1106.8041 | 14355.4146 | 7122.8146 | 21478.2292
project emissions from uncombusted methane PEUM (tCO2eq) | 508.398 | 42.4722 | 550.8702 | 6043.6003 | 6594.4704
methane destruction by unit i MDi (tCH4) | 4817.6766 | 402.4742 | 5220.1508 | 2590.1144 | 13030.416 | <- Input data calculated from heat demand
methane sent to unit i MMi (tCH4) | 4841.886 | 404.4967 | 5246.3827 | 2877.9049 | 13370.6703 | <- recalculation from heat demand
efficiency methane destruction of unit i Eff i | 99.5% | 99.5% |  | 90%
electricity own consumption CONSELEC (MWh) | 0 | 0 | 0 | 0 | 0
electrictity emission factor CEFELEC (tCO2/MWh)
Baseline Emissions BEy | 129296 | 10879 | 140175 | 60436 | 200611 | 50153 | 25%
Baseline emissions from methane release BEMR (tCO2eq) | 101679.6058 | 8494.4307 | 110174 | 60436.0026 | 170610.0391
Baseline emissions from production of power and heat BEUSE (tCO2eq) | 27616.4917 | 2384.8812 | 30001 | 0 | 30001.3729
CMM captured, sent to and destroyed by usi i | 4841.886 | 404.4967 | 5246.3827 | 2877.9049 | 13370.6703
power production GENY (MWh) | 0 | 0 | 0 | 0 | 0
baseline emissions power BEGEN (tCO2eq) | 0 | 0 | 0 | 0 | 0
heat production HEATy (MWh) | 59595.189 | 5146.47 | 64741.659 | 0 | 64741.659
which primal energy source is displaced? | coal | coal
EFCO2,HEAT heat (tCO2/MWh) - oil 0,2666 - natural gas 0,2020 - coal 0,3406 | 0.3406 | 0.3406
efficiency of coal boilers EffHEAT | 73.5% | 73.5%
baseline emissions heat production BEHEAT (tCO2eq) | 27616.4917 | 2384.8812 | 30001.3729 | 0 | 30001.3729
Emission reductions ERy | 115539 | 9730 | 125269 | 47270 | 172539 | 43135 | 25%
release | 25419.9015 | 2123.6077 | 27543.5091 | 15109.0006
PE | 3439.25 | 287.25 | 3726.5 | 3291.5
heat | 6904.1229 | 596.2203 | 7500.3432 | 0
| 25% | 25% | 25% | 25% |  |  | 25% | Values for 2008, operation since Oct 2008
|  |  |  | ER total for five years | 733291
calculations carried out assuming that: |  |  |  | average for five years | 146658
heat value methane 50.035 MJ/kg = 13.899 MWh/kg
efficiency of coal boilers 73,5% |  |  |  | Baseline for five years | 852597
PCNMHC lower than 1% |  |  |  | Project emissions 5 years | 119306
electricity own consumption CONSELEC is set to zero
- CMM is provided by existing gas pumps, no additional electricity needed
- the own conspumption of the additional measuring and controlling devices is negligible
heat demand is given by the coal mine
efficiencies and operation times of the coal boilers and upgraded boilers are given by the coal mine
Note on B21: Adam Hadulla: manufacturer data
Note on C21: Adam Hadulla: manufacturer data
Note on E29: Adam Hadulla: ACM0008, Version 3 and higher 90% versions 1 and 2 99,5% IPCC

## CEF ELEC
Carbon Emission Factor for the Ukrainian Grid [SenterNovem-ERUPT 5 tender]
2008 | 0.695 | tCO2/MWh
2009 | 0.68 | tCO2/MWh
2010 | 0.666 | tCO2/MWh
2011 | 0.651 | tCO2/MWh
2012 | 0.636 | tCO2/MWh

## CEF Coal
IPCC 2006 Values
Chapter | 2.2 DESCRIPTION OF SOURCES
TABLE | 2.2 DEFAULT EMISSION FACTORS FOR STATIONARY COMBUSTION IN THE ENERGY INDUSTRIES
(kg of greenhouse gas per TJ on a Net Calorific Basis)
Document: | V2_2_Ch2_Stationary_combustion.pdf
Default CO2 emissions factor
| kg CO2/TJ | t CO2/MWh
Anthracite | 98300 | 0.35388
Coking Coal | 94600 | 0.34056
Other Bituminous Coal | 94600 | 0.34056 | lowest value chosen (conservative)
Sub-Bituminous Coal | 96100 | 0.34596
1 INTRODUCTION
1.4 DATA COLLECTION ISSUES
1.4.1 Activity data
Chapter | 1.4.1.3 ACTIVITY DATA SOURCES
TABLE | TABLE 1.2 - DEFAULT NET CALORIFIC VALUES (NCVs) AND LOWER AND UPPER LIMITS OF THE 95% CONFIDENCE INTERVALS
Document: | V2_1_Ch1_Introduction.pdf
Net calorific value
| TJ/Gg | MWh/t
Anthracite | 26.7 | 7.4167
Coking Coal | 28.2 | 7.8333
Other Bituminous Coal | 25.8 | 7.1667 | value chosen
Sub-Bituminous Coal | 18.9 | 5.25
IPCC - Terms of Reference, Chapter1, Introduction, Source of Categories, Table 1.2

## figure
year | baseline emissions | emissions reduction | project emissions
2008 | 50153 | 43135 | 7018 | operation start in October 2008
2009 | 200611 | 172539 | 28072
2010 | 200611 | 172539 | 28072
2011 | 200611 | 172539 | 28072
2012 | 200611 | 172539 | 28072
sum | 852597 | 733291 | 119306
average | 170519 | 146658 | 23861