## Evaluation
EVALUATION OF BASELINE
Begin |  |  | 05.09.2007 10:00
End |  |  | 28.07.2008 24:00
Permitted data ranges from PDD
1 Burner | OT max |  | 769.5 | 0C
| OT min |  | 756 | 0C
2 Burner | OT max |  | 778 | 0C
| OT min |  | 764.1 | 0C
3 Burner | OT max |  | 778.7 | 0C
| OT min |  | 765.2 | 0C
4 Burner | OT max |  | 777.2 | 0C
| OT min |  | 761.4 | 0C
| OP max |  | 284 | kPa
| OP min |  | 243 | kPa
| AFR max |  | 11497.16 | kg/h
| AFR min |  | 9622.76 | kg/h
| AIFR max |  | 10.1 | %
| AIFR min |  | 9.3 | %
Gs Normal |  | Johnson Matthey
Gc Normal |  | 95% Pt/5%Rh (Gauze 1-3), 37%Pt/60%Pd/3%Rh (Gauze 4)
Gs Baseline |  | Johnson Matthey
Gc Baseline |  | 95% Pt/5%Rh (Gauze 1-3), 37%Pt/60%Pd/3%Rh (Gauze 4)
UNC |  |  | 5.12 | %
OHBC total |  |  | 7589 | h
OHBC in operation condition |  |  | 5045 | h | 66.4778 | %
VSGBC (mean) |  |  | 139039.5791 | Nm3/h | 5045 | values
VSGBC (st. dev.) |  |  | 6949.8398 | Nm3/h
VSGBC (mean 95 %) |  |  | 139117.3787 | Nm3/h | 4826 | values
NCSGBC (mean) |  |  | 2634.6868 | mg/Nm3 | 4980 | values
NCSGBC (st. dev.) |  |  | 167.7491 | mg/Nm3
NCSGBC (mean 95 %) |  |  | 2643.6515 | mg/Nm3 | 4793 | values
NAPBC |  |  | 299803.81 | t HNO3
BEBC |  |  | 2791.0662 | t N2O
EFBL |  |  | 0.008833 | tN2O / tHNO3
Explanations:
1.Monitoring data are transfered from database of the software “CDMN2O” in to sheet "baseline calculation " | [6 empty] | Columns A - AJ
In columns F-H are oxidation temparatures in burners No.2,3,4. Data was monitored and are transfered from DCS (Foxboro).
NCSG, VSG, PSG and TSG values are calibrated according QAL2 Calibration report in the software"CDMN2O"
In the sheet “Baseline calculation” are calculation of baseline campaign results.
2. A new column AL was created for NCSG values . There are included manually calculated NCSG values for downtime or maintenance periods.
Calculation of NCSG values during downtime or maintenance periods are performed in BH column and only for periods when the plant was in normal operating conditions (as stated in PDD)
Manually calculated NCSG values from BH column transferred in AL column and are colored in rose. Other NCSG values are unchanged and are transfered from column AA.
In columns BO-BS is calculated N2O concentration (g/s) for every hour. In case where N2O concentration was biger than ELV (104,98 g/s) as stated in IPPC permit,
the NCSG values of 2008 year were recalculated according 104,98 g/s and applied in further calculations. Recalculated NCSG values transferred in AM column.
Also in column AM were transferred unchanged NCSG values from AL column. For 2008 year the NCSG values were inputed in AM column by using logic formula. The formula applied since 2826 row.
3. In column AK is calculated nitric acid production NAPBC total
The lenght of full baseline campaign is shorter than the lenght of normal campaign (AV2), but the lenght of baseline is longer than the lenght of project campaign (AV5).
Therefore according the rule from methodolygy AM0034 "CLn<Clnormal" was set the new end of baseline campaign for calculations of NCSG.
The new end of basline is the last CLbl<CLn (cell AV11).
Further calculations of OH, VSG were performed from data of full baseline campaign
4. Calculation of total operating hours. Column AR
According the ranges of normal operating conditions (as stated in PDD) was calculated OH in operating conditions. Column AQ
Comparing OH total and OH in operating conditions was calculated percentage length of OH in operating conditions. Cell AW14
5. For NCSG and VSG values is performed filtering according the ranges of normal operating conditions (OTmin, OTmax, OPmin, OPmax, AFRmin, AFRmax, AIFRmin, AIFRmax).
Filtered NCSG and VSG values are written in to columns AZ,BA.
From filtered values are calculated NCSGmean and VSGmean, NCSG standard deviation and VSG standard deviation.
6. According ranges NCSGmean ± 1,96SD and VSGmean ± 1.96SD were filtered NCSG and VSG values.
Filtered NCSG and VSG values are written in to columns BC,BD. From filtered values are calculated NCSGmean95% and VSGmean95%.
7. Baseline emission is calculated by formula: BEBC=VSGmean95% * NCSGmean,95% * 10-9 * OHtotal
8. Emission factor is calculated by formula: EFBL=BEBC/NAP*(1-UNC/100%)
9. a) During downtimes of monitoring system was applied the lowest value between 4,5 kg (IPPC value) or last measured valid value (column BH).
For that was calculated hourly EF in BF column. Then hourly EF value was compared with 4,5 kg.
According the lower value of EF was calculated NCSG value ( BH column). This NCSG value was transferred in AL column and applied in further calculation.
b) During troubles of N2O analyser's span calibration, drift of NCSG was deducted from NCSG values registered for period since the last calibration till curent calibration (BJ-BM columns)
Then this value was calibrated with QAL2 coefficients (column BM) and transferred in column AL for futher calculations.
Calculation was performed according downtime periods which are registered in register of troubleshoots.
In the sheet "Downtime of AMS" are shown periods of downtime.
Note. Because in the PDD the unity of AFRmax is Nm3/h (15149,2 Nm3/h), therefore the AFRmax range is translated from Nm3/h in to kg/h by formula
15149,2 *(17*1000 / 22,4 *1000) =11497,16 kg/h.
Because in the PDD the unity of AFRmin is Nm3/h (12679,4 Nm3/h), therefore the AFRmax range is translated from Nm3/h in to kg/h by formula
12679,4 *(17*1000 / 22,4 *1000) =9622,76 kg/h.
17(g/mol) – mole weight of ammonia
22,4 (mol/l) – volume of 1 mole
In EMI system row data have folowing abbreviations:
XNN | Off line
GSB | Service
GWB | Maintenance
GIB | Failure of integration time (operation time less than 40 minutes)
UUU | Failure
GNB | Outside permited range (historical ranges). VSG, NCSG outside 95 % confidence interval.
GEB | Valid with substitution (manually inputed value)
GGB | Valid
Definitions of parameters extracted from Afriso system
OT | oxidation temperature, °C
OP | oxidation pressure, kPa
AFR | ammonia flow, kg/h
AIFR | ammonia/air ratio, %
PSG | pressure of stack gas, hPa
TSG | temperature of stack gas, °C
VSG.oc | volume flow rate of the stack gas, m³/h
VSG.norm | volume flow rate of the stack gas, Nm³/h
NCSG[L] | low range: N2O concentration, mg/Nm3
#NCSG[L] | low range: valid counter, s
NCSG[H] | high range: N2O concentration, mg/Nm3
#NCSG[H] | high range: valid counter, s
NCSG | N2O concentration, mg/Nm3
C[NAP] | HNO3 concentration, %
NAP | nitric acid production ( 100% concentrate), t/h
Calculations are prepared by Tomas Krejaras. SC"Achema" Deputy Chief of Nitric acid plant

## Downtime of AMS
Downtimes of AMS
Data, time |  | Event | Explanation | Applying values during downtime
from | until
18.05.2008 16:00 | 19.05.2008 10:00 | doesn't work N2O analyser, no reading of NCSG | N2O analyser was blocked due to error "Condensate generation at cooler unit" | For the downtime period was applied the lowest value between the conservative IPPC (4,5 kg N2O/ton HNO3) or the last measured value
26.05.2008 18:00 | 27.05.2008 10:00 | doesn't work N2O analyser, no reading of NCSG | Temperature controler of heated line out of order. Replaced by reserve controler
07.06.2008 17:00 | 09.06.2008 9:00 | doesn't work N2O analyser, no reading of NCSG | N2O analyser was blocked due to gas flow min alarm. Lines purged.
02.07.2008 12:00 | 02.07.2008 13:00 | doesn't work N2O analyser, no reading of NCSG | Maintenance works in gas preparation system
26.12.2007 05:00 | 27.12.2007 17:00 | TSG error | The TSG reading increased in 14 oC due to bad contact of termperature transmitter | The TSG value was unchanged because higher temperature reduces the VSG in 3000 (nm3/h) and during baseline it is conservative way.
28.03.2008 9:00 | 04.04.2008 8:00 | Drift of span calibration is 169 mg/m3 | 04-04-2008 after calibration of span N2O concentration increased in 169 mg/m3 | The N2O values since the last calibration were unchanged, because during this period the N2O concentration were lower and it is conservative way.
30.05.2008 9:00 | 06.06.2008 8:00 | Drift of span calibration is -261 mg/m3 | 06-06-2008 after calibration of span N2O concentration decreased in 261 mg/m3 | 261 mg/m3 was deductet from NCSG values registered for period since the last calibration (30-05-2008) till curent calibration
27.06.2008 9:00 | 04.07.2008 8:00 | Drift of span calibration is -307 mg/m3 | 04-07-2008 after calibration of span N2O concentration decreased in 307 mg/m3 | 307 mg/m3 was deductet from NCSG values registered for period since the last calibration (27-06-2008) till curent calibration
04.07.2008 9:00 | 11.07.2008 8:00 | Drift of span calibration is -339 mg/m3 | 11-07-2008 after calibration of span N2O concentration decreased in 339 mg/m3 | 339 mg/m3 was deductet from NCSG values registered for period since the last calibration (04-07-2008) till curent calibration
11.07.2008 9:00 | 18.07.2008 8:00 | Drift of span calibration is -305 mg/m3 | 18-07-2008 after calibration of span N2O concentration decreased in 305 mg/m3 | 305 mg/m3 was deductet from NCSG values registered for period since the last calibration (11-07-2008) till curent calibration
18.07.2008 9:00 | 25.07.2008 8:00 | Drift of span calibration is 120 mg/m3 | 25-07-2008 after calibration of span N2O concentration increased in 120 mg/m3 | The N2O values since the last calibration were unchanged, because during this period the N2O concentration were lower and it is conservative way.
21.05.2008 01:00 | 28.07.2008 24:00 | Nitric acid production accounting device was faulted | According DCS data, HNO3 production is calculated from nitric acid output from storage poz. FIQ_106 and considering nitric acid level in storages poz. LIAHL_101 (LIAHL_102) | NAP was calculated in excel file "GP JI. HNO3_production_v ­_1 (SMW)" and data was written in to EMI3000 system manually.
Shutdowns of GP plant
Data, time |  | Event | Explanation
from | until
05-09-2007, 6:53 |  | GP start | The beginning of baseline
08-10-2007, 4:04 | 11-10-2007, 11:20 | GP stop (shutdown period) | Repairing due to technological problem
29-12-2007, 6:24 | 04-01-2008, 20:40 | GP stop (shutdown period) | Power cut
05-01-2008, 2:11 | 06-01-2008, 11:50 | GP stop (shutdown period) | Repairing due to technological problem
29-07-2008, 3:00 |  | GP stop | The ond of baseline campaign

## Baseline calculation
Date, Time | OH |  | OT Burner 1 |  | OT Burner 2 | OT Burner 3 | OT Burner 4 | OP |  | AFR |  | AIFR |  | PSG |  | TSG |  | VSG.oc |  | VSG.norm |  | NCSG[L] | #NCSG[L] | NCSG[H] | #NCSG[H] | NCSG |  | C[NAP] |  | NAP(op) |  | NAP |  | NAP(tot) |  | NAPBC (total) calculated | NCSG, mg/Nm³ | NCSG, mg/Nm³ |  |  |  | OH in op.cond. | OH total | The lenght of campaigns |  |  |  | Filtering of values in operating condition |  | Filtering of values in 95% interval |  | Hourly EF | Parallel calculation of NCSG mg/Nm³ | Correction of NCSG values when the drift of span calibration was upper the limit |  |  |  | N2O concentration | recalculating of NCSG according ELVs form IPPC permit
| s |  | °C |  | °C | °C | °C | kPa |  | kg/h |  | % |  | hPa |  | °C |  | m³/h |  | Nm³/h |  | mg/Nm³ | s | mg/Nm³ | s | mg/Nm³ |  | % |  | t/h |  | t/h |  | t |  | t | including modified values | including IPPC values | Permitted data ranges from PDD |  |  | 5045 | 7589 | NAP (CLnormal) | 303129.33 | t HNO3 | CLbl is shorter than CLnormal | VSG Nm³/h | NCSG, mg/Nm³ | VSG 95 %, Nm³/h | NCSG 95%, mg/Nm³ | kg N2O/t HNO3 | which is equal IPCC value (4,5 kg ) | Not calibrated value of NCSG, mg/Nm3 | Drift, mg/Nm3 | Corrected NCSG value, mg/Nm3 | Callibrated NCSG value, mg/Nm3 | g/s | mg/Nm3 | ELVs, g/s = | 104.98
05.09.2007 10:00 | 3600 | 2 | 745.19 | GNB | 752.015 | 755.039 | 750.549 | 225.82 | GNB | 9712.14 | GGB | 9.94 | GGB | 1001.12 | GGB | 69.81 | GGB | 160219.08 | GGB | 126095.07 | GGB | 0 | 0 | 1163 | 3600 | 1148.69 | GGB | 100 | GGB | 5.83 | GGB | 5.83 | GGB | 5.83 | GGB | 5.83 | 1148.69 | 1148.69 | 1 Burner | OT max | 769.5 | 0 | 1 | NAPBC (CLbl) full | 299803.81 | t HNO3 | [11 empty] | 40.2345
05.09.2007 11:00 | 3600 | 2 | 745.04 | GNB | 753.113 | 756.164 | 751.648 | 223.97 | GNB | 9641.63 | GGB | 9.93 | GGB | 1001.45 | GGB | 70.15 | GGB | 159302.5 | GGB | 125293.12 | GGB | 0 | 0 | 2507 | 3600 | 2491.75 | GGB | 100 | GGB | 35.21 | GGB | 35.21 | GGB | 41.04 | GGB | 41.04 | 2491.75 | 2491.75 |  | OT min | 756 | 0 | 1 | NAP (CLn) | 402767.41 | t HNO3 | [11 empty] | 86.722
05.09.2007 12:00 | 3600 | 2 | 745.39 | GNB | 753.113 | 756.375 | 751.648 | 222.69 | GNB | 9583.66 | GGB | 9.93 | GGB | 1001.63 | GGB | 71.32 | GGB | 157906.17 | GGB | 123792.07 | GGB | 0 | 0 | 2463 | 3600 | 2447.42 | GGB | 100 | GGB | 34.88 | GGB | 34.88 | GGB | 75.92 | GGB | 75.92 | 2447.42 | 2447.42 | 2 Burner | OT max | 778 | 0 | 1 | CLbl is shorter than Clnormal | [13 empty] | 84.1587
05.09.2007 13:00 | 3600 | 2 | 745.63 | GNB | 753.113 | 756.633 | 752.381 | 221.6 | GNB | 9577.74 | GGB | 9.92 | GGB | 1000.9 | GGB | 71.92 | GGB | 158705.01 | GGB | 124113.43 | GGB | 0 | 0 | 2448 | 3600 | 2432.5 | GGB | 100 | GGB | 35.71 | GGB | 35.71 | GGB | 111.63 | GGB | 111.63 | 2432.5 | 2432.5 |  | OT min | 764.1 | 0 | 1 | [14 empty] | 83.8628
05.09.2007 14:00 | 3600 | 2 | 747.01 | GNB | 754.212 | 759.07 | 753.48 | 224.05 | GNB | 9683.15 | GGB | 9.92 | GGB | 1000.67 | GGB | 71.3 | GGB | 161847.58 | GGB | 126768.47 | GGB | 0 | 0 | 2422 | 3600 | 2406.39 | GGB | 100 | GGB | 38.07 | GGB | 38.07 | GGB | 149.7 | GGB | 149.7 | 2406.39 | 2406.39 | 3 Burner | OT max | 778.7 | 0 | 1 | CALCULATION OF EFBL | [13 empty] | 84.7373
05.09.2007 15:00 | 3600 | 2 | 747.77 | GNB | 755.311 | 758.977 | 753.846 | 223.4 | GNB | 9661.48 | GGB | 9.93 | GGB | 1000.45 | GGB | 71.54 | GGB | 161156.57 | GGB | 126113.1 | GGB | 0 | 0 | 2388 | 3600 | 2372.67 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 189.29 | GGB | 189.29 | 2372.67 | 2372.67 |  | OT min | 765.2 | 0 | 1 | Project campaign is longer than historic, | [13 empty] | 83.118
05.09.2007 16:00 | 3600 | 2 | 747.7 | GNB | 756.776 | 759.961 | 753.846 | 222.07 | GNB | 9651.47 | GGB | 9.93 | GGB | 999.83 | GGB | 72.03 | GGB | 159330.01 | GGB | 124428.97 | GGB | 0 | 0 | 2380 | 3600 | 2364.44 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 228.75 | GGB | 228.75 | 2364.44 | 2364.44 | 4 Burner | OT max | 777.2 | 0 | 1 | therefore all values of NCSGbc and VSGbc measured during | [13 empty] | 81.7236
05.09.2007 17:00 | 3600 | 2 | 747.66 | GNB | 755.678 | 758.906 | 753.846 | 222.21 | GNB | 9628.03 | GGB | 9.92 | GGB | 999.61 | GGB | 71.92 | GGB | 159122.04 | GGB | 124276.64 | GGB | 0 | 0 | 2361 | 3600 | 2345.79 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 268.32 | GGB | 268.32 | 2345.79 | 2345.79 |  | OT min | 761.4 | 0 | 1 | the baseline campaign can be used for the calculation of Efbl. | [13 empty] | 80.9797
05.09.2007 18:00 | 3600 | 2 | 747.75 | GNB | 755.678 | 758.93 | 753.846 | 222.15 | GNB | 9637.02 | GGB | 9.93 | GGB | 999.02 | GGB | 71.29 | GGB | 157594.77 | GGB | 123236.99 | GGB | 0 | 0 | 2342 | 3600 | 2327.19 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 306.95 | GGB | 306.95 | 2327.19 | 2327.19 |  | OP max | 284 | 0 | 1 | NAPBC for NCSGBC | 299803.81 | t HNO3 | [11 empty] | 79.6655
05.09.2007 19:00 | 3600 | 2 | 747.38 | GNB | 755.311 | 757.852 | 753.846 | 222.49 | GNB | 9651.81 | GGB | 9.92 | GGB | 999.1 | GGB | 70.96 | GGB | 155070.6 | GGB | 121390.94 | GGB | 0 | 0 | 2351 | 3600 | 2335.96 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 345.23 | GGB | 345.23 | 2335.96 | 2335.96 |  | OP min | 243 | 0 | 1 | [14 empty] | 78.7679
05.09.2007 20:00 | 3600 | 2 | 747.12 | GNB | 754.212 | 757.852 | 753.48 | 222.62 | GNB | 9697.01 | GGB | 9.92 | GGB | 999.76 | GGB | 70.75 | GGB | 153091.09 | GGB | 119993.65 | GGB | 0 | 0 | 2378 | 3600 | 2362.46 | GGB | 100 | GGB | 36.77 | GGB | 36.77 | GGB | 382 | GGB | 382 | 2362.46 | 2362.46 |  | AFR max | 11497.16 | 0 | 1 | OHBC total | 7589 | [12 empty] | 78.7445
05.09.2007 21:00 | 3600 | 2 | 746.72 | GNB | 755.311 | 758.016 | 752.381 | 223.35 | GNB | 9750.53 | GGB | 9.93 | GGB | 1000.61 | GGB | 69.67 | GGB | 153447.6 | GGB | 120754.47 | GGB | 0 | 0 | 2413 | 3600 | 2398.26 | GGB | 100 | GGB | 37.57 | GGB | 37.57 | GGB | 419.57 | GGB | 419.57 | 2398.26 | 2398.26 |  | AFR min | 9622.76 | 0 | 1 | OH in op. Condition | 5045 | 66.4778 | % | [10 empty] | 80.4446
05.09.2007 22:00 | 3600 | 2 | 746.44 | GNB | 754.212 | 756.094 | 752.381 | 225 | GNB | 9767.77 | GGB | 9.92 | GGB | 1001.59 | GGB | 67.57 | GGB | 155589.96 | GGB | 123317.07 | GGB | 0 | 0 | 2421 | 3600 | 2405.83 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 457.7 | GGB | 457.7 | 2405.83 | 2405.83 |  | AIFR max | 10.1 | 0 | 1 | [14 empty] | 82.4111
05.09.2007 23:00 | 3600 | 2 | 746.35 | GNB | 753.113 | 756.094 | 751.282 | 224.08 | GNB | 9793.25 | GGB | 9.92 | GGB | 1001.83 | GGB | 67.22 | GGB | 155552.55 | GGB | 123440.55 | GGB | 0 | 0 | 2443 | 3600 | 2427.99 | GGB | 100 | GGB | 36.44 | GGB | 36.44 | GGB | 494.15 | GGB | 494.14 | 2427.99 | 2427.99 |  | AIFR min | 9.3 | 0 | 1 |  | Statistical evaluation | [12 empty] | 83.2535
05.09.2007 24:00 | 3600 | 2 | 746.28 | GNB | 754.212 | 755.859 | 751.282 | 224.42 | GNB | 9816.64 | GGB | 9.93 | GGB | 1002.19 | GGB | 67.45 | GGB | 154989.17 | GGB | 122955.53 | GGB | 0 | 0 | 2468 | 3600 | 2452.66 | GGB | 100 | GGB | 37.44 | GGB | 37.44 | GGB | 531.59 | GGB | 531.58 | 2452.66 | 2452.66 |  |  |  | 0 | 1 |  | VSGBC Nm³/h | NCSGBC mg/Nm³ | [11 empty] | 83.7689
06.09.2007 01:00 | 3600 | 2 | 746.31 | GNB | 754.212 | 755.883 | 751.282 | 226.01 | GNB | 9813.27 | GGB | 9.93 | GGB | 1001.99 | GGB | 66.83 | GGB | 157478.14 | GGB | 125133.73 | GGB | 0 | 0 | 2449 | 3600 | 2433.55 | GGB | 100 | GGB | 37.15 | GGB | 37.15 | GGB | 568.74 | GGB | 568.73 | 2433.55 | 2433.55 |  |  |  | 0 | 1 | mean | 139039.5791 | 2634.6868 | [11 empty] | 84.5887
06.09.2007 02:00 | 3600 | 2 | 746.19 | GNB | 754.212 | 755.953 | 751.282 | 226.03 | GNB | 9820.04 | GGB | 9.93 | GGB | 1001.9 | GGB | 66.48 | GGB | 158007.4 | GGB | 125671.99 | GGB | 0 | 0 | 2451 | 3600 | 2435.59 | GGB | 100 | GGB | 36.9 | GGB | 36.9 | GGB | 605.63 | GGB | 605.63 | 2435.59 | 2435.59 |  |  |  | 0 | 1 | Standart deviation | 6949.8398 | 167.7491 | [11 empty] | 85.0237
06.09.2007 03:00 | 3600 | 2 | 745.88 | GNB | 753.113 | 755.953 | 751.282 | 225 | GNB | 9849.25 | GGB | 9.93 | GGB | 1001.89 | GGB | 66.65 | GGB | 156833.34 | GGB | 124673.43 | GGB | 0 | 0 | 2479 | 3600 | 2463.33 | GGB | 100 | GGB | 37.18 | GGB | 37.18 | GGB | 642.81 | GGB | 642.81 | 2463.33 | 2463.33 |  |  |  | 0 | 1 | min range | 125417.8931 | 2305.8986 | [11 empty] | 85.3088
06.09.2007 04:00 | 3600 | 2 | 745.6 | GNB | 753.113 | 754.898 | 751.282 | 225.07 | GNB | 9860.66 | GGB | 9.93 | GGB | 1001.79 | GGB | 66.71 | GGB | 157289.98 | GGB | 125003.7 | GGB | 0 | 0 | 2492 | 3600 | 2476.6 | GGB | 100 | GGB | 37.11 | GGB | 37.11 | GGB | 679.92 | GGB | 679.92 | 2476.6 | 2476.6 |  |  |  | 0 | 1 | max range | 152661.2652 | 2963.4749 | [11 empty] | 85.9956
06.09.2007 05:00 | 3600 | 2 | 745.87 | GNB | 753.113 | 755.906 | 751.282 | 226.43 | GNB | 9847.12 | GGB | 9.93 | GGB | 1001.76 | GGB | 65.87 | GGB | 159849.37 | GGB | 127349.94 | GGB | 0 | 0 | 2468 | 3600 | 2452.64 | GGB | 100 | GGB | 36.87 | GGB | 36.87 | GGB | 716.79 | GGB | 716.79 | 2452.64 | 2452.64 |  |  |  | 0 | 1 | New mean 95% | 139117.3787 | 2643.6515 | [11 empty] | 86.7621
06.09.2007 06:00 | 3600 | 2 | 745.84 | GNB | 753.113 | 754.898 | 750.183 | 226.31 | GNB | 9846.5 | GGB | 9.93 | GGB | 1001.61 | GGB | 65.5 | GGB | 160074.94 | GGB | 127647.57 | GGB | 0 | 0 | 2461 | 3600 | 2446.17 | GGB | 100 | GGB | 37.43 | GGB | 37.43 | GGB | 754.22 | GGB | 754.22 | 2446.17 | 2446.17 |  |  |  | 0 | 1 | [14 empty] | 86.7355
06.09.2007 07:00 | 3600 | 2 | 745.72 | GNB | 753.113 | 755.859 | 751.282 | 225.17 | GNB | 9862.54 | GGB | 9.93 | GGB | 1001.17 | GGB | 65.85 | GGB | 158612.59 | GGB | 126294.99 | GGB | 0 | 0 | 2480 | 3600 | 2464.62 | GGB | 100 | GGB | 36.98 | GGB | 36.98 | GGB | 791.2 | GGB | 791.2 | 2464.62 | 2464.62 |  |  |  | 0 | 1 | BEBC | 2791.0662 | t N2O | [11 empty] | 86.4637
06.09.2007 08:00 | 3600 | 2 | 745.8 | GNB | 754.212 | 756.938 | 751.282 | 224.4 | GNB | 9850.4 | GGB | 9.93 | GGB | 1001.02 | GGB | 66.43 | GGB | 157484.74 | GGB | 125164.3 | GGB | 0 | 0 | 2474 | 3600 | 2458.9 | GGB | 100 | GGB | 36.24 | GGB | 36.24 | GGB | 827.43 | GGB | 827.44 | 2458.9 | 2458.9 |  |  |  | 0 | 1 | [14 empty] | 85.4907
06.09.2007 09:00 | 3600 | 2 | 745.52 | GNB | 754.212 | 755.836 | 751.282 | 225.03 | GNB | 9799.23 | GGB | 9.92 | GGB | 1000.99 | GGB | 66.49 | GGB | 157752.12 | GGB | 125352.39 | GGB | 0 | 0 | 2462 | 3600 | 2446.5 | GGB | 100 | GGB | 35.87 | GGB | 35.87 | GGB | 863.3 | GGB | 863.31 | 2446.5 | 2446.5 |  |  |  | 0 | 1 | [14 empty] | 85.1874
06.09.2007 10:00 | 3600 | 2 | 746.76 | GNB | 755.311 | 757.148 | 752.015 | 225.21 | GNB | 9810.37 | GGB | 9.93 | GGB | 1000.68 | GGB | 66.6 | GGB | 157573.87 | GGB | 125129.81 | GGB | 0 | 0 | 2415 | 3600 | 2399.97 | GGB | 100 | GGB | 36.85 | GGB | 36.85 | GGB | 900.15 | GGB | 900.16 | 2399.97 | 2399.97 |  |  |  | 0 | 1 | [14 empty] | 83.4188
06.09.2007 11:00 | 3600 | 2 | 747.43 | GNB | 755.311 | 758.109 | 753.113 | 223.34 | GNB | 9715.4 | GGB | 9.93 | GGB | 1000.05 | GGB | 67.54 | GGB | 155595.46 | GGB | 123142.13 | GGB | 0 | 0 | 2351 | 3600 | 2335.42 | GGB | 100 | GGB | 36.31 | GGB | 36.31 | GGB | 936.46 | GGB | 936.47 | 2335.42 | 2335.42 |  |  |  | 0 | 1 | EFBL | 0.008833 | tN2O / tHNO3 | [11 empty] | 79.8857
06.09.2007 12:00 | 3600 | 2 | 749.27 | GNB | 757.875 | 760.43 | 755.311 | 224.71 | GNB | 9748.33 | GGB | 9.92 | GGB | 998.9 | GGB | 69.08 | GGB | 155591.06 | GGB | 122443.8 | GGB | 0 | 0 | 2336 | 3600 | 2321.31 | GGB | 100 | GGB | 37.1 | GGB | 37.1 | GGB | 973.56 | GGB | 973.57 | 2321.31 | 2321.31 |  |  |  | 0 | 1 | [14 empty] | 78.9528
06.09.2007 13:00 | 3600 | 2 | 751.92 | GNB | 760.44 | 763.734 | 758.974 | 229.05 | GNB | 9791.12 | GGB | 9.92 | GGB | 997.95 | GGB | 69.13 | GGB | 159346.51 | GGB | 125261.57 | GGB | 0 | 0 | 2270 | 3600 | 2255.12 | GGB | 100 | GGB | 37.18 | GGB | 37.18 | GGB | 1010.74 | GGB | 1010.75 | 2255.12 | 2255.12 |  |  |  | 0 | 1 | [14 empty] | 78.4666
06.09.2007 14:00 | 3600 | 2 | 753.35 | GNB | 760.44 | 764.906 | 757.875 | 232.91 | GNB | 9899.48 | GGB | 9.91 | GGB | 997.02 | GGB | 69.99 | GGB | 161695.73 | GGB | 126670.41 | GGB | 0 | 0 | 2263 | 3600 | 2247.76 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 1051.2 | GGB | 1051.21 | 2247.76 | 2247.76 |  |  |  | 0 | 1 | [14 empty] | 79.0902
06.09.2007 15:00 | 3600 | 2 | 757 | GGB | 766.667 | 770.414 | 764.102 | 243.51 | GGB | 10161.3 | GGB | 9.9 | GGB | 995.94 | GGB | 69.15 | GGB | 169911.95 | GGB | 133290.16 | GGB | 0 | 0 | 2243 | 3600 | 2228.45 | GGB | 100 | GGB | 41.58 | GGB | 41.58 | GGB | 1092.78 | GGB | 1092.79 | 2228.45 | 2228.45 |  |  |  | 1 | 1 |  |  |  |  | 133290.16 | 2228.45 | 133290.16 |  | 7.1436 | [5 empty] | 82.5085
06.09.2007 16:00 | 3600 | 2 | 759.2 | GGB | 766.667 | 770.18 | 763.37 | 247.32 | GGB | 10209.8 | GGB | 9.92 | GGB | 994.71 | GGB | 68.28 | GGB | 174045.92 | GGB | 136713.09 | GGB | 0 | 0 | 2175 | 3600 | 2160.42 | GNB | 100 | GGB | 33.8 | GGB | 33.8 | GGB | 1126.58 | GGB | 1126.59 | 2160.42 | 2160.42 |  |  |  | 1 | 1 |  |  |  |  | 136713.09 | 2160.42 | 136713.09 |  | 8.7384 | [5 empty] | 82.0438
06.09.2007 17:00 | 3600 | 2 | 759.06 | GGB | 766.667 | 770.32 | 763.37 | 245.91 | GGB | 10256.7 | GGB | 9.92 | GGB | 993.7 | GGB | 68.73 | GGB | 172455.94 | GGB | 135147.59 | GGB | 0 | 0 | 2213 | 3600 | 2198.2 | GNB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 1167.14 | GGB | 1167.15 | 2198.2 | 2198.2 |  |  |  | 1 | 1 |  |  |  |  | 135147.59 | 2198.2 | 135147.59 |  | 7.3245 | [5 empty] | 82.5226
06.09.2007 18:00 | 3600 | 2 | 758.74 | GGB | 766.667 | 770.25 | 763.37 | 246.08 | GGB | 10257.7 | GGB | 9.92 | GGB | 993.59 | GGB | 68.67 | GGB | 172809.14 | GGB | 135430.99 | GGB | 0 | 0 | 2222 | 3600 | 2206.63 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 1206.13 | GGB | 1206.14 | 2206.63 | 2206.63 |  |  |  | 1 | 1 |  |  |  |  | 135430.99 | 2206.63 | 135430.99 |  | 7.6647 | [5 empty] | 83.0128
06.09.2007 19:00 | 3600 | 2 | 758.47 | GGB | 766.667 | 770.18 | 763.37 | 247.79 | GGB | 10272.8 | GGB | 9.92 | GGB | 993.69 | GGB | 67.69 | GGB | 175267.3 | GGB | 137768.68 | GGB | 0 | 0 | 2231 | 3600 | 2216.13 | GGB | 100 | GGB | 37.98 | GGB | 37.98 | GGB | 1244.12 | GGB | 1244.12 | 2216.13 | 2216.13 |  |  |  | 1 | 1 |  |  |  |  | 137768.68 | 2216.13 | 137768.68 |  | 8.0388 | [5 empty] | 84.8093
06.09.2007 20:00 | 3600 | 2 | 758.01 | GGB | 765.201 | 768.023 | 762.271 | 248.1 | GGB | 10361.5 | GGB | 9.92 | GGB | 993.62 | GGB | 67.75 | GGB | 175416.94 | GGB | 137851.76 | GGB | 0 | 0 | 2287 | 3600 | 2271.8 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 1283.18 | GGB | 1283.19 | 2271.8 | 2271.8 |  |  |  | 1 | 1 |  |  |  |  | 137851.76 | 2271.8 | 137851.76 |  | 8.0157 | [5 empty] | 86.9921
06.09.2007 21:00 | 3600 | 2 | 757.12 | GGB | 766.3 | 768.984 | 763.37 | 250 | GGB | 10432 | GGB | 9.91 | GGB | 994.48 | GGB | 67.02 | GGB | 177832.19 | GGB | 140172.16 | GGB | 0 | 0 | 2341 | 3600 | 2325.81 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 1322.66 | GGB | 1322.66 | 2325.81 | 2325.81 |  |  |  | 1 | 1 |  |  |  |  | 140172.16 | 2325.81 | 140172.16 | 2325.81 | 8.2598 | [5 empty] | 90.5594
06.09.2007 22:00 | 3600 | 2 | 757.52 | GGB | 765.201 | 767.719 | 762.271 | 251.44 | GGB | 10515.3 | GGB | 9.92 | GGB | 995.47 | GGB | 65.93 | GGB | 180962.65 | GGB | 143237.49 | GGB | 0 | 0 | 2347 | 3600 | 2331.9 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 1361.53 | GGB | 1361.53 | 2331.9 | 2331.9 |  |  |  | 1 | 1 |  |  |  |  | 143237.49 | 2331.9 | 143237.49 | 2331.9 | 8.5931 | [5 empty] | 92.7821
06.09.2007 23:00 | 3600 | 2 | 757.77 | GGB | 767.766 | 768.867 | 764.469 | 252.95 | GGB | 10540.7 | GGB | 9.93 | GGB | 995.98 | GGB | 65.14 | GGB | 181727.38 | GGB | 144253.37 | GGB | 0 | 0 | 2337 | 3600 | 2321.79 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 1399.44 | GGB | 1399.44 | 2321.79 | 2321.79 |  |  |  | 1 | 1 |  |  |  |  | 144253.37 | 2321.79 | 144253.37 | 2321.79 | 8.8348 | [5 empty] | 93.035
06.09.2007 24:00 | 3600 | 2 | 757.43 | GGB | 765.201 | 767.625 | 762.271 | 251.94 | GGB | 10567.4 | GGB | 9.92 | GGB | 995.96 | GGB | 65.4 | GGB | 180575.33 | GGB | 143228.26 | GGB | 0 | 0 | 2360 | 3600 | 2345.02 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 1439.68 | GGB | 1439.68 | 2345.02 | 2345.02 |  |  |  | 1 | 1 |  |  |  |  | 143228.26 | 2345.02 | 143228.26 | 2345.02 | 8.3467 | [5 empty] | 93.2981
07.09.2007 01:00 | 3600 | 2 | 757.33 | GGB | 765.201 | 767.531 | 761.172 | 252.94 | GGB | 10605.9 | GGB | 9.92 | GGB | 995.99 | GGB | 65.1 | GGB | 182046.48 | GGB | 144526.09 | GGB | 0 | 0 | 2378 | 3600 | 2363.11 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 1479.66 | GGB | 1479.66 | 2363.11 | 2363.11 |  |  |  | 0 | 1 | [14 empty] | 94.8697
07.09.2007 02:00 | 3600 | 2 | 757.03 | GGB | 766.3 | 767.695 | 762.271 | 255.33 | GGB | 10642.6 | GGB | 9.91 | GGB | 996.44 | GGB | 64.09 | GGB | 185432.22 | GGB | 147722.21 | GGB | 0 | 0 | 2383 | 3600 | 2367.51 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 1518.93 | GGB | 1518.93 | 2367.51 | 2367.51 |  |  |  | 1 | 1 |  |  |  |  | 147722.21 | 2367.51 | 147722.21 | 2367.51 | 8.9059 | [5 empty] | 97.1483
07.09.2007 03:00 | 3600 | 2 | 756.76 | GGB | 763.004 | 765.492 | 759.707 | 257.34 | GGB | 10704.2 | GGB | 9.91 | GGB | 996.33 | GGB | 62.95 | GGB | 188616.6 | GGB | 150749.07 | GGB | 0 | 0 | 2398 | 3600 | 2383.3 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 1558.81 | GGB | 1558.81 | 2383.3 | 2383.3 |  |  |  | 0 | 1 | [14 empty] | 99.8001
07.09.2007 04:00 | 3600 | 2 | 755.2 | GNB | 765.201 | 766.688 | 761.172 | 257.96 | GGB | 10754.8 | GGB | 9.89 | GGB | 996.22 | GGB | 62.44 | GGB | 190332.02 | GGB | 152336.81 | GGB | 0 | 0 | 2472 | 3600 | 2456.43 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 1599.1 | GGB | 1599.1 | 2456.43 | 2456.43 |  |  |  | 0 | 1 | [14 empty] | 103.9458
07.09.2007 05:00 | 3600 | 2 | 756.39 | GGB | 765.201 | 766.805 | 760.806 | 257.48 | GGB | 10844.6 | GGB | 9.92 | GGB | 996.55 | GGB | 62.9 | GGB | 188900.48 | GGB | 151034.37 | GGB | 0 | 0 | 2468 | 3600 | 2452.98 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 1639.71 | GGB | 1639.71 | 2452.98 | 2452.98 |  |  |  | 0 | 1 | [14 empty] | 102.9123
07.09.2007 06:00 | 3600 | 2 | 756.32 | GGB | 765.201 | 766.945 | 760.806 | 258.1 | GGB | 10873.6 | GGB | 9.92 | GGB | 996.34 | GGB | 62.44 | GGB | 189408.84 | GGB | 151616.37 | GGB | 0 | 0 | 2481 | 3600 | 2465.32 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 1680.15 | GGB | 1680.16 | 2465.32 | 2465.32 |  |  |  | 0 | 1 | [14 empty] | 103.8286
07.09.2007 07:00 | 3600 | 2 | 756.35 | GGB | 766.3 | 767.93 | 762.271 | 259.16 | GGB | 10914.4 | GGB | 9.93 | GGB | 996.52 | GGB | 62.36 | GGB | 190677.53 | GGB | 152693.96 | GNB | 0 | 0 | 2499 | 3600 | 2483.93 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 1720.98 | GGB | 1720.99 | 2483.93 | 2483.93 |  |  |  | 1 | 1 |  |  |  |  | 152693.96 | 2483.93 |  | 2483.93 | 9.2893 | [5 empty] | 105.3559 | 2475.0684
07.09.2007 08:00 | 3600 | 2 | 756.45 | GGB | 765.201 | 765.844 | 761.172 | 259.19 | GGB | 10920 | GGB | 9.93 | GGB | 997.11 | GGB | 62.35 | GGB | 190621.41 | GGB | 152746.07 | GNB | 0 | 0 | 2496 | 3600 | 2480.8 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 1761.98 | GGB | 1761.99 | 2480.8 | 2480.8 |  |  |  | 0 | 1 | [14 empty] | 105.259 | 2474.2241
07.09.2007 09:00 | 3600 | 2 | 756.11 | GGB | 765.201 | 765.844 | 760.806 | 259.46 | GGB | 10869.2 | GGB | 9.92 | GGB | 996.97 | GGB | 62.43 | GGB | 190754.55 | GGB | 152794.85 | GNB | 0 | 0 | 2488 | 3207 | 2472.81 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 1802.27 | GGB | 1802.28 | 2472.81 | 2472.81 |  |  |  | 0 | 1 | [14 empty] | 104.9535
07.09.2007 10:00 | 3600 | 2 | 756.96 | GGB | 765.201 | 767.273 | 761.172 | 259.33 | GGB | 10853.7 | GGB | 9.93 | GGB | 997.05 | GGB | 62.51 | GGB | 190176.88 | GGB | 152307.95 | GGB | 0 | 0 | 2448 | 3600 | 2433.14 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 1842.22 | GGB | 1842.23 | 2433.14 | 2433.14 |  |  |  | 0 | 1 | [14 empty] | 102.9407
07.09.2007 11:00 | 3600 | 2 | 756.78 | GGB | 766.3 | 767.32 | 762.271 | 257.21 | GGB | 10824.9 | GGB | 9.93 | GGB | 996.97 | GGB | 63.62 | GGB | 187004.6 | GGB | 149260.41 | GGB | 0 | 0 | 2455 | 3600 | 2440.02 | GGB | 100 | GGB | 44.1 | GGB | 44.1 | GGB | 1886.32 | GGB | 1886.33 | 2440.02 | 2440.02 |  |  |  | 1 | 1 |  |  |  |  | 149260.41 | 2440.02 | 149260.41 | 2440.02 | 8.2585 | [5 empty] | 101.1662
07.09.2007 12:00 | 3600 | 2 | 757.48 | GGB | 766.667 | 768.422 | 762.271 | 254.9 | GGB | 10694.1 | GGB | 9.93 | GGB | 996.52 | GGB | 64.4 | GGB | 184473.82 | GGB | 146833.1 | GGB | 0 | 0 | 2371 | 3244 | 2356.29 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 1926.93 | GGB | 1926.94 | 2356.29 | 2356.29 |  |  |  | 1 | 1 |  |  |  |  | 146833.1 | 2356.29 | 146833.1 | 2356.29 | 8.5196 | [5 empty] | 96.1059
07.09.2007 13:00 | 3600 | 2 | 757.92 | GGB | 767.766 | 769.383 | 763.37 | 253.6 | GGB | 10585.7 | GGB | 9.93 | GGB | 995.85 | GGB | 64.39 | GGB | 172756.33 | GGB | 137419.3 | GGB | 0 | 0 | 2286 | 3600 | 2271.15 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 1965.5 | GGB | 1965.51 | 2271.15 | 2271.15 |  |  |  | 1 | 1 |  |  |  |  | 137419.3 | 2271.15 | 137419.3 |  | 8.0918 | [5 empty] | 86.6944
07.09.2007 14:00 | 3600 | 2 | 757.95 | GGB | 766.667 | 768.375 | 762.271 | 251.13 | GGB | 10540.4 | GGB | 9.93 | GGB | 995.11 | GGB | 65.14 | GGB | 157317.49 | GGB | 124768.7 | GGB | 0 | 0 | 2271 | 3600 | 2256.43 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 2005.65 | GGB | 2005.66 | 2256.43 | 2256.43 |  |  |  | 1 | 1 |  |  |  |  | 124768.7 | 2256.43 |  |  | 7.012 | [5 empty] | 78.2033
07.09.2007 15:00 | 3600 | 2 | 758.32 | GGB | 766.667 | 768.375 | 762.271 | 250.36 | GGB | 10512.9 | GGB | 9.93 | GGB | 994.67 | GGB | 65.53 | GGB | 156949.98 | GGB | 124278.93 | GGB | 0 | 0 | 2243 | 3600 | 2228.32 | GGB | 100 | GGB | 38.15 | GGB | 38.15 | GGB | 2043.8 | GGB | 2043.81 | 2228.32 | 2228.32 |  |  |  | 1 | 1 |  |  |  |  | 124278.93 | 2228.32 |  |  | 7.2591 | [5 empty] | 76.9259
07.09.2007 16:00 | 3600 | 2 | 758.25 | GGB | 766.667 | 768.703 | 763.37 | 250.41 | GGB | 10475.4 | GGB | 9.92 | GGB | 994.21 | GGB | 65.66 | GGB | 156799.23 | GGB | 124053.13 | GGB | 0 | 0 | 2237 | 3600 | 2222.21 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 2084.33 | GGB | 2084.34 | 2222.21 | 2222.21 |  |  |  | 1 | 1 |  |  |  |  | 124053.13 | 2222.21 |  |  | 6.8017 | [5 empty] | 76.5756
07.09.2007 17:00 | 3600 | 2 | 758.62 | GGB | 767.766 | 769.711 | 764.102 | 251.73 | GGB | 10458.1 | GGB | 9.93 | GGB | 993.79 | GGB | 65.07 | GGB | 158289.09 | GGB | 125397.85 | GGB | 0 | 0 | 2211 | 3600 | 2196.43 | GNB | 100 | GGB | 37.57 | GGB | 37.57 | GGB | 2121.9 | GGB | 2121.91 | 2196.43 | 2196.43 |  |  |  | 1 | 1 |  |  |  |  | 125397.85 | 2196.43 |  |  | 7.3311 | [5 empty] | 76.5077
07.09.2007 18:00 | 3600 | 2 | 758.19 | GGB | 766.667 | 769.5 | 763.004 | 251.32 | GGB | 10477.8 | GGB | 9.93 | GGB | 993.95 | GGB | 65.61 | GGB | 157061.11 | GGB | 124247.32 | GGB | 0 | 0 | 2237 | 3600 | 2221.96 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 2162.14 | GGB | 2162.15 | 2221.96 | 2221.96 |  |  |  | 1 | 1 |  |  |  |  | 124247.32 | 2221.96 |  |  | 6.8607 | [5 empty] | 76.6868
07.09.2007 19:00 | 3600 | 2 | 757.6 | GGB | 766.667 | 768.422 | 762.637 | 251.1 | GGB | 10529.6 | GGB | 9.92 | GGB | 993.96 | GGB | 65.4 | GGB | 155933.26 | GGB | 123433.63 | GNB | 0 | 0 | 2286 | 3600 | 2271.44 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 2200.7 | GGB | 2200.71 | 2271.44 | 2271.44 |  |  |  | 1 | 1 |  |  |  |  | 123433.63 | 2271.44 |  |  | 7.2711 | [5 empty] | 77.8811
07.09.2007 20:00 | 3600 | 2 | 757.29 | GGB | 766.667 | 768.328 | 761.538 | 252 | GGB | 10571.6 | GGB | 9.92 | GGB | 994.47 | GGB | 64.71 | GGB | 156315.08 | GGB | 124053.58 | GGB | 0 | 0 | 2318 | 3600 | 2303.29 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 2241.53 | GGB | 2241.54 | 2303.29 | 2303.29 |  |  |  | 1 | 1 |  |  |  |  | 124053.58 | 2303.29 |  |  | 6.9981 | [5 empty] | 79.3698
07.09.2007 21:00 | 3600 | 2 | 757.17 | GGB | 767.766 | 768.281 | 762.637 | 252.94 | GGB | 10609.4 | GGB | 9.92 | GGB | 995.01 | GGB | 64.3 | GGB | 156553.85 | GGB | 124458.33 | GGB | 0 | 0 | 2343 | 3600 | 2327.66 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 2279.87 | GGB | 2279.88 | 2327.66 | 2327.66 |  |  |  | 1 | 1 |  |  |  |  | 124458.33 | 2327.66 |  | 2327.66 | 7.556 | [5 empty] | 80.4713
07.09.2007 22:00 | 3600 | 2 | 756.91 | GGB | 766.3 | 767.156 | 761.538 | 253.71 | GGB | 10634.1 | GGB | 9.92 | GGB | 995.42 | GGB | 63.82 | GGB | 157045.71 | GGB | 125079.43 | GGB | 0 | 0 | 2354 | 3600 | 2338.81 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 2317.97 | GGB | 2317.98 | 2338.81 | 2338.81 |  |  |  | 1 | 1 |  |  |  |  | 125079.43 | 2338.81 |  | 2338.81 | 7.6781 | [5 empty] | 81.2603
07.09.2007 23:00 | 3600 | 2 | 757.12 | GGB | 766.667 | 767.016 | 761.538 | 254.25 | GGB | 10679.1 | GGB | 9.93 | GGB | 995.53 | GGB | 63.57 | GGB | 157260.27 | GGB | 125358.54 | GGB | 0 | 0 | 2368 | 3600 | 2353.07 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 2359.09 | GGB | 2359.1 | 2353.07 | 2353.07 |  |  |  | 1 | 1 |  |  |  |  | 125358.54 | 2353.07 |  | 2353.07 | 7.1736 | [5 empty] | 81.9382
07.09.2007 24:00 | 3600 | 2 | 756.88 | GGB | 766.667 | 768.117 | 761.538 | 254.64 | GGB | 10715.1 | GGB | 9.93 | GGB | 995.75 | GGB | 63.41 | GGB | 158078.92 | GGB | 126097.91 | GGB | 0 | 0 | 2390 | 3600 | 2374.75 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 2397.8 | GGB | 2397.82 | 2374.75 | 2374.75 |  |  |  | 1 | 1 |  |  |  |  | 126097.91 | 2374.75 | 126097.91 | 2374.75 | 7.7338 | [5 empty] | 83.1808
08.09.2007 01:00 | 3600 | 2 | 756.44 | GGB | 766.3 | 767.086 | 761.538 | 255.87 | GGB | 10706.5 | GGB | 9.92 | GGB | 995.72 | GGB | 63.66 | GGB | 158018.4 | GGB | 125951.91 | GGB | 0 | 0 | 2410 | 3600 | 2394.95 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 2439.44 | GGB | 2439.46 | 2394.95 | 2394.95 |  |  |  | 1 | 1 |  |  |  |  | 125951.91 | 2394.95 | 125951.91 | 2394.95 | 7.2442 | [5 empty] | 83.7913
08.09.2007 02:00 | 3600 | 2 | 756.78 | GGB | 766.3 | 766.992 | 761.538 | 256.49 | GGB | 10718.8 | GGB | 9.92 | GGB | 995.83 | GGB | 63.71 | GGB | 158384.82 | GGB | 126241.73 | GGB | 0 | 0 | 2415 | 3600 | 2399.64 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 2478.55 | GGB | 2478.57 | 2399.64 | 2399.64 |  |  |  | 1 | 1 |  |  |  |  | 126241.73 | 2399.64 | 126241.73 | 2399.64 | 7.7457 | [5 empty] | 84.1485
08.09.2007 03:00 | 3600 | 2 | 756.94 | GGB | 765.201 | 767.063 | 760.44 | 257.65 | GGB | 10699 | GGB | 9.92 | GGB | 995.87 | GGB | 63.12 | GGB | 160083.74 | GGB | 127821.42 | GGB | 0 | 0 | 2391 | 3600 | 2376.06 | GGB | 100 | GGB | 41.94 | GGB | 41.94 | GGB | 2520.49 | GGB | 2520.51 | 2376.06 | 2376.06 |  |  |  | 0 | 1 | [14 empty] | 84.3643
08.09.2007 04:00 | 3600 | 2 | 756.57 | GGB | 765.201 | 766.078 | 760.44 | 257.83 | GGB | 10761.4 | GGB | 9.92 | GGB | 995.71 | GGB | 63.07 | GGB | 159935.19 | GGB | 127704.35 | GGB | 0 | 0 | 2436 | 3600 | 2421.07 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 2559.39 | GGB | 2559.41 | 2421.07 | 2421.07 |  |  |  | 0 | 1 | [14 empty] | 85.8837
08.09.2007 05:00 | 3600 | 2 | 756.25 | GGB | 765.201 | 767.016 | 761.538 | 258.31 | GGB | 10802.5 | GGB | 9.92 | GGB | 995.44 | GGB | 63.1 | GGB | 160298.3 | GGB | 127944.57 | GGB | 0 | 0 | 2461 | 3600 | 2445.52 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 2600.22 | GGB | 2600.23 | 2445.52 | 2445.52 |  |  |  | 1 | 1 |  |  |  |  | 127944.57 | 2445.52 | 127944.57 | 2445.52 | 7.6651 | [5 empty] | 86.9142
08.09.2007 06:00 | 3600 | 2 | 756.02 | GGB | 764.102 | 765.844 | 759.341 | 259.12 | GGB | 10834.7 | GGB | 9.92 | GGB | 995.55 | GGB | 62.83 | GGB | 161326.02 | GGB | 128886.06 | GGB | 0 | 0 | 2485 | 3600 | 2469.99 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 2640.79 | GGB | 2640.81 | 2469.99 | 2469.99 |  |  |  | 0 | 1 | [14 empty] | 88.4298
08.09.2007 07:00 | 3600 | 2 | 755.89 | GNB | 765.201 | 766.5 | 761.538 | 259.69 | GGB | 10874 | GGB | 9.92 | GGB | 995.59 | GGB | 62.33 | GGB | 162325.13 | GGB | 129883.84 | GGB | 0 | 0 | 2506 | 3600 | 2490.74 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 2680.27 | GGB | 2680.28 | 2490.74 | 2490.74 |  |  |  | 0 | 1 | [14 empty] | 89.863
08.09.2007 08:00 | 3600 | 2 | 755.88 | GNB | 765.201 | 766.477 | 760.44 | 259.88 | GGB | 10885.7 | GGB | 9.92 | GGB | 995.59 | GGB | 62.26 | GGB | 162306.42 | GGB | 129893.6 | GGB | 0 | 0 | 2501 | 3600 | 2485.45 | GGB | 100 | GGB | 42 | GGB | 42 | GGB | 2722.26 | GGB | 2722.28 | 2485.45 | 2485.45 |  |  |  | 0 | 1 | [14 empty] | 89.6789
08.09.2007 09:00 | 3600 | 2 | 755.98 | GNB | 765.201 | 767.578 | 761.538 | 260.18 | GGB | 10890.6 | GGB | 9.93 | GGB | 995.32 | GGB | 62.19 | GGB | 162458.27 | GGB | 130006.9 | GGB | 0 | 0 | 2499 | 3600 | 2483.89 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 2761.85 | GGB | 2761.87 | 2483.89 | 2483.89 |  |  |  | 0 | 1 | [14 empty] | 89.7008
08.09.2007 10:00 | 3600 | 2 | 756.97 | GGB | 766.3 | 767.672 | 761.538 | 257.94 | GGB | 10830.9 | GGB | 9.94 | GGB | 994.84 | GGB | 62.71 | GGB | 160068.33 | GGB | 127833.59 | GGB | 0 | 0 | 2436 | 3600 | 2420.76 | GGB | 100 | GGB | 42.19 | GGB | 42.19 | GGB | 2804.04 | GGB | 2804.06 | 2420.76 | 2420.76 |  |  |  | 1 | 1 |  |  |  |  | 127833.59 | 2420.76 | 127833.59 | 2420.76 | 7.3348 | [5 empty] | 85.9596
08.09.2007 11:00 | 3600 | 2 | 757 | GGB | 766.3 | 767.836 | 761.538 | 256.3 | GGB | 10735.3 | GGB | 9.93 | GGB | 994.49 | GGB | 63.16 | GGB | 158502.55 | GGB | 126370.51 | GGB | 0 | 0 | 2393 | 3600 | 2377.95 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 2843.18 | GGB | 2843.2 | 2377.95 | 2377.95 |  |  |  | 1 | 1 |  |  |  |  | 126370.51 | 2377.95 | 126370.51 | 2377.95 | 7.6776 | [5 empty] | 83.473
08.09.2007 12:00 | 3600 | 2 | 757.25 | GGB | 766.667 | 768.844 | 762.637 | 256.41 | GGB | 10642.7 | GGB | 9.93 | GGB | 993.63 | GGB | 63.13 | GGB | 159169.36 | GGB | 126805.2 | GGB | 0 | 0 | 2332 | 3600 | 2316.7 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 2882.26 | GGB | 2882.28 | 2316.7 | 2316.7 |  |  |  | 1 | 1 |  |  |  |  | 126805.2 | 2316.7 | 126805.2 | 2316.7 | 7.5171 | [5 empty] | 81.6027
08.09.2007 13:00 | 3600 | 2 | 757.23 | GGB | 766.3 | 768.844 | 762.637 | 254.25 | GGB | 10631.2 | GGB | 9.93 | GGB | 992.62 | GGB | 63.8 | GGB | 156808.03 | GGB | 124546.01 | GGB | 0 | 0 | 2330 | 3600 | 2315.28 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 2923.66 | GGB | 2923.69 | 2315.28 | 2315.28 |  |  |  | 1 | 1 |  |  |  |  | 124546.01 | 2315.28 |  | 2315.28 | 6.9635 | [5 empty] | 80.0997
08.09.2007 14:00 | 3600 | 2 | 757.12 | GGB | 766.3 | 768.867 | 762.271 | 252.84 | GGB | 10586.3 | GGB | 9.93 | GGB | 992.32 | GGB | 64.37 | GGB | 155503.03 | GGB | 123263.52 | GNB | 0 | 0 | 2318 | 3600 | 2302.98 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 2962.55 | GGB | 2962.58 | 2302.98 | 2302.98 |  |  |  | 1 | 1 |  |  |  |  | 123263.52 | 2302.98 |  |  | 7.2994 | [5 empty] | 78.8537
08.09.2007 15:00 | 3600 | 2 | 757.26 | GGB | 765.934 | 768.281 | 761.538 | 252.38 | GGB | 10556.2 | GGB | 9.93 | GGB | 991.61 | GGB | 64.55 | GGB | 155067.3 | GGB | 122765.32 | GNB | 0 | 0 | 2302 | 3600 | 2286.81 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 3003.09 | GGB | 3003.13 | 2286.81 | 2286.81 |  |  |  | 1 | 1 |  |  |  |  | 122765.32 | 2286.81 |  |  | 6.9233 | [5 empty] | 77.9836
08.09.2007 16:00 | 3600 | 2 | 757.19 | GGB | 765.934 | 768.188 | 761.538 | 252.02 | GGB | 10545.2 | GGB | 9.93 | GGB | 990.35 | GGB | 64.84 | GGB | 154783.41 | GGB | 122281.4 | GNB | 0 | 0 | 2295 | 3600 | 2280.05 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 3041.93 | GGB | 3041.97 | 2280.05 | 2280.05 |  |  |  | 1 | 1 |  |  |  |  | 122281.4 | 2280.05 |  |  | 7.1784 | [5 empty] | 77.4466
08.09.2007 17:00 | 3600 | 2 | 757.41 | GGB | 765.934 | 768.328 | 761.538 | 250.99 | GGB | 10517.5 | GGB | 9.93 | GGB | 989.12 | GGB | 65.1 | GGB | 154454.41 | GGB | 121773.87 | GNB | 0 | 0 | 2278 | 3600 | 2262.62 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 3080.4 | GGB | 3080.44 | 2262.62 | 2262.62 |  |  |  | 1 | 1 |  |  |  |  | 121773.87 | 2262.62 |  |  | 7.1622 | [5 empty] | 76.5356
08.09.2007 18:00 | 3600 | 2 | 757.33 | GGB | 767.033 | 769.5 | 762.637 | 251.43 | GGB | 10517.4 | GGB | 9.92 | GGB | 987.77 | GGB | 64.87 | GGB | 154684.38 | GGB | 121874.5 | GNB | 0 | 0 | 2277 | 3600 | 2262.42 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 3121.45 | GGB | 3121.49 | 2262.42 | 2262.42 |  |  |  | 1 | 1 |  |  |  |  | 121874.5 | 2262.42 |  |  | 6.717 | [5 empty] | 76.592
08.09.2007 19:00 | 3600 | 2 | 757.36 | GGB | 767.033 | 769.688 | 762.637 | 251.93 | GGB | 10502.8 | GGB | 9.92 | GGB | 987.87 | GGB | 64.36 | GGB | 155570.15 | GGB | 122769.04 | GNB | 0 | 0 | 2266 | 3600 | 2250.84 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 3159.87 | GGB | 3159.91 | 2250.84 | 2250.84 |  |  |  | 1 | 1 |  |  |  |  | 122769.04 | 2250.84 |  |  | 7.1924 | [5 empty] | 76.7593
08.09.2007 20:00 | 3600 | 2 | 757.23 | GGB | 765.934 | 768.656 | 761.538 | 252.93 | GGB | 10564.4 | GGB | 9.93 | GGB | 987.73 | GGB | 64.07 | GGB | 155992.68 | GGB | 123189.85 | GNB | 0 | 0 | 2315 | 3600 | 2300.37 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 3198.25 | GGB | 3198.3 | 2300.37 | 2300.37 |  |  |  | 1 | 1 |  |  |  |  | 123189.85 | 2300.37 |  |  | 7.3817 | [5 empty] | 78.7173
08.09.2007 21:00 | 3600 | 2 | 756.69 | GGB | 764.835 | 767.625 | 760.44 | 252.97 | GGB | 10572.2 | GGB | 9.92 | GGB | 987.61 | GGB | 64.13 | GGB | 155677.99 | GGB | 122903.59 | GNB | 0 | 0 | 2346 | 3600 | 2331.15 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 3239.35 | GGB | 3239.4 | 2331.15 | 2331.15 |  |  |  | 0 | 1 | [14 empty] | 79.5852
08.09.2007 22:00 | 3600 | 2 | 756.61 | GGB | 764.835 | 767.578 | 760.44 | 254.53 | GGB | 10580.8 | GGB | 9.92 | GGB | 987.49 | GGB | 63.76 | GGB | 157200.85 | GGB | 124229.6 | GGB | 0 | 0 | 2343 | 3600 | 2328.29 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 3278.39 | GGB | 3278.44 | 2328.29 | 2328.29 |  |  |  | 0 | 1 | [14 empty] | 80.3451
08.09.2007 23:00 | 3600 | 2 | 756.64 | GGB | 764.835 | 768.844 | 761.538 | 254.34 | GGB | 10611.6 | GGB | 9.93 | GGB | 987.16 | GGB | 63.96 | GGB | 156626.48 | GGB | 123658.58 | GNB | 0 | 0 | 2365 | 3600 | 2350.11 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 3318.51 | GGB | 3318.56 | 2350.11 | 2350.11 |  |  |  | 1 | 1 |  |  |  |  | 123658.58 | 2350.11 |  | 2350.11 | 7.2436 | [5 empty] | 80.7254
08.09.2007 24:00 | 3600 | 2 | 756.59 | GGB | 765.934 | 768.844 | 761.538 | 255.73 | GGB | 10595.3 | GGB | 9.93 | GGB | 986.9 | GGB | 63.37 | GGB | 158515.76 | GGB | 125338.66 | GGB | 0 | 0 | 2354 | 3600 | 2339.3 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 3358.45 | GGB | 3358.5 | 2339.3 | 2339.3 |  |  |  | 1 | 1 |  |  |  |  | 125338.66 | 2339.3 |  | 2339.3 | 7.3411 | [5 empty] | 81.4458
09.09.2007 01:00 | 3600 | 2 | 756.5 | GGB | 765.934 | 769.617 | 762.637 | 255.29 | GGB | 10609.9 | GGB | 9.93 | GGB | 986.54 | GGB | 63.35 | GGB | 158314.4 | GGB | 125139.04 | GGB | 0 | 0 | 2361 | 3600 | 2346.23 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 3397 | GGB | 3397.05 | 2346.23 | 2346.23 |  |  |  | 1 | 1 |  |  |  |  | 125139.04 | 2346.23 |  | 2346.23 | 7.6162 | [5 empty] | 81.5569
09.09.2007 02:00 | 3600 | 2 | 756.19 | GGB | 764.835 | 768.375 | 760.44 | 254.33 | GGB | 10639 | GGB | 9.92 | GGB | 985.88 | GGB | 63.79 | GGB | 156933.47 | GGB | 123803.9 | GNB | 0 | 0 | 2393 | 3600 | 2378.06 | GGB | 100 | GGB | 41.69 | GGB | 41.69 | GGB | 3438.7 | GGB | 3438.74 | 2378.06 | 2378.06 |  |  |  | 0 | 1 | [14 empty] | 81.7814
09.09.2007 03:00 | 3600 | 2 | 756.05 | GGB | 764.835 | 768.281 | 760.44 | 254.29 | GGB | 10636.7 | GGB | 9.93 | GGB | 985.39 | GGB | 63.79 | GGB | 157078.72 | GGB | 123856.32 | GNB | 0 | 0 | 2395 | 3600 | 2379.52 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 3477.44 | GGB | 3477.48 | 2379.52 | 2379.52 |  |  |  | 0 | 1 | [14 empty] | 81.8663
09.09.2007 04:00 | 3600 | 2 | 756.15 | GGB | 764.835 | 768.188 | 760.44 | 255.37 | GGB | 10622.8 | GGB | 9.92 | GGB | 985.03 | GGB | 63.42 | GGB | 158388.12 | GGB | 124981.68 | GGB | 0 | 0 | 2386 | 3600 | 2370.46 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 3516.22 | GGB | 3516.27 | 2370.46 | 2370.46 |  |  |  | 0 | 1 | [14 empty] | 82.2956
09.09.2007 05:00 | 3600 | 2 | 756.21 | GGB | 765.934 | 769.102 | 761.538 | 255.62 | GGB | 10656.9 | GGB | 9.93 | GGB | 984.72 | GGB | 63.09 | GGB | 158775.44 | GGB | 125369.13 | GGB | 0 | 0 | 2390 | 3600 | 2374.68 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 3557.5 | GGB | 3557.55 | 2374.68 | 2374.68 |  |  |  | 1 | 1 |  |  |  |  | 125369.13 | 2374.68 |  | 2374.68 | 7.212 | [5 empty] | 82.6977
09.09.2007 06:00 | 3600 | 2 | 755.69 | GNB | 764.469 | 766.992 | 760.44 | 255.67 | GGB | 10664.2 | GGB | 9.92 | GGB | 984.69 | GGB | 63.19 | GGB | 158687.41 | GGB | 125260.67 | GGB | 0 | 0 | 2414 | 3600 | 2398.93 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 3596.89 | GGB | 3596.94 | 2398.93 | 2398.93 |  |  |  | 0 | 1 | [14 empty] | 83.4699
09.09.2007 07:00 | 3600 | 2 | 755.74 | GNB | 765.934 | 768 | 761.538 | 257.32 | GGB | 10663.8 | GGB | 9.92 | GGB | 984.7 | GGB | 62.53 | GGB | 160698.83 | GGB | 127097.62 | GGB | 0 | 0 | 2401 | 3600 | 2385.66 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 3635.97 | GGB | 3636.02 | 2385.66 | 2385.66 |  |  |  | 0 | 1 | [14 empty] | 84.2255
09.09.2007 08:00 | 3600 | 2 | 756.11 | GGB | 764.835 | 768.023 | 760.44 | 258.28 | GGB | 10664.8 | GGB | 9.92 | GGB | 984.85 | GGB | 62.49 | GGB | 160749.44 | GGB | 127171.85 | GGB | 0 | 0 | 2395 | 3600 | 2379.87 | GGB | 100 | GGB | 41.6 | GGB | 41.6 | GGB | 3677.57 | GGB | 3677.62 | 2379.87 | 2379.87 |  |  |  | 0 | 1 | [14 empty] | 84.0701
09.09.2007 09:00 | 3600 | 2 | 756.75 | GGB | 765.934 | 769.148 | 761.538 | 257.55 | GGB | 10652.2 | GGB | 9.93 | GGB | 984.98 | GGB | 63.38 | GGB | 157890.76 | GGB | 124598.44 | GGB | 0 | 0 | 2377 | 3600 | 2362.34 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 3716.64 | GGB | 3716.69 | 2362.34 | 2362.34 |  |  |  | 1 | 1 |  |  |  |  | 124598.44 | 2362.34 |  | 2362.34 | 7.5338 | [5 empty] | 81.7622
09.09.2007 10:00 | 3600 | 2 | 756.73 | GGB | 765.934 | 769.195 | 762.637 | 255.77 | GGB | 10617.9 | GGB | 9.93 | GGB | 985.24 | GGB | 63.67 | GGB | 156797.03 | GGB | 123659.41 | GNB | 0 | 0 | 2354 | 3600 | 2338.92 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 3755.7 | GGB | 3755.75 | 2338.92 | 2338.92 |  |  |  | 1 | 1 |  |  |  |  | 123659.41 | 2338.92 |  | 2338.92 | 7.4047 | [5 empty] | 80.3415
09.09.2007 11:00 | 3600 | 2 | 757.05 | GGB | 767.033 | 770.203 | 762.637 | 255.78 | GGB | 10540.9 | GGB | 9.93 | GGB | 985.6 | GGB | 63.65 | GGB | 156699.1 | GGB | 123634.26 | GNB | 0 | 0 | 2304 | 3600 | 2288.94 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 3796.99 | GGB | 3797.04 | 2288.94 | 2288.94 |  |  |  | 1 | 1 |  |  |  |  | 123634.26 | 2288.94 |  |  | 6.8538 | [5 empty] | 78.6087
09.09.2007 12:00 | 3600 | 2 | 757.53 | GGB | 765.934 | 769.102 | 763.004 | 254.53 | GGB | 10506 | GGB | 9.93 | GGB | 985.5 | GGB | 63.86 | GGB | 155614.17 | GGB | 122691.91 | GNB | 0 | 0 | 2262 | 3600 | 2247.39 | GGB | 100 | GGB | 38.15 | GGB | 38.15 | GGB | 3835.14 | GGB | 3835.19 | 2247.39 | 2247.39 |  |  |  | 1 | 1 |  |  |  |  | 122691.91 | 2247.39 |  |  | 7.2277 | [5 empty] | 76.5935
09.09.2007 13:00 | 3600 | 2 | 757.49 | GGB | 765.934 | 769.195 | 763.004 | 252.53 | GGB | 10481.8 | GGB | 9.93 | GGB | 985.23 | GGB | 64.56 | GGB | 154355.38 | GGB | 121413.08 | GNB | 0 | 0 | 2254 | 3600 | 2238.96 | GGB | 100 | GGB | 37.51 | GGB | 37.51 | GGB | 3872.65 | GGB | 3872.7 | 2238.96 | 2238.96 |  |  |  | 1 | 1 |  |  |  |  | 121413.08 | 2238.96 |  |  | 7.2471 | [5 empty] | 75.5108
09.09.2007 14:00 | 3600 | 2 | 757.54 | GGB | 768.132 | 770.227 | 764.102 | 252.08 | GGB | 10479.3 | GGB | 9.93 | GGB | 985.25 | GGB | 64.72 | GGB | 154525.93 | GGB | 121490.45 | GNB | 0 | 0 | 2248 | 3600 | 2232.72 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 3913.12 | GGB | 3913.17 | 2232.72 | 2232.72 |  |  |  | 1 | 1 |  |  |  |  | 121490.45 | 2232.72 |  |  | 6.7026 | [5 empty] | 75.3484
09.09.2007 15:00 | 3600 | 2 | 757.54 | GGB | 767.033 | 769.078 | 763.004 | 252.34 | GGB | 10491.1 | GGB | 9.92 | GGB | 985.03 | GGB | 64.68 | GGB | 155116.81 | GGB | 121941.97 | GNB | 0 | 0 | 2249 | 3600 | 2234.23 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 3951.51 | GGB | 3951.56 | 2234.23 | 2234.23 |  |  |  | 1 | 1 |  |  |  |  | 121941.97 | 2234.23 |  |  | 7.0968 | [5 empty] | 75.6796
09.09.2007 16:00 | 3600 | 2 | 757.57 | GGB | 765.934 | 768.914 | 761.538 | 253.27 | GGB | 10473.7 | GGB | 9.92 | GGB | 985.04 | GGB | 64.18 | GGB | 156681.49 | GGB | 123356.56 | GNB | 0 | 0 | 2234 | 3600 | 2219.44 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 3990.31 | GGB | 3990.37 | 2219.44 | 2219.44 |  |  |  | 1 | 1 |  |  |  |  | 123356.56 | 2219.44 |  |  | 7.0544 | [5 empty] | 76.0507
09.09.2007 17:00 | 3600 | 2 | 757.59 | GGB | 765.934 | 769.008 | 762.637 | 253.75 | GGB | 10494.1 | GGB | 9.92 | GGB | 985.35 | GGB | 63.8 | GGB | 157598.08 | GGB | 124256.99 | GGB | 0 | 0 | 2237 | 3600 | 2221.7 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 4030.81 | GGB | 4030.86 | 2221.7 | 2221.7 |  |  |  | 1 | 1 |  |  |  |  | 124256.99 | 2221.7 |  |  | 6.818 | [5 empty] | 76.6838
09.09.2007 18:00 | 3600 | 2 | 757.63 | GGB | 765.934 | 769.055 | 763.004 | 253.71 | GGB | 10555.6 | GGB | 9.93 | GGB | 985.88 | GGB | 63.99 | GGB | 157118.33 | GGB | 123875.37 | GNB | 0 | 0 | 2269 | 3600 | 2253.81 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 4069.79 | GGB | 4069.85 | 2253.81 | 2253.81 |  |  |  | 1 | 1 |  |  |  |  | 123875.37 | 2253.81 |  |  | 7.1606 | [5 empty] | 77.5532
09.09.2007 19:00 | 3600 | 2 | 757.13 | GGB | 765.934 | 768.023 | 762.637 | 254.06 | GGB | 10584.1 | GGB | 9.92 | GGB | 986.1 | GGB | 63.94 | GGB | 156951.08 | GGB | 123791.23 | GNB | 0 | 0 | 2303 | 3600 | 2287.73 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 4108.98 | GGB | 4109.03 | 2287.73 | 2287.73 |  |  |  | 1 | 1 |  |  |  |  | 123791.23 | 2287.73 |  |  | 7.2282 | [5 empty] | 78.6669
09.09.2007 20:00 | 3600 | 2 | 756.92 | GGB | 765.934 | 768.023 | 761.538 | 254.68 | GGB | 10625.2 | GGB | 9.92 | GGB | 987.03 | GGB | 62.87 | GGB | 157881.96 | GGB | 125039.35 | GGB | 0 | 0 | 2331 | 3600 | 2315.96 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 4148.11 | GGB | 4148.16 | 2315.96 | 2315.96 |  |  |  | 1 | 1 |  |  |  |  | 125039.35 | 2315.96 |  | 2315.96 | 7.4006 | [5 empty] | 80.4406
09.09.2007 21:00 | 3600 | 2 | 756.41 | GGB | 764.835 | 768.258 | 761.538 | 256.08 | GGB | 10680.2 | GGB | 9.92 | GGB | 987.72 | GGB | 62.79 | GGB | 159778.94 | GGB | 126657.58 | GGB | 0 | 0 | 2376 | 3600 | 2360.74 | GGB | 100 | GGB | 41.84 | GGB | 41.84 | GGB | 4189.95 | GGB | 4190 | 2360.74 | 2360.74 |  |  |  | 1 | 1 |  |  |  |  | 126657.58 | 2360.74 | 126657.58 | 2360.74 | 7.1464 | [5 empty] | 83.0571
09.09.2007 22:00 | 3600 | 2 | 756.29 | GGB | 764.835 | 767.109 | 760.44 | 257.63 | GGB | 10743 | GGB | 9.92 | GGB | 988.38 | GGB | 62.53 | GGB | 161429.45 | GGB | 128151.84 | GGB | 0 | 0 | 2407 | 3600 | 2392.31 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 4229.55 | GGB | 4229.61 | 2392.31 | 2392.31 |  |  |  | 0 | 1 | [14 empty] | 85.1608
09.09.2007 23:00 | 3600 | 2 | 755.99 | GNB | 765.934 | 767.109 | 761.538 | 258.39 | GGB | 10834.9 | GGB | 9.92 | GGB | 989.03 | GGB | 62.19 | GGB | 163792.98 | GGB | 130245.05 | GGB | 0 | 0 | 2458 | 3600 | 2442.78 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 4269.24 | GGB | 4269.29 | 2442.78 | 2442.78 |  |  |  | 0 | 1 | [14 empty] | 88.3778
09.09.2007 24:00 | 3600 | 2 | 756.5 | GGB | 767.033 | 768 | 762.637 | 258.76 | GGB | 10833.8 | GGB | 9.93 | GGB | 989.59 | GGB | 62.09 | GGB | 163182.29 | GGB | 129872.59 | GGB | 0 | 0 | 2440 | 3600 | 2424.88 | GGB | 100 | GGB | 42.94 | GGB | 42.94 | GGB | 4312.18 | GGB | 4312.23 | 2424.88 | 2424.88 |  |  |  | 1 | 1 |  |  |  |  | 129872.59 | 2424.88 | 129872.59 | 2424.88 | 7.3341 | [5 empty] | 87.4793
10.09.2007 01:00 | 3600 | 2 | 756.27 | GGB | 764.835 | 766.758 | 761.538 | 258.24 | GGB | 10818.1 | GGB | 9.92 | GGB | 989.62 | GGB | 62.11 | GGB | 162816.98 | GGB | 129577.78 | GGB | 0 | 0 | 2438 | 3600 | 2422.56 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 4352.06 | GGB | 4352.12 | 2422.56 | 2422.56 |  |  |  | 1 | 1 |  |  |  |  | 129577.78 | 2422.56 | 129577.78 | 2422.56 | 7.8694 | [5 empty] | 87.1972
10.09.2007 02:00 | 3600 | 2 | 756.15 | GGB | 765.934 | 767.766 | 762.637 | 258.89 | GGB | 10844 | GGB | 9.93 | GGB | 989.49 | GGB | 61.94 | GGB | 163465.08 | GGB | 130143.82 | GGB | 0 | 0 | 2460 | 3600 | 2444.41 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 4391.74 | GGB | 4391.79 | 2444.41 | 2444.41 |  |  |  | 1 | 1 |  |  |  |  | 130143.82 | 2444.41 | 130143.82 | 2444.41 | 8.0193 | [5 empty] | 88.368
10.09.2007 03:00 | 3600 | 2 | 755.95 | GNB | 765.934 | 767.789 | 761.538 | 259.51 | GGB | 10863.5 | GGB | 9.92 | GGB | 989.45 | GGB | 61.88 | GGB | 164065.86 | GGB | 130639.99 | GGB | 0 | 0 | 2471 | 3600 | 2455.9 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 4432.41 | GGB | 4432.47 | 2455.9 | 2455.9 |  |  |  | 0 | 1 | [14 empty] | 89.1219
10.09.2007 04:00 | 3600 | 2 | 755.39 | GNB | 764.835 | 767.063 | 761.538 | 261.23 | GGB | 10912.4 | GGB | 9.92 | GGB | 989.81 | GGB | 61.6 | GGB | 165878.12 | GGB | 132242.59 | GGB | 0 | 0 | 2515 | 3600 | 2499.54 | GGB | 100 | GGB | 42.28 | GGB | 42.28 | GGB | 4474.69 | GGB | 4474.75 | 2499.54 | 2499.54 |  |  |  | 0 | 1 | [14 empty] | 91.8182
10.09.2007 05:00 | 3600 | 2 | 755.05 | GNB | 763.37 | 764.906 | 760.44 | 262.71 | GGB | 10955.7 | GGB | 9.91 | GGB | 990.41 | GGB | 60.96 | GGB | 167557.23 | GGB | 133917.73 | GGB | 0 | 0 | 2554 | 3600 | 2538.63 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 4514.75 | GGB | 4514.81 | 2538.63 | 2538.63 |  |  |  | 0 | 1 | [14 empty] | 94.4354
10.09.2007 06:00 | 3600 | 2 | 754.05 | GNB | 763.37 | 764.906 | 758.974 | 264.45 | GGB | 11002.6 | GGB | 9.9 | GGB | 990.75 | GGB | 60.35 | GGB | 169567.55 | GGB | 135819.5 | GGB | 0 | 0 | 2616 | 3600 | 2601.16 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 4555.16 | GGB | 4555.23 | 2601.16 | 2601.16 |  |  |  | 0 | 1 | [14 empty] | 98.1356
10.09.2007 07:00 | 3600 | 2 | 752.82 | GNB | 759.707 | 761.625 | 755.678 | 265.06 | GGB | 11006.9 | GGB | 9.87 | GGB | 991.11 | GGB | 59.6 | GGB | 170978.18 | GGB | 137307.48 | GGB | 0 | 0 | 2676 | 3600 | 2660.27 | GGB | 100 | GGB | 43.41 | GGB | 43.41 | GGB | 4598.57 | GGB | 4598.64 | 2660.27 | 2660.27 |  |  |  | 0 | 1 | [14 empty] | 101.4653
10.09.2007 08:00 | 3600 | 2 | 751.82 | GNB | 760.806 | 762.68 | 756.776 | 265.23 | GGB | 11017.1 | GGB | 9.86 | GGB | 991.63 | GGB | 58.93 | GGB | 171704.41 | GGB | 138241.8 | GGB | 0 | 0 | 2727 | 3600 | 2711.22 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 4639.06 | GGB | 4639.12 | 2711.22 | 2711.22 |  |  |  | 0 | 1 | [14 empty] | 104.1122
10.09.2007 09:00 | 3600 | 2 | 755.14 | GNB | 764.835 | 766.922 | 761.538 | 262.88 | GGB | 11028.1 | GGB | 9.93 | GGB | 991.74 | GGB | 59.35 | GGB | 168725.79 | GGB | 135685.95 | GGB | 0 | 0 | 2581 | 3600 | 2566.13 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 4679.31 | GGB | 4679.37 | 2566.13 | 2566.13 |  |  |  | 0 | 1 | [14 empty] | 96.7188
10.09.2007 10:00 | 3600 | 2 | 756.38 | GGB | 764.835 | 767.977 | 762.637 | 259.42 | GGB | 10888.6 | GGB | 9.94 | GGB | 991.12 | GGB | 60.33 | GGB | 164957.13 | GGB | 132181.13 | GGB | 0 | 0 | 2460 | 3600 | 2444.93 | GGB | 100 | GGB | 41.77 | GGB | 41.77 | GGB | 4721.08 | GGB | 4721.14 | 2444.93 | 2444.93 |  |  |  | 1 | 1 |  |  |  |  | 132181.13 | 2444.93 | 132181.13 | 2444.93 | 7.737 | [5 empty] | 89.7704
10.09.2007 11:00 | 3600 | 2 | 757.01 | GGB | 765.934 | 769.148 | 763.004 | 257.22 | GGB | 10717.4 | GGB | 9.94 | GGB | 989.5 | GGB | 60.89 | GGB | 162412.05 | GGB | 129710.85 | GGB | 0 | 0 | 2347 | 3600 | 2332.21 | GGB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 4762.96 | GGB | 4763.02 | 2332.21 | 2332.21 |  |  |  | 1 | 1 |  |  |  |  | 129710.85 | 2332.21 | 129710.85 | 2332.21 | 7.2233 | [5 empty] | 84.0314
10.09.2007 12:00 | 3600 | 2 | 757.34 | GGB | 767.033 | 769.242 | 763.004 | 253.79 | GGB | 10613.2 | GGB | 9.93 | GGB | 988.29 | GGB | 62.13 | GGB | 159124.24 | GGB | 126462.09 | GGB | 0 | 0 | 2284 | 3600 | 2268.54 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 4803.1 | GGB | 4803.16 | 2268.54 | 2268.54 |  |  |  | 1 | 1 |  |  |  |  | 126462.09 | 2268.54 | 126462.09 |  | 7.1471 | [5 empty] | 79.6901
10.09.2007 13:00 | 3600 | 2 | 757.42 | GGB | 765.934 | 768.141 | 763.004 | 252.42 | GGB | 10549.7 | GGB | 9.92 | GGB | 987.25 | GGB | 62.81 | GGB | 157655.29 | GGB | 124909.05 | GGB | 0 | 0 | 2256 | 3600 | 2240.88 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 4841.66 | GGB | 4841.72 | 2240.88 | 2240.88 |  |  |  | 1 | 1 |  |  |  |  | 124909.05 | 2240.88 |  |  | 7.259 | [5 empty] | 77.7517
10.09.2007 14:00 | 3600 | 2 | 757.75 | GGB | 765.934 | 769.336 | 763.004 | 251.9 | GGB | 10541.6 | GGB | 9.93 | GGB | 986.91 | GGB | 63.02 | GGB | 157051.21 | GGB | 124310.68 | GGB | 0 | 0 | 2242 | 3600 | 2227.19 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 4880.97 | GGB | 4881.03 | 2227.19 | 2227.19 |  |  |  | 1 | 1 |  |  |  |  | 124310.68 | 2227.19 |  |  | 7.0431 | [5 empty] | 76.9065
10.09.2007 15:00 | 3600 | 2 | 757.87 | GGB | 767.033 | 769.336 | 763.004 | 251.11 | GGB | 10504 | GGB | 9.93 | GGB | 986.76 | GGB | 63.24 | GGB | 156465.83 | GGB | 123745.97 | GNB | 0 | 0 | 2228 | 3600 | 2212.56 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 4919.95 | GGB | 4920.01 | 2212.56 | 2212.56 |  |  |  | 1 | 1 |  |  |  |  | 123745.97 | 2212.56 |  |  | 7.024 | [5 empty] | 76.0543
10.09.2007 16:00 | 3600 | 2 | 757.9 | GGB | 766.3 | 769.242 | 763.004 | 250.42 | GGB | 10477.5 | GGB | 9.93 | GGB | 986.3 | GGB | 63.46 | GGB | 155877.15 | GGB | 123144.78 | GNB | 0 | 0 | 2217 | 3600 | 2201.6 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 4959.02 | GGB | 4959.08 | 2201.6 | 2201.6 |  |  |  | 1 | 1 |  |  |  |  | 123144.78 | 2201.6 |  |  | 6.9392 | [5 empty] | 75.3099
10.09.2007 17:00 | 3600 | 2 | 757.93 | GGB | 766.3 | 769.336 | 763.004 | 250.41 | GGB | 10470.2 | GGB | 9.93 | GGB | 985.98 | GGB | 63.64 | GGB | 155797.92 | GGB | 122974.05 | GNB | 0 | 0 | 2218 | 3600 | 2202.54 | GNB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 4998.27 | GGB | 4998.33 | 2202.54 | 2202.54 |  |  |  | 1 | 1 |  |  |  |  | 122974.05 | 2202.54 |  |  | 6.9008 | [5 empty] | 75.2376
10.09.2007 18:00 | 3600 | 2 | 757.57 | GGB | 767.033 | 769.219 | 763.004 | 251.01 | GGB | 10484.6 | GGB | 9.92 | GGB | 985.47 | GGB | 63.51 | GGB | 156231.46 | GGB | 123301.19 | GNB | 0 | 0 | 2238 | 3600 | 2223.23 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 5037.6 | GGB | 5037.66 | 2223.23 | 2223.23 |  |  |  | 1 | 1 |  |  |  |  | 123301.19 | 2223.23 |  |  | 6.9699 | [5 empty] | 76.1464
10.09.2007 19:00 | 3600 | 2 | 757.29 | GGB | 765.934 | 768.305 | 763.004 | 251.48 | GGB | 10501.1 | GGB | 9.93 | GGB | 985.54 | GGB | 63.5 | GGB | 156470.23 | GGB | 123503.46 | GNB | 0 | 0 | 2260 | 3600 | 2245.07 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 5076.77 | GGB | 5076.83 | 2245.07 | 2245.07 |  |  |  | 1 | 1 |  |  |  |  | 123503.46 | 2245.07 |  |  | 7.0787 | [5 empty] | 77.0205
10.09.2007 20:00 | 3600 | 2 | 757.1 | GGB | 765.934 | 768.305 | 762.637 | 252.21 | GGB | 10538.1 | GGB | 9.92 | GGB | 985.75 | GGB | 63.36 | GGB | 156800.33 | GGB | 123839.73 | GNB | 0 | 0 | 2295 | 3600 | 2280.41 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 5116.43 | GGB | 5116.49 | 2280.41 | 2280.41 |  |  |  | 1 | 1 |  |  |  |  | 123839.73 | 2280.41 |  |  | 7.1207 | [5 empty] | 78.4459
10.09.2007 21:00 | 3600 | 2 | 756.8 | GGB | 764.835 | 767.156 | 761.538 | 253.23 | GGB | 10582.4 | GGB | 9.92 | GGB | 986.52 | GGB | 63.23 | GGB | 157521.05 | GGB | 124553.4 | GGB | 0 | 0 | 2336 | 3600 | 2320.6 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 5156.28 | GGB | 5156.33 | 2320.6 | 2320.6 |  |  |  | 1 | 1 |  |  |  |  | 124553.4 | 2320.6 |  | 2320.6 | 7.255 | [5 empty] | 80.2885
10.09.2007 22:00 | 3600 | 2 | 756.8 | GGB | 764.835 | 768.188 | 761.538 | 253.81 | GGB | 10606.6 | GGB | 9.92 | GGB | 986.88 | GGB | 63.22 | GGB | 158084.42 | GGB | 125050.1 | GGB | 0 | 0 | 2354 | 3600 | 2338.39 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 5195.98 | GGB | 5196.04 | 2338.39 | 2338.39 |  |  |  | 1 | 1 |  |  |  |  | 125050.1 | 2338.39 |  | 2338.39 | 7.3638 | [5 empty] | 81.2266
10.09.2007 23:00 | 3600 | 2 | 756.79 | GGB | 765.934 | 769.289 | 762.637 | 253.8 | GGB | 10626.8 | GGB | 9.92 | GGB | 987.01 | GGB | 62.8 | GGB | 158480.55 | GGB | 125537.68 | GGB | 0 | 0 | 2359 | 3600 | 2344.04 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 5235.56 | GGB | 5235.62 | 2344.04 | 2344.04 |  |  |  | 1 | 1 |  |  |  |  | 125537.68 | 2344.04 | 125537.68 | 2344.04 | 7.4347 | [5 empty] | 81.7404
10.09.2007 24:00 | 3600 | 2 | 756.52 | GGB | 764.835 | 767.273 | 761.538 | 255.27 | GGB | 10641.8 | GGB | 9.92 | GGB | 987.42 | GGB | 62.9 | GGB | 158910.78 | GGB | 125891.02 | GGB | 0 | 0 | 2380 | 3600 | 2364.63 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 5275.26 | GGB | 5275.32 | 2364.63 | 2364.63 |  |  |  | 1 | 1 |  |  |  |  | 125891.02 | 2364.63 | 125891.02 | 2364.63 | 7.4984 | [5 empty] | 82.6905
11.09.2007 01:00 | 3600 | 2 | 756.24 | GGB | 764.469 | 766.125 | 760.44 | 257.14 | GGB | 10635.2 | GGB | 9.92 | GGB | 987.7 | GGB | 62.26 | GGB | 161416.25 | GGB | 128158.51 | GGB | 0 | 0 | 2382 | 3600 | 2366.84 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 5315.37 | GGB | 5315.43 | 2366.84 | 2366.84 |  |  |  | 0 | 1 | [14 empty] | 84.2585
11.09.2007 02:00 | 3600 | 2 | 756.48 | GGB | 764.469 | 767.18 | 760.44 | 257.14 | GGB | 10657.7 | GGB | 9.93 | GGB | 987.7 | GGB | 62.19 | GGB | 161352.43 | GGB | 128134.31 | GGB | 0 | 0 | 2382 | 3600 | 2367.02 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 5355.33 | GGB | 5355.39 | 2367.02 | 2367.02 |  |  |  | 0 | 1 | [14 empty] | 84.249
11.09.2007 03:00 | 3600 | 2 | 756.21 | GGB | 764.835 | 768.281 | 761.538 | 257.52 | GGB | 10695.8 | GGB | 9.93 | GGB | 987.95 | GGB | 62.16 | GGB | 161412.95 | GGB | 128224.95 | GGB | 0 | 0 | 2416 | 3600 | 2400.45 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 5395.01 | GGB | 5395.08 | 2400.45 | 2400.45 |  |  |  | 1 | 1 |  |  |  |  | 128224.95 | 2400.45 | 128224.95 | 2400.45 | 7.755 | [5 empty] | 85.4993
11.09.2007 04:00 | 3600 | 2 | 755.93 | GNB | 763.37 | 765.961 | 760.44 | 256.6 | GGB | 10719.6 | GGB | 9.92 | GGB | 988.55 | GGB | 62.6 | GGB | 160194.87 | GGB | 127170.44 | GGB | 0 | 0 | 2442 | 3600 | 2426.87 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 5435.22 | GGB | 5435.29 | 2426.87 | 2426.87 |  |  |  | 0 | 1 | [14 empty] | 85.7295
11.09.2007 05:00 | 3600 | 2 | 756.25 | GGB | 764.835 | 766.805 | 761.538 | 257.04 | GGB | 10740.8 | GGB | 9.93 | GGB | 989.12 | GGB | 62.52 | GGB | 160504.07 | GGB | 127517.09 | GGB | 0 | 0 | 2442 | 3600 | 2427.31 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 5475.43 | GGB | 5475.5 | 2427.31 | 2427.31 |  |  |  | 1 | 1 |  |  |  |  | 127517.09 | 2427.31 | 127517.09 | 2427.31 | 7.6977 | [5 empty] | 85.9788
11.09.2007 06:00 | 3600 | 2 | 755.83 | GNB | 764.835 | 766.734 | 760.44 | 259.34 | GGB | 10726.4 | GGB | 9.92 | GGB | 989.22 | GGB | 61.8 | GGB | 163285.72 | GGB | 130019.35 | GGB | 0 | 0 | 2441 | 3600 | 2425.58 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 5515.43 | GGB | 5515.5 | 2425.58 | 2425.58 |  |  |  | 0 | 1 | [14 empty] | 87.6034
11.09.2007 07:00 | 3600 | 2 | 756.22 | GGB | 764.469 | 766.711 | 761.538 | 259.58 | GGB | 10757.2 | GGB | 9.93 | GGB | 989.77 | GGB | 61.47 | GGB | 163887.61 | GGB | 130701.52 | GGB | 0 | 0 | 2435 | 3600 | 2420.1 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 5555.78 | GGB | 5555.85 | 2420.1 | 2420.1 |  |  |  | 1 | 1 |  |  |  |  | 130701.52 | 2420.1 | 130701.52 | 2420.1 | 7.8392 | [5 empty] | 87.8641
11.09.2007 08:00 | 3600 | 2 | 756.4 | GGB | 764.469 | 767.766 | 761.538 | 258.85 | GGB | 10792.3 | GGB | 9.93 | GGB | 990.88 | GGB | 61.54 | GGB | 163074.46 | GGB | 130171.55 | GGB | 0 | 0 | 2444 | 3600 | 2428.69 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 5595.92 | GGB | 5595.99 | 2428.69 | 2428.69 |  |  |  | 1 | 1 |  |  |  |  | 130171.55 | 2428.69 | 130171.55 | 2428.69 | 7.8761 | [5 empty] | 87.8184
11.09.2007 09:00 | 3600 | 2 | 756.45 | GGB | 764.835 | 767.742 | 761.538 | 257.51 | GGB | 10794.3 | GGB | 9.93 | GGB | 991.52 | GGB | 62.06 | GGB | 161542.79 | GGB | 128831.47 | GGB | 0 | 0 | 2452 | 3600 | 2436.67 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 5636.49 | GGB | 5636.56 | 2436.67 | 2436.67 |  |  |  | 1 | 1 |  |  |  |  | 128831.47 | 2436.67 | 128831.47 | 2436.67 | 7.7377 | [5 empty] | 87.1999
11.09.2007 10:00 | 3600 | 2 | 756.42 | GGB | 764.835 | 767.766 | 761.538 | 256.27 | GGB | 10744.8 | GGB | 9.93 | GGB | 991.86 | GGB | 62.39 | GGB | 160407.24 | GGB | 127841.79 | GGB | 0 | 0 | 2435 | 3600 | 2420.3 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 5676.91 | GGB | 5676.98 | 2420.3 | 2420.3 |  |  |  | 1 | 1 |  |  |  |  | 127841.79 | 2420.3 | 127841.79 | 2420.3 | 7.655 | [5 empty] | 85.9487
11.09.2007 11:00 | 3600 | 2 | 756.73 | GGB | 765.934 | 768.773 | 762.637 | 256.35 | GGB | 10689.1 | GGB | 9.93 | GGB | 992.58 | GGB | 62.28 | GGB | 160575.59 | GGB | 128112.67 | GGB | 0 | 0 | 2393 | 3600 | 2378.08 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 5717.02 | GGB | 5717.09 | 2378.08 | 2378.08 |  |  |  | 1 | 1 |  |  |  |  | 128112.67 | 2378.08 | 128112.67 | 2378.08 | 7.5957 | [5 empty] | 84.6284
11.09.2007 12:00 | 3600 | 2 | 756.82 | GGB | 765.934 | 768.75 | 761.538 | 254.78 | GGB | 10663.1 | GGB | 9.93 | GGB | 993.13 | GGB | 63.24 | GGB | 158755.63 | GGB | 126369.83 | GGB | 0 | 0 | 2393 | 3600 | 2378.28 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 5757.21 | GGB | 5757.28 | 2378.28 | 2378.28 |  |  |  | 1 | 1 |  |  |  |  | 126369.83 | 2378.28 | 126369.83 | 2378.28 | 7.4781 | [5 empty] | 83.4841
11.09.2007 13:00 | 3600 | 2 | 757.07 | GGB | 767.033 | 768.914 | 762.637 | 254.79 | GGB | 10586 | GGB | 9.93 | GGB | 993.17 | GGB | 63.35 | GGB | 158884.37 | GGB | 126436.12 | GGB | 0 | 0 | 2347 | 3600 | 2331.82 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 5797.15 | GGB | 5797.22 | 2331.82 | 2331.82 |  |  |  | 1 | 1 |  |  |  |  | 126436.12 | 2331.82 | 126436.12 | 2331.82 | 7.3817 | [5 empty] | 81.8962
11.09.2007 14:00 | 3600 | 2 | 757.43 | GGB | 767.033 | 768.938 | 763.004 | 254.3 | GGB | 10548.3 | GGB | 9.93 | GGB | 993 | GGB | 63.34 | GGB | 158648.9 | GGB | 126229.42 | GGB | 0 | 0 | 2307 | 3600 | 2291.56 | GGB | 100 | GGB | 42.82 | GGB | 42.82 | GGB | 5839.97 | GGB | 5840.04 | 2291.56 | 2291.56 |  |  |  | 1 | 1 |  |  |  |  | 126229.42 | 2291.56 | 126229.42 |  | 6.7553 | [5 empty] | 80.3506
11.09.2007 15:00 | 3600 | 2 | 757.59 | GGB | 767.033 | 768.938 | 762.637 | 254.01 | GGB | 10523.3 | GGB | 9.93 | GGB | 993.02 | GGB | 63.64 | GGB | 158403.52 | GGB | 125925.72 | GGB | 0 | 0 | 2287 | 3600 | 2272.15 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 5879.3 | GGB | 5879.37 | 2272.15 | 2272.15 |  |  |  | 1 | 1 |  |  |  |  | 125925.72 | 2272.15 | 125925.72 |  | 7.2749 | [5 empty] | 79.4784
11.09.2007 16:00 | 3600 | 2 | 757.56 | GGB | 767.033 | 768.938 | 761.538 | 252.83 | GGB | 10545.8 | GGB | 9.92 | GGB | 992.95 | GGB | 64.08 | GGB | 157098.52 | GGB | 124714.6 | GGB | 0 | 0 | 2311 | 3600 | 2295.66 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 5918.7 | GGB | 5918.77 | 2295.66 | 2295.66 |  |  |  | 1 | 1 |  |  |  |  | 124714.6 | 2295.66 |  |  | 7.2666 | [5 empty] | 79.5284
11.09.2007 17:00 | 3600 | 2 | 757.21 | GGB | 767.033 | 768.844 | 762.637 | 253.11 | GGB | 10567 | GGB | 9.92 | GGB | 993.71 | GGB | 64.46 | GGB | 156806.93 | GGB | 124440.65 | GGB | 0 | 0 | 2339 | 3600 | 2323.97 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 5958.43 | GGB | 5958.5 | 2323.97 | 2323.97 |  |  |  | 1 | 1 |  |  |  |  | 124440.65 | 2323.97 |  | 2323.97 | 7.279 | [5 empty] | 80.3323
11.09.2007 18:00 | 3600 | 2 | 756.71 | GGB | 764.835 | 766.664 | 760.44 | 254.24 | GGB | 10595 | GGB | 9.91 | GGB | 994.23 | GGB | 63.66 | GGB | 157956.79 | GGB | 125715.19 | GGB | 0 | 0 | 2367 | 3600 | 2352.32 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 5998.52 | GGB | 5998.59 | 2352.32 | 2352.32 |  |  |  | 0 | 1 | [14 empty] | 82.1451
11.09.2007 19:00 | 3600 | 2 | 757.04 | GGB | 767.033 | 768.797 | 762.637 | 257.66 | GGB | 10663 | GGB | 9.93 | GGB | 995.2 | GGB | 63.06 | GGB | 161242.39 | GGB | 128683.72 | GGB | 0 | 0 | 2388 | 3600 | 2373.07 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 6037.83 | GGB | 6037.9 | 2373.07 | 2373.07 |  |  |  | 1 | 1 |  |  |  |  | 128683.72 | 2373.07 | 128683.72 | 2373.07 | 7.7684 | [5 empty] | 84.8265
11.09.2007 20:00 | 3600 | 2 | 756.84 | GGB | 765.934 | 768.75 | 762.637 | 257.36 | GGB | 10659.3 | GGB | 9.92 | GGB | 995.98 | GGB | 63.24 | GGB | 161157.67 | GGB | 128650.64 | GGB | 0 | 0 | 2392 | 3600 | 2377.23 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 6077.74 | GGB | 6077.8 | 2377.23 | 2377.23 |  |  |  | 1 | 1 |  |  |  |  | 128650.64 | 2377.23 | 128650.64 | 2377.23 | 7.665 | [5 empty] | 84.9534
11.09.2007 21:00 | 3600 | 2 | 756.97 | GGB | 764.835 | 767.695 | 760.44 | 256.99 | GGB | 10680.3 | GGB | 9.92 | GGB | 996.2 | GGB | 63.47 | GGB | 160453.45 | GGB | 128027.02 | GGB | 0 | 0 | 2391 | 3600 | 2375.47 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 6117.71 | GGB | 6117.77 | 2375.47 | 2375.47 |  |  |  | 0 | 1 | [14 empty] | 84.479
11.09.2007 22:00 | 3600 | 2 | 756.79 | GGB | 767.033 | 768.703 | 762.637 | 257.25 | GGB | 10738.3 | GGB | 9.93 | GGB | 996.6 | GGB | 63.18 | GGB | 160069.43 | GGB | 127884.23 | GGB | 0 | 0 | 2441 | 3600 | 2425.6 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 6158.02 | GGB | 6158.08 | 2425.6 | 2425.6 |  |  |  | 1 | 1 |  |  |  |  | 127884.23 | 2425.6 | 127884.23 | 2425.6 | 7.6953 | [5 empty] | 86.1656
11.09.2007 23:00 | 3600 | 2 | 756.66 | GGB | 767.033 | 768.516 | 762.637 | 257.59 | GGB | 10761 | GGB | 9.92 | GGB | 996.77 | GGB | 63.37 | GGB | 160844.07 | GGB | 128450.26 | GGB | 0 | 0 | 2446 | 3600 | 2430.75 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 6197.89 | GGB | 6197.96 | 2430.75 | 2430.75 |  |  |  | 1 | 1 |  |  |  |  | 128450.26 | 2430.75 | 128450.26 | 2430.75 | 7.8292 | [5 empty] | 86.7307
11.09.2007 24:00 | 3600 | 2 | 756.51 | GGB | 765.934 | 767.461 | 761.538 | 259.23 | GGB | 10763 | GGB | 9.92 | GGB | 997.43 | GGB | 62.63 | GGB | 161702.33 | GGB | 129505.17 | GGB | 0 | 0 | 2461 | 3600 | 2446.12 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 6237.81 | GGB | 6237.88 | 2446.12 | 2446.12 |  |  |  | 1 | 1 |  |  |  |  | 129505.17 | 2446.12 | 129505.17 | 2446.12 | 7.9355 | [5 empty] | 87.9959
12.09.2007 01:00 | 3600 | 2 | 756.57 | GGB | 765.934 | 767.742 | 762.637 | 261.38 | GGB | 10756.5 | GGB | 9.92 | GGB | 997.51 | GGB | 62.16 | GGB | 163056.85 | GGB | 130786.37 | GGB | 0 | 0 | 2447 | 3600 | 2431.48 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 6277.74 | GGB | 6277.8 | 2431.48 | 2431.48 |  |  |  | 1 | 1 |  |  |  |  | 130786.37 | 2431.48 | 130786.37 | 2431.48 | 7.966 | [5 empty] | 88.3346
12.09.2007 02:00 | 3600 | 2 | 756.37 | GGB | 765.934 | 767.742 | 761.538 | 262.75 | GGB | 10754.6 | GGB | 9.91 | GGB | 997.79 | GGB | 62.59 | GGB | 163542.1 | GGB | 131042.74 | GGB | 0 | 0 | 2459 | 3600 | 2443.37 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 6317.29 | GGB | 6317.36 | 2443.37 | 2443.37 |  |  |  | 1 | 1 |  |  |  |  | 131042.74 | 2443.37 | 131042.74 | 2443.37 | 8.0937 | [5 empty] | 88.9405
12.09.2007 03:00 | 3600 | 2 | 756.51 | GGB | 764.835 | 767.742 | 760.44 | 263.98 | GGB | 10833 | GGB | 9.92 | GGB | 998.02 | GGB | 62.56 | GGB | 164432.27 | GGB | 131797.55 | GGB | 0 | 0 | 2487 | 3600 | 2471.37 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 6356.92 | GGB | 6356.98 | 2471.37 | 2471.37 |  |  |  | 0 | 1 | [14 empty] | 90.4779
12.09.2007 04:00 | 3600 | 2 | 756.22 | GGB | 765.934 | 767.297 | 761.538 | 263.92 | GGB | 10892.8 | GGB | 9.92 | GGB | 998.5 | GGB | 62.7 | GGB | 164627.03 | GGB | 131963.1 | GGB | 0 | 0 | 2525 | 3600 | 2509.8 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 6397.18 | GGB | 6397.25 | 2509.8 | 2509.8 |  |  |  | 1 | 1 |  |  |  |  | 131963.1 | 2509.8 | 131963.1 | 2509.8 | 8.2245 | [5 empty] | 92.0003
12.09.2007 05:00 | 3600 | 2 | 755.99 | GNB | 765.934 | 767.297 | 761.538 | 264.17 | GGB | 10912.5 | GGB | 9.92 | GGB | 998.43 | GGB | 62.42 | GGB | 164952.73 | GGB | 132324.41 | GGB | 0 | 0 | 2538 | 3600 | 2522.87 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 6437.54 | GGB | 6437.61 | 2522.87 | 2522.87 |  |  |  | 0 | 1 | [14 empty] | 92.7326
12.09.2007 06:00 | 3600 | 2 | 755.83 | GNB | 765.934 | 767.484 | 760.44 | 264.79 | GGB | 10941.5 | GGB | 9.92 | GGB | 998.69 | GGB | 62.2 | GGB | 166462.4 | GGB | 133658.71 | GGB | 0 | 0 | 2551 | 3600 | 2535.23 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 6477.94 | GGB | 6478.01 | 2535.23 | 2535.23 |  |  |  | 0 | 1 | [14 empty] | 94.1265
12.09.2007 07:00 | 3600 | 2 | 756.18 | GGB | 765.934 | 767.109 | 761.538 | 266.86 | GGB | 10947.5 | GGB | 9.92 | GGB | 999 | GGB | 61.23 | GGB | 169493.83 | GGB | 136529.37 | GGB | 0 | 0 | 2530 | 3600 | 2514.49 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 6518.78 | GGB | 6518.85 | 2514.49 | 2514.49 |  |  |  | 1 | 1 |  |  |  |  | 136529.37 | 2514.49 | 136529.37 | 2514.49 | 8.406 | [5 empty] | 95.3616
12.09.2007 08:00 | 3600 | 2 | 756.47 | GGB | 765.934 | 768.445 | 761.538 | 266.13 | GGB | 10943.4 | GGB | 9.93 | GGB | 998.91 | GGB | 61.35 | GGB | 168884.24 | GGB | 135977.1 | GGB | 0 | 0 | 2514 | 3600 | 2498.28 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 6559.75 | GGB | 6559.82 | 2498.28 | 2498.28 |  |  |  | 1 | 1 |  |  |  |  | 135977.1 | 2498.28 | 135977.1 | 2498.28 | 8.2916 | [5 empty] | 94.3636
12.09.2007 09:00 | 3600 | 2 | 756.94 | GGB | 767.033 | 768.281 | 762.637 | 264.97 | GGB | 10940.5 | GGB | 9.93 | GGB | 998.84 | GGB | 61.51 | GGB | 167728.88 | GGB | 134974.07 | GGB | 0 | 0 | 2498 | 3600 | 2482.89 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 6600.49 | GGB | 6600.56 | 2482.89 | 2482.89 |  |  |  | 1 | 1 |  |  |  |  | 134974.07 | 2482.89 | 134974.07 | 2482.89 | 8.226 | [5 empty] | 93.0905
12.09.2007 10:00 | 3600 | 2 | 756.23 | GGB | 765.934 | 767.227 | 761.538 | 262.9 | GGB | 10935.4 | GGB | 9.93 | GGB | 999.15 | GGB | 62.43 | GGB | 164946.13 | GGB | 132411.92 | GGB | 0 | 0 | 2515 | 3600 | 2499.27 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 6641.29 | GGB | 6641.37 | 2499.27 | 2499.27 |  |  |  | 1 | 1 |  |  |  |  | 132411.92 | 2499.27 | 132411.92 | 2499.27 | 8.1091 | [5 empty] | 91.9259
12.09.2007 11:00 | 3600 | 2 | 755.96 | GNB | 767.033 | 768.469 | 762.637 | 261.16 | GGB | 10875.3 | GGB | 9.94 | GGB | 999 | GGB | 63.06 | GGB | 163213.1 | GGB | 130753.55 | GGB | 0 | 0 | 2477 | 3600 | 2462 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 6680.74 | GGB | 6680.82 | 2462 | 2462 |  |  |  | 0 | 1 | [14 empty] | 89.4209
12.09.2007 12:00 | 3600 | 2 | 756.13 | GGB | 765.934 | 767.438 | 761.538 | 258.74 | GGB | 10772 | GGB | 9.94 | GGB | 998.83 | GGB | 63.88 | GGB | 160693.33 | GGB | 128401.33 | GGB | 0 | 0 | 2437 | 3600 | 2421.59 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 6719.63 | GGB | 6719.71 | 2421.59 | 2421.59 |  |  |  | 1 | 1 |  |  |  |  | 128401.33 | 2421.59 | 128401.33 | 2421.59 | 7.9953 | [5 empty] | 86.3709
12.09.2007 13:00 | 3600 | 2 | 756.38 | GGB | 764.835 | 767.344 | 760.44 | 256.84 | GGB | 10660.8 | GGB | 9.93 | GGB | 998.3 | GGB | 64.72 | GGB | 158667.6 | GGB | 126400.2 | GGB | 0 | 0 | 2381 | 2690 | 2366.04 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 6758.12 | GGB | 6758.2 | 2366.04 | 2366.04 |  |  |  | 0 | 1 | [14 empty] | 83.0744
12.09.2007 14:00 | 3600 | 2 | 756.7 | GGB | 768.498 | 772.172 | 765.201 | 256.56 | GGB | 10567.2 | GGB | 9.93 | GGB | 997.62 | GGB | 64.61 | GGB | 158911.88 | GGB | 126549.92 | GGB | 0 | 0 | 2330 | 3600 | 2314.54 | GGB | 100 | GGB | 37.72 | GGB | 37.72 | GGB | 6795.83 | GGB | 6795.92 | 2314.54 | 2314.54 |  |  |  | 1 | 1 |  |  |  |  | 126549.92 | 2314.54 | 126549.92 | 2314.54 | 7.7652 | [5 empty] | 81.3625
12.09.2007 15:00 | 3600 | 2 | 756.55 | GGB | 765.934 | 769.195 | 762.637 | 255 | GGB | 10546.5 | GGB | 9.93 | GGB | 997 | GGB | 64.6 | GGB | 158669.8 | GGB | 126282.87 | GGB | 0 | 0 | 2319 | 3600 | 2303.75 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 6834.02 | GGB | 6834.1 | 2303.75 | 2303.75 |  |  |  | 1 | 1 |  |  |  |  | 126282.87 | 2303.75 | 126282.87 |  | 7.6198 | [5 empty] | 80.8123
12.09.2007 16:00 | 3600 | 2 | 756.77 | GGB | 767.033 | 769.102 | 763.004 | 254.29 | GGB | 10538.1 | GGB | 9.92 | GGB | 996.35 | GGB | 64.27 | GGB | 158515.76 | GGB | 126198.38 | GGB | 0 | 0 | 2299 | 3600 | 2284.12 | GGB | 100 | GGB | 37.98 | GGB | 37.98 | GGB | 6872 | GGB | 6872.08 | 2284.12 | 2284.12 |  |  |  | 1 | 1 |  |  |  |  | 126198.38 | 2284.12 | 126198.38 |  | 7.5896 | [5 empty] | 80.0701
12.09.2007 17:00 | 3600 | 2 | 757.07 | GGB | 765.934 | 769.102 | 762.637 | 251.51 | GGB | 10523.1 | GGB | 9.93 | GGB | 996.07 | GGB | 64.94 | GGB | 155916.76 | GGB | 123849.38 | GNB | 0 | 0 | 2289 | 3600 | 2274.42 | GGB | 100 | GGB | 37.35 | GGB | 37.35 | GGB | 6909.35 | GGB | 6909.43 | 2274.42 | 2274.42 |  |  |  | 1 | 1 |  |  |  |  | 123849.38 | 2274.42 |  |  | 7.5418 | [5 empty] | 78.246
12.09.2007 18:00 | 3600 | 2 | 756.75 | GGB | 765.934 | 769.266 | 762.637 | 250.99 | GGB | 10498.8 | GGB | 9.92 | GGB | 995.64 | GGB | 65.18 | GGB | 155423.81 | GGB | 123318.81 | GNB | 0 | 0 | 2298 | 3600 | 2282.46 | GGB | 100 | GGB | 36 | GGB | 36 | GGB | 6945.35 | GGB | 6945.43 | 2282.46 | 2282.46 |  |  |  | 1 | 1 |  |  |  |  | 123318.81 | 2282.46 |  |  | 7.8186 | [5 empty] | 78.1862
12.09.2007 19:00 | 3600 | 2 | 756.66 | GGB | 764.835 | 768.188 | 761.538 | 251.45 | GGB | 10512 | GGB | 9.92 | GGB | 995.26 | GGB | 65.01 | GGB | 155326.98 | GGB | 123255.58 | GNB | 0 | 0 | 2318 | 3600 | 2302.95 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 6984.53 | GGB | 6984.61 | 2302.95 | 2302.95 |  |  |  | 1 | 1 |  |  |  |  | 123255.58 | 2302.95 |  |  | 7.2448 | [5 empty] | 78.8476
12.09.2007 20:00 | 3600 | 2 | 756.59 | GGB | 765.934 | 769.219 | 762.637 | 253.79 | GGB | 10522.6 | GGB | 9.92 | GGB | 995.48 | GGB | 64.08 | GGB | 157751.02 | GGB | 125551.32 | GGB | 0 | 0 | 2327 | 3600 | 2311.71 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 7022.39 | GGB | 7022.47 | 2311.71 | 2311.71 |  |  |  | 1 | 1 |  |  |  |  | 125551.32 | 2311.71 | 125551.32 | 2311.71 | 7.6661 | [5 empty] | 80.6217
12.09.2007 21:00 | 3600 | 2 | 756.63 | GGB | 765.934 | 768.164 | 762.637 | 254.8 | GGB | 10558.4 | GGB | 9.92 | GGB | 995.79 | GGB | 63.5 | GGB | 158719.32 | GGB | 126580.9 | GGB | 0 | 0 | 2336 | 3600 | 2320.56 | GGB | 100 | GGB | 37.37 | GGB | 37.37 | GGB | 7059.75 | GGB | 7059.84 | 2320.56 | 2320.56 |  |  |  | 1 | 1 |  |  |  |  | 126580.9 | 2320.56 | 126580.9 | 2320.56 | 7.8603 | [5 empty] | 81.594
12.09.2007 22:00 | 3600 | 2 | 756.19 | GGB | 764.835 | 768.352 | 761.538 | 254.21 | GGB | 10613.7 | GGB | 9.92 | GGB | 995.9 | GGB | 63.39 | GGB | 158906.38 | GGB | 126786.41 | GGB | 0 | 0 | 2373 | 3600 | 2357.44 | GGB | 100 | GGB | 35.31 | GGB | 35.31 | GGB | 7095.07 | GGB | 7095.15 | 2357.44 | 2357.44 |  |  |  | 1 | 1 |  |  |  |  | 126786.41 | 2357.44 | 126786.41 | 2357.44 | 8.4648 | [5 empty] | 83.0254
12.09.2007 23:00 | 3600 | 2 | 755.97 | GNB | 765.934 | 768.281 | 761.538 | 254.86 | GGB | 10648.9 | GGB | 9.92 | GGB | 995.8 | GGB | 63.61 | GGB | 158461.84 | GGB | 126335.45 | GGB | 0 | 0 | 2407 | 3600 | 2391.68 | GGB | 100 | GGB | 35.59 | GGB | 35.59 | GGB | 7130.66 | GGB | 7130.74 | 2391.68 | 2391.68 |  |  |  | 0 | 1 | [14 empty] | 83.9317
12.09.2007 24:00 | 3600 | 2 | 755.97 | GNB | 765.934 | 769.195 | 761.538 | 255.18 | GGB | 10682.7 | GGB | 9.93 | GGB | 995.37 | GGB | 63.4 | GGB | 158943.79 | GGB | 126744.9 | GGB | 0 | 0 | 2413 | 3600 | 2397.61 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 7169.13 | GGB | 7169.21 | 2397.61 | 2397.61 |  |  |  | 0 | 1 | [14 empty] | 84.4125
13.09.2007 01:00 | 3600 | 2 | 755.41 | GNB | 764.835 | 766.617 | 760.44 | 255.83 | GGB | 10686.4 | GGB | 9.92 | GGB | 994.94 | GGB | 62.75 | GGB | 159839.46 | GGB | 127649.4 | GGB | 0 | 0 | 2434 | 3600 | 2418.43 | GGB | 100 | GGB | 36.88 | GGB | 36.88 | GGB | 7206.01 | GGB | 7206.09 | 2418.43 | 2418.43 |  |  |  | 0 | 1 | [14 empty] | 85.7531
13.09.2007 02:00 | 3600 | 2 | 755.52 | GNB | 764.469 | 766.453 | 760.44 | 256.61 | GGB | 10709.9 | GGB | 9.93 | GGB | 994.78 | GGB | 62.73 | GGB | 160661.42 | GGB | 128291.53 | GGB | 0 | 0 | 2438 | 3600 | 2422.91 | GGB | 100 | GGB | 36.67 | GGB | 36.67 | GGB | 7242.68 | GGB | 7242.76 | 2422.91 | 2422.91 |  |  |  | 0 | 1 | [14 empty] | 86.3441
13.09.2007 03:00 | 3600 | 2 | 755.09 | GNB | 763.37 | 766.453 | 760.44 | 256.14 | GGB | 10700.4 | GGB | 9.92 | GGB | 994.56 | GGB | 63.04 | GGB | 159826.26 | GGB | 127478.95 | GGB | 0 | 0 | 2457 | 3600 | 2441.65 | GGB | 100 | GGB | 37.52 | GGB | 37.52 | GGB | 7280.2 | GGB | 7280.28 | 2441.65 | 2441.65 |  |  |  | 0 | 1 | [14 empty] | 86.4608
13.09.2007 04:00 | 3600 | 2 | 755.05 | GNB | 764.835 | 766.453 | 761.538 | 257.16 | GGB | 10660.3 | GGB | 9.93 | GGB | 994.16 | GGB | 62.5 | GGB | 161078.44 | GGB | 128632.24 | GGB | 0 | 0 | 2436 | 3600 | 2421.2 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 7319.88 | GGB | 7319.96 | 2421.2 | 2421.2 |  |  |  | 0 | 1 | [14 empty] | 86.5123
13.09.2007 05:00 | 3600 | 2 | 755.06 | GNB | 764.835 | 767.484 | 761.538 | 257.41 | GGB | 10658.4 | GGB | 9.92 | GGB | 993.92 | GGB | 62.56 | GGB | 161059.74 | GGB | 128563.67 | GGB | 0 | 0 | 2434 | 3600 | 2418.81 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 7359.38 | GGB | 7359.47 | 2418.81 | 2418.81 |  |  |  | 0 | 1 | [14 empty] | 86.3809
13.09.2007 06:00 | 3600 | 2 | 755.52 | GNB | 765.934 | 767.695 | 762.637 | 257.08 | GGB | 10675.8 | GGB | 9.93 | GGB | 994.3 | GGB | 62.56 | GGB | 160708.73 | GGB | 128334.9 | GGB | 0 | 0 | 2432 | 3600 | 2417.13 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 7397.43 | GGB | 7397.52 | 2417.13 | 2417.13 |  |  |  | 0 | 1 | [14 empty] | 86.1673
13.09.2007 07:00 | 3600 | 2 | 755.4 | GNB | 764.835 | 767.672 | 761.538 | 255.76 | GGB | 10696 | GGB | 9.92 | GGB | 994.43 | GGB | 63.24 | GGB | 159236.48 | GGB | 126916.81 | GGB | 0 | 0 | 2450 | 3600 | 2435.11 | GGB | 100 | GGB | 35.41 | GGB | 35.41 | GGB | 7432.84 | GGB | 7432.93 | 2435.11 | 2435.11 |  |  |  | 0 | 1 | [14 empty] | 85.849
13.09.2007 08:00 | 3600 | 2 | 754.97 | GNB | 764.835 | 766.805 | 760.44 | 256.35 | GGB | 10716.2 | GGB | 9.92 | GGB | 994.66 | GGB | 63.21 | GGB | 159541.27 | GGB | 127201.86 | GGB | 0 | 0 | 2473 | 3600 | 2457.46 | GGB | 100 | GGB | 42.5 | GGB | 42.5 | GGB | 7475.34 | GGB | 7475.43 | 2457.46 | 2457.46 |  |  |  | 0 | 1 | [14 empty] | 86.8315
13.09.2007 09:00 | 3600 | 2 | 754.68 | GNB | 764.469 | 766.805 | 760.44 | 257.77 | GGB | 10714 | GGB | 9.92 | GGB | 995 | GGB | 62.87 | GGB | 161293.01 | GGB | 128772.52 | GGB | 0 | 0 | 2479 | 3600 | 2463.42 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 7513.72 | GGB | 7513.81 | 2463.42 | 2463.42 |  |  |  | 0 | 1 | [14 empty] | 88.1169
13.09.2007 10:00 | 3600 | 2 | 755.88 | GNB | 765.934 | 767.813 | 761.538 | 258.11 | GGB | 10703.1 | GGB | 9.93 | GGB | 995.35 | GGB | 62.49 | GGB | 161785.96 | GGB | 129357.43 | GGB | 0 | 0 | 2428 | 3600 | 2413.16 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 7551.75 | GGB | 7551.84 | 2413.16 | 2413.16 |  |  |  | 0 | 1 | [14 empty] | 86.7112
13.09.2007 11:00 | 3600 | 2 | 756.29 | GGB | 767.033 | 768.867 | 762.637 | 256.45 | GGB | 10632.9 | GGB | 9.93 | GGB | 995.73 | GGB | 62.98 | GGB | 160502.97 | GGB | 128192.4 | GGB | 0 | 0 | 2381 | 3600 | 2365.44 | GGB | 100 | GGB | 36.37 | GGB | 36.37 | GGB | 7588.12 | GGB | 7588.21 | 2365.44 | 2365.44 |  |  |  | 1 | 1 |  |  |  |  | 128192.4 | 2365.44 | 128192.4 | 2365.44 | 8.3374 | [5 empty] | 84.231
13.09.2007 12:00 | 3600 | 2 | 755.65 | GNB | 764.835 | 767.766 | 761.538 | 255.04 | GGB | 10580.6 | GGB | 9.93 | GGB | 995.7 | GGB | 63.17 | GGB | 159517.06 | GGB | 127331.85 | GGB | 0 | 0 | 2357 | 3600 | 2341.46 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 7626.26 | GGB | 7626.35 | 2341.46 | 2341.46 |  |  |  | 0 | 1 | [14 empty] | 82.8173
13.09.2007 13:00 | 3600 | 2 | 755.84 | GNB | 765.934 | 768.82 | 762.637 | 253.84 | GGB | 10584.7 | GGB | 9.93 | GGB | 995.54 | GGB | 63.4 | GGB | 158772.14 | GGB | 126630.01 | GGB | 0 | 0 | 2341 | 3600 | 2326.22 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 7664.5 | GGB | 7664.59 | 2326.22 | 2326.22 |  |  |  | 0 | 1 | [14 empty] | 81.8248
13.09.2007 14:00 | 3600 | 2 | 755.39 | GNB | 764.835 | 767.531 | 761.538 | 252.98 | GGB | 10580.1 | GGB | 9.92 | GGB | 995.5 | GGB | 63.84 | GGB | 157833.55 | GGB | 125710.39 | GGB | 0 | 0 | 2355 | 3600 | 2339.42 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 7702.47 | GGB | 7702.56 | 2339.42 | 2339.42 |  |  |  | 0 | 1 | [14 empty] | 81.6915
13.09.2007 15:00 | 3600 | 2 | 756.07 | GGB | 765.934 | 767.555 | 761.538 | 254.37 | GGB | 10569 | GGB | 9.93 | GGB | 995.6 | GGB | 63.15 | GGB | 159758.04 | GGB | 127515.97 | GGB | 0 | 0 | 2316 | 3600 | 2300.67 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 7741.82 | GGB | 7741.91 | 2300.67 | 2300.67 |  |  |  | 1 | 1 |  |  |  |  | 127515.97 | 2300.67 | 127515.97 |  | 7.4555 | [5 empty] | 81.4923
13.09.2007 16:00 | 3600 | 2 | 755.95 | GNB | 765.201 | 768.797 | 761.538 | 254.2 | GGB | 10550.1 | GGB | 9.92 | GGB | 995.43 | GGB | 63.05 | GGB | 159729.43 | GGB | 127510.78 | GGB | 0 | 0 | 2306 | 3600 | 2291.19 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 7779.68 | GGB | 7779.77 | 2291.19 | 2291.19 |  |  |  | 0 | 1 | [14 empty] | 81.1532
13.09.2007 17:00 | 3600 | 2 | 755.61 | GNB | 765.201 | 767.672 | 761.538 | 255.12 | GGB | 10606.1 | GGB | 9.92 | GGB | 995.98 | GGB | 62.83 | GGB | 160248.79 | GGB | 128079.11 | GGB | 0 | 0 | 2357 | 3600 | 2341.6 | GGB | 100 | GGB | 37.75 | GGB | 37.75 | GGB | 7817.43 | GGB | 7817.52 | 2341.6 | 2341.6 |  |  |  | 0 | 1 | [14 empty] | 83.3083
13.09.2007 18:00 | 3600 | 2 | 755.7 | GNB | 765.201 | 767.578 | 761.538 | 254.59 | GGB | 10651 | GGB | 9.93 | GGB | 996.15 | GGB | 63.33 | GGB | 158991.1 | GGB | 126905.25 | GGB | 0 | 0 | 2377 | 3600 | 2362.36 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 7857.22 | GGB | 7857.31 | 2362.36 | 2362.36 |  |  |  | 0 | 1 | [14 empty] | 83.2766
13.09.2007 19:00 | 3600 | 2 | 755.45 | GNB | 765.201 | 767.906 | 761.538 | 254.81 | GGB | 10629 | GGB | 9.92 | GGB | 996.66 | GGB | 63.5 | GGB | 158877.77 | GGB | 126816.33 | GGB | 0 | 0 | 2389 | 3600 | 2374.22 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 7897.12 | GGB | 7897.21 | 2374.22 | 2374.22 |  |  |  | 0 | 1 | [14 empty] | 83.6361
13.09.2007 20:00 | 3600 | 2 | 755.03 | GNB | 765.201 | 766.781 | 761.538 | 256.19 | GGB | 10677.7 | GGB | 9.92 | GGB | 997.11 | GGB | 63.25 | GGB | 159991.31 | GGB | 127858.57 | GGB | 0 | 0 | 2417 | 3600 | 2401.83 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 7936.25 | GGB | 7936.34 | 2401.83 | 2401.83 |  |  |  | 0 | 1 | [14 empty] | 85.304
13.09.2007 21:00 | 3600 | 2 | 754.97 | GNB | 764.102 | 766.641 | 760.44 | 257.49 | GGB | 10734.4 | GGB | 9.92 | GGB | 998.3 | GGB | 62.85 | GGB | 161251.2 | GGB | 129172.83 | GGB | 0 | 0 | 2442 | 3600 | 2426.62 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 7974.68 | GGB | 7974.77 | 2426.62 | 2426.62 |  |  |  | 0 | 1 | [14 empty] | 87.0704
13.09.2007 22:00 | 3600 | 2 | 755.01 | GNB | 765.201 | 767.648 | 762.637 | 258.42 | GGB | 10792.2 | GGB | 9.93 | GGB | 999.26 | GGB | 62.54 | GGB | 162546.29 | GGB | 130456.39 | GGB | 0 | 0 | 2461 | 3600 | 2445.98 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 8014.12 | GGB | 8014.21 | 2445.98 | 2445.98 |  |  |  | 0 | 1 | [14 empty] | 88.6371
13.09.2007 23:00 | 3600 | 2 | 754.93 | GNB | 765.201 | 767.672 | 761.538 | 260.98 | GGB | 10752.9 | GGB | 9.92 | GGB | 999.85 | GGB | 62.6 | GGB | 163603.72 | GGB | 131358.06 | GGB | 0 | 0 | 2461 | 3600 | 2445.32 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 8054.83 | GGB | 8054.92 | 2445.32 | 2445.32 |  |  |  | 0 | 1 | [14 empty] | 89.2257
13.09.2007 24:00 | 3600 | 2 | 754.7 | GNB | 765.201 | 766.734 | 761.538 | 262.69 | GGB | 10786.5 | GGB | 9.91 | GGB | 1000.68 | GGB | 62.19 | GGB | 165017.65 | GGB | 132767.71 | GGB | 0 | 0 | 2493 | 3600 | 2477.48 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 8092.89 | GGB | 8092.98 | 2477.48 | 2477.48 |  |  |  | 0 | 1 | [14 empty] | 91.3693
14.09.2007 01:00 | 3600 | 2 | 754.78 | GNB | 764.102 | 766.523 | 760.44 | 262.71 | GGB | 10866.3 | GGB | 9.92 | GGB | 1001.09 | GGB | 62.39 | GGB | 164361.85 | GGB | 132214.82 | GGB | 0 | 0 | 2527 | 3600 | 2511.44 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 8133.51 | GGB | 8133.61 | 2511.44 | 2511.44 |  |  |  | 0 | 1 | [14 empty] | 92.236
14.09.2007 02:00 | 3600 | 2 | 754.45 | GNB | 765.201 | 767.648 | 762.637 | 264.21 | GGB | 10893 | GGB | 9.92 | GGB | 1001.55 | GGB | 61.86 | GGB | 165379.66 | GGB | 133303.52 | GGB | 0 | 0 | 2554 | 3600 | 2538.38 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 8171.92 | GGB | 8172.01 | 2538.38 | 2538.38 |  |  |  | 0 | 1 | [14 empty] | 93.9931
14.09.2007 03:00 | 3600 | 2 | 754.68 | GNB | 766.3 | 767.695 | 761.538 | 265.29 | GGB | 10938.8 | GGB | 9.92 | GGB | 1002.04 | GGB | 61.62 | GGB | 166444.79 | GGB | 134325.32 | GGB | 0 | 0 | 2567 | 3600 | 2551.22 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 8211.12 | GGB | 8211.21 | 2551.22 | 2551.22 |  |  |  | 0 | 1 | [14 empty] | 95.1926
14.09.2007 04:00 | 3600 | 2 | 754.2 | GNB | 764.102 | 766.734 | 760.44 | 266.09 | GGB | 10967.5 | GGB | 9.91 | GGB | 1002.19 | GGB | 61.43 | GGB | 167531.92 | GGB | 135300.88 | GGB | 0 | 0 | 2597 | 3600 | 2581.8 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 8251.38 | GGB | 8251.48 | 2581.8 | 2581.8 |  |  |  | 0 | 1 | [14 empty] | 97.0333
14.09.2007 05:00 | 3600 | 2 | 754.17 | GNB | 764.102 | 766.734 | 760.44 | 266.62 | GGB | 11007 | GGB | 9.92 | GGB | 1002.4 | GGB | 61.17 | GGB | 168704.88 | GGB | 136381.78 | GGB | 0 | 0 | 2608 | 3600 | 2592.58 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 8290.22 | GGB | 8290.32 | 2592.58 | 2592.58 |  |  |  | 0 | 1 | [14 empty] | 98.2169
14.09.2007 06:00 | 3600 | 2 | 753.28 | GNB | 764.102 | 765.586 | 760.44 | 267.26 | GGB | 11008.7 | GGB | 9.9 | GGB | 1002.55 | GGB | 60.91 | GGB | 169816.23 | GGB | 137407.86 | GGB | 0 | 0 | 2659 | 3600 | 2643.36 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 8331.22 | GGB | 8331.32 | 2643.36 | 2643.36 |  |  |  | 0 | 1 | [14 empty] | 100.894
14.09.2007 07:00 | 3600 | 2 | 753.1 | GNB | 762.637 | 763.617 | 758.974 | 267.59 | GGB | 11009 | GGB | 9.89 | GGB | 1002.67 | GGB | 60.8 | GGB | 170474.23 | GGB | 138002.18 | GGB | 0 | 0 | 2674 | 3600 | 2658.89 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 8370.3 | GGB | 8370.4 | 2658.89 | 2658.89 |  |  |  | 0 | 1 | [14 empty] | 101.9257
14.09.2007 08:00 | 3600 | 2 | 753.78 | GNB | 764.102 | 765.797 | 760.44 | 269.08 | GGB | 11005.3 | GGB | 9.91 | GGB | 1002.83 | GGB | 60.3 | GGB | 172662.8 | GGB | 140004.42 | GGB | 0 | 0 | 2628 | 3600 | 2612.73 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 8411.33 | GGB | 8411.43 | 2612.73 | 2612.73 |  |  |  | 0 | 1 | [14 empty] | 101.6094
14.09.2007 09:00 | 3600 | 2 | 756.09 | GGB | 766.3 | 767.789 | 762.637 | 266.87 | GGB | 11012 | GGB | 9.95 | GGB | 1002.78 | GGB | 61.06 | GGB | 169690.79 | GGB | 137273.44 | GGB | 0 | 0 | 2535 | 3208 | 2519.26 | GGB | 100 | GGB | 36.17 | GGB | 36.17 | GGB | 8447.5 | GGB | 8447.6 | 2519.26 | 2519.26 |  |  |  | 1 | 1 |  |  |  |  | 137273.44 | 2519.26 | 137273.44 | 2519.26 | 9.5612 | [5 empty] | 96.0632
14.09.2007 10:00 | 3600 | 2 | 755.75 | GNB | 765.201 | 767.438 | 761.538 | 263.81 | GGB | 10938.2 | GGB | 9.93 | GGB | 1002.29 | GGB | 62.44 | GGB | 166178.51 | GGB | 133817.06 | GGB | 0 | 0 | 2520 | 3600 | 2505 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 8488.57 | GGB | 8488.67 | 2505 | 2505 |  |  |  | 0 | 1 | [14 empty] | 93.1144
14.09.2007 11:00 | 3600 | 2 | 756.19 | GGB | 766.3 | 768.445 | 763.004 | 262.08 | GGB | 10868.3 | GGB | 9.94 | GGB | 1001.79 | GGB | 62.98 | GGB | 164222.11 | GGB | 131960.92 | GGB | 0 | 0 | 2474 | 3600 | 2458.76 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 8528.75 | GGB | 8528.85 | 2458.76 | 2458.76 |  |  |  | 1 | 1 |  |  |  |  | 131960.92 | 2458.76 | 131960.92 | 2458.76 | 8.0752 | [5 empty] | 90.1278
14.09.2007 12:00 | 3600 | 2 | 756.01 | GGB | 765.201 | 767.016 | 761.538 | 260.56 | GGB | 10775.7 | GGB | 9.93 | GGB | 1000.96 | GGB | 63.56 | GGB | 162689.34 | GGB | 130399.03 | GGB | 0 | 0 | 2432 | 3600 | 2417.33 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 8567.88 | GGB | 8567.98 | 2417.33 | 2417.33 |  |  |  | 1 | 1 |  |  |  |  | 130399.03 | 2417.33 | 130399.03 | 2417.33 | 8.0556 | [5 empty] | 87.5604
14.09.2007 13:00 | 3600 | 2 | 756.31 | GGB | 766.3 | 769.102 | 764.102 | 259.18 | GGB | 10717.4 | GGB | 9.93 | GGB | 999.98 | GGB | 64.2 | GGB | 161422.85 | GGB | 129009.97 | GGB | 0 | 0 | 2395 | 3600 | 2380.16 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 8607.72 | GGB | 8607.82 | 2380.16 | 2380.16 |  |  |  | 1 | 1 |  |  |  |  | 129009.97 | 2380.16 | 129009.97 | 2380.16 | 7.7074 | [5 empty] | 85.2957
14.09.2007 14:00 | 3600 | 2 | 756.19 | GGB | 767.766 | 769.969 | 764.102 | 258.4 | GGB | 10674.1 | GGB | 9.93 | GGB | 998.97 | GGB | 64.23 | GGB | 161068.54 | GGB | 128584.76 | GGB | 0 | 0 | 2372 | 3600 | 2356.64 | GGB | 100 | GGB | 37.84 | GGB | 37.84 | GGB | 8645.56 | GGB | 8645.66 | 2356.64 | 2356.64 |  |  |  | 1 | 1 |  |  |  |  | 128584.76 | 2356.64 | 128584.76 | 2356.64 | 8.0081 | [5 empty] | 84.1744
14.09.2007 15:00 | 3600 | 2 | 756.72 | GGB | 766.667 | 768.797 | 763.004 | 257.62 | GGB | 10635.4 | GGB | 9.93 | GGB | 998.08 | GGB | 64.48 | GGB | 160335.72 | GGB | 127792.18 | GGB | 0 | 0 | 2337 | 3600 | 2321.58 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 8683.67 | GGB | 8683.77 | 2321.58 | 2321.58 |  |  |  | 1 | 1 |  |  |  |  | 127792.18 | 2321.58 | 127792.18 | 2321.58 | 7.7848 | [5 empty] | 82.411
14.09.2007 16:00 | 3600 | 2 | 756.4 | GGB | 765.201 | 767.859 | 763.004 | 256.79 | GGB | 10589.8 | GGB | 9.93 | GGB | 997.14 | GGB | 64.76 | GGB | 159667.81 | GGB | 127033.06 | GGB | 0 | 0 | 2339 | 3600 | 2323.62 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 8722.99 | GGB | 8723.09 | 2323.62 | 2323.62 |  |  |  | 1 | 1 |  |  |  |  | 127033.06 | 2323.62 | 127033.06 | 2323.62 | 7.507 | [5 empty] | 81.9935
14.09.2007 17:00 | 3600 | 2 | 756.46 | GGB | 766.3 | 769.008 | 764.102 | 257.4 | GGB | 10561.3 | GGB | 9.92 | GGB | 996.35 | GGB | 64.72 | GGB | 160363.22 | GGB | 127500.89 | GGB | 0 | 0 | 2331 | 3600 | 2316.35 | GGB | 100 | GGB | 37.73 | GGB | 37.73 | GGB | 8760.73 | GGB | 8760.82 | 2316.35 | 2316.35 |  |  |  | 1 | 1 |  |  |  |  | 127500.89 | 2316.35 | 127500.89 | 2316.35 | 7.8276 | [5 empty] | 82.038
14.09.2007 18:00 | 3600 | 2 | 756.94 | GGB | 766.667 | 769.992 | 764.102 | 256.43 | GGB | 10547.1 | GGB | 9.93 | GGB | 995.77 | GGB | 64.88 | GGB | 159366.32 | GGB | 126576.02 | GGB | 0 | 0 | 2304 | 3600 | 2288.77 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 8799.13 | GGB | 8799.22 | 2288.77 | 2288.77 |  |  |  | 1 | 1 |  |  |  |  | 126576.02 | 2288.77 | 126576.02 |  | 7.5444 | [5 empty] | 80.4732
14.09.2007 19:00 | 3600 | 2 | 756.18 | GGB | 765.201 | 768.07 | 761.538 | 255.99 | GGB | 10536.6 | GGB | 9.92 | GGB | 994.57 | GGB | 65.37 | GGB | 158426.63 | GGB | 125496.04 | GGB | 0 | 0 | 2342 | 3600 | 2326.57 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 8837.76 | GGB | 8837.86 | 2326.57 | 2326.57 |  |  |  | 1 | 1 |  |  |  |  | 125496.04 | 2326.57 | 125496.04 | 2326.57 | 7.5563 | [5 empty] | 81.1043
14.09.2007 20:00 | 3600 | 2 | 755.58 | GNB | 766.3 | 768.258 | 762.637 | 257.32 | GGB | 10582.6 | GGB | 9.92 | GGB | 994.25 | GGB | 64.95 | GGB | 159134.15 | GGB | 126172.39 | GGB | 0 | 0 | 2391 | 3600 | 2376.24 | GGB | 100 | GGB | 36.73 | GGB | 36.73 | GGB | 8874.49 | GGB | 8874.59 | 2376.24 | 2376.24 |  |  |  | 0 | 1 | [14 empty] | 83.2822
14.09.2007 21:00 | 3600 | 2 | 755.69 | GNB | 765.201 | 767.063 | 761.538 | 259.04 | GGB | 10610.9 | GGB | 9.92 | GGB | 994.62 | GGB | 64.49 | GGB | 160705.43 | GGB | 127636.86 | GGB | 0 | 0 | 2395 | 3600 | 2379.52 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 8915.03 | GGB | 8915.13 | 2379.52 | 2379.52 |  |  |  | 0 | 1 | [14 empty] | 84.3651
14.09.2007 22:00 | 3600 | 2 | 755.51 | GNB | 764.102 | 767.086 | 761.538 | 258.28 | GGB | 10639.6 | GGB | 9.93 | GGB | 994.12 | GGB | 64.5 | GGB | 159915.39 | GGB | 126943.53 | GGB | 0 | 0 | 2410 | 3600 | 2395.06 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 8952.83 | GGB | 8952.94 | 2395.06 | 2395.06 |  |  |  | 0 | 1 | [14 empty] | 84.4548
14.09.2007 23:00 | 3600 | 2 | 755.49 | GNB | 765.201 | 768.117 | 761.538 | 258.37 | GGB | 10639.4 | GGB | 9.93 | GGB | 993.26 | GGB | 64.48 | GGB | 159995.71 | GGB | 126904.82 | GGB | 0 | 0 | 2421 | 3600 | 2405.46 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 8991.01 | GGB | 8991.12 | 2405.46 | 2405.46 |  |  |  | 0 | 1 | [14 empty] | 84.7957
14.09.2007 24:00 | 3600 | 2 | 755.7 | GNB | 765.201 | 768.117 | 762.637 | 258.01 | GGB | 10635.7 | GGB | 9.93 | GGB | 992.37 | GGB | 64.34 | GGB | 159810.85 | GGB | 126698.54 | GGB | 0 | 0 | 2417 | 3600 | 2401.39 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 9031.02 | GGB | 9031.13 | 2401.39 | 2401.39 |  |  |  | 0 | 1 | [14 empty] | 84.5146
15.09.2007 01:00 | 3600 | 2 | 755.28 | GNB | 765.201 | 768.117 | 762.637 | 257.47 | GGB | 10620.2 | GGB | 9.92 | GGB | 991.33 | GGB | 64.28 | GGB | 159655.71 | GGB | 126465.27 | GGB | 0 | 0 | 2419 | 3600 | 2403.76 | GGB | 100 | GGB | 37.71 | GGB | 37.71 | GGB | 9068.73 | GGB | 9068.84 | 2403.76 | 2403.76 |  |  |  | 0 | 1 | [14 empty] | 84.4423
15.09.2007 02:00 | 3600 | 2 | 755.35 | GNB | 765.201 | 767.297 | 761.538 | 257.18 | GGB | 10609.3 | GGB | 9.93 | GGB | 989.82 | GGB | 64.38 | GGB | 159337.71 | GGB | 125984.2 | GGB | 0 | 0 | 2410 | 3600 | 2395.01 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 9107.23 | GGB | 9107.34 | 2395.01 | 2395.01 |  |  |  | 0 | 1 | [14 empty] | 83.8148
15.09.2007 03:00 | 3600 | 2 | 755.46 | GNB | 765.201 | 768.375 | 762.637 | 257.19 | GGB | 10607.5 | GGB | 9.93 | GGB | 988.69 | GGB | 64.41 | GGB | 159166.06 | GGB | 125692.6 | GGB | 0 | 0 | 2408 | 3600 | 2392.5 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 9146.39 | GGB | 9146.51 | 2392.5 | 2392.5 |  |  |  | 0 | 1 | [14 empty] | 83.5332
15.09.2007 04:00 | 3600 | 2 | 755.28 | GNB | 765.201 | 767.367 | 762.637 | 257.18 | GGB | 10598.6 | GGB | 9.93 | GGB | 987.77 | GGB | 64.46 | GGB | 158961.39 | GGB | 125395.27 | GGB | 0 | 0 | 2416 | 3600 | 2400.81 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 9184.36 | GGB | 9184.48 | 2400.81 | 2400.81 |  |  |  | 0 | 1 | [14 empty] | 83.6251
15.09.2007 05:00 | 3600 | 2 | 755.21 | GNB | 765.201 | 767.391 | 762.637 | 257.02 | GGB | 10588.1 | GGB | 9.92 | GGB | 987.18 | GGB | 64.41 | GGB | 158747.93 | GGB | 125170.36 | GGB | 0 | 0 | 2415 | 3600 | 2400.31 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 9223.78 | GGB | 9223.9 | 2400.31 | 2400.31 |  |  |  | 0 | 1 | [14 empty] | 83.4577
15.09.2007 06:00 | 3600 | 2 | 755.25 | GNB | 765.201 | 768.445 | 762.637 | 257.34 | GGB | 10607.6 | GGB | 9.93 | GGB | 986.18 | GGB | 64.21 | GGB | 159111.04 | GGB | 125403.18 | GGB | 0 | 0 | 2420 | 3600 | 2404.92 | GGB | 100 | GGB | 37.9 | GGB | 37.9 | GGB | 9261.68 | GGB | 9261.8 | 2404.92 | 2404.92 |  |  |  | 0 | 1 | [14 empty] | 83.7735
15.09.2007 07:00 | 3600 | 2 | 755.05 | GNB | 764.102 | 767.648 | 761.538 | 256.81 | GGB | 10600.6 | GGB | 9.93 | GGB | 985.25 | GGB | 64.09 | GGB | 158771.04 | GGB | 125062.16 | GGB | 0 | 0 | 2422 | 3600 | 2407.08 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 9299.65 | GGB | 9299.77 | 2407.08 | 2407.08 |  |  |  | 0 | 1 | [14 empty] | 83.6207
15.09.2007 08:00 | 3600 | 2 | 754.8 | GNB | 765.201 | 767.648 | 762.637 | 256.4 | GGB | 10592.7 | GGB | 9.92 | GGB | 984.79 | GGB | 63.83 | GGB | 158572.97 | GGB | 124945.62 | GGB | 0 | 0 | 2439 | 3600 | 2423.99 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 9339.14 | GGB | 9339.26 | 2423.99 | 2423.99 |  |  |  | 0 | 1 | [14 empty] | 84.1297
15.09.2007 09:00 | 3600 | 2 | 754.81 | GNB | 765.201 | 767.367 | 761.538 | 256.21 | GGB | 10599.5 | GGB | 9.92 | GGB | 984.9 | GGB | 56.52 | GGB | 166812.3 | GGB | 134366.87 | GGB | 0 | 0 | 2453 | 3600 | 2438.19 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 9377.27 | GGB | 9377.39 | 2438.19 | 2438.19 |  |  |  | 0 | 1 | [14 empty] | 91.0033
15.09.2007 10:00 | 3600 | 2 | 754.53 | GNB | 765.201 | 767.391 | 762.637 | 256.53 | GGB | 10613.1 | GGB | 9.93 | GGB | 984.92 | GGB | 63.15 | GGB | 167195.22 | GGB | 132023.43 | GGB | 0 | 0 | 2467 | 3600 | 2451.98 | GGB | 100 | GGB | 37.84 | GGB | 37.84 | GGB | 9415.11 | GGB | 9415.23 | 2451.98 | 2451.98 |  |  |  | 0 | 1 | [14 empty] | 89.9219
15.09.2007 11:00 | 3600 | 2 | 753.83 | GNB | 764.102 | 766.57 | 761.538 | 256.61 | GGB | 10594.3 | GGB | 9.92 | GGB | 985.14 | GGB | 64.98 | GGB | 173318.6 | GGB | 136143.73 | GGB | 0 | 0 | 2473 | 3600 | 2457.59 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 9454.79 | GGB | 9454.91 | 2457.59 | 2457.59 |  |  |  | 0 | 1 | [14 empty] | 92.9404
15.09.2007 12:00 | 3600 | 2 | 753.76 | GNB | 760.44 | 763.477 | 757.509 | 256.56 | GGB | 10569.2 | GGB | 9.91 | GGB | 984.88 | GGB | 66.44 | GGB | 179350.65 | GGB | 140242.64 | GGB | 0 | 0 | 2464 | 3600 | 2449.19 | GGB | 100 | GGB | 37.83 | GGB | 37.83 | GGB | 9492.63 | GGB | 9492.74 | 2449.19 | 2449.19 |  |  |  | 0 | 1 | [14 empty] | 95.4114
15.09.2007 13:00 | 3600 | 2 | 755.12 | GNB | 765.201 | 768.07 | 762.271 | 257.99 | GGB | 10673.1 | GGB | 9.95 | GGB | 984.96 | GGB | 66.81 | GGB | 182097.1 | GGB | 142247.16 | GGB | 0 | 0 | 2453 | 3600 | 2437.7 | GGB | 100 | GGB | 37.07 | GGB | 37.07 | GGB | 9529.7 | GGB | 9529.81 | 2437.7 | 2437.7 |  |  |  | 0 | 1 | [14 empty] | 96.3211
15.09.2007 14:00 | 3600 | 2 | 754.34 | GNB | 764.102 | 767.273 | 762.271 | 255.69 | GGB | 10567.5 | GGB | 9.92 | GGB | 984.66 | GGB | 67.42 | GGB | 180228.72 | GGB | 140492.06 | GGB | 0 | 0 | 2416 | 3600 | 2400.45 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 9569.5 | GGB | 9569.61 | 2400.45 | 2400.45 |  |  |  | 0 | 1 | [14 empty] | 93.6789
15.09.2007 15:00 | 3600 | 2 | 754.02 | GNB | 765.201 | 766.266 | 762.271 | 257.52 | GGB | 10608.3 | GGB | 9.91 | GGB | 984.61 | GGB | 62.83 | GGB | 169798.62 | GGB | 134162.84 | GGB | 0 | 0 | 2437 | 3600 | 2421.34 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 9607.54 | GGB | 9607.65 | 2421.34 | 2421.34 |  |  |  | 0 | 1 | [14 empty] | 90.2372
15.09.2007 16:00 | 3600 | 2 | 755.37 | GNB | 764.102 | 766.195 | 761.172 | 256.02 | GGB | 10601.7 | GGB | 9.94 | GGB | 984.94 | GGB | 62.98 | GGB | 167606.75 | GGB | 132417.2 | GGB | 0 | 0 | 2388 | 3600 | 2372.85 | GGB | 100 | GGB | 37.49 | GGB | 37.49 | GGB | 9645.03 | GGB | 9645.14 | 2372.85 | 2372.85 |  |  |  | 0 | 1 | [14 empty] | 87.2795
15.09.2007 17:00 | 3600 | 2 | 754.49 | GNB | 763.004 | 766.172 | 759.707 | 255.71 | GGB | 10577.3 | GGB | 9.92 | GGB | 984.87 | GGB | 62.95 | GGB | 167135.8 | GGB | 132046.58 | GGB | 0 | 0 | 2408 | 3600 | 2392.74 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 9684.68 | GGB | 9684.79 | 2392.74 | 2392.74 |  |  |  | 0 | 1 | [14 empty] | 87.7648
15.09.2007 18:00 | 3600 | 2 | 754.59 | GNB | 765.201 | 768.234 | 762.271 | 258.6 | GGB | 10673.5 | GGB | 9.93 | GGB | 985.61 | GGB | 61.91 | GGB | 169874.54 | GGB | 134727.73 | GGB | 0 | 0 | 2463 | 3600 | 2447.49 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 9723.13 | GGB | 9723.24 | 2447.49 | 2447.49 |  |  |  | 0 | 1 | [14 empty] | 91.5958
15.09.2007 19:00 | 3600 | 2 | 754.27 | GNB | 765.201 | 767.227 | 762.271 | 258.01 | GGB | 10669.8 | GGB | 9.92 | GGB | 986.01 | GGB | 62.58 | GGB | 168865.53 | GGB | 133715.56 | GGB | 0 | 0 | 2465 | 3600 | 2450.17 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 9761.69 | GGB | 9761.8 | 2450.17 | 2450.17 |  |  |  | 0 | 1 | [14 empty] | 91.0072
15.09.2007 20:00 | 3600 | 2 | 754.2 | GNB | 764.102 | 766.102 | 761.172 | 258.57 | GGB | 10712.3 | GGB | 9.92 | GGB | 986.65 | GGB | 61.74 | GGB | 169343.08 | GGB | 134515.78 | GGB | 0 | 0 | 2496 | 3600 | 2481.25 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 9800.12 | GGB | 9800.23 | 2481.25 | 2481.25 |  |  |  | 0 | 1 | [14 empty] | 92.7131
15.09.2007 21:00 | 3600 | 2 | 754.32 | GNB | 764.102 | 767.203 | 761.172 | 260.34 | GGB | 10735 | GGB | 9.92 | GGB | 988 | GGB | 61.73 | GGB | 171332.49 | GGB | 136288.3 | GGB | 0 | 0 | 2503 | 3600 | 2487.67 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 9839.66 | GGB | 9839.78 | 2487.67 | 2487.67 |  |  |  | 0 | 1 | [14 empty] | 94.1779
15.09.2007 22:00 | 3600 | 2 | 754.29 | GNB | 764.102 | 767.438 | 761.172 | 259.34 | GGB | 10770.4 | GGB | 9.92 | GGB | 988.54 | GGB | 61.63 | GGB | 170724 | GGB | 135916.76 | GGB | 0 | 0 | 2517 | 3600 | 2501.41 | GGB | 100 | GGB | 38.41 | GGB | 38.41 | GGB | 9878.07 | GGB | 9878.19 | 2501.41 | 2501.41 |  |  |  | 0 | 1 | [14 empty] | 94.4399
15.09.2007 23:00 | 3600 | 2 | 754.27 | GNB | 764.102 | 766.547 | 761.172 | 260.47 | GGB | 10766.5 | GGB | 9.92 | GGB | 988.94 | GGB | 61.95 | GGB | 170494.03 | GGB | 135660.82 | GGB | 0 | 0 | 2527 | 3600 | 2511.33 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 9915.98 | GGB | 9916.1 | 2511.33 | 2511.33 |  |  |  | 0 | 1 | [14 empty] | 94.6359
15.09.2007 24:00 | 3600 | 2 | 754.39 | GNB | 764.102 | 766.758 | 761.172 | 261.25 | GGB | 10787.9 | GGB | 9.92 | GGB | 988.95 | GGB | 61.77 | GGB | 171459.03 | GGB | 136503.56 | GGB | 0 | 0 | 2536 | 3600 | 2520.39 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 9955.88 | GGB | 9956 | 2520.39 | 2520.39 |  |  |  | 0 | 1 | [14 empty] | 95.5673
16.09.2007 01:00 | 3600 | 2 | 754.7 | GNB | 764.102 | 766.758 | 762.271 | 261.44 | GGB | 10814.1 | GGB | 9.93 | GGB | 989.68 | GGB | 61.34 | GGB | 172216.06 | GGB | 137383.52 | GGB | 0 | 0 | 2531 | 3600 | 2515.81 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 9994.48 | GGB | 9994.6 | 2515.81 | 2515.81 |  |  |  | 0 | 1 | [14 empty] | 96.0086
16.09.2007 02:00 | 3600 | 2 | 754.81 | GNB | 764.102 | 766.711 | 761.172 | 261.2 | GGB | 10816.9 | GGB | 9.93 | GGB | 990.66 | GGB | 61.33 | GGB | 172065.32 | GGB | 137402.76 | GGB | 0 | 0 | 2517 | 3600 | 2502.02 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 10032.58 | GGB | 10032.7 | 2502.02 | 2502.02 |  |  |  | 0 | 1 | [14 empty] | 95.4957
16.09.2007 03:00 | 3600 | 2 | 754.59 | GNB | 764.102 | 766.664 | 761.172 | 260.81 | GGB | 10805.9 | GGB | 9.92 | GGB | 991.1 | GGB | 61.34 | GGB | 171731.91 | GGB | 137192.78 | GGB | 0 | 0 | 2516 | 3600 | 2501.24 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 10072.82 | GGB | 10072.95 | 2501.24 | 2501.24 |  |  |  | 0 | 1 | [14 empty] | 95.32
16.09.2007 04:00 | 3600 | 2 | 753.99 | GNB | 764.102 | 766.664 | 761.172 | 262.13 | GGB | 10844.1 | GGB | 9.92 | GGB | 991.59 | GGB | 61.27 | GGB | 172922.48 | GGB | 138243.39 | GGB | 0 | 0 | 2556 | 3600 | 2541.1 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 10112.19 | GGB | 10112.32 | 2541.1 | 2541.1 |  |  |  | 0 | 1 | [14 empty] | 97.5806
16.09.2007 05:00 | 3600 | 2 | 754.55 | GNB | 764.102 | 766.664 | 760.806 | 262.25 | GGB | 10859.2 | GGB | 9.93 | GGB | 991.88 | GGB | 61.3 | GGB | 172968.69 | GGB | 138306.04 | GGB | 0 | 0 | 2545 | 3600 | 2529.26 | GGB | 100 | GGB | 37.68 | GGB | 37.68 | GGB | 10149.88 | GGB | 10150 | 2529.26 | 2529.26 |  |  |  | 0 | 1 | [14 empty] | 97.17
16.09.2007 06:00 | 3600 | 2 | 754.34 | GNB | 764.102 | 766.711 | 761.172 | 262.36 | GGB | 10858.3 | GGB | 9.92 | GGB | 992.07 | GGB | 61.08 | GGB | 172997.3 | GGB | 138448.76 | GGB | 0 | 0 | 2550 | 3600 | 2535.03 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 10189.06 | GGB | 10189.19 | 2535.03 | 2535.03 |  |  |  | 0 | 1 | [14 empty] | 97.4922
16.09.2007 07:00 | 3600 | 2 | 754.38 | GNB | 764.102 | 766.711 | 760.806 | 262.62 | GGB | 10869.9 | GGB | 9.92 | GGB | 992.56 | GGB | 60.83 | GGB | 173482.55 | GGB | 139008.08 | GGB | 0 | 0 | 2553 | 3600 | 2538.07 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 10229.12 | GGB | 10229.25 | 2538.07 | 2538.07 |  |  |  | 0 | 1 | [14 empty] | 98.0034
16.09.2007 08:00 | 3600 | 2 | 754.34 | GNB | 765.201 | 766.688 | 762.271 | 263.64 | GGB | 10899.5 | GGB | 9.92 | GGB | 993.16 | GGB | 60.88 | GGB | 174219.78 | GGB | 139661.33 | GGB | 0 | 0 | 2576 | 3600 | 2560.3 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 10267.48 | GGB | 10267.61 | 2560.3 | 2560.3 |  |  |  | 0 | 1 | [14 empty] | 99.3264
16.09.2007 09:00 | 3600 | 2 | 755.14 | GNB | 765.201 | 767.695 | 762.271 | 263.11 | GGB | 10894.7 | GGB | 9.93 | GGB | 993.68 | GGB | 61.1 | GGB | 173083.13 | GGB | 138730.95 | GGB | 0 | 0 | 2551 | 3600 | 2535.23 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 10306.61 | GGB | 10306.74 | 2535.23 | 2535.23 |  |  |  | 0 | 1 | [14 empty] | 97.6986
16.09.2007 10:00 | 3600 | 2 | 755.57 | GNB | 765.201 | 767.695 | 762.271 | 261.34 | GGB | 10831.9 | GGB | 9.94 | GGB | 994.15 | GGB | 61.62 | GGB | 171293.98 | GGB | 137149.57 | GGB | 0 | 0 | 2503 | 3600 | 2487.85 | GGB | 100 | GGB | 38.26 | GGB | 38.26 | GGB | 10344.87 | GGB | 10345 | 2487.85 | 2487.85 |  |  |  | 0 | 1 | [14 empty] | 94.7799
16.09.2007 11:00 | 3600 | 2 | 755.47 | GNB | 765.201 | 767.672 | 762.271 | 259.56 | GGB | 10760.5 | GGB | 9.93 | GGB | 994.09 | GGB | 62.27 | GGB | 169311.17 | GGB | 135289.48 | GGB | 0 | 0 | 2467 | 3600 | 2451.66 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 10385.04 | GGB | 10385.17 | 2451.66 | 2451.66 |  |  |  | 0 | 1 | [14 empty] | 92.1344
16.09.2007 12:00 | 3600 | 2 | 755.9 | GNB | 765.934 | 768.773 | 763.37 | 258.44 | GGB | 10714.4 | GGB | 9.93 | GGB | 993.62 | GGB | 62.61 | GGB | 168069.99 | GGB | 134100.47 | GGB | 0 | 0 | 2439 | 3600 | 2423.68 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 10423.5 | GGB | 10423.63 | 2423.68 | 2423.68 |  |  |  | 0 | 1 | [14 empty] | 90.2824
16.09.2007 13:00 | 3600 | 2 | 755.91 | GNB | 765.934 | 768.797 | 763.37 | 257.64 | GGB | 10672.9 | GGB | 9.93 | GGB | 993.4 | GGB | 62.78 | GGB | 167377.88 | GGB | 133450.2 | GGB | 0 | 0 | 2412 | 3600 | 2397.27 | GGB | 100 | GGB | 37.93 | GGB | 37.93 | GGB | 10461.43 | GGB | 10461.56 | 2397.27 | 2397.27 |  |  |  | 0 | 1 | [14 empty] | 88.8656
16.09.2007 14:00 | 3600 | 2 | 756.05 | GGB | 764.835 | 767.859 | 763.37 | 257.01 | GGB | 10634.7 | GGB | 9.93 | GGB | 993.35 | GGB | 62.85 | GGB | 167071.98 | GGB | 133170.74 | GGB | 0 | 0 | 2379 | 3600 | 2363.86 | GGB | 100 | GGB | 38.15 | GGB | 38.15 | GGB | 10499.58 | GGB | 10499.71 | 2363.86 | 2363.86 |  |  |  | 1 | 1 |  |  |  |  | 133170.74 | 2363.86 | 133170.74 | 2363.86 | 8.2516 | [5 empty] | 87.4436
16.09.2007 15:00 | 3600 | 2 | 756.32 | GGB | 765.934 | 768.211 | 763.37 | 255.95 | GGB | 10606.2 | GGB | 9.93 | GGB | 993.09 | GGB | 63.02 | GGB | 166385.37 | GGB | 132523.84 | GGB | 0 | 0 | 2356 | 3600 | 2340.92 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 10538.73 | GGB | 10538.86 | 2340.92 | 2340.92 |  |  |  | 1 | 1 |  |  |  |  | 132523.84 | 2340.92 | 132523.84 | 2340.92 | 7.9241 | [5 empty] | 86.1744
16.09.2007 16:00 | 3600 | 2 | 756.09 | GGB | 765.934 | 768.914 | 763.37 | 256.82 | GGB | 10565.4 | GGB | 9.92 | GGB | 992.69 | GGB | 62.92 | GGB | 167255.74 | GGB | 133203.5 | GGB | 0 | 0 | 2348 | 3600 | 2333.19 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 10577.1 | GGB | 10577.23 | 2333.19 | 2333.19 |  |  |  | 1 | 1 |  |  |  |  | 133203.5 | 2333.19 | 133203.5 | 2333.19 | 8.0998 | [5 empty] | 86.3303
16.09.2007 17:00 | 3600 | 2 | 756.07 | GGB | 764.835 | 767.836 | 762.271 | 256.7 | GGB | 10585.1 | GGB | 9.92 | GGB | 992.66 | GGB | 62.82 | GGB | 166824.41 | GGB | 132894.66 | GGB | 0 | 0 | 2364 | 3600 | 2348.56 | GGB | 100 | GGB | 37.3 | GGB | 37.3 | GGB | 10614.4 | GGB | 10614.53 | 2348.56 | 2348.56 |  |  |  | 1 | 1 |  |  |  |  | 132894.66 | 2348.56 | 132894.66 | 2348.56 | 8.3676 | [5 empty] | 86.6975
16.09.2007 18:00 | 3600 | 2 | 755.78 | GNB | 764.835 | 767.789 | 762.271 | 256.64 | GGB | 10619.6 | GGB | 9.92 | GGB | 993.03 | GGB | 63.03 | GGB | 166197.21 | GGB | 132362.19 | GGB | 0 | 0 | 2396 | 3600 | 2380.36 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 10652.76 | GGB | 10652.89 | 2380.36 | 2380.36 |  |  |  | 0 | 1 | [14 empty] | 87.5194
16.09.2007 19:00 | 3600 | 2 | 755.62 | GNB | 764.835 | 767.789 | 762.271 | 258.13 | GGB | 10633.2 | GGB | 9.92 | GGB | 993.71 | GGB | 63.11 | GGB | 167098.39 | GGB | 133139.2 | GGB | 0 | 0 | 2413 | 3600 | 2398.14 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 10692.2 | GGB | 10692.33 | 2398.14 | 2398.14 |  |  |  | 0 | 1 | [14 empty] | 88.6907
16.09.2007 20:00 | 3600 | 2 | 755.51 | GNB | 764.469 | 767.742 | 762.271 | 258.42 | GGB | 10663 | GGB | 9.93 | GGB | 994.09 | GGB | 63.38 | GGB | 167205.12 | GGB | 133166.58 | GGB | 0 | 0 | 2432 | 3600 | 2417.16 | GGB | 100 | GGB | 37.88 | GGB | 37.88 | GGB | 10730.08 | GGB | 10730.21 | 2417.16 | 2417.16 |  |  |  | 0 | 1 | [14 empty] | 89.4125
16.09.2007 21:00 | 3600 | 2 | 755.27 | GNB | 763.37 | 766.688 | 761.172 | 258.89 | GGB | 10679.2 | GGB | 9.92 | GGB | 994.42 | GGB | 63.61 | GGB | 167035.67 | GGB | 132987.15 | GGB | 0 | 0 | 2467 | 3600 | 2452.11 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 10768.4 | GGB | 10768.54 | 2452.11 | 2452.11 |  |  |  | 0 | 1 | [14 empty] | 90.5831
16.09.2007 22:00 | 3600 | 2 | 755.09 | GNB | 763.37 | 766.5 | 761.172 | 259.29 | GGB | 10710.7 | GGB | 9.92 | GGB | 994.54 | GGB | 63.55 | GGB | 167813.61 | GGB | 133647.56 | GGB | 0 | 0 | 2498 | 3600 | 2482.87 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 10807.96 | GGB | 10808.1 | 2482.87 | 2482.87 |  |  |  | 0 | 1 | [14 empty] | 92.1749
16.09.2007 23:00 | 3600 | 2 | 755.38 | GNB | 765.934 | 768.609 | 762.271 | 259.68 | GGB | 10722.5 | GGB | 9.93 | GGB | 994.52 | GGB | 63.6 | GGB | 167507.72 | GGB | 133379.87 | GGB | 0 | 0 | 2503 | 3600 | 2487.51 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 10846.24 | GGB | 10846.38 | 2487.51 | 2487.51 |  |  |  | 0 | 1 | [14 empty] | 92.1622
16.09.2007 24:00 | 3600 | 2 | 755.75 | GNB | 764.835 | 768.609 | 762.271 | 259.41 | GGB | 10699.8 | GGB | 9.93 | GGB | 994.3 | GGB | 64.11 | GGB | 166959.75 | GGB | 132711.75 | GGB | 0 | 0 | 2486 | 3600 | 2470.51 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 10884.78 | GGB | 10884.92 | 2470.51 | 2470.51 |  |  |  | 0 | 1 | [14 empty] | 91.0738
17.09.2007 01:00 | 3600 | 2 | 755.23 | GNB | 764.469 | 767.273 | 761.172 | 259.15 | GGB | 10668 | GGB | 9.92 | GGB | 994.47 | GGB | 64.22 | GGB | 166549.32 | GGB | 132364.29 | GGB | 0 | 0 | 2496 | 3600 | 2480.58 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 10924.11 | GGB | 10924.25 | 2480.58 | 2480.58 |  |  |  | 0 | 1 | [14 empty] | 91.2056
17.09.2007 02:00 | 3600 | 2 | 755.11 | GNB | 764.835 | 767.344 | 762.271 | 259 | GGB | 10654.5 | GGB | 9.93 | GGB | 994.11 | GGB | 64.2 | GGB | 166178.51 | GGB | 132029.59 | GGB | 0 | 0 | 2490 | 3600 | 2475.12 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 10962.15 | GGB | 10962.3 | 2475.12 | 2475.12 |  |  |  | 0 | 1 | [14 empty] | 90.7747
17.09.2007 03:00 | 3600 | 2 | 755.2 | GNB | 764.835 | 767.344 | 762.271 | 258.91 | GGB | 10648.6 | GGB | 9.92 | GGB | 994.02 | GGB | 64.18 | GGB | 166078.38 | GGB | 131946.67 | GGB | 0 | 0 | 2484 | 3600 | 2468.62 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 11000.24 | GGB | 11000.38 | 2468.62 | 2468.62 |  |  |  | 0 | 1 | [14 empty] | 90.4795
17.09.2007 04:00 | 3600 | 2 | 755.29 | GNB | 764.835 | 768.492 | 762.271 | 259.14 | GGB | 10650.7 | GGB | 9.92 | GGB | 993.75 | GGB | 64.38 | GGB | 166209.32 | GGB | 131937.58 | GGB | 0 | 0 | 2483 | 3600 | 2467.81 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 11039.6 | GGB | 11039.74 | 2467.81 | 2467.81 |  |  |  | 0 | 1 | [14 empty] | 90.4436
17.09.2007 05:00 | 3600 | 2 | 755.42 | GNB | 764.835 | 768.539 | 762.271 | 258.85 | GGB | 10638.6 | GGB | 9.93 | GGB | 993.21 | GGB | 64.36 | GGB | 165957.34 | GGB | 131672.43 | GGB | 0 | 0 | 2473 | 3600 | 2458.05 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 11077.66 | GGB | 11077.8 | 2458.05 | 2458.05 |  |  |  | 0 | 1 | [14 empty] | 89.9048
17.09.2007 06:00 | 3600 | 2 | 754.94 | GNB | 764.835 | 767.531 | 762.271 | 259.01 | GGB | 10633.3 | GGB | 9.92 | GGB | 993.03 | GGB | 64.59 | GGB | 166152.1 | GGB | 131715.13 | GGB | 0 | 0 | 2484 | 3600 | 2468.54 | GGB | 100 | GGB | 37.76 | GGB | 37.76 | GGB | 11115.42 | GGB | 11115.56 | 2468.54 | 2468.54 |  |  |  | 0 | 1 | [14 empty] | 90.3178
17.09.2007 07:00 | 3600 | 2 | 754.76 | GNB | 764.469 | 767.531 | 762.271 | 259.64 | GGB | 10656.5 | GGB | 9.92 | GGB | 992.7 | GGB | 64.44 | GGB | 166883.83 | GGB | 132310.52 | GGB | 0 | 0 | 2498 | 3600 | 2483.27 | GGB | 100 | GGB | 38.15 | GGB | 38.15 | GGB | 11153.57 | GGB | 11153.71 | 2483.27 | 2483.27 |  |  |  | 0 | 1 | [14 empty] | 91.2674
17.09.2007 08:00 | 3600 | 2 | 755.13 | GNB | 764.835 | 767.531 | 761.172 | 260.25 | GGB | 10716.4 | GGB | 9.92 | GGB | 992.66 | GGB | 63.81 | GGB | 168063.39 | GGB | 133489.43 | GGB | 0 | 0 | 2504 | 3600 | 2488.32 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 11192.88 | GGB | 11193.03 | 2488.32 | 2488.32 |  |  |  | 0 | 1 | [14 empty] | 92.2679
17.09.2007 09:00 | 3600 | 2 | 755.55 | GNB | 763.37 | 766.547 | 761.172 | 260.28 | GGB | 10667.7 | GGB | 9.94 | GGB | 992.73 | GGB | 63.73 | GGB | 166432.69 | GGB | 132235.48 | GGB | 0 | 0 | 2481 | 3600 | 2465.87 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 11230.87 | GGB | 11231.02 | 2465.87 | 2465.87 |  |  |  | 0 | 1 | [14 empty] | 90.5765
17.09.2007 10:00 | 3600 | 2 | 755.36 | GNB | 765.934 | 768.703 | 763.37 | 260.27 | GGB | 10445.3 | GGB | 9.93 | GGB | 992.57 | GGB | 63.66 | GGB | 162482.47 | GGB | 129100.75 | GGB | 0 | 0 | 2413 | 3600 | 2398.25 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 11268.97 | GGB | 11269.12 | 2398.25 | 2398.25 |  |  |  | 0 | 1 | [14 empty] | 86.0044
17.09.2007 11:00 | 3600 | 2 | 756.32 | GGB | 764.835 | 768.797 | 762.271 | 256.39 | GGB | 10383 | GGB | 9.94 | GGB | 992.14 | GGB | 64.34 | GGB | 158674.21 | GGB | 125767.71 | GGB | 0 | 0 | 2351 | 3600 | 2335.43 | GGB | 100 | GGB | 36.66 | GGB | 36.66 | GGB | 11305.63 | GGB | 11305.78 | 2335.43 | 2335.43 |  |  |  | 1 | 1 |  |  |  |  | 125767.71 | 2335.43 | 125767.71 | 2335.43 | 8.012 | [5 empty] | 81.5894
17.09.2007 12:00 | 3600 | 2 | 755.61 | GNB | 764.835 | 768.773 | 763.37 | 254.65 | GGB | 10308.5 | GGB | 9.93 | GGB | 991.74 | GGB | 64.74 | GGB | 156597.87 | GGB | 123924.68 | GGB | 0 | 0 | 2351 | 3600 | 2335.62 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 11344.73 | GGB | 11344.88 | 2335.62 | 2335.62 |  |  |  | 0 | 1 | [14 empty] | 80.4003
17.09.2007 13:00 | 3600 | 2 | 755.94 | GNB | 764.835 | 768.844 | 763.37 | 253.05 | GGB | 10252.7 | GGB | 9.93 | GGB | 991.46 | GGB | 65.22 | GGB | 155320.38 | GGB | 122704.15 | GGB | 0 | 0 | 2319 | 3600 | 2303.61 | GGB | 100 | GGB | 36.8 | GGB | 36.8 | GGB | 11381.53 | GGB | 11381.68 | 2303.61 | 2303.61 |  |  |  | 0 | 1 | [14 empty] | 78.5174
17.09.2007 14:00 | 3600 | 2 | 755.8 | GNB | 764.835 | 767.813 | 763.37 | 251.7 | GGB | 10132.7 | GGB | 9.92 | GGB | 990.58 | GGB | 65.39 | GGB | 153841.52 | GGB | 121365.33 | GGB | 0 | 0 | 2278 | 3600 | 2262.66 | GGB | 100 | GGB | 36.64 | GGB | 36.64 | GGB | 11418.17 | GGB | 11418.32 | 2262.66 | 2262.66 |  |  |  | 0 | 1 | [14 empty] | 76.2801
17.09.2007 15:00 | 3600 | 2 | 756.21 | GGB | 765.934 | 768.938 | 763.37 | 250.27 | GGB | 10111.4 | GGB | 9.93 | GGB | 989.51 | GGB | 65.91 | GGB | 152244.93 | GGB | 119791.69 | GNB | 0 | 0 | 2255 | 3600 | 2240.25 | GGB | 100 | GGB | 36.31 | GGB | 36.31 | GGB | 11454.48 | GGB | 11454.63 | 2240.25 | 2240.25 |  |  |  | 1 | 1 |  |  |  |  | 119791.69 | 2240.25 |  |  | 7.3909 | [5 empty] | 74.5454
17.09.2007 16:00 | 3600 | 2 | 756.31 | GGB | 764.835 | 768.07 | 762.271 | 249.41 | GGB | 10069 | GGB | 9.93 | GGB | 988.74 | GGB | 66.59 | GGB | 150959.74 | GGB | 118451.57 | GNB | 0 | 0 | 2245 | 3600 | 2229.58 | GGB | 100 | GGB | 37.61 | GGB | 37.61 | GGB | 11492.08 | GGB | 11492.24 | 2229.58 | 2229.58 |  |  |  | 1 | 1 |  |  |  |  | 118451.57 | 2229.58 |  |  | 7.022 | [5 empty] | 73.3603
17.09.2007 17:00 | 3600 | 2 | 756.39 | GGB | 764.835 | 768.117 | 763.37 | 249.48 | GGB | 10037.7 | GGB | 9.92 | GGB | 988.43 | GGB | 66.7 | GGB | 150855.21 | GGB | 118294.59 | GNB | 0 | 0 | 2226 | 3600 | 2211.16 | GGB | 100 | GGB | 35.97 | GGB | 35.97 | GGB | 11528.05 | GGB | 11528.21 | 2211.16 | 2211.16 |  |  |  | 1 | 1 |  |  |  |  | 118294.59 | 2211.16 |  |  | 7.2718 | [5 empty] | 72.6579
17.09.2007 18:00 | 3600 | 2 | 756.02 | GGB | 764.835 | 769.383 | 763.37 | 250.69 | GGB | 10022 | GGB | 9.92 | GGB | 987.86 | GGB | 66.02 | GGB | 152253.73 | GGB | 119562.9 | GNB | 0 | 0 | 2228 | 3600 | 2213.49 | GGB | 100 | GGB | 36.03 | GGB | 36.03 | GGB | 11564.08 | GGB | 11564.24 | 2213.49 | 2213.49 |  |  |  | 1 | 1 |  |  |  |  | 119562.9 | 2213.49 |  |  | 7.3453 | [5 empty] | 73.5142
17.09.2007 19:00 | 3600 | 2 | 755.95 | GNB | 764.835 | 768.328 | 763.37 | 250.48 | GGB | 10098.1 | GGB | 9.93 | GGB | 988.3 | GGB | 66.68 | GGB | 151429.58 | GGB | 118736.55 | GGB | 0 | 0 | 2278 | 3600 | 2262.96 | GGB | 100 | GGB | 36.11 | GGB | 36.11 | GGB | 11600.2 | GGB | 11600.35 | 2262.96 | 2262.96 |  |  |  | 0 | 1 | [14 empty] | 74.6378
17.09.2007 20:00 | 3600 | 2 | 755.69 | GNB | 765.934 | 769.477 | 763.37 | 251.52 | GGB | 10133.5 | GGB | 9.92 | GGB | 988.59 | GGB | 66.49 | GGB | 152363.77 | GGB | 119572.52 | GGB | 0 | 0 | 2305 | 3600 | 2290.16 | GGB | 100 | GGB | 37.43 | GGB | 37.43 | GGB | 11637.63 | GGB | 11637.78 | 2290.16 | 2290.16 |  |  |  | 0 | 1 | [14 empty] | 76.0667
17.09.2007 21:00 | 3600 | 2 | 755.41 | GNB | 764.835 | 768.281 | 762.271 | 251.73 | GGB | 10152.8 | GGB | 9.92 | GGB | 989.2 | GGB | 66.39 | GGB | 152611.34 | GGB | 119876 | GGB | 0 | 0 | 2323 | 3600 | 2307.68 | GGB | 100 | GGB | 36.53 | GGB | 36.53 | GGB | 11674.15 | GGB | 11674.31 | 2307.68 | 2307.68 |  |  |  | 0 | 1 | [14 empty] | 76.8432
17.09.2007 22:00 | 3600 | 2 | 755.64 | GNB | 764.835 | 768.422 | 763.37 | 252.58 | GGB | 10184.5 | GGB | 9.93 | GGB | 989.16 | GGB | 66.22 | GGB | 153120.8 | GGB | 120330.87 | GGB | 0 | 0 | 2339 | 3600 | 2323.86 | GGB | 100 | GGB | 36.03 | GGB | 36.03 | GGB | 11710.19 | GGB | 11710.34 | 2323.86 | 2323.86 |  |  |  | 0 | 1 | [14 empty] | 77.6756
17.09.2007 23:00 | 3600 | 2 | 755.06 | GNB | 764.469 | 767.625 | 762.271 | 252.38 | GGB | 10207.4 | GGB | 9.92 | GGB | 989.29 | GGB | 65.69 | GGB | 153887.74 | GGB | 121137.13 | GGB | 0 | 0 | 2364 | 3600 | 2348.84 | GGB | 100 | GGB | 36.26 | GGB | 36.26 | GGB | 11746.45 | GGB | 11746.6 | 2348.84 | 2348.84 |  |  |  | 0 | 1 | [14 empty] | 79.0366
17.09.2007 24:00 | 3600 | 2 | 755.37 | GNB | 763.37 | 767.602 | 761.172 | 253.5 | GGB | 10194.1 | GGB | 9.92 | GGB | 989.27 | GGB | 65.78 | GGB | 154190.33 | GGB | 121340.05 | GGB | 0 | 0 | 2351 | 3600 | 2335.71 | GGB | 100 | GGB | 37.1 | GGB | 37.1 | GGB | 11783.55 | GGB | 11783.7 | 2335.71 | 2335.71 |  |  |  | 0 | 1 | [14 empty] | 78.7264
18.09.2007 01:00 | 3600 | 2 | 755.14 | GNB | 764.469 | 767.602 | 761.538 | 254.01 | GGB | 10187.7 | GGB | 9.92 | GGB | 989.2 | GGB | 65.48 | GGB | 154742.7 | GGB | 121873.86 | GGB | 0 | 0 | 2355 | 3600 | 2339.42 | GGB | 100 | GGB | 37.21 | GGB | 37.21 | GGB | 11820.75 | GGB | 11820.91 | 2339.42 | 2339.42 |  |  |  | 0 | 1 | [14 empty] | 79.1984
18.09.2007 02:00 | 3600 | 2 | 755.45 | GNB | 764.469 | 767.625 | 761.538 | 253.72 | GGB | 10222.1 | GGB | 9.93 | GGB | 989.73 | GGB | 65.69 | GGB | 154032.98 | GGB | 121304.97 | GGB | 0 | 0 | 2366 | 3600 | 2350.44 | GGB | 100 | GGB | 36.52 | GGB | 36.52 | GGB | 11857.28 | GGB | 11857.43 | 2350.44 | 2350.44 |  |  |  | 0 | 1 | [14 empty] | 79.2
18.09.2007 03:00 | 3600 | 2 | 755.14 | GNB | 763.37 | 768.023 | 761.538 | 255.51 | GGB | 10221.9 | GGB | 9.92 | GGB | 989.74 | GGB | 65.15 | GGB | 156024.59 | GGB | 123071.2 | GGB | 0 | 0 | 2378 | 3600 | 2363.23 | GGB | 100 | GGB | 36.66 | GGB | 36.66 | GGB | 11893.93 | GGB | 11894.09 | 2363.23 | 2363.23 |  |  |  | 0 | 1 | [14 empty] | 80.7904
18.09.2007 04:00 | 3600 | 2 | 755.13 | GNB | 763.37 | 766.758 | 761.538 | 255.09 | GGB | 10282.6 | GGB | 9.92 | GGB | 989.63 | GGB | 65.53 | GGB | 155551.45 | GGB | 122547.78 | GGB | 0 | 0 | 2410 | 3600 | 2395.19 | GGB | 100 | GGB | 36.21 | GGB | 36.21 | GGB | 11930.14 | GGB | 11930.3 | 2395.19 | 2395.19 |  |  |  | 0 | 1 | [14 empty] | 81.5348
18.09.2007 05:00 | 3600 | 2 | 754.9 | GNB | 765.934 | 768.984 | 763.004 | 256.21 | GGB | 10308.4 | GGB | 9.92 | GGB | 989 | GGB | 65.24 | GGB | 156892.76 | GGB | 123631.98 | GGB | 0 | 0 | 2427 | 3600 | 2411.36 | GGB | 100 | GGB | 36.95 | GGB | 36.95 | GGB | 11967.09 | GGB | 11967.25 | 2411.36 | 2411.36 |  |  |  | 0 | 1 | [14 empty] | 82.8114
18.09.2007 06:00 | 3600 | 2 | 754.74 | GNB | 764.835 | 768.047 | 763.004 | 257.37 | GGB | 10327.2 | GGB | 9.92 | GGB | 988.67 | GGB | 64.53 | GGB | 158298.99 | GGB | 124961.74 | GGB | 0 | 0 | 2435 | 3600 | 2419.54 | GGB | 100 | GGB | 37.82 | GGB | 37.82 | GGB | 12004.91 | GGB | 12005.07 | 2419.54 | 2419.54 |  |  |  | 0 | 1 | [14 empty] | 83.9861
18.09.2007 07:00 | 3600 | 2 | 754.72 | GNB | 765.934 | 767.953 | 762.637 | 255.66 | GGB | 10328.2 | GGB | 9.92 | GGB | 988.28 | GGB | 64.9 | GGB | 156706.8 | GGB | 123520.64 | GGB | 0 | 0 | 2443 | 3600 | 2427.57 | GGB | 100 | GGB | 37.04 | GGB | 37.04 | GGB | 12041.95 | GGB | 12042.11 | 2427.57 | 2427.57 |  |  |  | 0 | 1 | [14 empty] | 83.2931
18.09.2007 08:00 | 3600 | 2 | 755.11 | GNB | 765.934 | 769.242 | 764.102 | 256.5 | GGB | 10315.5 | GGB | 9.93 | GGB | 987.94 | GGB | 64.25 | GGB | 158031.61 | GGB | 124761.34 | GGB | 0 | 0 | 2410 | 3600 | 2394.37 | GGB | 100 | GGB | 36.88 | GGB | 36.88 | GGB | 12078.83 | GGB | 12078.99 | 2394.37 | 2394.37 |  |  |  | 0 | 1 | [14 empty] | 82.9791
18.09.2007 09:00 | 3600 | 2 | 755.69 | GNB | 765.934 | 769.172 | 764.102 | 254.7 | GGB | 10264.1 | GGB | 9.93 | GGB | 987.67 | GGB | 64.01 | GGB | 156713.4 | GGB | 123772.5 | GGB | 0 | 0 | 2363 | 3600 | 2347.54 | GGB | 100 | GGB | 36.8 | GGB | 36.8 | GGB | 12115.63 | GGB | 12115.79 | 2347.54 | 2347.54 |  |  |  | 0 | 1 | [14 empty] | 80.7114
18.09.2007 10:00 | 3600 | 2 | 755.88 | GNB | 767.033 | 771.445 | 766.3 | 252.04 | GGB | 10264.5 | GGB | 9.93 | GGB | 987.52 | GGB | 64.83 | GGB | 154403.79 | GGB | 121635.71 | GGB | 0 | 0 | 2350 | 3600 | 2334.47 | GGB | 100 | GGB | 36.46 | GGB | 36.46 | GGB | 12152.09 | GGB | 12152.25 | 2334.47 | 2334.47 |  |  |  | 0 | 1 | [14 empty] | 78.8764
18.09.2007 11:00 | 3600 | 2 | 757.19 | GGB | 767.033 | 770.391 | 765.201 | 251.41 | GGB | 10234.8 | GGB | 9.93 | GGB | 987.16 | GGB | 65.5 | GGB | 154413.7 | GGB | 121356.97 | GNB | 0 | 0 | 2281 | 3600 | 2265.47 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 12190.2 | GGB | 12190.35 | 2265.47 | 2265.47 |  |  |  | 1 | 1 |  |  |  |  | 121356.97 | 2265.47 |  |  | 7.216 | [5 empty] | 76.3696
18.09.2007 12:00 | 3600 | 2 | 757.57 | GGB | 767.033 | 771.398 | 765.201 | 250.75 | GGB | 10132.8 | GGB | 9.93 | GGB | 986.51 | GGB | 65.61 | GGB | 154200.23 | GGB | 121070.88 | GNB | 0 | 0 | 2214 | 3600 | 2198.95 | GNB | 100 | GGB | 36.32 | GGB | 36.32 | GGB | 12226.52 | GGB | 12226.67 | 2198.95 | 2198.95 |  |  |  | 1 | 1 |  |  |  |  | 121070.88 | 2198.95 |  |  | 7.3301 | [5 empty] | 73.9524
18.09.2007 13:00 | 3600 | 2 | 757.72 | GGB | 767.033 | 771.469 | 765.201 | 249.29 | GGB | 10100.9 | GGB | 9.93 | GGB | 985.57 | GGB | 65.9 | GGB | 152888.63 | GGB | 119823.08 | GNB | 0 | 0 | 2187 | 3600 | 2172.07 | GNB | 100 | GGB | 36.09 | GGB | 36.09 | GGB | 12262.61 | GGB | 12262.76 | 2172.07 | 2172.07 |  |  |  | 1 | 1 |  |  |  |  | 119823.08 | 2172.07 |  |  | 7.2115 | [5 empty] | 72.2956
18.09.2007 14:00 | 3600 | 2 | 757.63 | GGB | 765.934 | 770.32 | 764.102 | 247.18 | GGB | 10077.1 | GGB | 9.93 | GGB | 984.21 | GGB | 66.93 | GGB | 150672.55 | GGB | 117568.67 | GNB | 0 | 0 | 2186 | 3600 | 2170.81 | GNB | 100 | GGB | 36.58 | GGB | 36.58 | GGB | 12299.19 | GGB | 12299.34 | 2170.81 | 2170.81 |  |  |  | 1 | 1 |  |  |  |  | 117568.67 | 2170.81 |  |  | 6.977 | [5 empty] | 70.8942
18.09.2007 15:00 | 3600 | 2 | 757.77 | GGB | 767.033 | 771.398 | 765.201 | 246.27 | GGB | 10038.4 | GGB | 9.93 | GGB | 983.04 | GGB | 67.3 | GGB | 149643.73 | GGB | 116499.82 | GNB | 0 | 0 | 2169 | 3600 | 2154.17 | GNB | 100 | GGB | 35.68 | GGB | 35.68 | GGB | 12334.86 | GGB | 12335.02 | 2154.17 | 2154.17 |  |  |  | 1 | 1 |  |  |  |  | 116499.82 | 2154.17 |  |  | 7.0336 | [5 empty] | 69.7112
18.09.2007 16:00 | 3600 | 2 | 757.59 | GGB | 765.934 | 771.117 | 764.102 | 245.48 | GGB | 9989.72 | GGB | 9.92 | GGB | 981.87 | GGB | 67.58 | GGB | 148687.54 | GGB | 115519.68 | GNB | 0 | 0 | 2165 | 3600 | 2149.83 | GNB | 100 | GGB | 35.69 | GGB | 35.69 | GGB | 12370.55 | GGB | 12370.71 | 2149.83 | 2149.83 |  |  |  | 1 | 1 |  |  |  |  | 115519.68 | 2149.83 |  |  | 6.9585 | [5 empty] | 68.9855
18.09.2007 17:00 | 3600 | 2 | 757.5 | GGB | 767.033 | 771.234 | 765.201 | 245.17 | GGB | 9972.13 | GGB | 9.92 | GGB | 980.6 | GGB | 67.68 | GGB | 148070.25 | GGB | 114860.89 | GNB | 0 | 0 | 2167 | 3600 | 2151.75 | GNB | 100 | GGB | 35.28 | GGB | 35.28 | GGB | 12405.83 | GGB | 12405.99 | 2151.75 | 2151.75 |  |  |  | 1 | 1 |  |  |  |  | 114860.89 | 2151.75 |  |  | 7.0054 | [5 empty] | 68.6533
18.09.2007 18:00 | 3600 | 2 | 757.34 | GGB | 767.033 | 771.281 | 765.201 | 245.5 | GGB | 9968.42 | GGB | 9.92 | GGB | 979.86 | GGB | 67.6 | GGB | 147899.7 | GGB | 114665.94 | GNB | 0 | 0 | 2180 | 3600 | 2164.61 | GNB | 100 | GGB | 35.67 | GGB | 35.67 | GGB | 12441.49 | GGB | 12441.66 | 2164.61 | 2164.61 |  |  |  | 1 | 1 |  |  |  |  | 114665.94 | 2164.61 |  |  | 6.9584 | [5 empty] | 68.9464
18.09.2007 19:00 | 3600 | 2 | 757.18 | GGB | 765.934 | 770.273 | 764.102 | 247.5 | GGB | 9964.07 | GGB | 9.92 | GGB | 978.6 | GGB | 66.87 | GGB | 149871.5 | GGB | 116297.17 | GNB | 0 | 0 | 2188 | 3600 | 2173.32 | GNB | 100 | GGB | 35.87 | GGB | 35.87 | GGB | 12477.37 | GGB | 12477.53 | 2173.32 | 2173.32 |  |  |  | 1 | 1 |  |  |  |  | 116297.17 | 2173.32 |  |  | 7.0463 | [5 empty] | 70.2086
18.09.2007 20:00 | 3600 | 2 | 756.84 | GGB | 765.934 | 770.273 | 764.102 | 247.5 | GGB | 10047.6 | GGB | 9.92 | GGB | 978.35 | GGB | 67 | GGB | 149245.41 | GGB | 115737.35 | GNB | 0 | 0 | 2248 | 3600 | 2232.81 | GGB | 100 | GGB | 35.57 | GGB | 35.57 | GGB | 12512.94 | GGB | 12513.1 | 2232.81 | 2232.81 |  |  |  | 1 | 1 |  |  |  |  | 115737.35 | 2232.81 |  |  | 7.2651 | [5 empty] | 71.7832
18.09.2007 21:00 | 3600 | 2 | 757.03 | GGB | 767.033 | 771.492 | 765.201 | 248.21 | GGB | 10062.1 | GGB | 9.92 | GGB | 978.97 | GGB | 66.89 | GGB | 150005.74 | GGB | 116438.14 | GNB | 0 | 0 | 2243 | 3600 | 2227.84 | GGB | 100 | GGB | 35.9 | GGB | 35.9 | GGB | 12548.84 | GGB | 12549 | 2227.84 | 2227.84 |  |  |  | 1 | 1 |  |  |  |  | 116438.14 | 2227.84 |  |  | 7.2258 | [5 empty] | 72.0571
18.09.2007 22:00 | 3600 | 2 | 756.33 | GGB | 763.37 | 767.391 | 762.271 | 249.47 | GGB | 10068.7 | GGB | 9.91 | GGB | 979.37 | GGB | 65.22 | GGB | 152315.35 | GGB | 118862.19 | GNB | 0 | 0 | 2252 | 3600 | 2237.14 | GGB | 100 | GGB | 36.01 | GGB | 36.01 | GGB | 12584.85 | GGB | 12585.01 | 2237.14 | 2237.14 |  |  |  | 0 | 1 | [14 empty] | 73.8643
18.09.2007 23:00 | 3600 | 2 | 755.91 | GNB | 765.934 | 769.758 | 763.37 | 252.28 | GGB | 10234 | GGB | 9.93 | GGB | 980.36 | GGB | 63.4 | GGB | 154435.7 | GGB | 121291.75 | GGB | 0 | 0 | 2359 | 3600 | 2343.87 | GGB | 100 | GGB | 35 | GGB | 35 | GGB | 12619.84 | GGB | 12620.01 | 2343.87 | 2343.87 |  |  |  | 0 | 1 | [14 empty] | 78.97
18.09.2007 24:00 | 3600 | 2 | 755.44 | GNB | 764.835 | 768.398 | 763.37 | 252.33 | GGB | 10251.9 | GGB | 9.92 | GGB | 980.93 | GGB | 65.43 | GGB | 153863.53 | GGB | 120187.38 | GGB | 0 | 0 | 2396 | 3600 | 2381.1 | GGB | 100 | GGB | 35.08 | GGB | 35.08 | GGB | 12654.93 | GGB | 12655.09 | 2381.1 | 2381.1 |  |  |  | 0 | 1 | [14 empty] | 79.4939
19.09.2007 01:00 | 3600 | 2 | 755.33 | GNB | 763.37 | 768.398 | 762.271 | 252.35 | GGB | 10267 | GGB | 9.92 | GGB | 981.04 | GGB | 64.91 | GGB | 154106.7 | GGB | 120576.04 | GGB | 0 | 0 | 2404 | 3600 | 2388.45 | GGB | 100 | GGB | 35.55 | GGB | 35.55 | GGB | 12690.47 | GGB | 12690.64 | 2388.45 | 2388.45 |  |  |  | 0 | 1 | [14 empty] | 79.9972
19.09.2007 02:00 | 3600 | 2 | 754.92 | GNB | 764.469 | 768.258 | 762.271 | 253.5 | GGB | 10325.2 | GGB | 9.92 | GGB | 981.46 | GGB | 63.95 | GGB | 155621.87 | GGB | 122160.45 | GGB | 0 | 0 | 2434 | 3600 | 2418.96 | GGB | 100 | GGB | 37 | GGB | 37 | GGB | 12727.47 | GGB | 12727.64 | 2418.96 | 2418.96 |  |  |  | 0 | 1 | [14 empty] | 82.0837
19.09.2007 03:00 | 3600 | 2 | 755.37 | GNB | 764.469 | 768.258 | 762.271 | 255.18 | GGB | 10413.2 | GGB | 9.92 | GGB | 982.16 | GGB | 62.9 | GGB | 157714.71 | GGB | 124280.78 | GGB | 0 | 0 | 2447 | 3600 | 2431.6 | GGB | 100 | GGB | 35.67 | GGB | 35.67 | GGB | 12763.14 | GGB | 12763.31 | 2431.6 | 2431.6 |  |  |  | 0 | 1 | [14 empty] | 83.9448
19.09.2007 04:00 | 3600 | 2 | 755.46 | GNB | 764.469 | 768.188 | 763.37 | 256.02 | GGB | 10441.5 | GGB | 9.92 | GGB | 983.06 | GGB | 63.6 | GGB | 158937.19 | GGB | 125094.38 | GGB | 0 | 0 | 2447 | 3600 | 2431.66 | GGB | 100 | GGB | 37.28 | GGB | 37.28 | GGB | 12800.42 | GGB | 12800.59 | 2431.66 | 2431.66 |  |  |  | 0 | 1 | [14 empty] | 84.4964
19.09.2007 05:00 | 3600 | 2 | 755.26 | GNB | 764.469 | 768.141 | 762.271 | 256.99 | GGB | 10481.4 | GGB | 9.92 | GGB | 984.03 | GGB | 63.19 | GGB | 160291.7 | GGB | 126440.21 | GGB | 0 | 0 | 2461 | 3600 | 2446.11 | GGB | 100 | GGB | 36.74 | GGB | 36.74 | GGB | 12837.16 | GGB | 12837.33 | 2446.11 | 2446.11 |  |  |  | 0 | 1 | [14 empty] | 85.913
19.09.2007 06:00 | 3600 | 2 | 755.09 | GNB | 764.469 | 768.141 | 763.37 | 258.52 | GGB | 10547.9 | GGB | 9.92 | GGB | 985.12 | GGB | 62.55 | GGB | 161977.42 | GGB | 128157.08 | GGB | 0 | 0 | 2484 | 3600 | 2468.8 | GGB | 100 | GGB | 37.2 | GGB | 37.2 | GGB | 12874.37 | GGB | 12874.53 | 2468.8 | 2468.8 |  |  |  | 0 | 1 | [14 empty] | 87.8873
19.09.2007 07:00 | 3600 | 2 | 755.06 | GNB | 763.37 | 767.039 | 762.271 | 259.25 | GGB | 10561.9 | GGB | 9.92 | GGB | 985.95 | GGB | 62.36 | GGB | 163133.87 | GGB | 129252.31 | GGB | 0 | 0 | 2487 | 3600 | 2471.74 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 12912.45 | GGB | 12912.61 | 2471.74 | 2471.74 |  |  |  | 0 | 1 | [14 empty] | 88.7439
19.09.2007 08:00 | 3600 | 2 | 755.17 | GNB | 763.37 | 766.922 | 761.172 | 261.04 | GGB | 10577.6 | GGB | 9.92 | GGB | 986.57 | GGB | 61.28 | GGB | 165633.84 | GGB | 131741.72 | GGB | 0 | 0 | 2469 | 3600 | 2453.89 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 12949.41 | GGB | 12949.57 | 2453.89 | 2453.89 |  |  |  | 0 | 1 | [14 empty] | 89.7999
19.09.2007 09:00 | 3600 | 2 | 755.38 | GNB | 764.469 | 767.672 | 762.271 | 260.42 | GGB | 10641.9 | GGB | 9.93 | GGB | 987.4 | GGB | 61.73 | GGB | 164846 | GGB | 131046.85 | GGB | 0 | 0 | 2495 | 3600 | 2479.56 | GGB | 100 | GGB | 37.64 | GGB | 37.64 | GGB | 12987.05 | GGB | 12987.21 | 2479.56 | 2479.56 |  |  |  | 0 | 1 | [14 empty] | 90.2607
19.09.2007 10:00 | 3600 | 2 | 755.27 | GNB | 764.835 | 768.938 | 763.37 | 259.64 | GGB | 10644.7 | GGB | 9.93 | GGB | 987.99 | GGB | 61.8 | GGB | 164344.25 | GGB | 130699.78 | GGB | 0 | 0 | 2504 | 3600 | 2488.46 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 13025.05 | GGB | 13025.21 | 2488.46 | 2488.46 |  |  |  | 0 | 1 | [14 empty] | 90.3448
19.09.2007 11:00 | 3600 | 2 | 754.98 | GNB | 764.835 | 767.906 | 763.37 | 259.8 | GGB | 10601.7 | GGB | 9.92 | GGB | 988.59 | GGB | 61.56 | GGB | 164643.54 | GGB | 131111.56 | GGB | 0 | 0 | 2481 | 3600 | 2466.03 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 13062.61 | GGB | 13062.76 | 2466.03 | 2466.03 |  |  |  | 0 | 1 | [14 empty] | 89.8125
19.09.2007 12:00 | 3600 | 2 | 755.73 | GNB | 765.934 | 768.141 | 763.37 | 260.2 | GGB | 10582.2 | GGB | 9.93 | GGB | 989.3 | GGB | 61.23 | GGB | 165395.07 | GGB | 131934.18 | GGB | 0 | 0 | 2434 | 3600 | 2418.46 | GGB | 100 | GGB | 37.72 | GGB | 37.72 | GGB | 13100.33 | GGB | 13100.48 | 2418.46 | 2418.46 |  |  |  | 0 | 1 | [14 empty] | 88.6326
19.09.2007 13:00 | 3600 | 2 | 756.22 | GGB | 765.934 | 769.359 | 763.37 | 259.68 | GGB | 10598.8 | GGB | 9.93 | GGB | 990.61 | GGB | 61.19 | GGB | 164808.59 | GGB | 131656 | GGB | 0 | 0 | 2418 | 3600 | 2402.71 | GGB | 100 | GGB | 37.82 | GGB | 37.82 | GGB | 13138.14 | GGB | 13138.3 | 2402.71 | 2402.71 |  |  |  | 1 | 1 |  |  |  |  | 131656 | 2402.71 | 131656 | 2402.71 | 8.3641 | [5 empty] | 87.8698
19.09.2007 14:00 | 3600 | 2 | 755.78 | GNB | 765.934 | 770.016 | 764.469 | 258.86 | GGB | 10578.1 | GGB | 9.92 | GGB | 991.83 | GGB | 62.35 | GGB | 162840.08 | GGB | 129792.15 | GGB | 0 | 0 | 2441 | 3600 | 2425.48 | GGB | 100 | GGB | 37.08 | GGB | 37.08 | GGB | 13175.22 | GGB | 13175.38 | 2425.48 | 2425.48 |  |  |  | 0 | 1 | [14 empty] | 87.4467
19.09.2007 15:00 | 3600 | 2 | 756.26 | GGB | 765.934 | 769.195 | 764.469 | 259.33 | GGB | 10576.5 | GGB | 9.92 | GGB | 993.15 | GGB | 62.78 | GGB | 162779.57 | GGB | 129750.67 | GGB | 0 | 0 | 2430 | 3600 | 2414.53 | GGB | 100 | GGB | 37.63 | GGB | 37.63 | GGB | 13212.85 | GGB | 13213.01 | 2414.53 | 2414.53 |  |  |  | 1 | 1 |  |  |  |  | 129750.67 | 2414.53 | 129750.67 | 2414.53 | 8.3255 | [5 empty] | 87.0241
19.09.2007 16:00 | 3600 | 2 | 755.99 | GNB | 767.033 | 770.297 | 765.934 | 260.15 | GGB | 10585.8 | GGB | 9.92 | GGB | 994.29 | GGB | 63.11 | GGB | 163143.78 | GGB | 130063.17 | GGB | 0 | 0 | 2444 | 3600 | 2428.7 | GGB | 100 | GGB | 37.73 | GGB | 37.73 | GGB | 13250.57 | GGB | 13250.74 | 2428.7 | 2428.7 |  |  |  | 0 | 1 | [14 empty] | 87.7457
19.09.2007 17:00 | 3600 | 2 | 756.2 | GGB | 765.934 | 770.344 | 764.102 | 262.76 | GGB | 10605.8 | GGB | 9.92 | GGB | 995.19 | GGB | 62.39 | GGB | 165665.75 | GGB | 132475.33 | GGB | 0 | 0 | 2440 | 3600 | 2424.73 | GGB | 100 | GGB | 37.29 | GGB | 37.29 | GGB | 13287.87 | GGB | 13288.03 | 2424.73 | 2424.73 |  |  |  | 1 | 1 |  |  |  |  | 132475.33 | 2424.73 | 132475.33 | 2424.73 | 8.614 | [5 empty] | 89.2269
19.09.2007 18:00 | 3600 | 2 | 756.17 | GGB | 765.934 | 770.273 | 764.102 | 263.45 | GGB | 10646.6 | GGB | 9.92 | GGB | 996.12 | GGB | 62.56 | GGB | 165841.81 | GGB | 132674.86 | GGB | 0 | 0 | 2465 | 3600 | 2450.21 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 13325.78 | GGB | 13325.94 | 2450.21 | 2450.21 |  |  |  | 1 | 1 |  |  |  |  | 132674.86 | 2450.21 | 132674.86 | 2450.21 | 8.5751 | [5 empty] | 90.3004
19.09.2007 19:00 | 3600 | 2 | 756.38 | GGB | 765.934 | 769.477 | 764.102 | 262.29 | GGB | 10654.9 | GGB | 9.92 | GGB | 997.26 | GGB | 63.1 | GGB | 164466.38 | GGB | 131511.62 | GGB | 0 | 0 | 2470 | 3600 | 2455.08 | GGB | 100 | GGB | 37.73 | GGB | 37.73 | GGB | 13363.5 | GGB | 13363.67 | 2455.08 | 2455.08 |  |  |  | 1 | 1 |  |  |  |  | 131511.62 | 2455.08 | 131511.62 | 2455.08 | 8.5574 | [5 empty] | 89.6865
19.09.2007 20:00 | 3600 | 2 | 756.21 | GGB | 765.934 | 769.453 | 764.102 | 263.08 | GGB | 10675.7 | GGB | 9.92 | GGB | 998.12 | GGB | 63.11 | GGB | 165070.47 | GGB | 132106.8 | GGB | 0 | 0 | 2488 | 3600 | 2473.22 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 13401.31 | GGB | 13401.48 | 2473.22 | 2473.22 |  |  |  | 1 | 1 |  |  |  |  | 132106.8 | 2473.22 | 132106.8 | 2473.22 | 8.6413 | [5 empty] | 90.7581
19.09.2007 21:00 | 3600 | 2 | 755.69 | GNB | 765.934 | 768.469 | 764.102 | 264.5 | GGB | 10720.1 | GGB | 9.91 | GGB | 999.17 | GGB | 62.84 | GGB | 166078.38 | GGB | 133158.68 | GGB | 0 | 0 | 2523 | 3600 | 2507.87 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 13439.66 | GGB | 13439.82 | 2507.87 | 2507.87 |  |  |  | 0 | 1 | [14 empty] | 92.7624
19.09.2007 22:00 | 3600 | 2 | 755.66 | GNB | 764.469 | 768.281 | 762.637 | 265.96 | GGB | 10763.5 | GGB | 9.92 | GGB | 1000.39 | GGB | 62.62 | GGB | 167204.02 | GGB | 134313.42 | GGB | 0 | 0 | 2554 | 3600 | 2538.37 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 13477.47 | GGB | 13477.63 | 2538.37 | 2538.37 |  |  |  | 0 | 1 | [14 empty] | 94.7048
19.09.2007 23:00 | 3600 | 2 | 755.41 | GNB | 763.37 | 767.156 | 761.538 | 266.64 | GGB | 10809.2 | GGB | 9.92 | GGB | 1001.29 | GGB | 62.17 | GGB | 168266.95 | GGB | 135470.45 | GGB | 0 | 0 | 2582 | 3600 | 2566.99 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 13514.74 | GGB | 13514.9 | 2566.99 | 2566.99 |  |  |  | 0 | 1 | [14 empty] | 96.5976
19.09.2007 24:00 | 3600 | 2 | 755.21 | GNB | 764.469 | 767.555 | 762.637 | 268.09 | GGB | 10841.8 | GGB | 9.92 | GGB | 1002.05 | GGB | 62.01 | GGB | 169129.61 | GGB | 136336.4 | GGB | 0 | 0 | 2612 | 3600 | 2596.65 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 13553.08 | GGB | 13553.24 | 2596.65 | 2596.65 |  |  |  | 0 | 1 | [14 empty] | 98.3383
20.09.2007 01:00 | 3600 | 2 | 755.22 | GNB | 764.469 | 767.555 | 762.637 | 269.05 | GGB | 10874.2 | GGB | 9.92 | GGB | 1002.95 | GGB | 61.9 | GGB | 170049.5 | GGB | 137245.19 | GGB | 0 | 0 | 2624 | 3600 | 2608.21 | GGB | 100 | GGB | 37.61 | GGB | 37.61 | GGB | 13590.69 | GGB | 13590.85 | 2608.21 | 2608.21 |  |  |  | 0 | 1 | [14 empty] | 99.4345
20.09.2007 02:00 | 3600 | 2 | 755.59 | GNB | 764.835 | 768.82 | 763.004 | 270.91 | GGB | 10874.9 | GGB | 9.92 | GGB | 1003.38 | GGB | 61.04 | GGB | 172476.84 | GGB | 139620.52 | GGB | 0 | 0 | 2608 | 3600 | 2592.26 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 13631.32 | GGB | 13631.49 | 2592.26 | 2592.26 |  |  |  | 0 | 1 | [14 empty] | 100.5369
20.09.2007 03:00 | 3600 | 2 | 756.25 | GGB | 764.469 | 767.789 | 762.271 | 270.11 | GGB | 10927.6 | GGB | 9.93 | GGB | 1003.96 | GGB | 61.22 | GGB | 171642.79 | GGB | 138949.97 | GGB | 0 | 0 | 2605 | 3600 | 2589.5 | GGB | 100 | GGB | 37.64 | GGB | 37.64 | GGB | 13668.96 | GGB | 13669.13 | 2589.5 | 2589.5 |  |  |  | 1 | 1 |  |  |  |  | 138949.97 | 2589.5 | 138949.97 | 2589.5 | 9.5593 | [5 empty] | 99.9475
20.09.2007 04:00 | 3600 | 2 | 755.35 | GNB | 764.469 | 767.766 | 763.37 | 270.41 | GGB | 10948.8 | GGB | 9.92 | GGB | 1004.1 | GGB | 61.2 | GGB | 171887.06 | GGB | 139176.41 | GGB | 0 | 0 | 2651 | 3600 | 2635.91 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 13708.59 | GGB | 13708.75 | 2635.91 | 2635.91 |  |  |  | 0 | 1 | [14 empty] | 101.9046
20.09.2007 05:00 | 3600 | 2 | 755.96 | GNB | 764.835 | 768.773 | 763.37 | 270.21 | GGB | 10963.5 | GGB | 9.93 | GGB | 1004.25 | GGB | 61.21 | GGB | 171883.76 | GGB | 139191.26 | GGB | 0 | 0 | 2632 | 3600 | 2616.97 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 13747.94 | GGB | 13748.1 | 2616.97 | 2616.97 |  |  |  | 0 | 1 | [14 empty] | 101.1832
20.09.2007 06:00 | 3600 | 2 | 755.69 | GNB | 764.835 | 768.773 | 762.271 | 270.28 | GGB | 10956.4 | GGB | 9.92 | GGB | 1004.51 | GGB | 61.22 | GGB | 171680.2 | GGB | 139057.31 | GGB | 0 | 0 | 2637 | 3600 | 2621.41 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 13786.53 | GGB | 13786.69 | 2621.41 | 2621.41 |  |  |  | 0 | 1 | [14 empty] | 101.2573
20.09.2007 07:00 | 3600 | 2 | 756.04 | GGB | 764.835 | 768.82 | 763.37 | 270.02 | GGB | 10956.6 | GGB | 9.93 | GGB | 1004.57 | GGB | 61.32 | GGB | 171420.52 | GGB | 138815.45 | GGB | 0 | 0 | 2629 | 3600 | 2614.11 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 13826.25 | GGB | 13826.41 | 2614.11 | 2614.11 |  |  |  | 1 | 1 |  |  |  |  | 138815.45 | 2614.11 | 138815.45 | 2614.11 | 9.1359 | [5 empty] | 100.7997
20.09.2007 08:00 | 3600 | 2 | 755.69 | GNB | 767.033 | 770.344 | 765.934 | 270.39 | GGB | 10912.7 | GGB | 9.92 | GGB | 1004.54 | GGB | 61.03 | GGB | 172052.11 | GGB | 139440.84 | GGB | 0 | 0 | 2617 | 3600 | 2601.91 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 13866.61 | GGB | 13866.77 | 2601.91 | 2601.91 |  |  |  | 0 | 1 | [14 empty] | 100.7813
20.09.2007 09:00 | 3600 | 2 | 757.14 | GGB | 765.934 | 769.242 | 764.835 | 269.65 | GGB | 10874.9 | GGB | 9.94 | GGB | 1004.44 | GGB | 60.97 | GGB | 171400.71 | GGB | 138927.57 | GGB | 0 | 0 | 2532 | 3600 | 2516.6 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 13905.4 | GGB | 13905.56 | 2516.6 | 2516.6 |  |  |  | 1 | 1 |  |  |  |  | 138927.57 | 2516.6 | 138927.57 | 2516.6 | 9.0133 | [5 empty] | 97.1181
20.09.2007 10:00 | 3600 | 2 | 757.2 | GGB | 765.934 | 769.383 | 764.469 | 266.5 | GGB | 10847.7 | GGB | 9.94 | GGB | 1004.43 | GGB | 62.05 | GGB | 167739.89 | GGB | 135520.28 | GGB | 0 | 0 | 2524 | 3600 | 2509.18 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 13944.25 | GGB | 13944.41 | 2509.18 | 2509.18 |  |  |  | 1 | 1 |  |  |  |  | 135520.28 | 2509.18 | 135520.28 | 2509.18 | 8.7528 | [5 empty] | 94.4569
20.09.2007 11:00 | 3600 | 2 | 756.85 | GGB | 765.934 | 769.57 | 764.835 | 265.38 | GGB | 10787.3 | GGB | 9.93 | GGB | 1004.42 | GGB | 62.67 | GGB | 166431.59 | GGB | 134213.99 | GGB | 0 | 0 | 2517 | 3600 | 2501.74 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 13983.11 | GGB | 13983.27 | 2501.74 | 2501.74 |  |  |  | 1 | 1 |  |  |  |  | 134213.99 | 2501.74 | 134213.99 | 2501.74 | 8.6405 | [5 empty] | 93.269
20.09.2007 12:00 | 3600 | 2 | 757.5 | GGB | 765.934 | 769.523 | 764.835 | 263.55 | GGB | 10715.1 | GGB | 9.94 | GGB | 1004.32 | GGB | 63.18 | GGB | 164680.95 | GGB | 132584.56 | GGB | 0 | 0 | 2449 | 3600 | 2433.69 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 14021.55 | GGB | 14021.71 | 2433.69 | 2433.69 |  |  |  | 1 | 1 |  |  |  |  | 132584.56 | 2433.69 | 132584.56 | 2433.69 | 8.3941 | [5 empty] | 89.6305
20.09.2007 13:00 | 3600 | 2 | 757.92 | GGB | 765.934 | 770.578 | 764.835 | 262.33 | GGB | 10651.1 | GGB | 9.94 | GGB | 1004.27 | GGB | 63.59 | GGB | 163314.33 | GGB | 131321.09 | GGB | 0 | 0 | 2398 | 3600 | 2382.46 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 14059.67 | GGB | 14059.84 | 2382.46 | 2382.46 |  |  |  | 1 | 1 |  |  |  |  | 131321.09 | 2382.46 | 131321.09 | 2382.46 | 8.2053 | [5 empty] | 86.9076
20.09.2007 14:00 | 3600 | 2 | 757.65 | GGB | 768.132 | 771.727 | 767.033 | 261.36 | GGB | 10574.4 | GGB | 9.93 | GGB | 1004.22 | GGB | 64.25 | GGB | 161907 | GGB | 129925.43 | GGB | 0 | 0 | 2385 | 3600 | 2370.01 | GGB | 100 | GGB | 37.92 | GGB | 37.92 | GGB | 14097.59 | GGB | 14097.76 | 2370.01 | 2370.01 |  |  |  | 1 | 1 |  |  |  |  | 129925.43 | 2370.01 | 129925.43 | 2370.01 | 8.1204 | [5 empty] | 85.5346
20.09.2007 15:00 | 3600 | 2 | 757.62 | GGB | 767.033 | 770.813 | 764.835 | 260.67 | GGB | 10505.6 | GGB | 9.92 | GGB | 1003.57 | GGB | 64.83 | GGB | 160863.88 | GGB | 128784.5 | GGB | 0 | 0 | 2352 | 3600 | 2337.35 | GGB | 100 | GGB | 37.78 | GGB | 37.78 | GGB | 14135.37 | GGB | 14135.54 | 2337.35 | 2337.35 |  |  |  | 1 | 1 |  |  |  |  | 128784.5 | 2337.35 | 128784.5 | 2337.35 | 7.9676 | [5 empty] | 83.6151
20.09.2007 16:00 | 3600 | 2 | 757.73 | GGB | 765.934 | 770.672 | 764.835 | 260.91 | GGB | 10476.3 | GGB | 9.92 | GGB | 1003.06 | GGB | 64.79 | GGB | 161176.37 | GGB | 128985.44 | GGB | 0 | 0 | 2331 | 3600 | 2315.87 | GGB | 100 | GGB | 37.5 | GGB | 37.5 | GGB | 14172.86 | GGB | 14173.04 | 2315.87 | 2315.87 |  |  |  | 1 | 1 |  |  |  |  | 128985.44 | 2315.87 | 128985.44 | 2315.87 | 7.9657 | [5 empty] | 82.976
20.09.2007 17:00 | 3600 | 2 | 758.09 | GGB | 768.132 | 772.711 | 767.033 | 261.73 | GGB | 10469.5 | GGB | 9.93 | GGB | 1003.34 | GGB | 64.66 | GGB | 162004.93 | GGB | 129731.41 | GGB | 0 | 0 | 2311 | 3600 | 2296.38 | GGB | 100 | GGB | 37.84 | GGB | 37.84 | GGB | 14210.7 | GGB | 14210.88 | 2296.38 | 2296.38 |  |  |  | 1 | 1 |  |  |  |  | 129731.41 | 2296.38 | 129731.41 |  | 7.873 | [5 empty] | 82.7535
20.09.2007 18:00 | 3600 | 2 | 757.78 | GGB | 767.033 | 771.609 | 765.934 | 260.7 | GGB | 10493.8 | GGB | 9.92 | GGB | 1002.94 | GGB | 64.84 | GGB | 157389.01 | GGB | 125919.14 | GGB | 0 | 0 | 2336 | 3600 | 2320.59 | GGB | 100 | GGB | 37.29 | GGB | 37.29 | GGB | 14247.99 | GGB | 14248.17 | 2320.59 | 2320.59 |  |  |  | 1 | 1 |  |  |  |  | 125919.14 | 2320.59 | 125919.14 | 2320.59 | 7.8361 | [5 empty] | 81.1685
20.09.2007 19:00 | 3600 | 2 | 757.1 | GGB | 765.934 | 770.508 | 765.934 | 262.18 | GGB | 10534.6 | GGB | 9.91 | GGB | 1002.92 | GGB | 64.64 | GGB | 157579.37 | GGB | 126143.58 | GGB | 0 | 0 | 2391 | 3600 | 2375.65 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 14286.07 | GGB | 14286.25 | 2375.65 | 2375.65 |  |  |  | 1 | 1 |  |  |  |  | 126143.58 | 2375.65 | 126143.58 | 2375.65 | 7.8696 | [5 empty] | 83.2425
20.09.2007 20:00 | 3600 | 2 | 756.56 | GGB | 765.934 | 769.57 | 764.469 | 263.97 | GGB | 10583.1 | GGB | 9.91 | GGB | 1003.78 | GGB | 64.34 | GGB | 159056.02 | GGB | 127548.12 | GGB | 0 | 0 | 2440 | 3600 | 2425.32 | GGB | 100 | GGB | 37.84 | GGB | 37.84 | GGB | 14323.91 | GGB | 14324.09 | 2425.32 | 2425.32 |  |  |  | 1 | 1 |  |  |  |  | 127548.12 | 2425.32 | 127548.12 | 2425.32 | 8.1751 | [5 empty] | 85.9292
20.09.2007 21:00 | 3600 | 2 | 757.27 | GGB | 764.835 | 769.336 | 763.37 | 265.47 | GGB | 10664.9 | GGB | 9.92 | GGB | 1004.79 | GGB | 63.95 | GGB | 160732.94 | GGB | 129173.64 | GGB | 0 | 0 | 2453 | 3600 | 2437.34 | GGB | 100 | GGB | 36.01 | GGB | 36.01 | GGB | 14359.92 | GGB | 14360.1 | 2437.34 | 2437.34 |  |  |  | 1 | 1 |  |  |  |  | 129173.64 | 2437.34 | 129173.64 | 2437.34 | 8.7431 | [5 empty] | 87.4556
20.09.2007 22:00 | 3600 | 2 | 756.84 | GGB | 764.835 | 770.391 | 764.102 | 265.82 | GGB | 10720.8 | GGB | 9.93 | GGB | 1005.26 | GGB | 63.48 | GGB | 162441.76 | GGB | 130788.68 | GGB | 0 | 0 | 2485 | 3600 | 2469.85 | GGB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 14398.03 | GGB | 14398.22 | 2469.85 | 2469.85 |  |  |  | 1 | 1 |  |  |  |  | 130788.68 | 2469.85 | 130788.68 | 2469.85 | 8.474 | [5 empty] | 89.7301
20.09.2007 23:00 | 3600 | 2 | 755.94 | GNB | 765.934 | 770.273 | 764.102 | 267.27 | GGB | 10732.3 | GGB | 9.91 | GGB | 1005.45 | GGB | 63.13 | GGB | 163195.49 | GGB | 131558.26 | GGB | 0 | 0 | 2538 | 3600 | 2523.05 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 14436.6 | GGB | 14436.79 | 2523.05 | 2523.05 |  |  |  | 0 | 1 | [14 empty] | 92.2022
20.09.2007 24:00 | 3600 | 2 | 756.36 | GGB | 765.934 | 769.148 | 764.102 | 267.87 | GGB | 10772.8 | GGB | 9.92 | GGB | 1005.87 | GGB | 62.87 | GGB | 163709.35 | GGB | 132129.59 | GGB | 0 | 0 | 2539 | 3600 | 2524.02 | GGB | 100 | GGB | 36.86 | GGB | 36.86 | GGB | 14473.46 | GGB | 14473.65 | 2524.02 | 2524.02 |  |  |  | 1 | 1 |  |  |  |  | 132129.59 | 2524.02 | 132129.59 | 2524.02 | 9.0477 | [5 empty] | 92.6383
21.09.2007 01:00 | 3600 | 2 | 755.81 | GNB | 767.033 | 770.25 | 765.201 | 270.53 | GGB | 10764.3 | GGB | 9.91 | GGB | 1006.41 | GGB | 62.04 | GGB | 165706.46 | GGB | 134146.1 | GGB | 0 | 0 | 2549 | 3600 | 2533.93 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 14512.86 | GGB | 14513.05 | 2533.93 | 2533.93 |  |  |  | 0 | 1 | [14 empty] | 94.4213
21.09.2007 02:00 | 3600 | 2 | 756.56 | GGB | 764.835 | 768.141 | 763.004 | 270.03 | GGB | 10818.8 | GGB | 9.92 | GGB | 1006.64 | GGB | 62.26 | GGB | 164959.33 | GGB | 133483 | GGB | 0 | 0 | 2547 | 3600 | 2531.66 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 14551.03 | GGB | 14551.22 | 2531.66 | 2531.66 |  |  |  | 1 | 1 |  |  |  |  | 133483 | 2531.66 | 133483 | 2531.66 | 8.8534 | [5 empty] | 93.8704
21.09.2007 03:00 | 3600 | 2 | 756.04 | GGB | 765.934 | 770.297 | 764.469 | 271.66 | GGB | 10817.1 | GGB | 9.92 | GGB | 1006.56 | GGB | 61.57 | GGB | 166824.41 | GGB | 135259.22 | GGB | 0 | 0 | 2563 | 3600 | 2547.83 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 14590.28 | GGB | 14590.47 | 2547.83 | 2547.83 |  |  |  | 1 | 1 |  |  |  |  | 135259.22 | 2547.83 | 135259.22 | 2547.83 | 8.7801 | [5 empty] | 95.7271
21.09.2007 04:00 | 3600 | 2 | 756.89 | GGB | 767.033 | 770.25 | 764.835 | 270.94 | GGB | 10848.8 | GGB | 9.93 | GGB | 1006.5 | GGB | 61.58 | GGB | 166488.8 | GGB | 134974.16 | GGB | 0 | 0 | 2546 | 3600 | 2530.39 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 14628.99 | GGB | 14629.18 | 2530.39 | 2530.39 |  |  |  | 1 | 1 |  |  |  |  | 134974.16 | 2530.39 | 134974.16 | 2530.39 | 8.823 | [5 empty] | 94.8715
21.09.2007 05:00 | 3600 | 2 | 755.99 | GNB | 764.835 | 769.055 | 763.37 | 269.92 | GGB | 10868.6 | GGB | 9.92 | GGB | 1006.64 | GGB | 61.96 | GGB | 165411.57 | GGB | 133968.56 | GGB | 0 | 0 | 2593 | 3600 | 2577.39 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 14667.8 | GGB | 14668 | 2577.39 | 2577.39 |  |  |  | 0 | 1 | [14 empty] | 95.9137
21.09.2007 06:00 | 3600 | 2 | 755.78 | GNB | 763.37 | 767.836 | 762.271 | 270.72 | GGB | 10859.6 | GGB | 9.92 | GGB | 1006.73 | GGB | 61.58 | GGB | 166428.29 | GGB | 134956.95 | GGB | 0 | 0 | 2594 | 3600 | 2578.98 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 14706.86 | GGB | 14707.06 | 2578.98 | 2578.98 |  |  |  | 0 | 1 | [14 empty] | 96.6809
21.09.2007 07:00 | 3600 | 2 | 756.74 | GGB | 764.835 | 769.852 | 763.37 | 270.38 | GGB | 10884.1 | GGB | 9.93 | GGB | 1007.05 | GGB | 61.44 | GGB | 166351.26 | GGB | 134994.44 | GGB | 0 | 0 | 2567 | 3600 | 2552.11 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 14745.14 | GGB | 14745.34 | 2552.11 | 2552.11 |  |  |  | 1 | 1 |  |  |  |  | 134994.44 | 2552.11 | 134994.44 | 2552.11 | 9 | [5 empty] | 95.7002
21.09.2007 08:00 | 3600 | 2 | 756.12 | GGB | 765.934 | 769.336 | 764.469 | 269.82 | GGB | 10891.4 | GGB | 9.93 | GGB | 1006.98 | GGB | 61.76 | GGB | 165527.11 | GGB | 134187.64 | GGB | 0 | 0 | 2599 | 3600 | 2583.73 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 14784.41 | GGB | 14784.62 | 2583.73 | 2583.73 |  |  |  | 1 | 1 |  |  |  |  | 134187.64 | 2583.73 | 134187.64 | 2583.73 | 8.8265 | [5 empty] | 96.3068
21.09.2007 09:00 | 3600 | 2 | 756.98 | GGB | 767.033 | 770.25 | 765.934 | 268.85 | GGB | 10872.9 | GGB | 9.94 | GGB | 1007.03 | GGB | 61.96 | GGB | 164413.57 | GGB | 133212.26 | GGB | 0 | 0 | 2555 | 3208 | 2539.31 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 14822.98 | GGB | 14823.19 | 2539.31 | 2539.31 |  |  |  | 1 | 1 |  |  |  |  | 133212.26 | 2539.31 | 133212.26 | 2539.31 | 8.7702 | [5 empty] | 93.9631
21.09.2007 10:00 | 3600 | 2 | 756.39 | GGB | 769.597 | 773.742 | 768.132 | 269.41 | GGB | 10925.8 | GGB | 9.9 | GGB | 1007.03 | GGB | 61.46 | GGB | 167169.91 | GGB | 135645.07 | GGB | 0 | 0 | 2579 | 3600 | 2563.79 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 14862.13 | GGB | 14862.33 | 2563.79 | 2563.79 |  |  |  | 1 | 1 |  |  |  |  | 135645.07 | 2563.79 | 135645.07 | 2563.79 | 8.8852 | [5 empty] | 96.6015
21.09.2007 11:00 | 3600 | 2 | 759.82 | GGB | 769.597 | 773.93 | 768.498 | 269 | GGB | 10990.4 | GGB | 9.94 | GGB | 1006.79 | GGB | 62.08 | GGB | 167769.6 | GGB | 135851.06 | GGB | 0 | 0 | 2432 | 3600 | 2416.35 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 14900.94 | GGB | 14901.14 | 2416.35 | 2416.35 |  |  |  | 1 | 1 |  |  |  |  | 135851.06 | 2416.35 | 135851.06 | 2416.35 | 8.4582 | [5 empty] | 91.1844
21.09.2007 12:00 | 3600 | 2 | 760.13 | GGB | 769.597 | 774.938 | 768.498 | 266.46 | GGB | 10888.7 | GGB | 9.94 | GGB | 1006.45 | GGB | 62.77 | GGB | 165533.71 | GGB | 133717.2 | GGB | 0 | 0 | 2370 | 3600 | 2355.35 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 14940.86 | GGB | 14941.07 | 2355.35 | 2355.35 |  |  |  | 1 | 1 |  |  |  |  | 133717.2 | 2355.35 | 133717.2 | 2355.35 | 7.8876 | [5 empty] | 87.4863
21.09.2007 13:00 | 3600 | 2 | 760.04 | GGB | 769.597 | 774.938 | 768.132 | 264.7 | GGB | 10800.3 | GGB | 9.93 | GGB | 1006.28 | GGB | 63.47 | GGB | 164280.43 | GGB | 132407.51 | GGB | 0 | 0 | 2337 | 3600 | 2321.95 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 14979.8 | GGB | 14980 | 2321.95 | 2321.95 |  |  |  | 1 | 1 |  |  |  |  | 132407.51 | 2321.95 | 132407.51 | 2321.95 | 7.8973 | [5 empty] | 85.401
21.09.2007 14:00 | 3600 | 2 | 759.92 | GGB | 768.498 | 772.805 | 767.033 | 263.54 | GGB | 10732.2 | GGB | 9.93 | GGB | 1006.18 | GGB | 63.77 | GGB | 163085.46 | GGB | 131316.04 | GGB | 0 | 0 | 2316 | 3600 | 2300.58 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 15018.11 | GGB | 15018.31 | 2300.58 | 2300.58 |  |  |  | 1 | 1 |  |  |  |  | 131316.04 | 2300.58 | 131316.04 |  | 7.8857 | [5 empty] | 83.9175
21.09.2007 15:00 | 3600 | 2 | 759.41 | GGB | 769.597 | 773.836 | 768.132 | 263.06 | GGB | 10699.8 | GGB | 9.92 | GGB | 1005.7 | GGB | 64 | GGB | 162416.45 | GGB | 130623.9 | GGB | 0 | 0 | 2321 | 3600 | 2306.37 | GGB | 100 | GGB | 38.26 | GGB | 38.26 | GGB | 15056.37 | GGB | 15056.57 | 2306.37 | 2306.37 |  |  |  | 1 | 1 |  |  |  |  | 130623.9 | 2306.37 | 130623.9 | 2306.37 | 7.8742 | [5 empty] | 83.6853
21.09.2007 16:00 | 3600 | 2 | 760.04 | GGB | 768.498 | 772.758 | 767.033 | 263.51 | GGB | 10688 | GGB | 9.93 | GGB | 1005.66 | GGB | 63.82 | GGB | 162969.92 | GGB | 131133.03 | GGB | 0 | 0 | 2282 | 3600 | 2267.39 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 15094.77 | GGB | 15094.97 | 2267.39 | 2267.39 |  |  |  | 1 | 1 |  |  |  |  | 131133.03 | 2267.39 | 131133.03 |  | 7.743 | [5 empty] | 82.5916
21.09.2007 17:00 | 3600 | 2 | 760 | GGB | 770.696 | 774.938 | 768.864 | 263.5 | GGB | 10703.7 | GGB | 9.93 | GGB | 1005.42 | GGB | 63.64 | GGB | 162825.78 | GGB | 131058.34 | GGB | 0 | 0 | 2296 | 3600 | 2281.02 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 15132.91 | GGB | 15133.11 | 2281.02 | 2281.02 |  |  |  | 1 | 1 |  |  |  |  | 131058.34 | 2281.02 | 131058.34 |  | 7.8381 | [5 empty] | 83.0407
21.09.2007 18:00 | 3600 | 2 | 759.64 | GGB | 769.597 | 773.883 | 768.864 | 262.99 | GGB | 10713.7 | GGB | 9.92 | GGB | 1005.58 | GGB | 64.13 | GGB | 161850.88 | GGB | 130102.92 | GGB | 0 | 0 | 2324 | 3600 | 2309.37 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 15171.57 | GGB | 15171.78 | 2309.37 | 2309.37 |  |  |  | 1 | 1 |  |  |  |  | 130102.92 | 2309.37 | 130102.92 | 2309.37 | 7.7697 | [5 empty] | 83.4599
21.09.2007 19:00 | 3600 | 2 | 759.28 | GGB | 768.498 | 772.781 | 766.667 | 264.01 | GGB | 10732.8 | GGB | 9.91 | GGB | 1005.13 | GGB | 64.12 | GGB | 162277.81 | GGB | 130391.4 | GGB | 0 | 0 | 2357 | 3600 | 2341.97 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 15209.64 | GGB | 15209.84 | 2341.97 | 2341.97 |  |  |  | 1 | 1 |  |  |  |  | 130391.4 | 2341.97 | 130391.4 | 2341.97 | 8.0235 | [5 empty] | 84.8258
21.09.2007 20:00 | 3600 | 2 | 758.63 | GGB | 767.033 | 771.68 | 766.3 | 265.6 | GGB | 10781.3 | GGB | 9.91 | GGB | 1005.5 | GGB | 63.76 | GGB | 163841.39 | GGB | 131839.21 | GGB | 0 | 0 | 2410 | 3600 | 2394.75 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 15248.23 | GGB | 15248.43 | 2394.75 | 2394.75 |  |  |  | 1 | 1 |  |  |  |  | 131839.21 | 2394.75 | 131839.21 | 2394.75 | 8.1814 | [5 empty] | 87.7005
21.09.2007 21:00 | 3600 | 2 | 758.86 | GGB | 767.033 | 771.445 | 764.835 | 267.51 | GGB | 10828.1 | GGB | 9.92 | GGB | 1006.12 | GGB | 63.2 | GGB | 166471.2 | GGB | 134259.89 | GGB | 0 | 0 | 2417 | 3600 | 2401.47 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 15286.77 | GGB | 15286.97 | 2401.47 | 2401.47 |  |  |  | 1 | 1 |  |  |  |  | 134259.89 | 2401.47 | 134259.89 | 2401.47 | 8.3659 | [5 empty] | 89.5614
21.09.2007 22:00 | 3600 | 2 | 759.01 | GGB | 767.033 | 771.422 | 764.835 | 268.34 | GGB | 10865.2 | GGB | 9.93 | GGB | 1006.27 | GGB | 62.28 | GGB | 168446.31 | GGB | 136246.55 | GGB | 0 | 0 | 2406 | 3600 | 2390.75 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 15325.31 | GGB | 15325.51 | 2390.75 | 2390.75 |  |  |  | 1 | 1 |  |  |  |  | 136246.55 | 2390.75 | 136246.55 | 2390.75 | 8.4518 | [5 empty] | 90.481
21.09.2007 23:00 | 3600 | 2 | 758.57 | GGB | 767.033 | 771.656 | 764.835 | 268.14 | GGB | 10905.2 | GGB | 9.92 | GGB | 1006.31 | GGB | 62.51 | GGB | 167731.09 | GGB | 135578.29 | GGB | 0 | 0 | 2450 | 3600 | 2434.95 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 15364.42 | GGB | 15364.62 | 2434.95 | 2434.95 |  |  |  | 1 | 1 |  |  |  |  | 135578.29 | 2434.95 | 135578.29 | 2434.95 | 8.441 | [5 empty] | 91.7018
21.09.2007 24:00 | 3600 | 2 | 758.15 | GGB | 767.033 | 772.641 | 765.934 | 269.09 | GGB | 10942.6 | GGB | 9.92 | GGB | 1006.61 | GGB | 62.44 | GGB | 168350.58 | GGB | 136151.19 | GGB | 0 | 0 | 2486 | 3600 | 2470.77 | GGB | 100 | GGB | 37.72 | GGB | 37.72 | GGB | 15402.13 | GGB | 15402.34 | 2470.77 | 2470.77 |  |  |  | 1 | 1 |  |  |  |  | 136151.19 | 2470.77 | 136151.19 | 2470.77 | 8.9183 | [5 empty] | 93.444
22.09.2007 01:00 | 3600 | 2 | 757.96 | GGB | 768.132 | 772.523 | 767.033 | 269.97 | GGB | 10986.3 | GGB | 9.92 | GGB | 1006.64 | GGB | 62.25 | GGB | 168919.45 | GGB | 136690.53 | GGB | 0 | 0 | 2514 | 3600 | 2498.59 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 15441.2 | GGB | 15441.41 | 2498.59 | 2498.59 |  |  |  | 1 | 1 |  |  |  |  | 136690.53 | 2498.59 | 136690.53 | 2498.59 | 8.7416 | [5 empty] | 94.8704
22.09.2007 02:00 | 3600 | 2 | 758.44 | GGB | 768.498 | 772.523 | 767.033 | 270.12 | GGB | 11010.6 | GGB | 9.92 | GGB | 1006.94 | GGB | 62.13 | GGB | 169251.75 | GGB | 137047.84 | GGB | 0 | 0 | 2511 | 3600 | 2496.2 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 15480.75 | GGB | 15480.96 | 2496.2 | 2496.2 |  |  |  | 1 | 1 |  |  |  |  | 137047.84 | 2496.2 | 137047.84 | 2496.2 | 8.6498 | [5 empty] | 95.0274
22.09.2007 03:00 | 3600 | 2 | 757.81 | GGB | 767.033 | 771.469 | 764.835 | 270.98 | GGB | 11025.6 | GGB | 9.91 | GGB | 1006.85 | GGB | 61.97 | GGB | 169821.73 | GGB | 137564.54 | GGB | 0 | 0 | 2541 | 3600 | 2525.64 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 15519.59 | GGB | 15519.8 | 2525.64 | 2525.64 |  |  |  | 1 | 1 |  |  |  |  | 137564.54 | 2525.64 | 137564.54 | 2525.64 | 8.9454 | [5 empty] | 96.5107
22.09.2007 04:00 | 3600 | 2 | 757.92 | GGB | 768.132 | 771.656 | 765.934 | 271.45 | GGB | 11063.1 | GGB | 9.92 | GGB | 1006.5 | GGB | 61.78 | GGB | 170301.47 | GGB | 137982.32 | GGB | 0 | 0 | 2552 | 3600 | 2536.3 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 15559.42 | GGB | 15559.64 | 2536.3 | 2536.3 |  |  |  | 1 | 1 |  |  |  |  | 137982.32 | 2536.3 | 137982.32 | 2536.3 | 8.7843 | [5 empty] | 97.2124
22.09.2007 05:00 | 3600 | 2 | 758.13 | GGB | 767.033 | 771.633 | 764.835 | 271.62 | GGB | 11070.5 | GGB | 9.92 | GGB | 1006.36 | GGB | 61.65 | GGB | 170569.96 | GGB | 138235.65 | GGB | 0 | 0 | 2545 | 3600 | 2529.84 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 15598.82 | GGB | 15599.04 | 2529.84 | 2529.84 |  |  |  | 1 | 1 |  |  |  |  | 138235.65 | 2529.84 | 138235.65 | 2529.84 | 8.876 | [5 empty] | 97.1428
22.09.2007 06:00 | 3600 | 2 | 757.85 | GGB | 767.033 | 771.563 | 765.934 | 272.08 | GGB | 11080.9 | GGB | 9.92 | GGB | 1006.31 | GGB | 61.42 | GGB | 170662.39 | GGB | 138398.64 | GGB | 0 | 0 | 2565 | 3600 | 2549.26 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 15638.27 | GGB | 15638.49 | 2549.26 | 2549.26 |  |  |  | 1 | 1 |  |  |  |  | 138398.64 | 2549.26 | 138398.64 | 2549.26 | 8.9433 | [5 empty] | 98.0039
22.09.2007 07:00 | 3600 | 2 | 757.95 | GGB | 768.132 | 772.43 | 767.033 | 272.5 | GGB | 11105 | GGB | 9.92 | GGB | 1006.41 | GGB | 61.08 | GGB | 171038.7 | GGB | 138859.86 | GGB | 0 | 0 | 2572 | 3600 | 2556.53 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 15678.1 | GGB | 15678.31 | 2556.53 | 2556.53 |  |  |  | 1 | 1 |  |  |  |  | 138859.86 | 2556.53 | 138859.86 | 2556.53 | 8.9151 | [5 empty] | 98.6109
22.09.2007 08:00 | 3600 | 2 | 758.28 | GGB | 768.132 | 772.453 | 767.033 | 272.17 | GGB | 11104.9 | GGB | 9.93 | GGB | 1006.48 | GGB | 60.99 | GGB | 171326.99 | GGB | 139139.43 | GGB | 0 | 0 | 2555 | 3600 | 2540.07 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 15717.42 | GGB | 15717.63 | 2540.07 | 2540.07 |  |  |  | 1 | 1 |  |  |  |  | 139139.43 | 2540.07 | 139139.43 | 2540.07 | 8.9884 | [5 empty] | 98.1733
22.09.2007 09:00 | 3600 | 2 | 758.6 | GGB | 768.132 | 772.266 | 767.033 | 271.23 | GGB | 11086.3 | GGB | 9.93 | GGB | 1006.35 | GGB | 61.01 | GGB | 170608.47 | GGB | 138528.65 | GGB | 0 | 0 | 2528 | 3600 | 2512.72 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 15757.27 | GGB | 15757.48 | 2512.72 | 2512.72 |  |  |  | 1 | 1 |  |  |  |  | 138528.65 | 2512.72 | 138528.65 | 2512.72 | 8.7348 | [5 empty] | 96.6899
22.09.2007 10:00 | 3600 | 2 | 758.64 | GGB | 768.132 | 772.289 | 767.033 | 269.72 | GGB | 11050.2 | GGB | 9.94 | GGB | 1006.12 | GGB | 61.34 | GGB | 169322.17 | GGB | 137318.53 | GGB | 0 | 0 | 2489 | 3600 | 2473.79 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 15796.58 | GGB | 15796.8 | 2473.79 | 2473.79 |  |  |  | 1 | 1 |  |  |  |  | 137318.53 | 2473.79 | 137318.53 | 2473.79 | 8.6393 | [5 empty] | 94.3603
22.09.2007 11:00 | 3600 | 2 | 759.13 | GGB | 768.498 | 773.227 | 767.033 | 267.55 | GGB | 10971.1 | GGB | 9.94 | GGB | 1005.56 | GGB | 62 | GGB | 167972.06 | GGB | 135878.13 | GGB | 0 | 0 | 2430 | 3600 | 2415.15 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 15835.84 | GGB | 15836.05 | 2415.15 | 2415.15 |  |  |  | 1 | 1 |  |  |  |  | 135878.13 | 2415.15 | 135878.13 | 2415.15 | 8.3609 | [5 empty] | 91.1572
22.09.2007 12:00 | 3600 | 2 | 759.32 | GGB | 768.498 | 773.344 | 767.033 | 265.45 | GGB | 10882.1 | GGB | 9.94 | GGB | 1005.14 | GGB | 62.51 | GGB | 166217.02 | GGB | 134199.88 | GGB | 0 | 0 | 2381 | 3600 | 2365.73 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 15874.99 | GGB | 15875.2 | 2365.73 | 2365.73 |  |  |  | 1 | 1 |  |  |  |  | 134199.88 | 2365.73 | 134199.88 | 2365.73 | 8.1093 | [5 empty] | 88.1891
22.09.2007 13:00 | 3600 | 2 | 759.69 | GGB | 768.498 | 773.203 | 767.033 | 263.6 | GGB | 10804.9 | GGB | 9.94 | GGB | 1004.72 | GGB | 63.02 | GGB | 164534.6 | GGB | 132582.68 | GGB | 0 | 0 | 2334 | 3600 | 2319.22 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 15913.76 | GGB | 15913.97 | 2319.22 | 2319.22 |  |  |  | 1 | 1 |  |  |  |  | 132582.68 | 2319.22 | 132582.68 | 2319.22 | 7.9311 | [5 empty] | 85.4134
22.09.2007 14:00 | 3600 | 2 | 759.56 | GGB | 769.597 | 773.227 | 767.033 | 262.47 | GGB | 10742.2 | GGB | 9.93 | GGB | 1004.08 | GGB | 63.52 | GGB | 163276.92 | GGB | 131291.45 | GGB | 0 | 0 | 2318 | 3600 | 2303.39 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 15952.93 | GGB | 15953.14 | 2303.39 | 2303.39 |  |  |  | 1 | 1 |  |  |  |  | 131291.45 | 2303.39 | 131291.45 |  | 7.7206 | [5 empty] | 84.0043
22.09.2007 15:00 | 3600 | 2 | 759.69 | GGB | 769.597 | 774.328 | 768.498 | 262.23 | GGB | 10717 | GGB | 9.93 | GGB | 1003.88 | GGB | 63.93 | GGB | 162431.86 | GGB | 130424.52 | GGB | 0 | 0 | 2313 | 3600 | 2298.35 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 15991.42 | GGB | 15991.63 | 2298.35 | 2298.35 |  |  |  | 1 | 1 |  |  |  |  | 130424.52 | 2298.35 | 130424.52 |  | 7.788 | [5 empty] | 83.267
22.09.2007 16:00 | 3600 | 2 | 759.62 | GGB | 768.498 | 773.438 | 767.033 | 261.59 | GGB | 10677.5 | GGB | 9.92 | GGB | 1003.29 | GGB | 64.33 | GGB | 161726.54 | GGB | 129631.72 | GGB | 0 | 0 | 2299 | 3600 | 2283.59 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 16030.01 | GGB | 16030.22 | 2283.59 | 2283.59 |  |  |  | 1 | 1 |  |  |  |  | 129631.72 | 2283.59 | 129631.72 |  | 7.671 | [5 empty] | 82.2294
22.09.2007 17:00 | 3600 | 2 | 759.95 | GGB | 769.597 | 774.68 | 768.132 | 261.28 | GGB | 10665.4 | GGB | 9.93 | GGB | 1002.16 | GGB | 64.42 | GGB | 161614.31 | GGB | 129359.78 | GGB | 0 | 0 | 2283 | 3600 | 2267.87 | GGB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 16068.13 | GGB | 16068.34 | 2267.87 | 2267.87 |  |  |  | 1 | 1 |  |  |  |  | 129359.78 | 2267.87 | 129359.78 |  | 7.696 | [5 empty] | 81.492
22.09.2007 18:00 | 3600 | 2 | 759.26 | GGB | 768.498 | 773.672 | 768.132 | 262.46 | GGB | 10656 | GGB | 9.91 | GGB | 1001.46 | GGB | 64.3 | GGB | 162222.79 | GGB | 129802.31 | GGB | 0 | 0 | 2322 | 3600 | 2307.41 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 16106.57 | GGB | 16106.78 | 2307.41 | 2307.41 |  |  |  | 1 | 1 |  |  |  |  | 129802.31 | 2307.41 | 129802.31 | 2307.41 | 7.7915 | [5 empty] | 83.1964
22.09.2007 19:00 | 3600 | 2 | 759.19 | GGB | 768.498 | 773.602 | 767.766 | 264.47 | GGB | 10674.9 | GGB | 9.92 | GGB | 1001.47 | GGB | 63.48 | GGB | 164237.51 | GGB | 131737.57 | GGB | 0 | 0 | 2320 | 3600 | 2304.53 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 16144.91 | GGB | 16145.12 | 2304.53 | 2304.53 |  |  |  | 1 | 1 |  |  |  |  | 131737.57 | 2304.53 | 131737.57 |  | 7.9184 | [5 empty] | 84.3314
22.09.2007 20:00 | 3600 | 2 | 758.58 | GGB | 767.033 | 772.594 | 767.033 | 264.59 | GGB | 10751.3 | GGB | 9.92 | GGB | 1001.93 | GGB | 63.59 | GGB | 163930.52 | GGB | 131505.97 | GGB | 0 | 0 | 2383 | 3600 | 2367.92 | GGB | 100 | GGB | 38.23 | GGB | 38.23 | GGB | 16183.14 | GGB | 16183.35 | 2367.92 | 2367.92 |  |  |  | 1 | 1 |  |  |  |  | 131505.97 | 2367.92 | 131505.97 | 2367.92 | 8.1453 | [5 empty] | 86.4988
22.09.2007 21:00 | 3600 | 2 | 758.3 | GGB | 768.498 | 773.625 | 768.132 | 266.32 | GGB | 10809 | GGB | 9.92 | GGB | 1003.22 | GGB | 63.27 | GGB | 165260.83 | GGB | 132872.75 | GGB | 0 | 0 | 2420 | 3600 | 2405.08 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 16221.55 | GGB | 16221.77 | 2405.08 | 2405.08 |  |  |  | 1 | 1 |  |  |  |  | 132872.75 | 2405.08 | 132872.75 | 2405.08 | 8.3178 | [5 empty] | 88.7693
22.09.2007 22:00 | 3600 | 2 | 757.75 | GGB | 765.934 | 770.133 | 764.835 | 267.86 | GGB | 10836.5 | GGB | 9.91 | GGB | 1003.36 | GGB | 62.8 | GGB | 167019.17 | GGB | 134491.49 | GGB | 0 | 0 | 2449 | 3600 | 2433.77 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 16260.43 | GGB | 16260.65 | 2433.77 | 2433.77 |  |  |  | 1 | 1 |  |  |  |  | 134491.49 | 2433.77 | 134491.49 | 2433.77 | 8.4188 | [5 empty] | 90.9226
22.09.2007 23:00 | 3600 | 2 | 757.86 | GGB | 765.934 | 771.586 | 765.934 | 269.95 | GGB | 10871 | GGB | 9.91 | GGB | 1003.68 | GGB | 61.76 | GGB | 169904.25 | GGB | 137284.85 | GGB | 0 | 0 | 2459 | 3600 | 2443.9 | GGB | 100 | GGB | 38.21 | GGB | 38.21 | GGB | 16298.64 | GGB | 16298.86 | 2443.9 | 2443.9 |  |  |  | 1 | 1 |  |  |  |  | 137284.85 | 2443.9 | 137284.85 | 2443.9 | 8.7807 | [5 empty] | 93.1973
22.09.2007 24:00 | 3600 | 2 | 758.59 | GGB | 768.132 | 772.523 | 765.934 | 268.51 | GGB | 10933.6 | GGB | 9.93 | GGB | 1003.83 | GGB | 62.24 | GGB | 168104.1 | GGB | 135654.75 | GGB | 0 | 0 | 2467 | 3600 | 2451.59 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 16337.83 | GGB | 16338.04 | 2451.59 | 2451.59 |  |  |  | 1 | 1 |  |  |  |  | 135654.75 | 2451.59 | 135654.75 | 2451.59 | 8.4883 | [5 empty] | 92.3805
23.09.2007 01:00 | 3600 | 2 | 757.41 | GGB | 767.033 | 771.492 | 765.934 | 269.46 | GGB | 10941.5 | GGB | 9.91 | GGB | 1003.92 | GGB | 62.03 | GGB | 168813.82 | GGB | 136326.08 | GGB | 0 | 0 | 2526 | 3600 | 2510.62 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 16376.54 | GGB | 16376.76 | 2510.62 | 2510.62 |  |  |  | 1 | 1 |  |  |  |  | 136326.08 | 2510.62 | 136326.08 | 2510.62 | 8.8394 | [5 empty] | 95.0731
23.09.2007 02:00 | 3600 | 2 | 757.4 | GGB | 767.033 | 771.609 | 765.934 | 270.48 | GGB | 10974.2 | GGB | 9.92 | GGB | 1004.34 | GGB | 61.81 | GGB | 169443.21 | GGB | 136982.13 | GGB | 0 | 0 | 2539 | 3600 | 2524.1 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 16415.91 | GGB | 16416.13 | 2524.1 | 2524.1 |  |  |  | 1 | 1 |  |  |  |  | 136982.13 | 2524.1 | 136982.13 | 2524.1 | 8.7822 | [5 empty] | 96.0435
23.09.2007 03:00 | 3600 | 2 | 757.61 | GGB | 767.033 | 772.523 | 765.934 | 270.83 | GGB | 11005.6 | GGB | 9.92 | GGB | 1004.46 | GGB | 61.69 | GGB | 169497.13 | GGB | 137090.56 | GGB | 0 | 0 | 2548 | 3600 | 2532.27 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 16454.73 | GGB | 16454.95 | 2532.27 | 2532.27 |  |  |  | 1 | 1 |  |  |  |  | 137090.56 | 2532.27 | 137090.56 | 2532.27 | 8.9426 | [5 empty] | 96.4306
23.09.2007 04:00 | 3600 | 2 | 756.86 | GGB | 767.033 | 771.422 | 765.934 | 272.09 | GGB | 11034.4 | GGB | 9.91 | GGB | 1004.56 | GGB | 61.37 | GGB | 170254.16 | GGB | 137849.64 | GGB | 0 | 0 | 2598 | 3600 | 2582.22 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 16494.07 | GGB | 16494.29 | 2582.22 | 2582.22 |  |  |  | 1 | 1 |  |  |  |  | 137849.64 | 2582.22 | 137849.64 | 2582.22 | 9.0482 | [5 empty] | 98.8772
23.09.2007 05:00 | 3600 | 2 | 758.03 | GGB | 768.132 | 772.406 | 767.033 | 271.96 | GGB | 11065.4 | GGB | 9.93 | GGB | 1004.75 | GGB | 61.35 | GGB | 170084.71 | GGB | 137746.41 | GGB | 0 | 0 | 2563 | 3600 | 2548.04 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 16533.45 | GGB | 16533.68 | 2548.04 | 2548.04 |  |  |  | 1 | 1 |  |  |  |  | 137746.41 | 2548.04 | 137746.41 | 2548.04 | 8.9105 | [5 empty] | 97.4954
23.09.2007 06:00 | 3600 | 2 | 758.01 | GGB | 767.033 | 771.516 | 764.835 | 271.55 | GGB | 11058.9 | GGB | 9.93 | GGB | 1004.69 | GGB | 61.35 | GGB | 169759.01 | GGB | 137471.63 | GGB | 0 | 0 | 2558 | 3600 | 2542.35 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 16571.65 | GGB | 16571.88 | 2542.35 | 2542.35 |  |  |  | 1 | 1 |  |  |  |  | 137471.63 | 2542.35 | 137471.63 | 2542.35 | 9.1492 | [5 empty] | 97.0836
23.09.2007 07:00 | 3600 | 2 | 757.39 | GGB | 768.132 | 771.773 | 767.033 | 271.54 | GGB | 11055 | GGB | 9.92 | GGB | 1005.02 | GGB | 61.24 | GGB | 169722.7 | GGB | 137533.77 | GGB | 0 | 0 | 2584 | 3600 | 2568.56 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 16611.9 | GGB | 16612.14 | 2568.56 | 2568.56 |  |  |  | 1 | 1 |  |  |  |  | 137533.77 | 2568.56 | 137533.77 | 2568.56 | 8.7746 | [5 empty] | 98.1288
23.09.2007 08:00 | 3600 | 2 | 757.53 | GGB | 767.033 | 770.719 | 765.934 | 271.88 | GGB | 11075.7 | GGB | 9.92 | GGB | 1005.46 | GGB | 61.01 | GGB | 170180.44 | GGB | 138058.96 | GGB | 0 | 0 | 2587 | 3600 | 2571.54 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 16650.76 | GGB | 16650.99 | 2571.54 | 2571.54 |  |  |  | 1 | 1 |  |  |  |  | 138058.96 | 2571.54 | 138058.96 | 2571.54 | 9.1383 | [5 empty] | 98.6178
23.09.2007 09:00 | 3600 | 2 | 758.09 | GGB | 768.132 | 771.844 | 767.033 | 271.56 | GGB | 11087.3 | GGB | 9.93 | GGB | 1006.05 | GGB | 61.12 | GGB | 170176.04 | GGB | 138090.94 | GGB | 0 | 0 | 2564 | 3600 | 2548.39 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 16689.86 | GGB | 16690.09 | 2548.39 | 2548.39 |  |  |  | 1 | 1 |  |  |  |  | 138090.94 | 2548.39 | 138090.94 | 2548.39 | 9.0002 | [5 empty] | 97.7527
23.09.2007 10:00 | 3600 | 2 | 758.63 | GGB | 768.132 | 772.922 | 767.033 | 269.95 | GGB | 11048.3 | GGB | 9.94 | GGB | 1006.25 | GGB | 61.42 | GGB | 168752.2 | GGB | 136842.89 | GGB | 0 | 0 | 2529 | 3600 | 2513.74 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 16730.15 | GGB | 16730.38 | 2513.74 | 2513.74 |  |  |  | 1 | 1 |  |  |  |  | 136842.89 | 2513.74 | 136842.89 | 2513.74 | 8.5378 | [5 empty] | 95.5521
23.09.2007 11:00 | 3600 | 2 | 758.98 | GGB | 768.498 | 773.789 | 767.033 | 268.38 | GGB | 10989.4 | GGB | 9.94 | GGB | 1006.49 | GGB | 61.98 | GGB | 166936.64 | GGB | 135173.81 | GGB | 0 | 0 | 2504 | 3600 | 2488.82 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 16769.93 | GGB | 16770.16 | 2488.82 | 2488.82 |  |  |  | 1 | 1 |  |  |  |  | 135173.81 | 2488.82 | 135173.81 | 2488.82 | 8.4571 | [5 empty] | 93.4509
23.09.2007 12:00 | 3600 | 2 | 758.7 | GGB | 767.766 | 772.688 | 767.033 | 267.32 | GGB | 10925.4 | GGB | 9.93 | GGB | 1006.62 | GGB | 62.44 | GGB | 165415.97 | GGB | 133777.46 | GGB | 0 | 0 | 2493 | 3600 | 2478.04 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 16809.9 | GGB | 16810.13 | 2478.04 | 2478.04 |  |  |  | 1 | 1 |  |  |  |  | 133777.46 | 2478.04 | 133777.46 | 2478.04 | 8.2939 | [5 empty] | 92.085
23.09.2007 13:00 | 3600 | 2 | 759.07 | GGB | 768.864 | 772.664 | 767.033 | 266.24 | GGB | 10875 | GGB | 9.93 | GGB | 1006.66 | GGB | 62.93 | GGB | 164052.66 | GGB | 132485.86 | GGB | 0 | 0 | 2454 | 3600 | 2438.96 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 16849.32 | GGB | 16849.55 | 2438.96 | 2438.96 |  |  |  | 1 | 1 |  |  |  |  | 132485.86 | 2438.96 | 132485.86 | 2438.96 | 8.1971 | [5 empty] | 89.7577
23.09.2007 14:00 | 3600 | 2 | 758.94 | GGB | 767.766 | 771.75 | 767.033 | 265.49 | GGB | 10821.5 | GGB | 9.92 | GGB | 1006.88 | GGB | 63.39 | GGB | 163355.04 | GGB | 131772.48 | GGB | 0 | 0 | 2432 | 3600 | 2416.71 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 16888.32 | GGB | 16888.55 | 2416.71 | 2416.71 |  |  |  | 1 | 1 |  |  |  |  | 131772.48 | 2416.71 | 131772.48 | 2416.71 | 8.1655 | [5 empty] | 88.46
23.09.2007 15:00 | 3600 | 2 | 759.43 | GGB | 768.864 | 772.922 | 768.132 | 265.35 | GGB | 10812.9 | GGB | 9.93 | GGB | 1007.29 | GGB | 63.64 | GGB | 163457.37 | GGB | 131811.25 | GGB | 0 | 0 | 2395 | 3600 | 2380.24 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 16927.91 | GGB | 16928.14 | 2380.24 | 2380.24 |  |  |  | 1 | 1 |  |  |  |  | 131811.25 | 2380.24 | 131811.25 | 2380.24 | 7.9248 | [5 empty] | 87.1507
23.09.2007 16:00 | 3600 | 2 | 759.3 | GGB | 767.766 | 771.867 | 767.033 | 264.49 | GGB | 10769.3 | GGB | 9.92 | GGB | 1006.13 | GGB | 63.8 | GGB | 163001.83 | GGB | 131227.95 | GGB | 0 | 0 | 2372 | 3600 | 2357.03 | GGB | 100 | GGB | 37.37 | GGB | 37.37 | GGB | 16965.28 | GGB | 16965.51 | 2357.03 | 2357.03 |  |  |  | 1 | 1 |  |  |  |  | 131227.95 | 2357.03 | 131227.95 | 2357.03 | 8.2769 | [5 empty] | 85.9189
23.09.2007 17:00 | 3600 | 2 | 760.7 | GGB | 768.864 | 773.156 | 767.033 | 263.54 | GGB | 10778.1 | GGB | 9.95 | GGB | 1006.18 | GGB | 64.16 | GGB | 162308.62 | GGB | 130538.09 | GGB | 0 | 0 | 2310 | 3600 | 2295.36 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 17003.91 | GGB | 17004.14 | 2295.36 | 2295.36 |  |  |  | 1 | 1 |  |  |  |  | 130538.09 | 2295.36 | 130538.09 |  | 7.7565 | [5 empty] | 83.2311
23.09.2007 18:00 | 3600 | 2 | 759.56 | GGB | 769.963 | 774.164 | 768.498 | 263.32 | GGB | 10729.7 | GGB | 9.92 | GGB | 1005.14 | GGB | 63.99 | GGB | 162077.55 | GGB | 130282.01 | GGB | 0 | 0 | 2344 | 3600 | 2329.17 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 17042.43 | GGB | 17042.66 | 2329.17 | 2329.17 |  |  |  | 1 | 1 |  |  |  |  | 130282.01 | 2329.17 | 130282.01 | 2329.17 | 7.8777 | [5 empty] | 84.2914
23.09.2007 19:00 | 3600 | 2 | 759.38 | GGB | 768.864 | 773.156 | 768.132 | 263.73 | GGB | 10742.4 | GGB | 9.92 | GGB | 1004.15 | GGB | 63.8 | GGB | 162179.88 | GGB | 130310.33 | GGB | 0 | 0 | 2363 | 3600 | 2348.11 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 17080.72 | GGB | 17080.95 | 2348.11 | 2348.11 |  |  |  | 1 | 1 |  |  |  |  | 130310.33 | 2348.11 | 130310.33 | 2348.11 | 7.9912 | [5 empty] | 84.9953
23.09.2007 20:00 | 3600 | 2 | 758.54 | GGB | 765.201 | 770.977 | 764.835 | 266.23 | GGB | 10763.5 | GGB | 9.9 | GGB | 1005.52 | GGB | 63.29 | GGB | 164011.94 | GGB | 132163.42 | GGB | 0 | 0 | 2408 | 3600 | 2392.64 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 17119.37 | GGB | 17119.59 | 2392.64 | 2392.64 |  |  |  | 1 | 1 |  |  |  |  | 132163.42 | 2392.64 | 132163.42 | 2392.64 | 8.1837 | [5 empty] | 87.8387
23.09.2007 21:00 | 3600 | 2 | 757.77 | GGB | 768.864 | 773.039 | 767.033 | 270.53 | GGB | 10853.9 | GGB | 9.9 | GGB | 1006.69 | GGB | 62.1 | GGB | 167755.29 | GGB | 135816.11 | GGB | 0 | 0 | 2487 | 3600 | 2471.31 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 17157.88 | GGB | 17158.1 | 2471.31 | 2471.31 |  |  |  | 1 | 1 |  |  |  |  | 135816.11 | 2471.31 | 135816.11 | 2471.31 | 8.7158 | [5 empty] | 93.2344
23.09.2007 22:00 | 3600 | 2 | 758.35 | GGB | 767.766 | 772.969 | 767.033 | 270.69 | GGB | 11002.2 | GGB | 9.92 | GGB | 1007.3 | GGB | 62.28 | GGB | 167715.68 | GGB | 135795.51 | GGB | 0 | 0 | 2530 | 3600 | 2515.13 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 17197.37 | GGB | 17197.59 | 2515.13 | 2515.13 |  |  |  | 1 | 1 |  |  |  |  | 135795.51 | 2515.13 | 135795.51 | 2515.13 | 8.6489 | [5 empty] | 94.8732
23.09.2007 23:00 | 3600 | 2 | 757.14 | GGB | 767.766 | 770.93 | 765.934 | 272.49 | GGB | 11043.6 | GGB | 9.91 | GGB | 1008.21 | GGB | 61.58 | GGB | 169675.38 | GGB | 137791.69 | GGB | 0 | 0 | 2599 | 3600 | 2583.68 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 17236.16 | GGB | 17236.39 | 2583.68 | 2583.68 |  |  |  | 1 | 1 |  |  |  |  | 137791.69 | 2583.68 | 137791.69 | 2583.68 | 9.1755 | [5 empty] | 98.8916
23.09.2007 24:00 | 3600 | 2 | 757.02 | GGB | 766.667 | 771.023 | 765.201 | 274.81 | GGB | 11072.5 | GGB | 9.9 | GGB | 1008.9 | GGB | 60.6 | GGB | 172221.56 | GGB | 140368.14 | GGB | 0 | 0 | 2602 | 3600 | 2586.31 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 17275.84 | GGB | 17276.06 | 2586.31 | 2586.31 |  |  |  | 1 | 1 |  |  |  |  | 140368.14 | 2586.31 | 140368.14 | 2586.31 | 9.1514 | [5 empty] | 100.8432
24.09.2007 01:00 | 3600 | 2 | 757.95 | GGB | 767.766 | 771.914 | 766.3 | 274.1 | GGB | 11172.9 | GGB | 9.93 | GGB | 1009.31 | GGB | 60.5 | GGB | 171837.55 | GGB | 140151.48 | GGB | 0 | 0 | 2604 | 3600 | 2588.6 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 17315.21 | GGB | 17315.44 | 2588.6 | 2588.6 |  |  |  | 1 | 1 |  |  |  |  | 140151.48 | 2588.6 | 140151.48 | 2588.6 | 9.2127 | [5 empty] | 100.7767
24.09.2007 02:00 | 3600 | 2 | 757.22 | GGB | 766.667 | 771.094 | 765.201 | 274.41 | GGB | 11188.6 | GGB | 9.92 | GGB | 1009.65 | GGB | 60.39 | GGB | 172519.76 | GGB | 140801.21 | GGB | 0 | 0 | 2644 | 3600 | 2629.1 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 17354.96 | GGB | 17355.19 | 2629.1 | 2629.1 |  |  |  | 1 | 1 |  |  |  |  | 140801.21 | 2629.1 | 140801.21 | 2629.1 | 9.3127 | [5 empty] | 102.8279
24.09.2007 03:00 | 3600 | 2 | 757.23 | GGB | 767.766 | 771.094 | 766.3 | 275.23 | GGB | 11224.8 | GGB | 9.92 | GGB | 1009.77 | GGB | 60.05 | GGB | 173305.4 | GGB | 141604.2 | GGB | 0 | 0 | 2660 | 3600 | 2644.83 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 17394.96 | GGB | 17395.19 | 2644.83 | 2644.83 |  |  |  | 1 | 1 |  |  |  |  | 141604.2 | 2644.83 | 141604.2 | 2644.83 | 9.363 | [5 empty] | 104.0331
24.09.2007 04:00 | 3600 | 2 | 757 | GGB | 765.201 | 768.914 | 764.102 | 275.57 | GGB | 11250.1 | GGB | 9.92 | GGB | 1010 | GGB | 59.8 | GGB | 173828.06 | GGB | 142171.09 | GGB | 0 | 0 | 2682 | 3600 | 2667 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 17434.57 | GGB | 17434.8 | 2667 | 2667 |  |  |  | 1 | 1 |  |  |  |  | 142171.09 | 2667 | 142171.09 | 2667 | 9.5726 | [5 empty] | 105.3251 | 2658.262
24.09.2007 05:00 | 3600 | 2 | 756.84 | GGB | 765.201 | 770.18 | 764.102 | 276.26 | GGB | 11295.8 | GGB | 9.92 | GGB | 1010.18 | GGB | 59.19 | GGB | 174815.06 | GGB | 143265.44 | GGB | 0 | 0 | 2713 | 3600 | 2697.49 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 17474.99 | GGB | 17475.22 | 2697.49 | 2697.49 |  |  |  | 1 | 1 |  |  |  |  | 143265.44 | 2697.49 | 143265.44 | 2697.49 | 9.561 | [5 empty] | 107.3492 | 2637.9565
24.09.2007 06:00 | 3600 | 2 | 756.09 | GGB | 766.3 | 770.133 | 764.102 | 276.69 | GGB | 11313.9 | GGB | 9.91 | GGB | 1010.39 | GGB | 58.78 | GGB | 175615.01 | GGB | 144129.56 | GGB | 0 | 0 | 2758 | 3600 | 2742.66 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 17514.79 | GGB | 17515.02 | 2742.66 | 2742.66 |  |  |  | 1 | 1 |  |  |  |  | 144129.56 | 2742.66 | 144129.56 | 2742.66 | 9.9321 | [5 empty] | 109.8051 | 2622.1408
24.09.2007 07:00 | 3600 | 2 | 756.2 | GGB | 765.201 | 770.109 | 764.102 | 276.34 | GGB | 11308.9 | GGB | 9.91 | GGB | 1010.35 | GGB | 58.7 | GGB | 175106.65 | GGB | 143738.96 | GGB | 0 | 0 | 2742 | 3600 | 2726.39 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 17555.4 | GGB | 17555.63 | 2726.39 | 2726.39 |  |  |  | 1 | 1 |  |  |  |  | 143738.96 | 2726.39 | 143738.96 | 2726.39 | 9.65 | [5 empty] | 108.8579 | 2629.2663
24.09.2007 08:00 | 3600 | 2 | 755.2 | GNB | 766.3 | 770.109 | 764.102 | 278.34 | GGB | 11273.8 | GGB | 9.89 | GGB | 1010.58 | GGB | 58.39 | GGB | 176274.11 | GGB | 144870.51 | GGB | 0 | 0 | 2783 | 3600 | 2767.15 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 17595.62 | GGB | 17595.85 | 2767.15 | 2767.15 |  |  |  | 0 | 1 | [14 empty] | 111.3551 | 2608.7297
24.09.2007 09:00 | 3600 | 2 | 757.58 | GGB | 767.766 | 770.953 | 766.3 | 278.29 | GGB | 11303.7 | GGB | 9.94 | GGB | 1010.64 | GGB | 58.64 | GGB | 175382.83 | GGB | 144037.06 | GGB | 0 | 0 | 2681 | 3600 | 2665.78 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 17636.18 | GGB | 17636.41 | 2665.78 | 2665.78 |  |  |  | 1 | 1 |  |  |  |  | 144037.06 | 2665.78 | 144037.06 | 2665.78 | 9.4667 | [5 empty] | 106.6586 | 2623.8247
24.09.2007 10:00 | 3600 | 2 | 759.75 | GGB | 768.864 | 774.023 | 767.766 | 274.57 | GGB | 11242.8 | GGB | 9.98 | GGB | 1010.6 | GGB | 59.43 | GGB | 172261.18 | GGB | 141130.02 | GGB | 0 | 0 | 2543 | 3600 | 2528.17 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 17675.66 | GGB | 17675.9 | 2528.17 | 2528.17 |  |  |  | 1 | 1 |  |  |  |  | 141130.02 | 2528.17 | 141130.02 | 2528.17 | 9.0352 | [5 empty] | 99.1113
24.09.2007 11:00 | 3600 | 2 | 758.98 | GGB | 769.963 | 775.102 | 768.864 | 269.73 | GGB | 11038.5 | GGB | 9.96 | GGB | 1009.97 | GGB | 61.03 | GGB | 167821.31 | GGB | 136749.86 | GGB | 0 | 0 | 2478 | 3600 | 2463.29 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 17716.36 | GGB | 17716.6 | 2463.29 | 2463.29 |  |  |  | 1 | 1 |  |  |  |  | 136749.86 | 2463.29 | 136749.86 | 2463.29 | 8.2765 | [5 empty] | 93.5707
24.09.2007 12:00 | 3600 | 2 | 759.49 | GGB | 768.864 | 774 | 767.766 | 265.31 | GGB | 10886.3 | GGB | 9.95 | GGB | 1009.05 | GGB | 62.58 | GGB | 163556.4 | GGB | 132536.79 | GGB | 0 | 0 | 2391 | 3600 | 2375.71 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 17754.76 | GGB | 17755 | 2375.71 | 2375.71 |  |  |  | 1 | 1 |  |  |  |  | 132536.79 | 2375.71 | 132536.79 | 2375.71 | 8.1997 | [5 empty] | 87.4636
24.09.2007 13:00 | 3600 | 2 | 759.3 | GGB | 769.963 | 773.977 | 767.766 | 263.83 | GGB | 10780.3 | GGB | 9.93 | GGB | 1008.08 | GGB | 63.29 | GGB | 162205.19 | GGB | 131037.09 | GGB | 0 | 0 | 2355 | 3600 | 2339.72 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 17793.6 | GGB | 17793.85 | 2339.72 | 2339.72 |  |  |  | 1 | 1 |  |  |  |  | 131037.09 | 2339.72 | 131037.09 | 2339.72 | 7.8916 | [5 empty] | 85.1639
24.09.2007 14:00 | 3600 | 2 | 759.38 | GGB | 769.597 | 775.172 | 768.864 | 264.6 | GGB | 10686.3 | GGB | 9.92 | GGB | 1006.28 | GGB | 63.23 | GGB | 162891.8 | GGB | 131382.98 | GGB | 0 | 0 | 2308 | 3600 | 2292.6 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 17831.71 | GGB | 17831.96 | 2292.6 | 2292.6 |  |  |  | 1 | 1 |  |  |  |  | 131382.98 | 2292.6 | 131382.98 |  | 7.9037 | [5 empty] | 83.6691
24.09.2007 15:00 | 3600 | 2 | 759.6 | GGB | 768.498 | 773.906 | 767.766 | 263.67 | GGB | 10636.6 | GGB | 9.92 | GGB | 1005.6 | GGB | 63.54 | GGB | 161991.72 | GGB | 130446.31 | GGB | 0 | 0 | 2280 | 3600 | 2265.03 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 17870.11 | GGB | 17870.36 | 2265.03 | 2265.03 |  |  |  | 1 | 1 |  |  |  |  | 130446.31 | 2265.03 | 130446.31 |  | 7.6944 | [5 empty] | 82.0736
24.09.2007 16:00 | 3600 | 2 | 760.19 | GGB | 770.696 | 775.945 | 768.864 | 262.3 | GGB | 10620.6 | GGB | 9.93 | GGB | 1004.75 | GGB | 63.69 | GGB | 161462.46 | GGB | 129855 | GGB | 0 | 0 | 2248 | 3600 | 2232.88 | GGB | 100 | GGB | 37.77 | GGB | 37.77 | GGB | 17907.88 | GGB | 17908.13 | 2232.88 | 2232.88 |  |  |  | 1 | 1 |  |  |  |  | 129855 | 2232.88 | 129855 |  | 7.6767 | [5 empty] | 80.5418
24.09.2007 17:00 | 3600 | 2 | 760.23 | GGB | 770.33 | 774.82 | 768.864 | 260.4 | GGB | 10631 | GGB | 9.93 | GGB | 1003.96 | GGB | 64.13 | GGB | 159617.19 | GGB | 128098.57 | GGB | 0 | 0 | 2247 | 3600 | 2231.67 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 17945.93 | GGB | 17946.17 | 2231.67 | 2231.67 |  |  |  | 1 | 1 |  |  |  |  | 128098.57 | 2231.67 | 128098.57 |  | 7.5151 | [5 empty] | 79.4094
24.09.2007 18:00 | 3600 | 2 | 759.37 | GGB | 768.864 | 773.695 | 767.766 | 259.87 | GGB | 10632.8 | GGB | 9.92 | GGB | 1002.55 | GGB | 64.34 | GGB | 159221.07 | GGB | 127524.59 | GGB | 0 | 0 | 2295 | 3600 | 2279.89 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 17984.11 | GGB | 17984.35 | 2279.89 | 2279.89 |  |  |  | 1 | 1 |  |  |  |  | 127524.59 | 2279.89 | 127524.59 |  | 7.615 | [5 empty] | 80.7617
24.09.2007 19:00 | 3600 | 2 | 759.32 | GGB | 768.864 | 773.461 | 767.766 | 260.34 | GGB | 10652.9 | GGB | 9.92 | GGB | 1000.85 | GGB | 64.47 | GGB | 159513.76 | GGB | 127493.47 | GGB | 0 | 0 | 2314 | 3600 | 2299.42 | GGB | 100 | GGB | 37.79 | GGB | 37.79 | GGB | 18021.89 | GGB | 18022.14 | 2299.42 | 2299.42 |  |  |  | 1 | 1 |  |  |  |  | 127493.47 | 2299.42 | 127493.47 |  | 7.7576 | [5 empty] | 81.4336
24.09.2007 20:00 | 3600 | 2 | 757.99 | GGB | 767.766 | 772.383 | 766.3 | 262.08 | GGB | 10707.4 | GGB | 9.91 | GGB | 1001.52 | GGB | 64.15 | GGB | 161258.9 | GGB | 129096.75 | GGB | 0 | 0 | 2391 | 3600 | 2376.27 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 18060.38 | GGB | 18060.63 | 2376.27 | 2376.27 |  |  |  | 1 | 1 |  |  |  |  | 129096.75 | 2376.27 | 129096.75 | 2376.27 | 7.9701 | [5 empty] | 85.2135
24.09.2007 21:00 | 3600 | 2 | 758.09 | GGB | 767.766 | 772.219 | 766.3 | 263.67 | GGB | 10784.5 | GGB | 9.92 | GGB | 1002.52 | GGB | 63.49 | GGB | 163095.36 | GGB | 130952.71 | GGB | 0 | 0 | 2422 | 3600 | 2406.56 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 18098.58 | GGB | 18098.83 | 2406.56 | 2406.56 |  |  |  | 1 | 1 |  |  |  |  | 130952.71 | 2406.56 | 130952.71 | 2406.56 | 8.2499 | [5 empty] | 87.5404
24.09.2007 22:00 | 3600 | 2 | 757.63 | GGB | 765.201 | 771.023 | 764.102 | 264.71 | GGB | 10828.2 | GGB | 9.91 | GGB | 1003.1 | GGB | 63 | GGB | 164404.76 | GGB | 132272.25 | GGB | 0 | 0 | 2456 | 3600 | 2440.82 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 18137.43 | GGB | 18137.68 | 2440.82 | 2440.82 |  |  |  | 1 | 1 |  |  |  |  | 132272.25 | 2440.82 | 132272.25 | 2440.82 | 8.3102 | [5 empty] | 89.6813
24.09.2007 23:00 | 3600 | 2 | 757.94 | GGB | 765.201 | 770.016 | 764.102 | 264.78 | GGB | 10894.7 | GGB | 9.93 | GGB | 1003.66 | GGB | 62.44 | GGB | 165750.48 | GGB | 133654.12 | GGB | 0 | 0 | 2473 | 3600 | 2457.56 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 18176.14 | GGB | 18176.39 | 2457.56 | 2457.56 |  |  |  | 1 | 1 |  |  |  |  | 133654.12 | 2457.56 | 133654.12 | 2457.56 | 8.4852 | [5 empty] | 91.2397
24.09.2007 24:00 | 3600 | 2 | 756.82 | GGB | 766.3 | 769.992 | 764.102 | 265.84 | GGB | 10905.1 | GGB | 9.91 | GGB | 1003.55 | GGB | 62.13 | GGB | 166626.35 | GGB | 134469.56 | GGB | 0 | 0 | 2521 | 3600 | 2505.53 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 18214.52 | GGB | 18214.77 | 2505.53 | 2505.53 |  |  |  | 1 | 1 |  |  |  |  | 134469.56 | 2505.53 | 134469.56 | 2505.53 | 8.7785 | [5 empty] | 93.5882
25.09.2007 01:00 | 3600 | 2 | 757.11 | GGB | 765.201 | 769.734 | 764.102 | 266.74 | GGB | 10942.1 | GGB | 9.92 | GGB | 1003.22 | GGB | 61.7 | GGB | 167480.21 | GGB | 135288.25 | GGB | 0 | 0 | 2521 | 3600 | 2505.33 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 18253.13 | GGB | 18253.38 | 2505.33 | 2505.33 |  |  |  | 1 | 1 |  |  |  |  | 135288.25 | 2505.33 | 135288.25 | 2505.33 | 8.7786 | [5 empty] | 94.1505
25.09.2007 02:00 | 3600 | 2 | 756.83 | GGB | 766.667 | 771.703 | 765.934 | 267.62 | GGB | 10960.9 | GGB | 9.92 | GGB | 1003.45 | GGB | 61.2 | GGB | 168744.5 | GGB | 136545.64 | GGB | 0 | 0 | 2536 | 3600 | 2520.67 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 18292.26 | GGB | 18292.51 | 2520.67 | 2520.67 |  |  |  | 1 | 1 |  |  |  |  | 136545.64 | 2520.67 | 136545.64 | 2520.67 | 8.796 | [5 empty] | 95.6074
25.09.2007 03:00 | 3600 | 2 | 756.54 | GGB | 767.766 | 772.711 | 766.3 | 269.28 | GGB | 10967.1 | GGB | 9.91 | GGB | 1003.5 | GGB | 60.61 | GGB | 170529.24 | GGB | 138238 | GGB | 0 | 0 | 2547 | 3600 | 2532.08 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 18331.05 | GGB | 18331.3 | 2532.08 | 2532.08 |  |  |  | 1 | 1 |  |  |  |  | 138238 | 2532.08 | 138238 | 2532.08 | 9.0237 | [5 empty] | 97.2305
25.09.2007 04:00 | 3600 | 2 | 757.15 | GGB | 765.201 | 769.383 | 763.37 | 269.39 | GGB | 11022 | GGB | 9.92 | GGB | 1003.23 | GGB | 60.44 | GGB | 170374.1 | GGB | 138148.35 | GGB | 0 | 0 | 2544 | 3600 | 2529.15 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 18370.4 | GGB | 18370.65 | 2529.15 | 2529.15 |  |  |  | 1 | 1 |  |  |  |  | 138148.35 | 2529.15 | 138148.35 | 2529.15 | 8.8792 | [5 empty] | 97.055
25.09.2007 05:00 | 3600 | 2 | 756.34 | GGB | 765.201 | 769.664 | 763.37 | 270.41 | GGB | 11021 | GGB | 9.91 | GGB | 1003.49 | GGB | 59.6 | GGB | 171821.04 | GGB | 139709.43 | GGB | 0 | 0 | 2572 | 3600 | 2557.01 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 18409.5 | GGB | 18409.75 | 2557.01 | 2557.01 |  |  |  | 1 | 1 |  |  |  |  | 139709.43 | 2557.01 | 139709.43 | 2557.01 | 9.1365 | [5 empty] | 99.2329
25.09.2007 06:00 | 3600 | 2 | 757.46 | GGB | 766.667 | 771.75 | 764.835 | 270.07 | GGB | 11085.5 | GGB | 9.94 | GGB | 1003.25 | GGB | 59.48 | GGB | 171647.19 | GGB | 139584.8 | GGB | 0 | 0 | 2554 | 3600 | 2538.29 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 18448.84 | GGB | 18449.09 | 2538.29 | 2538.29 |  |  |  | 1 | 1 |  |  |  |  | 139584.8 | 2538.29 | 139584.8 | 2538.29 | 9.0063 | [5 empty] | 98.4185
25.09.2007 07:00 | 3600 | 2 | 755.96 | GNB | 765.201 | 769.453 | 763.37 | 270.2 | GGB | 11067.7 | GGB | 9.91 | GGB | 1003.08 | GGB | 59.3 | GGB | 171913.47 | GGB | 139854.43 | GGB | 0 | 0 | 2616 | 3600 | 2600.71 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 18488.67 | GGB | 18488.92 | 2600.71 | 2600.71 |  |  |  | 0 | 1 | [14 empty] | 101.0336
25.09.2007 08:00 | 3600 | 2 | 757.22 | GGB | 767.766 | 772.57 | 767.033 | 270.61 | GGB | 11111.4 | GGB | 9.93 | GGB | 1002.76 | GGB | 58.89 | GGB | 172773.93 | GGB | 140678.85 | GGB | 0 | 0 | 2568 | 3600 | 2553.06 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 18527.56 | GGB | 18527.81 | 2553.06 | 2553.06 |  |  |  | 1 | 1 |  |  |  |  | 140678.85 | 2553.06 | 140678.85 | 2553.06 | 9.2353 | [5 empty] | 99.7671
25.09.2007 09:00 | 3600 | 2 | 757.67 | GGB | 766.3 | 771.305 | 765.934 | 268.76 | GGB | 11104.5 | GGB | 9.94 | GGB | 1002.66 | GGB | 59.93 | GGB | 170887.95 | GGB | 138697.89 | GGB | 0 | 0 | 2558 | 3600 | 2542.68 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 18567.76 | GGB | 18568.01 | 2542.68 | 2542.68 |  |  |  | 1 | 1 |  |  |  |  | 138697.89 | 2542.68 | 138697.89 | 2542.68 | 8.7727 | [5 empty] | 97.9623
25.09.2007 10:00 | 3600 | 2 | 757.97 | GGB | 767.766 | 773.438 | 767.033 | 268.71 | GGB | 10978 | GGB | 9.94 | GGB | 1002.44 | GGB | 60.3 | GGB | 169892.15 | GGB | 137703.46 | GGB | 0 | 0 | 2484 | 3600 | 2468.84 | GGB | 100 | GGB | 38.68 | GGB | 38.68 | GGB | 18606.44 | GGB | 18606.69 | 2468.84 | 2468.84 |  |  |  | 1 | 1 |  |  |  |  | 137703.46 | 2468.84 | 137703.46 | 2468.84 | 8.7892 | [5 empty] | 94.4355
25.09.2007 11:00 | 3600 | 2 | 758.81 | GGB | 769.963 | 774.445 | 768.132 | 265.95 | GGB | 10883.9 | GGB | 9.95 | GGB | 1002.1 | GGB | 61.63 | GGB | 166656.06 | GGB | 134501.03 | GGB | 0 | 0 | 2398 | 3600 | 2382.82 | GGB | 100 | GGB | 35.8 | GGB | 35.8 | GGB | 18642.24 | GGB | 18642.49 | 2382.82 | 2382.82 |  |  |  | 1 | 1 |  |  |  |  | 134501.03 | 2382.82 | 134501.03 | 2382.82 | 8.9523 | [5 empty] | 89.0255
25.09.2007 12:00 | 3600 | 2 | 758.77 | GGB | 768.864 | 774.563 | 768.498 | 261.56 | GGB | 10778.8 | GGB | 9.94 | GGB | 1001.47 | GGB | 63.8 | GGB | 162195.29 | GGB | 129975.87 | GGB | 0 | 0 | 2366 | 3600 | 2350.45 | GGB | 100 | GGB | 35.91 | GGB | 35.91 | GGB | 18678.15 | GGB | 18678.4 | 2350.45 | 2350.45 |  |  |  | 1 | 1 |  |  |  |  | 129975.87 | 2350.45 | 129975.87 | 2350.45 | 8.5074 | [5 empty] | 84.8616
25.09.2007 13:00 | 3600 | 2 | 759.07 | GGB | 768.864 | 773.508 | 767.766 | 259.36 | GGB | 10697.8 | GGB | 9.93 | GGB | 999.94 | GGB | 64.34 | GGB | 160845.17 | GGB | 128491.88 | GGB | 0 | 0 | 2320 | 3600 | 2305.01 | GGB | 100 | GGB | 34.15 | GGB | 34.15 | GGB | 18712.3 | GGB | 18712.55 | 2305.01 | 2305.01 |  |  |  | 1 | 1 |  |  |  |  | 128491.88 | 2305.01 | 128491.88 |  | 8.6728 | [5 empty] | 82.2709
25.09.2007 14:00 | 3600 | 2 | 759.19 | GGB | 767.766 | 773.508 | 767.766 | 258.91 | GGB | 10626.4 | GGB | 9.92 | GGB | 998.91 | GGB | 64.68 | GGB | 160419.34 | GGB | 127889.92 | GGB | 0 | 0 | 2289 | 3600 | 2274.4 | GGB | 100 | GGB | 36.55 | GGB | 36.55 | GGB | 18748.85 | GGB | 18749.1 | 2274.4 | 2274.4 |  |  |  | 1 | 1 |  |  |  |  | 127889.92 | 2274.4 | 127889.92 |  | 7.9582 | [5 empty] | 80.798
25.09.2007 15:00 | 3600 | 2 | 759.41 | GGB | 768.864 | 773.648 | 767.766 | 259.4 | GGB | 10604 | GGB | 9.92 | GGB | 997.65 | GGB | 64.28 | GGB | 161848.68 | GGB | 129015.73 | GGB | 0 | 0 | 2262 | 3600 | 2247.27 | GGB | 100 | GGB | 34.8 | GGB | 34.8 | GGB | 18783.65 | GGB | 18783.9 | 2247.27 | 2247.27 |  |  |  | 1 | 1 |  |  |  |  | 129015.73 | 2247.27 | 129015.73 |  | 8.3314 | [5 empty] | 80.537
25.09.2007 16:00 | 3600 | 2 | 759.52 | GGB | 768.864 | 773.766 | 768.864 | 257.63 | GGB | 10612.4 | GGB | 9.93 | GGB | 997.36 | GGB | 65.27 | GGB | 160029.82 | GGB | 127157.24 | GGB | 0 | 0 | 2261 | 3600 | 2246.17 | GGB | 100 | GGB | 35.35 | GGB | 35.35 | GGB | 18819 | GGB | 18819.25 | 2246.17 | 2246.17 |  |  |  | 1 | 1 |  |  |  |  | 127157.24 | 2246.17 | 127157.24 |  | 8.0797 | [5 empty] | 79.338
25.09.2007 17:00 | 3600 | 2 | 759.65 | GGB | 768.864 | 773.953 | 767.766 | 258.32 | GGB | 10574.5 | GGB | 9.92 | GGB | 996.49 | GGB | 65.28 | GGB | 160992.62 | GGB | 127805.47 | GGB | 0 | 0 | 2235 | 3600 | 2219.7 | GGB | 100 | GGB | 35.68 | GGB | 35.68 | GGB | 18854.68 | GGB | 18854.93 | 2219.7 | 2219.7 |  |  |  | 1 | 1 |  |  |  |  | 127805.47 | 2219.7 | 127805.47 |  | 7.9509 | [5 empty] | 78.8027
25.09.2007 18:00 | 3600 | 2 | 759.75 | GGB | 768.864 | 773.953 | 767.766 | 259.46 | GGB | 10576.1 | GGB | 9.92 | GGB | 995.02 | GGB | 64.58 | GGB | 162432.96 | GGB | 129027.9 | GGB | 0 | 0 | 2232 | 3600 | 2216.54 | GGB | 100 | GGB | 34.97 | GGB | 34.97 | GGB | 18889.65 | GGB | 18889.9 | 2216.54 | 2216.54 |  |  |  | 1 | 1 |  |  |  |  | 129027.9 | 2216.54 | 129027.9 |  | 8.1783 | [5 empty] | 79.4432
25.09.2007 19:00 | 3600 | 2 | 759.06 | GGB | 767.766 | 772.875 | 767.766 | 261.15 | GGB | 10623 | GGB | 9.92 | GGB | 994.03 | GGB | 64.13 | GGB | 163260.41 | GGB | 129727.42 | GGB | 0 | 0 | 2286 | 3600 | 2270.61 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 18930.68 | GGB | 18930.93 | 2270.61 | 2270.61 |  |  |  | 1 | 1 |  |  |  |  | 129727.42 | 2270.61 | 129727.42 |  | 7.1791 | [5 empty] | 81.8223
25.09.2007 20:00 | 3600 | 2 | 758.62 | GGB | 768.864 | 772.781 | 767.766 | 261.12 | GGB | 10711.4 | GGB | 9.92 | GGB | 995.58 | GGB | 64.15 | GGB | 162583.71 | GGB | 129384.79 | GGB | 0 | 0 | 2344 | 3600 | 2328.79 | GGB | 100 | GGB | 37.66 | GGB | 37.66 | GGB | 18968.34 | GGB | 18968.59 | 2328.79 | 2328.79 |  |  |  | 1 | 1 |  |  |  |  | 129384.79 | 2328.79 | 129384.79 | 2328.79 | 8.0008 | [5 empty] | 83.6972
25.09.2007 21:00 | 3600 | 2 | 757.98 | GGB | 766.667 | 771.961 | 766.3 | 262.12 | GGB | 10768.5 | GGB | 9.91 | GGB | 996.16 | GGB | 63.52 | GGB | 163527.8 | GGB | 130456.48 | GGB | 0 | 0 | 2400 | 3600 | 2384.5 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 19008.23 | GGB | 19008.48 | 2384.5 | 2384.5 |  |  |  | 1 | 1 |  |  |  |  | 130456.48 | 2384.5 | 130456.48 | 2384.5 | 7.7983 | [5 empty] | 86.4093
25.09.2007 22:00 | 3600 | 2 | 758.05 | GGB | 767.766 | 771.984 | 766.3 | 262.51 | GGB | 10809.3 | GGB | 9.92 | GGB | 996.73 | GGB | 62.98 | GGB | 164556.61 | GGB | 131563.83 | GGB | 0 | 0 | 2414 | 3600 | 2399.24 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 19047.3 | GGB | 19047.55 | 2399.24 | 2399.24 |  |  |  | 1 | 1 |  |  |  |  | 131563.83 | 2399.24 | 131563.83 | 2399.24 | 8.0792 | [5 empty] | 87.6814
25.09.2007 23:00 | 3600 | 2 | 757.63 | GGB | 766.667 | 771.961 | 766.3 | 264.92 | GGB | 10815.2 | GGB | 9.92 | GGB | 997.05 | GGB | 62.02 | GGB | 166998.26 | GGB | 133939.06 | GGB | 0 | 0 | 2428 | 3600 | 2412.52 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 19086.1 | GGB | 19086.35 | 2412.52 | 2412.52 |  |  |  | 1 | 1 |  |  |  |  | 133939.06 | 2412.52 | 133939.06 | 2412.52 | 8.3281 | [5 empty] | 89.7585
25.09.2007 24:00 | 3600 | 2 | 757.37 | GGB | 766.3 | 771.07 | 765.201 | 265.08 | GGB | 10852 | GGB | 9.92 | GGB | 997.19 | GGB | 61.24 | GGB | 167974.26 | GGB | 135054.88 | GGB | 0 | 0 | 2449 | 3600 | 2433.32 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 19125.45 | GGB | 19125.7 | 2433.32 | 2433.32 |  |  |  | 1 | 1 |  |  |  |  | 135054.88 | 2433.32 | 135054.88 | 2433.32 | 8.3515 | [5 empty] | 91.2866
26.09.2007 01:00 | 3600 | 2 | 758.05 | GGB | 766.667 | 771 | 766.3 | 264.81 | GGB | 10894.7 | GGB | 9.93 | GGB | 997.37 | GGB | 61.6 | GGB | 167033.47 | GGB | 134180.55 | GGB | 0 | 0 | 2451 | 3600 | 2435.93 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 19164.05 | GGB | 19164.29 | 2435.93 | 2435.93 |  |  |  | 1 | 1 |  |  |  |  | 134180.55 | 2435.93 | 134180.55 | 2435.93 | 8.4699 | [5 empty] | 90.7929
26.09.2007 02:00 | 3600 | 2 | 757.1 | GGB | 767.766 | 773.227 | 767.766 | 264.93 | GGB | 10924 | GGB | 9.92 | GGB | 997.38 | GGB | 61.53 | GGB | 166769.39 | GGB | 133996.84 | GGB | 0 | 0 | 2508 | 3600 | 2493.2 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 19203.41 | GGB | 19203.66 | 2493.2 | 2493.2 |  |  |  | 1 | 1 |  |  |  |  | 133996.84 | 2493.2 | 133996.84 | 2493.2 | 8.4857 | [5 empty] | 92.8003
26.09.2007 03:00 | 3600 | 2 | 756.47 | GGB | 764.102 | 768.773 | 763.37 | 267.44 | GGB | 10902.2 | GGB | 9.9 | GGB | 997.35 | GGB | 60.71 | GGB | 169119.71 | GGB | 136214.68 | GGB | 0 | 0 | 2512 | 3600 | 2497.17 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 19242.23 | GGB | 19242.47 | 2497.17 | 2497.17 |  |  |  | 1 | 1 |  |  |  |  | 136214.68 | 2497.17 | 136214.68 | 2497.17 | 8.7645 | [5 empty] | 94.4864
26.09.2007 04:00 | 3600 | 2 | 757.48 | GGB | 767.766 | 771.938 | 765.934 | 267.77 | GGB | 10985.7 | GGB | 9.93 | GGB | 997.27 | GGB | 60.34 | GGB | 169531.24 | GGB | 136687.23 | GGB | 0 | 0 | 2506 | 3600 | 2491.23 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 19281.12 | GGB | 19281.37 | 2491.23 | 2491.23 |  |  |  | 1 | 1 |  |  |  |  | 136687.23 | 2491.23 | 136687.23 | 2491.23 | 8.7537 | [5 empty] | 94.5887
26.09.2007 05:00 | 3600 | 2 | 756.95 | GGB | 765.201 | 769.898 | 763.37 | 266.72 | GGB | 11008.7 | GGB | 9.92 | GGB | 997.07 | GGB | 60.62 | GGB | 168383.59 | GGB | 135619.79 | GGB | 0 | 0 | 2550 | 3600 | 2534.98 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 19320.42 | GGB | 19320.66 | 2534.98 | 2534.98 |  |  |  | 1 | 1 |  |  |  |  | 135619.79 | 2534.98 | 135619.79 | 2534.98 | 8.7502 | [5 empty] | 95.4982
26.09.2007 06:00 | 3600 | 2 | 756.81 | GGB | 767.766 | 772.055 | 765.934 | 267.8 | GGB | 10999.3 | GGB | 9.92 | GGB | 996.98 | GGB | 60.19 | GGB | 169694.09 | GGB | 136839.45 | GGB | 0 | 0 | 2555 | 3600 | 2540.1 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 19359.3 | GGB | 19359.54 | 2540.1 | 2540.1 |  |  |  | 1 | 1 |  |  |  |  | 136839.45 | 2540.1 | 136839.45 | 2540.1 | 8.94 | [5 empty] | 96.5516
26.09.2007 07:00 | 3600 | 2 | 757.57 | GGB | 767.766 | 771.984 | 765.934 | 267.95 | GGB | 10989.8 | GGB | 9.93 | GGB | 996.79 | GGB | 59.72 | GGB | 170078.11 | GGB | 137319.55 | GGB | 0 | 0 | 2510 | 3600 | 2494.83 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 19398.69 | GGB | 19398.93 | 2494.83 | 2494.83 |  |  |  | 1 | 1 |  |  |  |  | 137319.55 | 2494.83 | 137319.55 | 2494.83 | 8.6974 | [5 empty] | 95.1636
26.09.2007 08:00 | 3600 | 2 | 757.41 | GGB | 766.3 | 769.922 | 764.835 | 265.67 | GGB | 11003.2 | GGB | 9.93 | GGB | 996.74 | GGB | 60.46 | GGB | 167948.95 | GGB | 135291.95 | GGB | 0 | 0 | 2530 | 3600 | 2515.02 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 19437.27 | GGB | 19437.51 | 2515.02 | 2515.02 |  |  |  | 1 | 1 |  |  |  |  | 135291.95 | 2515.02 | 135291.95 | 2515.02 | 8.8196 | [5 empty] | 94.5172
26.09.2007 09:00 | 3600 | 2 | 757.34 | GGB | 766.667 | 771.047 | 764.835 | 265.53 | GGB | 10991.5 | GGB | 9.93 | GGB | 997.1 | GGB | 60.66 | GGB | 167505.52 | GGB | 134900.19 | GGB | 0 | 0 | 2531 | 3600 | 2515.47 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 19476.11 | GGB | 19476.35 | 2515.47 | 2515.47 |  |  |  | 1 | 1 |  |  |  |  | 134900.19 | 2515.47 | 134900.19 | 2515.47 | 8.7368 | [5 empty] | 94.2604
26.09.2007 10:00 | 3600 | 2 | 757.59 | GGB | 767.766 | 772.289 | 765.934 | 266.48 | GGB | 10930.5 | GGB | 9.93 | GGB | 996.94 | GGB | 60.36 | GGB | 168271.35 | GGB | 135618.92 | GGB | 0 | 0 | 2484 | 3600 | 2469.26 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 19516.05 | GGB | 19516.29 | 2469.26 | 2469.26 |  |  |  | 1 | 1 |  |  |  |  | 135618.92 | 2469.26 | 135618.92 | 2469.26 | 8.3845 | [5 empty] | 93.0218
26.09.2007 11:00 | 3600 | 2 | 758.03 | GGB | 767.766 | 772.289 | 767.033 | 265.2 | GGB | 10894.1 | GGB | 9.93 | GGB | 996.71 | GGB | 60.62 | GGB | 167133.6 | GGB | 134564.22 | GGB | 0 | 0 | 2440 | 3600 | 2424.54 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 19555.46 | GGB | 19555.7 | 2424.54 | 2424.54 |  |  |  | 1 | 1 |  |  |  |  | 134564.22 | 2424.54 | 134564.22 | 2424.54 | 8.2785 | [5 empty] | 90.6268
26.09.2007 12:00 | 3600 | 2 | 758.23 | GGB | 766.667 | 771.398 | 765.934 | 263.13 | GGB | 10885.3 | GGB | 9.93 | GGB | 996.82 | GGB | 61.62 | GGB | 164712.86 | GGB | 132233.85 | GGB | 0 | 0 | 2432 | 3600 | 2416.54 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 19594.09 | GGB | 19594.33 | 2416.54 | 2416.54 |  |  |  | 1 | 1 |  |  |  |  | 132233.85 | 2416.54 | 132233.85 | 2416.54 | 8.272 | [5 empty] | 88.7634
26.09.2007 13:00 | 3600 | 2 | 758.39 | GGB | 766.667 | 772.547 | 767.033 | 261.44 | GGB | 10824.6 | GGB | 9.94 | GGB | 997 | GGB | 62.33 | GGB | 162754.26 | GGB | 130408.39 | GGB | 0 | 0 | 2403 | 3600 | 2388.27 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 19633.73 | GGB | 19633.97 | 2388.27 | 2388.27 |  |  |  | 1 | 1 |  |  |  |  | 130408.39 | 2388.27 | 130408.39 | 2388.27 | 7.857 | [5 empty] | 86.514
26.09.2007 14:00 | 3600 | 2 | 758.54 | GGB | 768.864 | 773.578 | 768.132 | 261.36 | GGB | 10739.1 | GGB | 9.93 | GGB | 996.42 | GGB | 62.7 | GGB | 162496.78 | GGB | 129985.29 | GGB | 0 | 0 | 2365 | 3600 | 2349.96 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 19672.3 | GGB | 19672.55 | 2349.96 | 2349.96 |  |  |  | 1 | 1 |  |  |  |  | 129985.29 | 2349.96 | 129985.29 | 2349.96 | 7.9176 | [5 empty] | 84.8501
26.09.2007 15:00 | 3600 | 2 | 758.99 | GGB | 767.766 | 773.414 | 766.667 | 261.06 | GGB | 10670.5 | GGB | 9.92 | GGB | 995.8 | GGB | 62.72 | GGB | 162556.2 | GGB | 129943.53 | GGB | 0 | 0 | 2318 | 3600 | 2302.74 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 19711.17 | GGB | 19711.42 | 2302.74 | 2302.74 |  |  |  | 1 | 1 |  |  |  |  | 129943.53 | 2302.74 | 129943.53 |  | 7.6981 | [5 empty] | 83.1184
26.09.2007 16:00 | 3600 | 2 | 759.33 | GGB | 768.864 | 773.508 | 767.766 | 260.88 | GGB | 10654.4 | GGB | 9.93 | GGB | 995.77 | GGB | 63.03 | GGB | 161788.16 | GGB | 129206.51 | GGB | 0 | 0 | 2303 | 3600 | 2288.05 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 19750.42 | GGB | 19750.67 | 2288.05 | 2288.05 |  |  |  | 1 | 1 |  |  |  |  | 129206.51 | 2288.05 | 129206.51 |  | 7.532 | [5 empty] | 82.1197
26.09.2007 17:00 | 3600 | 2 | 758.57 | GGB | 767.766 | 772.359 | 766.667 | 261.23 | GGB | 10652.7 | GGB | 9.92 | GGB | 995.5 | GGB | 62.98 | GGB | 162451.66 | GGB | 129719.9 | GGB | 0 | 0 | 2328 | 3600 | 2312.57 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 19788.85 | GGB | 19789.1 | 2312.57 | 2312.57 |  |  |  | 1 | 1 |  |  |  |  | 129719.9 | 2312.57 | 129719.9 | 2312.57 | 7.806 | [5 empty] | 83.3295
26.09.2007 18:00 | 3600 | 2 | 758.9 | GGB | 766.667 | 772.359 | 765.934 | 261.67 | GGB | 10681.2 | GGB | 9.92 | GGB | 995.87 | GGB | 63 | GGB | 162570.5 | GGB | 129856.18 | GGB | 0 | 0 | 2334 | 3600 | 2318.76 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 19827.56 | GGB | 19827.8 | 2318.76 | 2318.76 |  |  |  | 1 | 1 |  |  |  |  | 129856.18 | 2318.76 | 129856.18 | 2318.76 | 7.7805 | [5 empty] | 83.6404
26.09.2007 19:00 | 3600 | 2 | 758.37 | GGB | 768.864 | 773.578 | 768.132 | 262.58 | GGB | 10704.7 | GGB | 9.92 | GGB | 996.16 | GGB | 62.8 | GGB | 163294.52 | GGB | 130547.48 | GGB | 0 | 0 | 2358 | 3600 | 2343.32 | GGB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 19866.08 | GGB | 19866.33 | 2343.32 | 2343.32 |  |  |  | 1 | 1 |  |  |  |  | 130547.48 | 2343.32 | 130547.48 | 2343.32 | 7.9396 | [5 empty] | 84.9763
26.09.2007 20:00 | 3600 | 2 | 758.35 | GGB | 767.766 | 771.938 | 767.033 | 261.41 | GGB | 10771.2 | GGB | 9.93 | GGB | 996.32 | GGB | 63.31 | GGB | 161662.72 | GGB | 129067.99 | GGB | 0 | 0 | 2392 | 3600 | 2377.07 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 19905.48 | GGB | 19905.72 | 2377.07 | 2377.07 |  |  |  | 1 | 1 |  |  |  |  | 129067.99 | 2377.07 | 129067.99 | 2377.07 | 7.7889 | [5 empty] | 85.2232
26.09.2007 21:00 | 3600 | 2 | 757.83 | GGB | 767.766 | 772.922 | 765.934 | 262.49 | GGB | 10796.3 | GGB | 9.92 | GGB | 996.52 | GGB | 63.04 | GGB | 163046.95 | GGB | 130303.47 | GGB | 0 | 0 | 2431 | 3600 | 2416.15 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 19944.33 | GGB | 19944.58 | 2416.15 | 2416.15 |  |  |  | 1 | 1 |  |  |  |  | 130303.47 | 2416.15 | 130303.47 | 2416.15 | 8.1017 | [5 empty] | 87.4535
26.09.2007 22:00 | 3600 | 2 | 757.77 | GGB | 767.766 | 772.969 | 767.033 | 264.12 | GGB | 10803.2 | GGB | 9.92 | GGB | 996.95 | GGB | 62.41 | GGB | 164431.17 | GGB | 131715.17 | GGB | 0 | 0 | 2436 | 3600 | 2421 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 19984.01 | GGB | 19984.25 | 2421 | 2421 |  |  |  | 1 | 1 |  |  |  |  | 131715.17 | 2421 | 131715.17 | 2421 | 8.0384 | [5 empty] | 88.5785
26.09.2007 23:00 | 3600 | 2 | 757.51 | GGB | 765.934 | 770.508 | 765.934 | 265.41 | GGB | 10819.1 | GGB | 9.91 | GGB | 997.39 | GGB | 61.68 | GGB | 165815.4 | GGB | 133172.61 | GGB | 0 | 0 | 2456 | 3600 | 2441.01 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 20023.49 | GGB | 20023.73 | 2441.01 | 2441.01 |  |  |  | 1 | 1 |  |  |  |  | 133172.61 | 2441.01 | 133172.61 | 2441.01 | 8.2339 | [5 empty] | 90.2988
26.09.2007 24:00 | 3600 | 2 | 757.84 | GGB | 764.835 | 769.547 | 763.37 | 265.56 | GGB | 10863.5 | GGB | 9.92 | GGB | 997.73 | GGB | 61.15 | GGB | 165892.42 | GGB | 133490.89 | GGB | 0 | 0 | 2460 | 3600 | 2444.43 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 20062.28 | GGB | 20062.52 | 2444.43 | 2444.43 |  |  |  | 1 | 1 |  |  |  |  | 133490.89 | 2444.43 | 133490.89 | 2444.43 | 8.4122 | [5 empty] | 90.6414
27.09.2007 01:00 | 3600 | 2 | 757.93 | GGB | 768.132 | 772.781 | 767.033 | 264.75 | GGB | 10912 | GGB | 9.93 | GGB | 997.99 | GGB | 61.85 | GGB | 164332.14 | GGB | 131993.82 | GGB | 0 | 0 | 2491 | 3600 | 2476.04 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 20102.85 | GGB | 20103.09 | 2476.04 | 2476.04 |  |  |  | 1 | 1 |  |  |  |  | 131993.82 | 2476.04 | 131993.82 | 2476.04 | 8.0558 | [5 empty] | 90.7839
27.09.2007 02:00 | 3600 | 2 | 757.24 | GGB | 768.132 | 772.102 | 767.033 | 266.23 | GGB | 10887.7 | GGB | 9.91 | GGB | 997.88 | GGB | 61.32 | GGB | 165930.93 | GGB | 133475.33 | GGB | 0 | 0 | 2503 | 3600 | 2487.94 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 20141.21 | GGB | 20141.45 | 2487.94 | 2487.94 |  |  |  | 1 | 1 |  |  |  |  | 133475.33 | 2487.94 | 133475.33 | 2487.94 | 8.6569 | [5 empty] | 92.2441
27.09.2007 03:00 | 3600 | 2 | 757.25 | GGB | 768.132 | 772.594 | 767.766 | 267.55 | GGB | 10915.7 | GGB | 9.92 | GGB | 998.37 | GGB | 60.76 | GGB | 167534.13 | GGB | 135057.23 | GGB | 0 | 0 | 2516 | 3600 | 2500.83 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 20181.66 | GGB | 20181.9 | 2500.83 | 2500.83 |  |  |  | 1 | 1 |  |  |  |  | 135057.23 | 2500.83 | 135057.23 | 2500.83 | 8.3499 | [5 empty] | 93.8209
27.09.2007 04:00 | 3600 | 2 | 758 | GGB | 765.934 | 771.258 | 765.201 | 266.62 | GGB | 10964.5 | GGB | 9.93 | GGB | 998.87 | GGB | 60.96 | GGB | 166870.62 | GGB | 134507.83 | GGB | 0 | 0 | 2504 | 3600 | 2489.22 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 20219.93 | GGB | 20220.17 | 2489.22 | 2489.22 |  |  |  | 1 | 1 |  |  |  |  | 134507.83 | 2489.22 | 134507.83 | 2489.22 | 8.7489 | [5 empty] | 93.0054
27.09.2007 05:00 | 3600 | 2 | 757.4 | GGB | 765.934 | 770.133 | 765.201 | 265.49 | GGB | 10954.9 | GGB | 9.92 | GGB | 998.79 | GGB | 61.44 | GGB | 165526.01 | GGB | 133224.47 | GGB | 0 | 0 | 2536 | 3600 | 2520.28 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 20260.72 | GGB | 20260.96 | 2520.28 | 2520.28 |  |  |  | 1 | 1 |  |  |  |  | 133224.47 | 2520.28 | 133224.47 | 2520.28 | 8.2315 | [5 empty] | 93.2675
27.09.2007 06:00 | 3600 | 2 | 757.08 | GGB | 765.934 | 770.484 | 764.102 | 266.02 | GGB | 10952 | GGB | 9.92 | GGB | 998.63 | GGB | 61.28 | GGB | 166190.61 | GGB | 133798.74 | GGB | 0 | 0 | 2543 | 3600 | 2528.14 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 20299.47 | GGB | 20299.71 | 2528.14 | 2528.14 |  |  |  | 1 | 1 |  |  |  |  | 133798.74 | 2528.14 | 133798.74 | 2528.14 | 8.7293 | [5 empty] | 93.9617
27.09.2007 07:00 | 3600 | 2 | 757.3 | GGB | 767.033 | 771.516 | 766.3 | 267.61 | GGB | 10939.8 | GGB | 9.92 | GGB | 999.29 | GGB | 60.62 | GGB | 168115.1 | GGB | 135704.62 | GGB | 0 | 0 | 2518 | 3600 | 2503.08 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 20339.7 | GGB | 20339.94 | 2503.08 | 2503.08 |  |  |  | 1 | 1 |  |  |  |  | 135704.62 | 2503.08 | 135704.62 | 2503.08 | 8.4434 | [5 empty] | 94.3554
27.09.2007 08:00 | 3600 | 2 | 757.67 | GGB | 767.033 | 771.516 | 766.3 | 266.21 | GGB | 10979.7 | GGB | 9.93 | GGB | 999.31 | GGB | 61.02 | GGB | 166171.91 | GGB | 133980.15 | GGB | 0 | 0 | 2524 | 3600 | 2508.96 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 20378.66 | GGB | 20378.9 | 2508.96 | 2508.96 |  |  |  | 1 | 1 |  |  |  |  | 133980.15 | 2508.96 | 133980.15 | 2508.96 | 8.6281 | [5 empty] | 93.3752
27.09.2007 09:00 | 3600 | 2 | 757.72 | GGB | 767.033 | 771.422 | 766.3 | 265.8 | GGB | 10978.8 | GGB | 9.93 | GGB | 999.78 | GGB | 61.27 | GGB | 165620.64 | GGB | 133498.44 | GGB | 0 | 0 | 2529 | 3600 | 2513.88 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 20418.81 | GGB | 20419.05 | 2513.88 | 2513.88 |  |  |  | 1 | 1 |  |  |  |  | 133498.44 | 2513.88 | 133498.44 | 2513.88 | 8.3586 | [5 empty] | 93.222
27.09.2007 10:00 | 3600 | 2 | 757.5 | GGB | 767.033 | 770.461 | 766.3 | 265.86 | GGB | 10920.3 | GGB | 9.92 | GGB | 999.87 | GGB | 61.27 | GGB | 165573.32 | GGB | 133473 | GGB | 0 | 0 | 2508 | 3600 | 2492.39 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 20458.25 | GGB | 20458.5 | 2492.39 | 2492.39 |  |  |  | 1 | 1 |  |  |  |  | 133473 | 2492.39 | 133473 | 2492.39 | 8.4326 | [5 empty] | 92.4074
27.09.2007 11:00 | 3600 | 2 | 758.39 | GGB | 768.132 | 772.734 | 766.667 | 265.78 | GGB | 10889.8 | GGB | 9.93 | GGB | 1000.34 | GGB | 61.15 | GGB | 165644.85 | GGB | 133638.62 | GGB | 0 | 0 | 2452 | 3600 | 2437.11 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 20496.55 | GGB | 20496.8 | 2437.11 | 2437.11 |  |  |  | 1 | 1 |  |  |  |  | 133638.62 | 2437.11 | 133638.62 | 2437.11 | 8.5037 | [5 empty] | 90.47
27.09.2007 12:00 | 3600 | 2 | 758.62 | GGB | 769.597 | 773.742 | 767.766 | 263.99 | GGB | 10857.2 | GGB | 9.94 | GGB | 1000.66 | GGB | 61.83 | GGB | 163798.48 | GGB | 131925.86 | GGB | 0 | 0 | 2429 | 3600 | 2413.86 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 20535.45 | GGB | 20535.7 | 2413.86 | 2413.86 |  |  |  | 1 | 1 |  |  |  |  | 131925.86 | 2413.86 | 131925.86 | 2413.86 | 8.1864 | [5 empty] | 88.4585
27.09.2007 13:00 | 3600 | 2 | 758.12 | GGB | 768.132 | 772.336 | 766.667 | 262.15 | GGB | 10804.6 | GGB | 9.93 | GGB | 1000.94 | GGB | 62.89 | GGB | 161536.18 | GGB | 129729.35 | GGB | 0 | 0 | 2443 | 3600 | 2427.6 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 20573.91 | GGB | 20574.16 | 2427.6 | 2427.6 |  |  |  | 1 | 1 |  |  |  |  | 129729.35 | 2427.6 | 129729.35 | 2427.6 | 8.1885 | [5 empty] | 87.4808
27.09.2007 14:00 | 3600 | 2 | 758.14 | GGB | 767.033 | 771.094 | 766.3 | 261.88 | GGB | 10746.8 | GGB | 9.92 | GGB | 1000.96 | GGB | 63.26 | GGB | 161102.65 | GGB | 129239.26 | GGB | 0 | 0 | 2421 | 3600 | 2405.54 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 20612.27 | GGB | 20612.52 | 2405.54 | 2405.54 |  |  |  | 1 | 1 |  |  |  |  | 129239.26 | 2405.54 | 129239.26 | 2405.54 | 8.1045 | [5 empty] | 86.3584
27.09.2007 15:00 | 3600 | 2 | 758.55 | GGB | 768.132 | 773.273 | 767.766 | 262.25 | GGB | 10681.1 | GGB | 9.93 | GGB | 1000.91 | GGB | 63.15 | GGB | 161543.89 | GGB | 129628.96 | GGB | 0 | 0 | 2369 | 3600 | 2353.55 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 20650.67 | GGB | 20650.92 | 2353.55 | 2353.55 |  |  |  | 1 | 1 |  |  |  |  | 129628.96 | 2353.55 | 129628.96 | 2353.55 | 7.945 | [5 empty] | 84.7467
27.09.2007 16:00 | 3600 | 2 | 758.71 | GGB | 768.132 | 773.273 | 767.766 | 260.87 | GGB | 10627.2 | GGB | 9.93 | GGB | 1000.46 | GGB | 63.56 | GGB | 160298.3 | GGB | 128416.05 | GGB | 0 | 0 | 2334 | 3600 | 2318.79 | GGB | 100 | GGB | 37.49 | GGB | 37.49 | GGB | 20688.15 | GGB | 20688.41 | 2318.79 | 2318.79 |  |  |  | 1 | 1 |  |  |  |  | 128416.05 | 2318.79 | 128416.05 | 2318.79 | 7.9426 | [5 empty] | 82.7138
27.09.2007 17:00 | 3600 | 2 | 759.02 | GGB | 768.132 | 772.945 | 767.033 | 258.89 | GGB | 10619.5 | GGB | 9.93 | GGB | 999.29 | GGB | 64.59 | GGB | 157773.03 | GGB | 125860.16 | GGB | 0 | 0 | 2333 | 3600 | 2317.44 | GGB | 100 | GGB | 37.71 | GGB | 37.71 | GGB | 20725.86 | GGB | 20726.12 | 2317.44 | 2317.44 |  |  |  | 1 | 1 |  |  |  |  | 125860.16 | 2317.44 | 125860.16 | 2317.44 | 7.7346 | [5 empty] | 81.0204
27.09.2007 18:00 | 3600 | 2 | 758.2 | GGB | 767.033 | 771.797 | 765.934 | 259.47 | GGB | 10596.4 | GGB | 9.92 | GGB | 997.96 | GGB | 64.35 | GGB | 158717.12 | GGB | 126535.67 | GGB | 0 | 0 | 2350 | 3600 | 2335.36 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 20763.99 | GGB | 20764.25 | 2335.36 | 2335.36 |  |  |  | 1 | 1 |  |  |  |  | 126535.67 | 2335.36 | 126535.67 | 2335.36 | 7.75 | [5 empty] | 82.0851
27.09.2007 19:00 | 3600 | 2 | 757.91 | GGB | 765.934 | 771.797 | 765.934 | 261.37 | GGB | 10602.9 | GGB | 9.91 | GGB | 997.34 | GGB | 63.31 | GGB | 161094.95 | GGB | 128748.39 | GGB | 0 | 0 | 2362 | 3600 | 2347.31 | GGB | 100 | GGB | 37.82 | GGB | 37.82 | GGB | 20801.81 | GGB | 20802.07 | 2347.31 | 2347.31 |  |  |  | 1 | 1 |  |  |  |  | 128748.39 | 2347.31 | 128748.39 | 2347.31 | 7.9908 | [5 empty] | 83.9479
27.09.2007 20:00 | 3600 | 2 | 757.78 | GGB | 767.033 | 771.633 | 765.934 | 262.65 | GGB | 10685.2 | GGB | 9.92 | GGB | 999.05 | GGB | 63.11 | GGB | 161977.42 | GGB | 129753.18 | GGB | 0 | 0 | 2397 | 3600 | 2381.95 | GGB | 100 | GGB | 38.02 | GGB | 38.02 | GGB | 20839.83 | GGB | 20840.09 | 2381.95 | 2381.95 |  |  |  | 1 | 1 |  |  |  |  | 129753.18 | 2381.95 | 129753.18 | 2381.95 | 8.129 | [5 empty] | 85.8516
27.09.2007 21:00 | 3600 | 2 | 757.17 | GGB | 764.835 | 770.484 | 764.835 | 263.3 | GGB | 10802.3 | GGB | 9.92 | GGB | 1000.27 | GGB | 62.97 | GGB | 162848.89 | GGB | 130663.99 | GGB | 0 | 0 | 2483 | 3600 | 2467.95 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 20878 | GGB | 20878.27 | 2467.95 | 2467.95 |  |  |  | 1 | 1 |  |  |  |  | 130663.99 | 2467.95 | 130663.99 | 2467.95 | 8.4461 | [5 empty] | 89.5756
27.09.2007 22:00 | 3600 | 2 | 756.6 | GGB | 765.934 | 770.695 | 765.201 | 265.81 | GGB | 10836.1 | GGB | 9.9 | GGB | 1001.09 | GGB | 62.46 | GGB | 164844.9 | GGB | 132576.6 | GGB | 0 | 0 | 2535 | 3600 | 2519.27 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 20916.6 | GGB | 20916.87 | 2519.27 | 2519.27 |  |  |  | 1 | 1 |  |  |  |  | 132576.6 | 2519.27 | 132576.6 | 2519.27 | 8.6528 | [5 empty] | 92.7767
27.09.2007 23:00 | 3600 | 2 | 756.82 | GGB | 765.934 | 771.258 | 765.201 | 267.5 | GGB | 10861.2 | GGB | 9.91 | GGB | 1001.32 | GGB | 61.51 | GGB | 166481.1 | GGB | 134302.6 | GGB | 0 | 0 | 2521 | 3600 | 2506.05 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 20954.88 | GGB | 20955.15 | 2506.05 | 2506.05 |  |  |  | 1 | 1 |  |  |  |  | 134302.6 | 2506.05 | 134302.6 | 2506.05 | 8.7923 | [5 empty] | 93.4914
27.09.2007 24:00 | 3600 | 2 | 757.59 | GGB | 765.934 | 771.375 | 765.201 | 266.22 | GGB | 10935.1 | GGB | 9.94 | GGB | 1001.43 | GGB | 61.73 | GGB | 165252.02 | GGB | 133236.63 | GGB | 0 | 0 | 2526 | 3600 | 2510.39 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 20993.59 | GGB | 20993.86 | 2510.39 | 2510.39 |  |  |  | 1 | 1 |  |  |  |  | 133236.63 | 2510.39 | 133236.63 | 2510.39 | 8.6406 | [5 empty] | 92.91
28.09.2007 01:00 | 3600 | 2 | 756.63 | GGB | 765.934 | 770.367 | 765.201 | 266.57 | GGB | 10936.3 | GGB | 9.92 | GGB | 1001.39 | GGB | 61.51 | GGB | 165786.79 | GGB | 133749.65 | GGB | 0 | 0 | 2568 | 3600 | 2552.41 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 21032.01 | GGB | 21032.28 | 2552.41 | 2552.41 |  |  |  | 1 | 1 |  |  |  |  | 133749.65 | 2552.41 | 133749.65 | 2552.41 | 8.8856 | [5 empty] | 94.8289
28.09.2007 02:00 | 3600 | 2 | 756.35 | GGB | 767.033 | 770.766 | 766.3 | 267.29 | GGB | 10965.5 | GGB | 9.92 | GGB | 1001.47 | GGB | 61.26 | GGB | 166694.57 | GGB | 134595.22 | GGB | 0 | 0 | 2594 | 3600 | 2578.47 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 21072.58 | GGB | 21072.85 | 2578.47 | 2578.47 |  |  |  | 1 | 1 |  |  |  |  | 134595.22 | 2578.47 | 134595.22 | 2578.47 | 8.5543 | [5 empty] | 96.4027
28.09.2007 03:00 | 3600 | 2 | 757.08 | GGB | 767.033 | 770.859 | 765.934 | 266.72 | GGB | 10971.7 | GGB | 9.93 | GGB | 1001.59 | GGB | 61.26 | GGB | 166689.07 | GGB | 134604.63 | GGB | 0 | 0 | 2563 | 3600 | 2547.84 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 21111.03 | GGB | 21111.3 | 2547.84 | 2547.84 |  |  |  | 1 | 1 |  |  |  |  | 134604.63 | 2547.84 | 134604.63 | 2547.84 | 8.9194 | [5 empty] | 95.2642
28.09.2007 04:00 | 3600 | 2 | 756.8 | GGB | 765.934 | 769.617 | 764.469 | 266.29 | GGB | 10954.1 | GGB | 9.92 | GGB | 1001.23 | GGB | 61.24 | GGB | 166410.68 | GGB | 134341.01 | GGB | 0 | 0 | 2565 | 3600 | 2549.56 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 21150.28 | GGB | 21150.55 | 2549.56 | 2549.56 |  |  |  | 1 | 1 |  |  |  |  | 134341.01 | 2549.56 | 134341.01 | 2549.56 | 8.7264 | [5 empty] | 95.1418
28.09.2007 05:00 | 3600 | 2 | 757.14 | GGB | 765.934 | 770.742 | 764.835 | 266.87 | GGB | 10969 | GGB | 9.93 | GGB | 1000.54 | GGB | 61.39 | GGB | 166411.78 | GGB | 134189.02 | GGB | 0 | 0 | 2565 | 3600 | 2549.39 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 21189.16 | GGB | 21189.43 | 2549.39 | 2549.39 |  |  |  | 1 | 1 |  |  |  |  | 134189.02 | 2549.39 | 134189.02 | 2549.39 | 8.7989 | [5 empty] | 95.0278
28.09.2007 06:00 | 3600 | 2 | 757.22 | GGB | 767.033 | 770.813 | 765.934 | 266.12 | GGB | 10951.7 | GGB | 9.93 | GGB | 1000.27 | GGB | 61.65 | GGB | 165729.57 | GGB | 133500.56 | GGB | 0 | 0 | 2552 | 3600 | 2536.29 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 21227.78 | GGB | 21228.05 | 2536.29 | 2536.29 |  |  |  | 1 | 1 |  |  |  |  | 133500.56 | 2536.29 | 133500.56 | 2536.29 | 8.7674 | [5 empty] | 94.0545
28.09.2007 07:00 | 3600 | 2 | 757.23 | GGB | 767.033 | 772.078 | 765.934 | 266.05 | GGB | 10938.6 | GGB | 9.92 | GGB | 1000.03 | GGB | 61.82 | GGB | 165704.26 | GGB | 133380.55 | GGB | 0 | 0 | 2554 | 3600 | 2538.82 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 21267.13 | GGB | 21267.41 | 2538.82 | 2538.82 |  |  |  | 1 | 1 |  |  |  |  | 133380.55 | 2538.82 | 133380.55 | 2538.82 | 8.6034 | [5 empty] | 94.0637
28.09.2007 08:00 | 3600 | 2 | 757.34 | GGB | 767.033 | 772.102 | 765.934 | 265.87 | GGB | 10935.7 | GGB | 9.93 | GGB | 999.88 | GGB | 62.01 | GGB | 165662.45 | GGB | 133249.74 | GGB | 0 | 0 | 2545 | 3600 | 2529.53 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 21305.71 | GGB | 21305.99 | 2529.53 | 2529.53 |  |  |  | 1 | 1 |  |  |  |  | 133249.74 | 2529.53 | 133249.74 | 2529.53 | 8.7366 | [5 empty] | 93.6276
28.09.2007 09:00 | 3600 | 2 | 757.7 | GGB | 767.033 | 772.242 | 767.033 | 264.8 | GGB | 10897.2 | GGB | 9.93 | GGB | 1000.07 | GGB | 62.34 | GGB | 164175.89 | GGB | 131950.44 | GGB | 0 | 0 | 2536 | 3207 | 2520.92 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 21344.89 | GGB | 21345.17 | 2520.92 | 2520.92 |  |  |  | 1 | 1 |  |  |  |  | 131950.44 | 2520.92 | 131950.44 | 2520.92 | 8.49 | [5 empty] | 92.399
28.09.2007 10:00 | 3600 | 2 | 757.86 | GGB | 767.033 | 772.055 | 767.033 | 263.57 | GGB | 10846.1 | GGB | 9.93 | GGB | 999.71 | GGB | 62.71 | GGB | 162725.65 | GGB | 130593.56 | GGB | 0 | 0 | 2518 | 3600 | 2502.82 | GGB | 100 | GGB | 38.69 | GGB | 38.69 | GGB | 21383.58 | GGB | 21383.86 | 2502.82 | 2502.82 |  |  |  | 1 | 1 |  |  |  |  | 130593.56 | 2502.82 | 130593.56 | 2502.82 | 8.448 | [5 empty] | 90.7923
28.09.2007 11:00 | 3600 | 2 | 758.03 | GGB | 767.033 | 773.203 | 767.033 | 261.48 | GGB | 10752.4 | GGB | 9.94 | GGB | 999.75 | GGB | 63.32 | GGB | 160084.84 | GGB | 128245.34 | GGB | 0 | 0 | 2470 | 3600 | 2454.71 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 21421.94 | GGB | 21422.23 | 2454.71 | 2454.71 |  |  |  | 1 | 1 |  |  |  |  | 128245.34 | 2454.71 | 128245.34 | 2454.71 | 8.2045 | [5 empty] | 87.4459
28.09.2007 12:00 | 3600 | 2 | 757.93 | GGB | 768.132 | 772.219 | 767.033 | 260.21 | GGB | 10673.8 | GGB | 9.93 | GGB | 999.38 | GGB | 63.73 | GGB | 158168.05 | GGB | 126509.71 | GGB | 0 | 0 | 2444 | 3600 | 2429.1 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 21460.17 | GGB | 21460.45 | 2429.1 | 2429.1 |  |  |  | 1 | 1 |  |  |  |  | 126509.71 | 2429.1 | 126509.71 | 2429.1 | 8.0404 | [5 empty] | 85.3624
28.09.2007 13:00 | 3600 | 2 | 757.99 | GGB | 767.033 | 773.227 | 767.033 | 259.72 | GGB | 10631.5 | GGB | 9.93 | GGB | 998.62 | GGB | 64.27 | GGB | 157342.8 | GGB | 125550.95 | GGB | 0 | 0 | 2431 | 3600 | 2415.95 | GGB | 100 | GGB | 37.93 | GGB | 37.93 | GGB | 21498.09 | GGB | 21498.38 | 2415.95 | 2415.95 |  |  |  | 1 | 1 |  |  |  |  | 125550.95 | 2415.95 | 125550.95 | 2415.95 | 7.997 | [5 empty] | 84.2569
28.09.2007 14:00 | 3600 | 2 | 757.95 | GGB | 767.033 | 772.125 | 767.033 | 259.23 | GGB | 10585.7 | GGB | 9.93 | GGB | 998.64 | GGB | 64.81 | GGB | 156744.21 | GGB | 124877.51 | GGB | 0 | 0 | 2417 | 3600 | 2401.44 | GGB | 100 | GGB | 38.09 | GGB | 38.09 | GGB | 21536.18 | GGB | 21536.47 | 2401.44 | 2401.44 |  |  |  | 1 | 1 |  |  |  |  | 124877.51 | 2401.44 |  | 2401.44 | 7.8731 | [5 empty] | 83.3016
28.09.2007 15:00 | 3600 | 2 | 757.9 | GGB | 769.597 | 774.258 | 768.498 | 260.04 | GGB | 10562.2 | GGB | 9.93 | GGB | 998.25 | GGB | 64.63 | GGB | 157364.8 | GGB | 125389.74 | GGB | 0 | 0 | 2404 | 3600 | 2388.95 | GGB | 100 | GGB | 37.58 | GGB | 37.58 | GGB | 21573.76 | GGB | 21574.05 | 2388.95 | 2388.95 |  |  |  | 1 | 1 |  |  |  |  | 125389.74 | 2388.95 |  | 2388.95 | 7.971 | [5 empty] | 83.2083
28.09.2007 16:00 | 3600 | 2 | 757.71 | GGB | 767.033 | 772.219 | 767.033 | 258.88 | GGB | 10559.8 | GGB | 9.92 | GGB | 998.01 | GGB | 65.12 | GGB | 156241.36 | GGB | 124284.79 | GGB | 0 | 0 | 2414 | 3600 | 2398.78 | GGB | 100 | GGB | 37.67 | GGB | 37.67 | GGB | 21611.43 | GGB | 21611.72 | 2398.78 | 2398.78 |  |  |  | 1 | 1 |  |  |  |  | 124284.79 | 2398.78 |  | 2398.78 | 7.9143 | [5 empty] | 82.8144
28.09.2007 17:00 | 3600 | 2 | 757.77 | GGB | 767.033 | 773.273 | 767.033 | 258.72 | GGB | 10556.8 | GGB | 9.93 | GGB | 997.48 | GGB | 65.12 | GGB | 156236.96 | GGB | 124213 | GGB | 0 | 0 | 2411 | 3600 | 2396.3 | GGB | 100 | GGB | 37.45 | GGB | 37.45 | GGB | 21648.88 | GGB | 21649.17 | 2396.3 | 2396.3 |  |  |  | 1 | 1 |  |  |  |  | 124213 | 2396.3 |  | 2396.3 | 7.948 | [5 empty] | 82.681
28.09.2007 18:00 | 3600 | 2 | 757.62 | GGB | 768.132 | 773.203 | 767.033 | 260.13 | GGB | 10519.5 | GGB | 9.92 | GGB | 997.54 | GGB | 64.68 | GGB | 157730.12 | GGB | 125571.15 | GGB | 0 | 0 | 2401 | 3600 | 2385.93 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 21686.79 | GGB | 21687.08 | 2385.93 | 2385.93 |  |  |  | 1 | 1 |  |  |  |  | 125571.15 | 2385.93 | 125571.15 | 2385.93 | 7.903 | [5 empty] | 83.2233
28.09.2007 19:00 | 3600 | 2 | 757.91 | GGB | 768.132 | 773.156 | 767.033 | 259.84 | GGB | 10522.1 | GGB | 9.92 | GGB | 997.67 | GGB | 64.92 | GGB | 156923.57 | GGB | 124858.93 | GGB | 0 | 0 | 2387 | 3600 | 2371.71 | GGB | 100 | GGB | 37.05 | GGB | 37.05 | GGB | 21723.84 | GGB | 21724.13 | 2371.71 | 2371.71 |  |  |  | 1 | 1 |  |  |  |  | 124858.93 | 2371.71 |  | 2371.71 | 7.9927 | [5 empty] | 82.2581
28.09.2007 20:00 | 3600 | 2 | 757.42 | GGB | 767.033 | 772.055 | 765.934 | 259.69 | GGB | 10558.8 | GGB | 9.92 | GGB | 997.39 | GGB | 65.35 | GGB | 156309.58 | GGB | 124176.89 | GGB | 0 | 0 | 2430 | 3600 | 2414.86 | GGB | 100 | GGB | 37.88 | GGB | 37.88 | GGB | 21761.71 | GGB | 21762.01 | 2414.86 | 2414.86 |  |  |  | 1 | 1 |  |  |  |  | 124176.89 | 2414.86 |  | 2414.86 | 7.9163 | [5 empty] | 83.2972
28.09.2007 21:00 | 3600 | 2 | 757.83 | GGB | 767.033 | 772.172 | 765.934 | 261.04 | GGB | 10620.5 | GGB | 9.93 | GGB | 997.14 | GGB | 64.81 | GGB | 157427.52 | GGB | 125231.28 | GGB | 0 | 0 | 2447 | 3600 | 2431.64 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 21798.87 | GGB | 21799.17 | 2431.64 | 2431.64 |  |  |  | 1 | 1 |  |  |  |  | 125231.28 | 2431.64 |  | 2431.64 | 8.1948 | [5 empty] | 84.5882
28.09.2007 22:00 | 3600 | 2 | 757.25 | GGB | 767.033 | 771.938 | 767.033 | 261.07 | GGB | 10619.4 | GGB | 9.92 | GGB | 997.43 | GGB | 64.48 | GGB | 157866.56 | GGB | 125742.66 | GGB | 0 | 0 | 2476 | 3600 | 2461.28 | GGB | 100 | GGB | 37.76 | GGB | 37.76 | GGB | 21836.63 | GGB | 21836.93 | 2461.28 | 2461.28 |  |  |  | 1 | 1 |  |  |  |  | 125742.66 | 2461.28 | 125742.66 | 2461.28 | 8.1962 | [5 empty] | 85.9689
28.09.2007 23:00 | 3600 | 2 | 757.61 | GGB | 765.934 | 771.117 | 765.934 | 260.4 | GGB | 10652.5 | GGB | 9.93 | GGB | 997.21 | GGB | 64.14 | GGB | 158387.02 | GGB | 126255.67 | GGB | 0 | 0 | 2461 | 3600 | 2445.58 | GGB | 100 | GGB | 36.29 | GGB | 36.29 | GGB | 21872.92 | GGB | 21873.22 | 2445.58 | 2445.58 |  |  |  | 1 | 1 |  |  |  |  | 126255.67 | 2445.58 | 126255.67 | 2445.58 | 8.5084 | [5 empty] | 85.769
28.09.2007 24:00 | 3600 | 2 | 757.79 | GGB | 767.033 | 771.984 | 765.934 | 260.11 | GGB | 10621.1 | GGB | 9.93 | GGB | 997.56 | GGB | 64.67 | GGB | 159776.74 | GGB | 127208.74 | GGB | 0 | 0 | 2448 | 3600 | 2433.29 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 21911.42 | GGB | 21911.72 | 2433.29 | 2433.29 |  |  |  | 1 | 1 |  |  |  |  | 127208.74 | 2433.29 | 127208.74 | 2433.29 | 8.0399 | [5 empty] | 85.9822
29.09.2007 01:00 | 3600 | 2 | 757.57 | GGB | 767.033 | 771.984 | 765.934 | 259.23 | GGB | 10586.2 | GGB | 9.93 | GGB | 997.23 | GGB | 64.84 | GGB | 160155.26 | GGB | 127404.23 | GGB | 0 | 0 | 2428 | 3600 | 2412.82 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 21949.5 | GGB | 21949.8 | 2412.82 | 2412.82 |  |  |  | 1 | 1 |  |  |  |  | 127404.23 | 2412.82 | 127404.23 | 2412.82 | 8.0726 | [5 empty] | 85.3899
29.09.2007 02:00 | 3600 | 2 | 757.55 | GGB | 767.033 | 772.102 | 767.033 | 259.19 | GGB | 10580.8 | GGB | 9.93 | GGB | 997.05 | GGB | 64.75 | GGB | 160299.4 | GGB | 127528.48 | GGB | 0 | 0 | 2428 | 3600 | 2412.33 | GGB | 100 | GGB | 37.49 | GGB | 37.49 | GGB | 21986.99 | GGB | 21987.29 | 2412.33 | 2412.33 |  |  |  | 1 | 1 |  |  |  |  | 127528.48 | 2412.33 | 127528.48 | 2412.33 | 8.2059 | [5 empty] | 85.4558
29.09.2007 03:00 | 3600 | 2 | 757.4 | GGB | 767.033 | 772.055 | 765.934 | 259.63 | GGB | 10584.4 | GGB | 9.92 | GGB | 997.28 | GGB | 64.74 | GGB | 160249.89 | GGB | 127520.97 | GGB | 0 | 0 | 2438 | 3600 | 2422.77 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 22024.79 | GGB | 22025.1 | 2422.77 | 2422.77 |  |  |  | 1 | 1 |  |  |  |  | 127520.97 | 2422.77 | 127520.97 | 2422.77 | 8.1712 | [5 empty] | 85.8206
29.09.2007 04:00 | 3600 | 2 | 757.26 | GGB | 767.033 | 772.055 | 765.934 | 261.07 | GGB | 10565.8 | GGB | 9.92 | GGB | 997.33 | GGB | 64.41 | GGB | 161689.13 | GGB | 128800.77 | GGB | 0 | 0 | 2432 | 3600 | 2416.52 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 22062.6 | GGB | 22062.91 | 2416.52 | 2416.52 |  |  |  | 1 | 1 |  |  |  |  | 128800.77 | 2416.52 | 128800.77 | 2416.52 | 8.2319 | [5 empty] | 86.4582
29.09.2007 05:00 | 3600 | 2 | 757.63 | GGB | 765.934 | 771.141 | 765.934 | 261.44 | GGB | 10570.6 | GGB | 9.93 | GGB | 997.6 | GGB | 64.02 | GGB | 162782.87 | GGB | 129857.06 | GGB | 0 | 0 | 2411 | 3600 | 2396.06 | GGB | 100 | GGB | 37.51 | GGB | 37.51 | GGB | 22100.11 | GGB | 22100.42 | 2396.06 | 2396.06 |  |  |  | 1 | 1 |  |  |  |  | 129857.06 | 2396.06 | 129857.06 | 2396.06 | 8.295 | [5 empty] | 86.4293
29.09.2007 06:00 | 3600 | 2 | 757.68 | GGB | 767.033 | 772.5 | 765.934 | 260.65 | GGB | 10583.2 | GGB | 9.93 | GGB | 998.01 | GGB | 64.08 | GGB | 160388.53 | GGB | 127974.88 | GGB | 0 | 0 | 2418 | 3600 | 2402.38 | GGB | 100 | GGB | 37.69 | GGB | 37.69 | GGB | 22137.79 | GGB | 22138.11 | 2402.38 | 2402.38 |  |  |  | 1 | 1 |  |  |  |  | 127974.88 | 2402.38 | 127974.88 | 2402.38 | 8.1572 | [5 empty] | 85.4012
29.09.2007 07:00 | 3600 | 2 | 757.2 | GGB | 767.033 | 772.477 | 767.033 | 259.96 | GGB | 10590.9 | GGB | 9.92 | GGB | 998.11 | GGB | 64.64 | GGB | 158223.07 | GGB | 126051.48 | GGB | 0 | 0 | 2449 | 3600 | 2434.1 | GGB | 100 | GGB | 37.66 | GGB | 37.66 | GGB | 22175.45 | GGB | 22175.77 | 2434.1 | 2434.1 |  |  |  | 1 | 1 |  |  |  |  | 126051.48 | 2434.1 | 126051.48 | 2434.1 | 8.1472 | [5 empty] | 85.2283
29.09.2007 08:00 | 3600 | 2 | 757.51 | GGB | 767.033 | 772.359 | 765.934 | 259.93 | GGB | 10583 | GGB | 9.92 | GGB | 998.29 | GGB | 64.74 | GGB | 158053.61 | GGB | 125901.3 | GGB | 0 | 0 | 2442 | 3600 | 2426.78 | GGB | 100 | GGB | 37.83 | GGB | 37.83 | GGB | 22213.28 | GGB | 22213.6 | 2426.78 | 2426.78 |  |  |  | 1 | 1 |  |  |  |  | 125901.3 | 2426.78 | 125901.3 | 2426.78 | 8.0765 | [5 empty] | 84.8708
29.09.2007 09:00 | 3600 | 2 | 757.63 | GGB | 767.033 | 772.313 | 767.033 | 259.99 | GGB | 10584.5 | GGB | 9.93 | GGB | 999.63 | GGB | 65 | GGB | 157456.13 | GGB | 125498.15 | GGB | 0 | 0 | 2441 | 3600 | 2425.33 | GGB | 100 | GGB | 37.82 | GGB | 37.82 | GGB | 22251.1 | GGB | 22251.42 | 2425.33 | 2425.33 |  |  |  | 1 | 1 |  |  |  |  | 125498.15 | 2425.33 | 125498.15 | 2425.33 | 8.048 | [5 empty] | 84.5485
29.09.2007 10:00 | 3600 | 2 | 757.67 | GGB | 765.934 | 771.234 | 765.934 | 258.89 | GGB | 10537.8 | GGB | 9.92 | GGB | 1000.22 | GGB | 65.32 | GGB | 156348.09 | GGB | 124568.53 | GGB | 0 | 0 | 2418 | 3600 | 2402.51 | GGB | 100 | GGB | 37.57 | GGB | 37.57 | GGB | 22288.67 | GGB | 22288.99 | 2402.51 | 2402.51 |  |  |  | 1 | 1 |  |  |  |  | 124568.53 | 2402.51 |  | 2402.51 | 7.9659 | [5 empty] | 83.1325
29.09.2007 11:00 | 3600 | 2 | 758.13 | GGB | 768.132 | 773.18 | 768.132 | 258.67 | GGB | 10525.2 | GGB | 9.93 | GGB | 1000.85 | GGB | 65.58 | GGB | 155983.88 | GGB | 124262.2 | GGB | 0 | 0 | 2385 | 3600 | 2369.97 | GGB | 100 | GGB | 37.66 | GGB | 37.66 | GGB | 22326.33 | GGB | 22326.65 | 2369.97 | 2369.97 |  |  |  | 1 | 1 |  |  |  |  | 124262.2 | 2369.97 |  | 2369.97 | 7.8199 | [5 empty] | 81.8049
29.09.2007 12:00 | 3600 | 2 | 758.14 | GGB | 768.498 | 773.461 | 767.766 | 259.01 | GGB | 10501.6 | GGB | 9.92 | GGB | 1000.93 | GGB | 65.42 | GGB | 156380 | GGB | 124648.82 | GGB | 0 | 0 | 2366 | 3600 | 2350.49 | GGB | 100 | GGB | 37.35 | GGB | 37.35 | GGB | 22363.68 | GGB | 22364 | 2350.49 | 2350.49 |  |  |  | 1 | 1 |  |  |  |  | 124648.82 | 2350.49 |  | 2350.49 | 7.8443 | [5 empty] | 81.3849
29.09.2007 13:00 | 3600 | 2 | 757.93 | GGB | 768.132 | 773.414 | 766.667 | 258.87 | GGB | 10533.4 | GGB | 9.93 | GGB | 1001.12 | GGB | 65.55 | GGB | 155860.64 | GGB | 124208.42 | GGB | 0 | 0 | 2393 | 3600 | 2378.32 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 22401.54 | GGB | 22401.86 | 2378.32 | 2378.32 |  |  |  | 1 | 1 |  |  |  |  | 124208.42 | 2378.32 |  | 2378.32 | 7.8026 | [5 empty] | 82.0576
29.09.2007 14:00 | 3600 | 2 | 758.19 | GGB | 767.033 | 772.172 | 766.667 | 257.6 | GGB | 10492.6 | GGB | 9.93 | GGB | 1002.02 | GGB | 66.03 | GGB | 154790.01 | GGB | 123294.1 | GNB | 0 | 0 | 2373 | 3600 | 2357.76 | GGB | 100 | GGB | 37.52 | GGB | 37.52 | GGB | 22439.06 | GGB | 22439.38 | 2357.76 | 2357.76 |  |  |  | 1 | 1 |  |  |  |  | 123294.1 | 2357.76 |  | 2357.76 | 7.7478 | [5 empty] | 80.7494
29.09.2007 15:00 | 3600 | 2 | 758.24 | GGB | 768.132 | 773.32 | 767.766 | 256.6 | GGB | 10443.8 | GGB | 9.93 | GGB | 1002.13 | GGB | 66.47 | GGB | 153617.05 | GGB | 122212.59 | GNB | 0 | 0 | 2347 | 3600 | 2332.18 | GGB | 100 | GGB | 37.6 | GGB | 37.6 | GGB | 22476.66 | GGB | 22476.98 | 2332.18 | 2332.18 |  |  |  | 1 | 1 |  |  |  |  | 122212.59 | 2332.18 |  | 2332.18 | 7.5804 | [5 empty] | 79.1727
29.09.2007 16:00 | 3600 | 2 | 758.64 | GGB | 768.132 | 774.422 | 767.766 | 255.97 | GGB | 10412.1 | GGB | 9.93 | GGB | 1002.05 | GGB | 66.73 | GGB | 153651.16 | GGB | 122135.51 | GNB | 0 | 0 | 2309 | 3600 | 2293.9 | GGB | 100 | GGB | 37.25 | GGB | 37.25 | GGB | 22513.91 | GGB | 22514.23 | 2293.9 | 2293.9 |  |  |  | 1 | 1 |  |  |  |  | 122135.51 | 2293.9 |  |  | 7.5213 | [5 empty] | 77.8241
29.09.2007 17:00 | 3600 | 2 | 758.52 | GGB | 767.033 | 772.758 | 767.766 | 255.71 | GGB | 10393.3 | GGB | 9.92 | GGB | 1001.56 | GGB | 66.92 | GGB | 153530.13 | GGB | 121911.7 | GNB | 0 | 0 | 2299 | 3600 | 2284.05 | GGB | 100 | GGB | 37.18 | GGB | 37.18 | GGB | 22551.09 | GGB | 22551.41 | 2284.05 | 2284.05 |  |  |  | 1 | 1 |  |  |  |  | 121911.7 | 2284.05 |  |  | 7.4893 | [5 empty] | 77.3479
29.09.2007 18:00 | 3600 | 2 | 758.1 | GGB | 768.132 | 772.828 | 767.766 | 256.81 | GGB | 10433.2 | GGB | 9.92 | GGB | 993.36 | GGB | 66.59 | GGB | 154575.45 | GGB | 121854.68 | GNB | 0 | 0 | 2338 | 3600 | 2323.15 | GGB | 100 | GGB | 37.34 | GGB | 37.34 | GGB | 22588.43 | GGB | 22588.75 | 2323.15 | 2323.15 |  |  |  | 1 | 1 |  |  |  |  | 121854.68 | 2323.15 |  | 2323.15 | 7.5813 | [5 empty] | 78.6352
29.09.2007 19:00 | 3600 | 2 | 757.81 | GGB | 768.132 | 773.086 | 767.766 | 258 | GGB | 10463.5 | GGB | 9.92 | GGB | 995.19 | GGB | 66.26 | GGB | 155420.51 | GGB | 122865.02 | GNB | 0 | 0 | 2368 | 3600 | 2353.07 | GGB | 100 | GGB | 37.52 | GGB | 37.52 | GGB | 22625.94 | GGB | 22626.27 | 2353.07 | 2353.07 |  |  |  | 1 | 1 |  |  |  |  | 122865.02 | 2353.07 |  | 2353.07 | 7.7055 | [5 empty] | 80.3083
29.09.2007 20:00 | 3600 | 2 | 757.53 | GGB | 767.033 | 773.297 | 766.3 | 260.65 | GGB | 10470.4 | GGB | 9.91 | GGB | 996.41 | GGB | 65.21 | GGB | 158668.7 | GGB | 125979.56 | GGB | 0 | 0 | 2382 | 3600 | 2366.79 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 22663.26 | GGB | 22663.59 | 2366.79 | 2366.79 |  |  |  | 1 | 1 |  |  |  |  | 125979.56 | 2366.79 | 125979.56 | 2366.79 | 7.9895 | [5 empty] | 82.8242
29.09.2007 21:00 | 3600 | 2 | 757.79 | GGB | 767.033 | 773.227 | 767.766 | 260.97 | GGB | 10558.4 | GGB | 9.93 | GGB | 1001.31 | GGB | 64.84 | GGB | 159612.79 | GGB | 127490.41 | GGB | 0 | 0 | 2408 | 3600 | 2392.51 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 22700.81 | GGB | 22701.14 | 2392.51 | 2392.51 |  |  |  | 1 | 1 |  |  |  |  | 127490.41 | 2392.51 | 127490.41 | 2392.51 | 8.1231 | [5 empty] | 84.7284
29.09.2007 22:00 | 3600 | 2 | 757.5 | GGB | 767.033 | 772.102 | 766.667 | 259.42 | GGB | 10560.6 | GGB | 9.93 | GGB | 1003.19 | GGB | 65.26 | GGB | 157073.21 | GGB | 125541.06 | GGB | 0 | 0 | 2439 | 3600 | 2424.05 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 22737.76 | GGB | 22738.1 | 2424.05 | 2424.05 |  |  |  | 1 | 1 |  |  |  |  | 125541.06 | 2424.05 | 125541.06 | 2424.05 | 8.2337 | [5 empty] | 84.5327
29.09.2007 23:00 | 3600 | 2 | 756.96 | GGB | 763.37 | 769.875 | 764.102 | 259.63 | GGB | 10586.6 | GGB | 9.92 | GGB | 1003.49 | GGB | 64.76 | GGB | 157491.34 | GGB | 126100.84 | GGB | 0 | 0 | 2473 | 3600 | 2457.89 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 22776.83 | GGB | 22777.16 | 2457.89 | 2457.89 |  |  |  | 0 | 1 | [14 empty] | 86.095
29.09.2007 24:00 | 3600 | 2 | 756.57 | GGB | 765.934 | 771.094 | 765.201 | 261.43 | GGB | 10628.7 | GGB | 9.92 | GGB | 1004.2 | GGB | 64.11 | GGB | 158912.98 | GGB | 127573.18 | GGB | 0 | 0 | 2523 | 3600 | 2508.23 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 22815.23 | GGB | 22815.56 | 2508.23 | 2508.23 |  |  |  | 1 | 1 |  |  |  |  | 127573.18 | 2508.23 | 127573.18 | 2508.23 | 8.3329 | [5 empty] | 88.8841
30.09.2007 01:00 | 3600 | 2 | 756.55 | GGB | 765.934 | 771.164 | 765.201 | 262.35 | GGB | 10677.6 | GGB | 9.92 | GGB | 1004.69 | GGB | 63.8 | GGB | 159808.65 | GGB | 128472.28 | GGB | 0 | 0 | 2534 | 3600 | 2519.24 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 22853.18 | GGB | 22853.51 | 2519.24 | 2519.24 |  |  |  | 1 | 1 |  |  |  |  | 128472.28 | 2519.24 | 128472.28 | 2519.24 | 8.5284 | [5 empty] | 89.9035
30.09.2007 02:00 | 3600 | 2 | 756.49 | GGB | 767.033 | 771.984 | 766.3 | 263.05 | GGB | 10715 | GGB | 9.92 | GGB | 1004.8 | GGB | 63.46 | GGB | 160823.17 | GGB | 129434.1 | GGB | 0 | 0 | 2550 | 3600 | 2535.2 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 22891.69 | GGB | 22892.03 | 2535.2 | 2535.2 |  |  |  | 1 | 1 |  |  |  |  | 129434.1 | 2535.2 | 129434.1 | 2535.2 | 8.5187 | [5 empty] | 91.1504
30.09.2007 03:00 | 3600 | 2 | 756.35 | GGB | 765.934 | 771.914 | 765.201 | 263.24 | GGB | 10737.3 | GGB | 9.92 | GGB | 1005.52 | GGB | 63.45 | GGB | 161124.66 | GGB | 129772.66 | GGB | 0 | 0 | 2565 | 3600 | 2549.9 | GGB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 22929.82 | GGB | 22930.15 | 2549.9 | 2549.9 |  |  |  | 1 | 1 |  |  |  |  | 129772.66 | 2549.9 | 129772.66 | 2549.9 | 8.6807 | [5 empty] | 91.9187
30.09.2007 04:00 | 3600 | 2 | 756.25 | GGB | 764.835 | 770.109 | 765.201 | 264.02 | GGB | 10744 | GGB | 9.92 | GGB | 1005.62 | GGB | 63.39 | GGB | 161937.81 | GGB | 130465.47 | GGB | 0 | 0 | 2577 | 3600 | 2561.85 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 22968.45 | GGB | 22968.79 | 2561.85 | 2561.85 |  |  |  | 1 | 1 |  |  |  |  | 130465.47 | 2561.85 | 130465.47 | 2561.85 | 8.6499 | [5 empty] | 92.8425
30.09.2007 05:00 | 3600 | 2 | 756.47 | GGB | 767.033 | 772.148 | 766.3 | 265.33 | GGB | 10751.6 | GGB | 9.92 | GGB | 1005.61 | GGB | 62.92 | GGB | 163313.23 | GGB | 131755.02 | GGB | 0 | 0 | 2567 | 3600 | 2551.88 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 23006.84 | GGB | 23007.17 | 2551.88 | 2551.88 |  |  |  | 1 | 1 |  |  |  |  | 131755.02 | 2551.88 | 131755.02 | 2551.88 | 8.7604 | [5 empty] | 93.3953
30.09.2007 06:00 | 3600 | 2 | 756.68 | GGB | 767.033 | 771.656 | 765.934 | 265.51 | GGB | 10748.4 | GGB | 9.92 | GGB | 1005.98 | GGB | 62.69 | GGB | 163659.84 | GGB | 132174.12 | GGB | 0 | 0 | 2558 | 3600 | 2542.47 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 23045.11 | GGB | 23045.44 | 2542.47 | 2542.47 |  |  |  | 1 | 1 |  |  |  |  | 132174.12 | 2542.47 | 132174.12 | 2542.47 | 8.781 | [5 empty] | 93.3469
30.09.2007 07:00 | 3600 | 2 | 756.82 | GGB | 765.934 | 771.469 | 765.934 | 265.06 | GGB | 10753.5 | GGB | 9.93 | GGB | 1006.09 | GGB | 62.72 | GGB | 163295.62 | GGB | 131882.62 | GGB | 0 | 0 | 2545 | 3600 | 2529.77 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 23085.12 | GGB | 23085.45 | 2529.77 | 2529.77 |  |  |  | 1 | 1 |  |  |  |  | 131882.62 | 2529.77 | 131882.62 | 2529.77 | 8.3387 | [5 empty] | 92.6757
30.09.2007 08:00 | 3600 | 2 | 756.72 | GGB | 767.033 | 772.922 | 767.033 | 267.88 | GGB | 10870.3 | GGB | 9.89 | GGB | 1006.63 | GGB | 62.09 | GGB | 167491.21 | GGB | 135597.86 | GGB | 0 | 0 | 2598 | 3600 | 2582.41 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 23124.62 | GGB | 23124.95 | 2582.41 | 2582.41 |  |  |  | 1 | 1 |  |  |  |  | 135597.86 | 2582.41 | 135597.86 | 2582.41 | 8.865 | [5 empty] | 97.2692
30.09.2007 09:00 | 3600 | 2 | 758.58 | GGB | 768.132 | 771.773 | 767.033 | 267.92 | GGB | 10922.8 | GGB | 9.93 | GGB | 1007.34 | GGB | 62.3 | GGB | 167035.67 | GGB | 135240.01 | GGB | 0 | 0 | 2530 | 3600 | 2514.72 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 23165.38 | GGB | 23165.71 | 2514.72 | 2514.72 |  |  |  | 1 | 1 |  |  |  |  | 135240.01 | 2514.72 | 135240.01 | 2514.72 | 8.3437 | [5 empty] | 94.4697
30.09.2007 10:00 | 3600 | 2 | 758.88 | GGB | 767.033 | 772.922 | 767.033 | 267.26 | GGB | 10897.8 | GGB | 9.93 | GGB | 1007.28 | GGB | 62.44 | GGB | 166215.92 | GGB | 134513.24 | GGB | 0 | 0 | 2507 | 3600 | 2491.71 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 23205.61 | GGB | 23205.94 | 2491.71 | 2491.71 |  |  |  | 1 | 1 |  |  |  |  | 134513.24 | 2491.71 | 134513.24 | 2491.71 | 8.3313 | [5 empty] | 93.1022
30.09.2007 11:00 | 3600 | 2 | 759.32 | GGB | 768.498 | 774.094 | 768.132 | 266.23 | GGB | 10860.9 | GGB | 9.93 | GGB | 1008.04 | GGB | 62.81 | GGB | 165140.89 | GGB | 133596.5 | GGB | 0 | 0 | 2478 | 3600 | 2462.65 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 23245.75 | GGB | 23246.07 | 2462.65 | 2462.65 |  |  |  | 1 | 1 |  |  |  |  | 133596.5 | 2462.65 | 133596.5 | 2462.65 | 8.1984 | [5 empty] | 91.3893
30.09.2007 12:00 | 3600 | 2 | 759.58 | GGB | 768.498 | 773.789 | 768.132 | 264.71 | GGB | 10794.7 | GGB | 9.93 | GGB | 1008.03 | GGB | 63.23 | GGB | 163526.69 | GGB | 132124.72 | GGB | 0 | 0 | 2434 | 3600 | 2419.32 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 23285.98 | GGB | 23286.3 | 2419.32 | 2419.32 |  |  |  | 1 | 1 |  |  |  |  | 132124.72 | 2419.32 | 132124.72 | 2419.32 | 7.9456 | [5 empty] | 88.7922
30.09.2007 13:00 | 3600 | 2 | 760.11 | GGB | 769.597 | 774.914 | 768.498 | 261.98 | GGB | 10739.4 | GGB | 9.94 | GGB | 1008.55 | GGB | 64.25 | GGB | 160811.06 | GGB | 129602.11 | GGB | 0 | 0 | 2391 | 3600 | 2376.06 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 23325.43 | GGB | 23325.75 | 2376.06 | 2376.06 |  |  |  | 1 | 1 |  |  |  |  | 129602.11 | 2376.06 | 129602.11 | 2376.06 | 7.8059 | [5 empty] | 85.5396
30.09.2007 14:00 | 3600 | 2 | 760.29 | GGB | 769.597 | 775.078 | 769.597 | 259.46 | GGB | 10647.3 | GGB | 9.93 | GGB | 1007.68 | GGB | 65.48 | GGB | 157690.5 | GGB | 126518.88 | GGB | 0 | 0 | 2358 | 3600 | 2343.38 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 23365.35 | GGB | 23365.67 | 2343.38 | 2343.38 |  |  |  | 1 | 1 |  |  |  |  | 126518.88 | 2343.38 | 126518.88 | 2343.38 | 7.4269 | [5 empty] | 82.3561
30.09.2007 15:00 | 3600 | 2 | 760.23 | GGB | 769.597 | 775.125 | 769.597 | 258.38 | GGB | 10573.2 | GGB | 9.92 | GGB | 1006.39 | GGB | 66.15 | GGB | 156355.79 | GGB | 125040.06 | GGB | 0 | 0 | 2320 | 3600 | 2304.65 | GGB | 100 | GGB | 38.26 | GGB | 38.26 | GGB | 23403.6 | GGB | 23403.93 | 2304.65 | 2304.65 |  |  |  | 1 | 1 |  |  |  |  | 125040.06 | 2304.65 |  |  | 7.532 | [5 empty] | 80.0482
30.09.2007 16:00 | 3600 | 2 | 760.33 | GGB | 769.597 | 775.125 | 769.597 | 258.14 | GGB | 10554.2 | GGB | 9.92 | GGB | 1004.54 | GGB | 66.43 | GGB | 156362.4 | GGB | 124711.99 | GGB | 0 | 0 | 2298 | 3600 | 2282.8 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 23441.93 | GGB | 23442.26 | 2282.8 | 2282.8 |  |  |  | 1 | 1 |  |  |  |  | 124711.99 | 2282.8 |  |  | 7.4274 | [5 empty] | 79.0813
30.09.2007 17:00 | 3600 | 2 | 760.16 | GGB | 769.597 | 775.148 | 769.597 | 258.59 | GGB | 10563.2 | GGB | 9.92 | GGB | 1002.86 | GGB | 66.41 | GGB | 156321.68 | GGB | 124477.46 | GGB | 0 | 0 | 2331 | 3600 | 2316.28 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 23481.78 | GGB | 23482.11 | 2316.28 | 2316.28 |  |  |  | 1 | 1 |  |  |  |  | 124477.46 | 2316.28 |  | 2316.28 | 7.2352 | [5 empty] | 80.0902
30.09.2007 18:00 | 3600 | 2 | 759.91 | GGB | 769.597 | 775.289 | 769.597 | 259.27 | GGB | 10575.5 | GGB | 9.92 | GGB | 1003.12 | GGB | 66.26 | GGB | 156980.79 | GGB | 125089.74 | GGB | 0 | 0 | 2348 | 3600 | 2332.53 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 23520.75 | GGB | 23521.08 | 2332.53 | 2332.53 |  |  |  | 1 | 1 |  |  |  |  | 125089.74 | 2332.53 |  | 2332.53 | 7.4872 | [5 empty] | 81.0488
30.09.2007 19:00 | 3600 | 2 | 759.72 | GGB | 768.498 | 773.859 | 768.132 | 260.38 | GGB | 10616 | GGB | 9.92 | GGB | 1003.79 | GGB | 66.15 | GGB | 158103.13 | GGB | 126110.08 | GGB | 0 | 0 | 2376 | 3600 | 2361.31 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 23560.39 | GGB | 23560.72 | 2361.31 | 2361.31 |  |  |  | 1 | 1 |  |  |  |  | 126110.08 | 2361.31 | 126110.08 | 2361.31 | 7.5122 | [5 empty] | 82.7181
30.09.2007 20:00 | 3600 | 2 | 759.62 | GGB | 767.033 | 772.664 | 767.033 | 261.14 | GGB | 10676.3 | GGB | 9.93 | GGB | 1004.39 | GGB | 65.76 | GGB | 159235.38 | GGB | 127234.47 | GGB | 0 | 0 | 2406 | 3600 | 2390.38 | GGB | 100 | GGB | 37.88 | GGB | 37.88 | GGB | 23598.27 | GGB | 23598.6 | 2390.38 | 2390.38 |  |  |  | 1 | 1 |  |  |  |  | 127234.47 | 2390.38 | 127234.47 | 2390.38 | 8.029 | [5 empty] | 84.483
30.09.2007 21:00 | 3600 | 2 | 758.58 | GGB | 768.498 | 773.719 | 768.498 | 263.54 | GGB | 10657.7 | GGB | 9.91 | GGB | 1005.01 | GGB | 64.75 | GGB | 162074.25 | GGB | 129970.09 | GGB | 0 | 0 | 2444 | 3600 | 2428.5 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 23636.87 | GGB | 23637.21 | 2428.5 | 2428.5 |  |  |  | 1 | 1 |  |  |  |  | 129970.09 | 2428.5 | 129970.09 | 2428.5 | 8.1749 | [5 empty] | 87.6757
30.09.2007 22:00 | 3600 | 2 | 759.5 | GGB | 767.033 | 772.641 | 767.033 | 262.58 | GGB | 10715.2 | GGB | 9.93 | GGB | 1005.71 | GGB | 64.81 | GGB | 161795.86 | GGB | 129812.35 | GGB | 0 | 0 | 2421 | 3600 | 2405.49 | GGB | 100 | GGB | 37.92 | GGB | 37.92 | GGB | 23674.8 | GGB | 23675.13 | 2405.49 | 2405.49 |  |  |  | 1 | 1 |  |  |  |  | 129812.35 | 2405.49 | 129812.35 | 2405.49 | 8.2348 | [5 empty] | 86.7395
30.09.2007 23:00 | 3600 | 2 | 758.81 | GGB | 768.132 | 773.766 | 768.132 | 262.29 | GGB | 10758.7 | GGB | 9.92 | GGB | 1005.83 | GGB | 64.82 | GGB | 162121.56 | GGB | 130088.22 | GGB | 0 | 0 | 2450 | 3600 | 2435.12 | GGB | 100 | GGB | 37.92 | GGB | 37.92 | GGB | 23712.72 | GGB | 23713.05 | 2435.12 | 2435.12 |  |  |  | 1 | 1 |  |  |  |  | 130088.22 | 2435.12 | 130088.22 | 2435.12 | 8.3539 | [5 empty] | 87.9946
30.09.2007 24:00 | 3600 | 2 | 758.69 | GGB | 768.498 | 773.695 | 768.498 | 262.89 | GGB | 10785.6 | GGB | 9.92 | GGB | 1006.13 | GGB | 64.35 | GGB | 162514.38 | GGB | 130622.56 | GGB | 0 | 0 | 2476 | 3600 | 2460.62 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 23750.85 | GGB | 23751.18 | 2460.62 | 2460.62 |  |  |  | 1 | 1 |  |  |  |  | 130622.56 | 2460.62 | 130622.56 | 2460.62 | 8.4294 | [5 empty] | 89.2812
01.10.2007 01:00 | 3600 | 2 | 758.32 | GGB | 767.033 | 772.5 | 766.667 | 263.89 | GGB | 10802.6 | GGB | 9.92 | GGB | 1006.25 | GGB | 64.13 | GGB | 163472.78 | GGB | 131494.43 | GGB | 0 | 0 | 2503 | 3600 | 2487.94 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 23789.59 | GGB | 23789.92 | 2487.94 | 2487.94 |  |  |  | 1 | 1 |  |  |  |  | 131494.43 | 2487.94 | 131494.43 | 2487.94 | 8.4448 | [5 empty] | 90.8751
01.10.2007 02:00 | 3600 | 2 | 758.15 | GGB | 765.934 | 771.398 | 766.667 | 264.51 | GGB | 10830.5 | GGB | 9.92 | GGB | 1006.35 | GGB | 63.65 | GGB | 163899.71 | GGB | 132038.66 | GGB | 0 | 0 | 2521 | 3600 | 2506 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 23827.92 | GGB | 23828.25 | 2506 | 2506 |  |  |  | 1 | 1 |  |  |  |  | 132038.66 | 2506 | 132038.66 | 2506 | 8.6326 | [5 empty] | 91.9136
01.10.2007 03:00 | 3600 | 2 | 758 | GGB | 765.934 | 771.375 | 765.201 | 266.48 | GGB | 10840.9 | GGB | 9.91 | GGB | 1006.55 | GGB | 63.05 | GGB | 165433.58 | GGB | 133541.29 | GGB | 0 | 0 | 2533 | 3600 | 2518.16 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 23866.79 | GGB | 23867.12 | 2518.16 | 2518.16 |  |  |  | 1 | 1 |  |  |  |  | 133541.29 | 2518.16 | 133541.29 | 2518.16 | 8.6514 | [5 empty] | 93.4106
01.10.2007 04:00 | 3600 | 2 | 758.2 | GGB | 768.132 | 772.43 | 767.766 | 268.44 | GGB | 10889.8 | GGB | 9.92 | GGB | 1006.68 | GGB | 62.35 | GGB | 167162.21 | GGB | 135234.26 | GGB | 0 | 0 | 2540 | 3600 | 2524.95 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 23905.31 | GGB | 23905.64 | 2524.95 | 2524.95 |  |  |  | 1 | 1 |  |  |  |  | 135234.26 | 2524.95 | 135234.26 | 2524.95 | 8.8645 | [5 empty] | 94.8499
01.10.2007 05:00 | 3600 | 2 | 758.8 | GGB | 767.033 | 772.594 | 767.766 | 268.63 | GGB | 10919.6 | GGB | 9.93 | GGB | 1007.24 | GGB | 62.19 | GGB | 167494.51 | GGB | 135641.77 | GGB | 0 | 0 | 2525 | 3600 | 2509.51 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 23944.33 | GGB | 23944.66 | 2509.51 | 2509.51 |  |  |  | 1 | 1 |  |  |  |  | 135641.77 | 2509.51 | 135641.77 | 2509.51 | 8.7236 | [5 empty] | 94.554
01.10.2007 06:00 | 3600 | 2 | 758.45 | GGB | 767.033 | 772.594 | 766.667 | 267.82 | GGB | 10910 | GGB | 9.93 | GGB | 1007.28 | GGB | 62.05 | GGB | 166853.02 | GGB | 135186.32 | GGB | 0 | 0 | 2528 | 3600 | 2512.93 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 23983.35 | GGB | 23983.68 | 2512.93 | 2512.93 |  |  |  | 1 | 1 |  |  |  |  | 135186.32 | 2512.93 | 135186.32 | 2512.93 | 8.7061 | [5 empty] | 94.3649
01.10.2007 07:00 | 3600 | 2 | 757.98 | GGB | 768.132 | 772.57 | 767.766 | 268.66 | GGB | 10920.6 | GGB | 9.91 | GGB | 1007.71 | GGB | 61.8 | GGB | 167409.79 | GGB | 135793.8 | GGB | 0 | 0 | 2557 | 3600 | 2541.31 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 24022.62 | GGB | 24022.95 | 2541.31 | 2541.31 |  |  |  | 1 | 1 |  |  |  |  | 135793.8 | 2541.31 | 135793.8 | 2541.31 | 8.7877 | [5 empty] | 95.8595
01.10.2007 08:00 | 3600 | 2 | 758.06 | GGB | 767.033 | 772.664 | 766.667 | 269.34 | GGB | 10958.1 | GGB | 9.92 | GGB | 1008.26 | GGB | 61.6 | GGB | 168305.46 | GGB | 136676.77 | GGB | 0 | 0 | 2563 | 3600 | 2547.88 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 24061.87 | GGB | 24062.2 | 2547.88 | 2547.88 |  |  |  | 1 | 1 |  |  |  |  | 136676.77 | 2547.88 | 136676.77 | 2547.88 | 8.8723 | [5 empty] | 96.7322
01.10.2007 09:00 | 3600 | 2 | 758.25 | GGB | 767.033 | 771.563 | 766.667 | 269.38 | GGB | 10975.5 | GGB | 9.92 | GGB | 1008.64 | GGB | 61.49 | GGB | 168515.63 | GGB | 136944.27 | GGB | 0 | 0 | 2565 | 3600 | 2549.73 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 24100.9 | GGB | 24101.23 | 2549.73 | 2549.73 |  |  |  | 1 | 1 |  |  |  |  | 136944.27 | 2549.73 | 136944.27 | 2549.73 | 8.9462 | [5 empty] | 96.9919
01.10.2007 10:00 | 3600 | 2 | 758.49 | GGB | 768.132 | 773.695 | 767.766 | 269.16 | GGB | 10986.8 | GGB | 9.93 | GGB | 1009.01 | GGB | 61.53 | GGB | 168632.26 | GGB | 137073.35 | GGB | 0 | 0 | 2557 | 3600 | 2541.67 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 24140.15 | GGB | 24140.48 | 2541.67 | 2541.67 |  |  |  | 1 | 1 |  |  |  |  | 137073.35 | 2541.67 | 137073.35 | 2541.67 | 8.8763 | [5 empty] | 96.7765
01.10.2007 11:00 | 3600 | 2 | 759.2 | GGB | 769.597 | 774.82 | 768.864 | 268.03 | GGB | 11000.9 | GGB | 9.94 | GGB | 1009.43 | GGB | 61.94 | GGB | 166971.85 | GGB | 135613.34 | GGB | 0 | 0 | 2534 | 3600 | 2518.29 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 24178.78 | GGB | 24179.11 | 2518.29 | 2518.29 |  |  |  | 1 | 1 |  |  |  |  | 135613.34 | 2518.29 | 135613.34 | 2518.29 | 8.8406 | [5 empty] | 94.8649
01.10.2007 12:00 | 3600 | 2 | 759.63 | GGB | 769.597 | 773.672 | 768.864 | 264.38 | GGB | 10917.4 | GGB | 9.94 | GGB | 1010.09 | GGB | 63.16 | GGB | 163351.74 | GGB | 132277.13 | GGB | 0 | 0 | 2485 | 3600 | 2470.25 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 24218.17 | GGB | 24218.5 | 2470.25 | 2470.25 |  |  |  | 1 | 1 |  |  |  |  | 132277.13 | 2470.25 | 132277.13 | 2470.25 | 8.2954 | [5 empty] | 90.766
01.10.2007 13:00 | 3600 | 2 | 760.01 | GGB | 769.597 | 774.75 | 769.963 | 261.63 | GGB | 10797.8 | GGB | 9.94 | GGB | 1009.3 | GGB | 63.86 | GGB | 160552.48 | GGB | 129640.23 | GGB | 0 | 0 | 2414 | 3600 | 2399.27 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 24256.9 | GGB | 24257.23 | 2399.27 | 2399.27 |  |  |  | 1 | 1 |  |  |  |  | 129640.23 | 2399.27 | 129640.23 | 2399.27 | 8.031 | [5 empty] | 86.4005
01.10.2007 14:00 | 3600 | 2 | 759.98 | GGB | 769.597 | 774.727 | 769.963 | 261.81 | GGB | 10656.7 | GGB | 9.92 | GGB | 1007.88 | GGB | 63.87 | GGB | 161000.32 | GGB | 129815.12 | GGB | 0 | 0 | 2346 | 3600 | 2330.41 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 24295.66 | GGB | 24295.99 | 2330.41 | 2330.41 |  |  |  | 1 | 1 |  |  |  |  | 129815.12 | 2330.41 | 129815.12 | 2330.41 | 7.805 | [5 empty] | 84.034
01.10.2007 15:00 | 3600 | 2 | 760.14 | GGB | 769.597 | 775.055 | 769.597 | 261.73 | GGB | 10635.8 | GGB | 9.92 | GGB | 1006.39 | GGB | 63.84 | GGB | 161289.71 | GGB | 129869.93 | GGB | 0 | 0 | 2323 | 3600 | 2307.64 | GGB | 100 | GGB | 37.7 | GGB | 37.7 | GGB | 24333.36 | GGB | 24333.69 | 2307.64 | 2307.64 |  |  |  | 1 | 1 |  |  |  |  | 129869.93 | 2307.64 | 129869.93 | 2307.64 | 7.9494 | [5 empty] | 83.2481
01.10.2007 16:00 | 3600 | 2 | 760.39 | GGB | 769.597 | 775.219 | 769.597 | 260.63 | GGB | 10659.1 | GGB | 9.93 | GGB | 1005.69 | GGB | 64.25 | GGB | 159396.03 | GGB | 128097.28 | GGB | 0 | 0 | 2323 | 3600 | 2307.98 | GGB | 100 | GGB | 37.63 | GGB | 37.63 | GGB | 24370.99 | GGB | 24371.32 | 2307.98 | 2307.98 |  |  |  | 1 | 1 |  |  |  |  | 128097.28 | 2307.98 | 128097.28 | 2307.98 | 7.8567 | [5 empty] | 82.1239
01.10.2007 17:00 | 3600 | 2 | 759.61 | GGB | 768.498 | 773.227 | 768.498 | 260.1 | GGB | 10656.7 | GGB | 9.92 | GGB | 1005.63 | GGB | 64.56 | GGB | 158125.14 | GGB | 126953.13 | GGB | 0 | 0 | 2358 | 3600 | 2343.28 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 24409.33 | GGB | 24409.65 | 2343.28 | 2343.28 |  |  |  | 1 | 1 |  |  |  |  | 126953.13 | 2343.28 | 126953.13 | 2343.28 | 7.7612 | [5 empty] | 82.6352
01.10.2007 18:00 | 3600 | 2 | 759.66 | GGB | 768.132 | 773.484 | 767.033 | 261.2 | GGB | 10693.5 | GGB | 9.92 | GGB | 1005.55 | GGB | 64.25 | GGB | 158608.19 | GGB | 127449.31 | GGB | 0 | 0 | 2376 | 3600 | 2360.88 | GGB | 100 | GGB | 37.75 | GGB | 37.75 | GGB | 24447.08 | GGB | 24447.4 | 2360.88 | 2360.88 |  |  |  | 1 | 1 |  |  |  |  | 127449.31 | 2360.88 | 127449.31 | 2360.88 | 7.9707 | [5 empty] | 83.5813
01.10.2007 19:00 | 3600 | 2 | 759.21 | GGB | 767.033 | 773.484 | 767.033 | 263.65 | GGB | 10710.1 | GGB | 9.92 | GGB | 1005.27 | GGB | 63.3 | GGB | 160982.71 | GGB | 129685.75 | GGB | 0 | 0 | 2409 | 3600 | 2393.84 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 24485.43 | GGB | 24485.76 | 2393.84 | 2393.84 |  |  |  | 1 | 1 |  |  |  |  | 129685.75 | 2393.84 | 129685.75 | 2393.84 | 8.093 | [5 empty] | 86.2353
01.10.2007 20:00 | 3600 | 2 | 758.84 | GGB | 767.033 | 772.336 | 767.033 | 265.16 | GGB | 10758.7 | GGB | 9.91 | GGB | 1006.18 | GGB | 63.04 | GGB | 161908.1 | GGB | 130650.3 | GGB | 0 | 0 | 2446 | 3600 | 2430.6 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 24523.84 | GGB | 24524.16 | 2430.6 | 2430.6 |  |  |  | 1 | 1 |  |  |  |  | 130650.3 | 2430.6 | 130650.3 | 2430.6 | 8.2698 | [5 empty] | 88.2107
01.10.2007 21:00 | 3600 | 2 | 758.19 | GGB | 764.102 | 769.219 | 764.835 | 266.77 | GGB | 10798.9 | GGB | 9.9 | GGB | 1006.58 | GGB | 62.55 | GGB | 163283.52 | GGB | 132002.37 | GGB | 0 | 0 | 2493 | 3600 | 2478.21 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 24562.33 | GGB | 24562.65 | 2478.21 | 2478.21 |  |  |  | 1 | 1 |  |  |  |  | 132002.37 | 2478.21 | 132002.37 | 2478.21 | 8.4991 | [5 empty] | 90.8693
01.10.2007 22:00 | 3600 | 2 | 758.27 | GGB | 766.3 | 771.352 | 767.033 | 267.4 | GGB | 10925.8 | GGB | 9.92 | GGB | 1006.93 | GGB | 62.49 | GGB | 163638.93 | GGB | 132359.52 | GGB | 0 | 0 | 2550 | 3600 | 2534.61 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 24600.9 | GGB | 24601.22 | 2534.61 | 2534.61 |  |  |  | 1 | 1 |  |  |  |  | 132359.52 | 2534.61 | 132359.52 | 2534.61 | 8.6979 | [5 empty] | 93.1888
01.10.2007 23:00 | 3600 | 2 | 757.56 | GGB | 767.766 | 771.305 | 765.934 | 267.34 | GGB | 10960.8 | GGB | 9.92 | GGB | 1006.94 | GGB | 62.39 | GGB | 164399.26 | GGB | 133016.9 | GGB | 0 | 0 | 2591 | 3600 | 2576.11 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 24640.17 | GGB | 24640.48 | 2576.11 | 2576.11 |  |  |  | 1 | 1 |  |  |  |  | 133016.9 | 2576.11 | 133016.9 | 2576.11 | 8.7281 | [5 empty] | 95.185
01.10.2007 24:00 | 3600 | 2 | 757.4 | GGB | 765.201 | 771.305 | 764.469 | 268.42 | GGB | 10990.5 | GGB | 9.91 | GGB | 1007.21 | GGB | 61.73 | GGB | 165214.61 | GGB | 133975.99 | GGB | 0 | 0 | 2611 | 3600 | 2596.14 | GGB | 100 | GGB | 37.83 | GGB | 37.83 | GGB | 24678 | GGB | 24678.31 | 2596.14 | 2596.14 |  |  |  | 1 | 1 |  |  |  |  | 133975.99 | 2596.14 | 133975.99 | 2596.14 | 9.1943 | [5 empty] | 96.6168
02.10.2007 01:00 | 3600 | 2 | 757.63 | GGB | 767.766 | 772.477 | 768.132 | 271.12 | GGB | 11040.6 | GGB | 9.92 | GGB | 1007.43 | GGB | 60.45 | GGB | 167962.16 | GGB | 136757.3 | GGB | 0 | 0 | 2610 | 3600 | 2594.44 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 24717.7 | GGB | 24718.01 | 2594.44 | 2594.44 |  |  |  | 1 | 1 |  |  |  |  | 136757.3 | 2594.44 | 136757.3 | 2594.44 | 8.9372 | [5 empty] | 98.5579
02.10.2007 02:00 | 3600 | 2 | 758 | GGB | 767.766 | 772.336 | 767.033 | 271.08 | GGB | 11059.8 | GGB | 9.93 | GGB | 1007.83 | GGB | 60.31 | GGB | 168191.03 | GGB | 137053.36 | GGB | 0 | 0 | 2600 | 3600 | 2584.31 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 24757.54 | GGB | 24757.85 | 2584.31 | 2584.31 |  |  |  | 1 | 1 |  |  |  |  | 137053.36 | 2584.31 | 137053.36 | 2584.31 | 8.8903 | [5 empty] | 98.3857
02.10.2007 03:00 | 3600 | 2 | 758.18 | GGB | 766.667 | 772.078 | 765.934 | 270.25 | GGB | 11055.4 | GGB | 9.93 | GGB | 1007.72 | GGB | 60.37 | GGB | 168077.69 | GGB | 136923.59 | GGB | 0 | 0 | 2583 | 3600 | 2567.94 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 24796.94 | GGB | 24797.25 | 2567.94 | 2567.94 |  |  |  | 1 | 1 |  |  |  |  | 136923.59 | 2567.94 | 136923.59 | 2567.94 | 8.9242 | [5 empty] | 97.6699
02.10.2007 04:00 | 3600 | 2 | 758.01 | GGB | 767.033 | 771.844 | 767.033 | 269.77 | GGB | 11091.2 | GGB | 9.93 | GGB | 1007.15 | GGB | 60.59 | GGB | 167410.89 | GGB | 136214.37 | GGB | 0 | 0 | 2607 | 3600 | 2591.63 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 24836.59 | GGB | 24836.89 | 2591.63 | 2591.63 |  |  |  | 1 | 1 |  |  |  |  | 136214.37 | 2591.63 | 136214.37 | 2591.63 | 8.9056 | [5 empty] | 98.0603
02.10.2007 05:00 | 3600 | 2 | 758.01 | GGB | 767.033 | 771.633 | 767.033 | 268.53 | GGB | 11100.4 | GGB | 9.93 | GGB | 1006.63 | GGB | 60.91 | GGB | 166461.3 | GGB | 135239.37 | GGB | 0 | 0 | 2616 | 3600 | 2600.17 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 24876.23 | GGB | 24876.54 | 2600.17 | 2600.17 |  |  |  | 1 | 1 |  |  |  |  | 135239.37 | 2600.17 | 135239.37 | 2600.17 | 8.8687 | [5 empty] | 97.6793
02.10.2007 06:00 | 3600 | 2 | 757.92 | GGB | 767.033 | 771.703 | 767.033 | 268.2 | GGB | 11077 | GGB | 9.92 | GGB | 1006.27 | GGB | 60.97 | GGB | 165864.91 | GGB | 134683.19 | GGB | 0 | 0 | 2619 | 3600 | 2603.25 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 24915.78 | GGB | 24916.09 | 2603.25 | 2603.25 |  |  |  | 1 | 1 |  |  |  |  | 134683.19 | 2603.25 | 134683.19 | 2603.25 | 8.8651 | [5 empty] | 97.3928
02.10.2007 07:00 | 3600 | 2 | 757.56 | GGB | 767.033 | 771.281 | 767.033 | 268.76 | GGB | 11041 | GGB | 9.91 | GGB | 1006.18 | GGB | 60.76 | GGB | 166454.69 | GGB | 135235.69 | GGB | 0 | 0 | 2617 | 3600 | 2601.64 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 24955.53 | GGB | 24955.83 | 2601.64 | 2601.64 |  |  |  | 1 | 1 |  |  |  |  | 135235.69 | 2601.64 | 135235.69 | 2601.64 | 8.8534 | [5 empty] | 97.7318
02.10.2007 08:00 | 3600 | 2 | 758.48 | GGB | 768.132 | 772.57 | 768.132 | 269.48 | GGB | 11043.8 | GGB | 9.93 | GGB | 1006.13 | GGB | 60.22 | GGB | 166916.84 | GGB | 135821.61 | GGB | 0 | 0 | 2566 | 3600 | 2550.63 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 24994.79 | GGB | 24995.1 | 2550.63 | 2550.63 |  |  |  | 1 | 1 |  |  |  |  | 135821.61 | 2550.63 | 135821.61 | 2550.63 | 8.8218 | [5 empty] | 96.2307
02.10.2007 09:00 | 3600 | 2 | 758.29 | GGB | 767.033 | 772.359 | 767.033 | 269.01 | GGB | 11010.3 | GGB | 9.92 | GGB | 1006.01 | GGB | 60.35 | GGB | 166357.86 | GGB | 135298.16 | GGB | 0 | 0 | 2570 | 3600 | 2554.45 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 25035.65 | GGB | 25035.95 | 2554.45 | 2554.45 |  |  |  | 1 | 1 |  |  |  |  | 135298.16 | 2554.45 | 135298.16 | 2554.45 | 8.4605 | [5 empty] | 96.0034
02.10.2007 10:00 | 3600 | 2 | 758.7 | GGB | 767.033 | 772.266 | 767.033 | 267.11 | GGB | 11024 | GGB | 9.94 | GGB | 1005.96 | GGB | 61.24 | GGB | 164320.04 | GGB | 133279.2 | GGB | 0 | 0 | 2564 | 3600 | 2548.95 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 25074.49 | GGB | 25074.79 | 2548.95 | 2548.95 |  |  |  | 1 | 1 |  |  |  |  | 133279.2 | 2548.95 | 133279.2 | 2548.95 | 8.7467 | [5 empty] | 94.3672
02.10.2007 11:00 | 3600 | 2 | 757.99 | GGB | 767.033 | 772.477 | 767.033 | 266.03 | GGB | 10986.9 | GGB | 9.93 | GGB | 1005.28 | GGB | 61.4 | GGB | 163247.21 | GGB | 132256.08 | GGB | 0 | 0 | 2582 | 3600 | 2566.8 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 25114.38 | GGB | 25114.69 | 2566.8 | 2566.8 |  |  |  | 1 | 1 |  |  |  |  | 132256.08 | 2566.8 | 132256.08 | 2566.8 | 8.5081 | [5 empty] | 94.2986
02.10.2007 12:00 | 3600 | 2 | 757.96 | GGB | 765.934 | 772.594 | 767.033 | 265.77 | GGB | 10955.4 | GGB | 9.92 | GGB | 1004.77 | GGB | 61.89 | GGB | 162754.26 | GGB | 131596.22 | GGB | 0 | 0 | 2570 | 3600 | 2554.64 | GGB | 100 | GGB | 37.34 | GGB | 37.34 | GGB | 25151.73 | GGB | 25152.03 | 2554.64 | 2554.64 |  |  |  | 1 | 1 |  |  |  |  | 131596.22 | 2554.64 | 131596.22 | 2554.64 | 9.0032 | [5 empty] | 93.3836
02.10.2007 13:00 | 3600 | 2 | 757.97 | GGB | 768.132 | 772.477 | 768.132 | 267.82 | GGB | 10910.5 | GGB | 9.92 | GGB | 1004.52 | GGB | 61.61 | GGB | 163830.39 | GGB | 132547.95 | GGB | 0 | 0 | 2550 | 3600 | 2534.57 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 25192.17 | GGB | 25192.47 | 2534.57 | 2534.57 |  |  |  | 1 | 1 |  |  |  |  | 132547.95 | 2534.57 | 132547.95 | 2534.57 | 8.3074 | [5 empty] | 93.32
02.10.2007 14:00 | 3600 | 2 | 758.37 | GGB | 766.667 | 773.484 | 767.033 | 266.93 | GGB | 10888 | GGB | 9.93 | GGB | 1004.01 | GGB | 61.83 | GGB | 163323.13 | GGB | 131979.53 | GGB | 0 | 0 | 2512 | 3600 | 2497.14 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 25231.03 | GGB | 25231.33 | 2497.14 | 2497.14 |  |  |  | 1 | 1 |  |  |  |  | 131979.53 | 2497.14 | 131979.53 | 2497.14 | 8.481 | [5 empty] | 91.5476
02.10.2007 15:00 | 3600 | 2 | 759.21 | GGB | 767.766 | 773.484 | 767.033 | 265.22 | GGB | 10847.2 | GGB | 9.94 | GGB | 1003.22 | GGB | 62.19 | GGB | 162407.65 | GGB | 130997.14 | GGB | 0 | 0 | 2469 | 3600 | 2453.95 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 25269.45 | GGB | 25269.75 | 2453.95 | 2453.95 |  |  |  | 1 | 1 |  |  |  |  | 130997.14 | 2453.95 | 130997.14 | 2453.95 | 8.367 | [5 empty] | 89.2946
02.10.2007 16:00 | 3600 | 2 | 758.76 | GGB | 767.766 | 772.453 | 767.033 | 264.59 | GGB | 10802.4 | GGB | 9.93 | GGB | 1002.33 | GGB | 62.34 | GGB | 161450.36 | GGB | 130051.44 | GGB | 0 | 0 | 2467 | 3600 | 2451.42 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 25309.22 | GGB | 25309.52 | 2451.42 | 2451.42 |  |  |  | 1 | 1 |  |  |  |  | 130051.44 | 2451.42 | 130051.44 | 2451.42 | 8.0164 | [5 empty] | 88.5585
02.10.2007 17:00 | 3600 | 2 | 758.93 | GGB | 768.864 | 774.469 | 769.597 | 263.8 | GGB | 10809.6 | GGB | 9.93 | GGB | 1001.85 | GGB | 62.59 | GGB | 160823.17 | GGB | 129386.45 | GGB | 0 | 0 | 2464 | 3600 | 2448.64 | GGB | 100 | GGB | 37.61 | GGB | 37.61 | GGB | 25346.83 | GGB | 25347.13 | 2448.64 | 2448.64 |  |  |  | 1 | 1 |  |  |  |  | 129386.45 | 2448.64 | 129386.45 | 2448.64 | 8.4238 | [5 empty] | 88.0058
02.10.2007 18:00 | 3600 | 2 | 758.06 | GGB | 766.667 | 772.336 | 765.934 | 262.88 | GGB | 10809.9 | GGB | 9.92 | GGB | 1001.33 | GGB | 62.66 | GGB | 159704.12 | GGB | 128394.54 | GGB | 0 | 0 | 2510 | 3600 | 2495.11 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 25386.35 | GGB | 25386.65 | 2495.11 | 2495.11 |  |  |  | 1 | 1 |  |  |  |  | 128394.54 | 2495.11 | 128394.54 | 2495.11 | 8.1062 | [5 empty] | 88.9885
02.10.2007 19:00 | 3600 | 2 | 758.07 | GGB | 767.766 | 773.531 | 768.132 | 264.09 | GGB | 10846.4 | GGB | 9.92 | GGB | 1001.1 | GGB | 62.6 | GGB | 160683.42 | GGB | 129174.99 | GGB | 0 | 0 | 2522 | 3600 | 2506.32 | GGB | 100 | GGB | 37.79 | GGB | 37.79 | GGB | 25424.14 | GGB | 25424.44 | 2506.32 | 2506.32 |  |  |  | 1 | 1 |  |  |  |  | 129174.99 | 2506.32 | 129174.99 | 2506.32 | 8.5672 | [5 empty] | 89.9316
02.10.2007 20:00 | 3600 | 2 | 757.66 | GGB | 765.201 | 771.375 | 764.835 | 264.99 | GGB | 10855.3 | GGB | 9.91 | GGB | 1001.04 | GGB | 62.33 | GGB | 161418.45 | GGB | 129863.87 | GGB | 0 | 0 | 2535 | 3600 | 2520.15 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 25464.94 | GGB | 25465.24 | 2520.15 | 2520.15 |  |  |  | 1 | 1 |  |  |  |  | 129863.87 | 2520.15 | 129863.87 | 2520.15 | 8.0215 | [5 empty] | 90.9101
02.10.2007 21:00 | 3600 | 2 | 757.65 | GGB | 766.667 | 772.195 | 765.934 | 266.95 | GGB | 10865.2 | GGB | 9.92 | GGB | 1000.54 | GGB | 61.81 | GGB | 163763.27 | GGB | 131889.36 | GGB | 0 | 0 | 2529 | 3600 | 2513.84 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 25503.75 | GGB | 25504.05 | 2513.84 | 2513.84 |  |  |  | 1 | 1 |  |  |  |  | 131889.36 | 2513.84 | 131889.36 | 2513.84 | 8.5429 | [5 empty] | 92.0969
02.10.2007 22:00 | 3600 | 2 | 758.34 | GGB | 766.3 | 770.953 | 765.934 | 265.22 | GGB | 10918.2 | GGB | 9.93 | GGB | 1000.21 | GGB | 62.23 | GGB | 162528.69 | GGB | 130687.37 | GGB | 0 | 0 | 2530 | 3600 | 2515 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 25542.39 | GGB | 25542.69 | 2515 | 2515 |  |  |  | 1 | 1 |  |  |  |  | 130687.37 | 2515 | 130687.37 | 2515 | 8.5062 | [5 empty] | 91.2996
02.10.2007 23:00 | 3600 | 2 | 757.68 | GGB | 767.766 | 772.078 | 767.033 | 265.39 | GGB | 10921.9 | GGB | 9.92 | GGB | 999.65 | GGB | 62.27 | GGB | 162459.37 | GGB | 130542.04 | GGB | 0 | 0 | 2558 | 3600 | 2542.73 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 25581.05 | GGB | 25581.36 | 2542.73 | 2542.73 |  |  |  | 1 | 1 |  |  |  |  | 130542.04 | 2542.73 | 130542.04 | 2542.73 | 8.5837 | [5 empty] | 92.2037
02.10.2007 24:00 | 3600 | 2 | 757.63 | GGB | 768.864 | 772.969 | 768.132 | 267.17 | GGB | 10885.5 | GGB | 9.92 | GGB | 998.91 | GGB | 61.63 | GGB | 164090.07 | GGB | 132008.31 | GGB | 0 | 0 | 2543 | 3600 | 2527.81 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 25620.51 | GGB | 25620.82 | 2527.81 | 2527.81 |  |  |  | 1 | 1 |  |  |  |  | 132008.31 | 2527.81 | 132008.31 | 2527.81 | 8.4565 | [5 empty] | 92.6922
03.10.2007 01:00 | 3600 | 2 | 758.19 | GGB | 766.3 | 771.703 | 766.667 | 266.06 | GGB | 10894.1 | GGB | 9.93 | GGB | 998.4 | GGB | 60.87 | GGB | 163630.13 | GGB | 131868 | GGB | 0 | 0 | 2513 | 3600 | 2497.41 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 25659.04 | GGB | 25659.34 | 2497.41 | 2497.41 |  |  |  | 1 | 1 |  |  |  |  | 131868 | 2497.41 | 131868 | 2497.41 | 8.5495 | [5 empty] | 91.4801
03.10.2007 02:00 | 3600 | 2 | 757.96 | GGB | 765.201 | 770.766 | 766.667 | 265.23 | GGB | 10920 | GGB | 9.93 | GGB | 997.99 | GGB | 61.32 | GGB | 162090.75 | GGB | 130401.43 | GGB | 0 | 0 | 2539 | 3600 | 2524.07 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 25697.64 | GGB | 25697.94 | 2524.07 | 2524.07 |  |  |  | 1 | 1 |  |  |  |  | 130401.43 | 2524.07 | 130401.43 | 2524.07 | 8.527 | [5 empty] | 91.4284
03.10.2007 03:00 | 3600 | 2 | 757.55 | GGB | 766.667 | 771.82 | 766.3 | 264.63 | GGB | 10901.8 | GGB | 9.92 | GGB | 997.98 | GGB | 62.05 | GGB | 161891.59 | GGB | 129954.9 | GGB | 0 | 0 | 2557 | 3600 | 2541.98 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 25736.81 | GGB | 25737.12 | 2541.98 | 2541.98 |  |  |  | 1 | 1 |  |  |  |  | 129954.9 | 2541.98 | 129954.9 | 2541.98 | 8.4314 | [5 empty] | 91.7619
03.10.2007 04:00 | 3600 | 2 | 757.77 | GGB | 767.766 | 771.656 | 766.667 | 264.55 | GGB | 10906 | GGB | 9.92 | GGB | 997.72 | GGB | 61.85 | GGB | 162112.76 | GGB | 130174.55 | GGB | 0 | 0 | 2549 | 3600 | 2533.97 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 25775.63 | GGB | 25775.94 | 2533.97 | 2533.97 |  |  |  | 1 | 1 |  |  |  |  | 130174.55 | 2533.97 | 130174.55 | 2533.97 | 8.4971 | [5 empty] | 91.6273
03.10.2007 05:00 | 3600 | 2 | 757.53 | GGB | 766.667 | 771.633 | 766.667 | 264.94 | GGB | 10910.1 | GGB | 9.92 | GGB | 997.61 | GGB | 61.71 | GGB | 162127.07 | GGB | 130225.72 | GGB | 0 | 0 | 2564 | 3600 | 2548.7 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 25814.45 | GGB | 25814.76 | 2548.7 | 2548.7 |  |  |  | 1 | 1 |  |  |  |  | 130225.72 | 2548.7 | 130225.72 | 2548.7 | 8.5499 | [5 empty] | 92.1962
03.10.2007 06:00 | 3600 | 2 | 757.54 | GGB | 766.667 | 771.492 | 765.201 | 265.96 | GGB | 10897.7 | GGB | 9.92 | GGB | 997.86 | GGB | 61.27 | GGB | 163581.71 | GGB | 131603.31 | GGB | 0 | 0 | 2549 | 3600 | 2534.15 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 25853.8 | GGB | 25854.11 | 2534.15 | 2534.15 |  |  |  | 1 | 1 |  |  |  |  | 131603.31 | 2534.15 | 131603.31 | 2534.15 | 8.4753 | [5 empty] | 92.6396
03.10.2007 07:00 | 3600 | 2 | 757.6 | GGB | 766.667 | 771.492 | 766.667 | 266.44 | GGB | 10893.2 | GGB | 9.92 | GGB | 997.95 | GGB | 60.99 | GGB | 164318.94 | GGB | 132316.07 | GGB | 0 | 0 | 2534 | 3600 | 2518.49 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 25892.22 | GGB | 25892.53 | 2518.49 | 2518.49 |  |  |  | 1 | 1 |  |  |  |  | 132316.07 | 2518.49 | 132316.07 | 2518.49 | 8.6735 | [5 empty] | 92.5657
03.10.2007 08:00 | 3600 | 2 | 757.52 | GGB | 766.3 | 771.422 | 766.3 | 266.52 | GGB | 10914 | GGB | 9.92 | GGB | 998.12 | GGB | 60.82 | GGB | 164105.47 | GGB | 132234.84 | GGB | 0 | 0 | 2549 | 3600 | 2533.52 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 25931.43 | GGB | 25931.74 | 2533.52 | 2533.52 |  |  |  | 1 | 1 |  |  |  |  | 132234.84 | 2533.52 | 132234.84 | 2533.52 | 8.5442 | [5 empty] | 93.061
03.10.2007 09:00 | 3600 | 2 | 757.85 | GGB | 766.667 | 772.5 | 766.667 | 265.15 | GGB | 10967.8 | GGB | 9.93 | GGB | 998.44 | GGB | 61.16 | GGB | 163021.64 | GGB | 131268.89 | GGB | 0 | 0 | 2557 | 3600 | 2542.08 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 25970.48 | GGB | 25970.8 | 2542.08 | 2542.08 |  |  |  | 1 | 1 |  |  |  |  | 131268.89 | 2542.08 | 131268.89 | 2542.08 | 8.5432 | [5 empty] | 92.6933
03.10.2007 10:00 | 3600 | 2 | 757.38 | GGB | 766.3 | 771.375 | 766.3 | 265.68 | GGB | 10969.3 | GGB | 9.92 | GGB | 998.83 | GGB | 61 | GGB | 163183.39 | GGB | 131515.19 | GGB | 0 | 0 | 2582 | 3600 | 2566.76 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 26009.4 | GGB | 26009.72 | 2566.76 | 2566.76 |  |  |  | 1 | 1 |  |  |  |  | 131515.19 | 2566.76 | 131515.19 | 2566.76 | 8.6734 | [5 empty] | 93.7689
03.10.2007 11:00 | 3600 | 2 | 757.66 | GGB | 766.3 | 771.047 | 766.3 | 265.33 | GGB | 10951.3 | GGB | 9.92 | GGB | 999.12 | GGB | 61.1 | GGB | 162827.98 | GGB | 131227.07 | GGB | 0 | 0 | 2560 | 3600 | 2545.19 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 26048.87 | GGB | 26049.19 | 2545.19 | 2545.19 |  |  |  | 1 | 1 |  |  |  |  | 131227.07 | 2545.19 | 131227.07 | 2545.19 | 8.4621 | [5 empty] | 92.7772
03.10.2007 12:00 | 3600 | 2 | 757.41 | GGB | 767.766 | 772.008 | 766.667 | 267.34 | GGB | 10940.3 | GGB | 9.92 | GGB | 999.21 | GGB | 60.12 | GGB | 164976.94 | GGB | 133362.4 | GGB | 0 | 0 | 2555 | 3600 | 2540.03 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 26087.4 | GGB | 26087.71 | 2540.03 | 2540.03 |  |  |  | 1 | 1 |  |  |  |  | 133362.4 | 2540.03 | 133362.4 | 2540.03 | 8.794 | [5 empty] | 94.0957
03.10.2007 13:00 | 3600 | 2 | 757.73 | GGB | 766.667 | 771.961 | 766.667 | 267.2 | GGB | 10950.7 | GGB | 9.92 | GGB | 999.4 | GGB | 60.07 | GGB | 165171.7 | GGB | 133566.73 | GGB | 0 | 0 | 2543 | 3600 | 2527.49 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 26126.83 | GGB | 26127.15 | 2527.49 | 2527.49 |  |  |  | 1 | 1 |  |  |  |  | 133566.73 | 2527.49 | 133566.73 | 2527.49 | 8.5595 | [5 empty] | 93.7746
03.10.2007 14:00 | 3600 | 2 | 758.18 | GGB | 766.667 | 772.008 | 766.667 | 266.01 | GGB | 10971.9 | GGB | 9.93 | GGB | 999.77 | GGB | 60.49 | GGB | 164131.88 | GGB | 132604.31 | GGB | 0 | 0 | 2536 | 3600 | 2520.67 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 26165.25 | GGB | 26165.58 | 2520.67 | 2520.67 |  |  |  | 1 | 1 |  |  |  |  | 132604.31 | 2520.67 | 132604.31 | 2520.67 | 8.6977 | [5 empty] | 92.8477
03.10.2007 15:00 | 3600 | 2 | 757.97 | GGB | 766.667 | 772.242 | 766.667 | 264.54 | GGB | 10951.6 | GGB | 9.93 | GGB | 999.44 | GGB | 60.96 | GGB | 162355.94 | GGB | 130945.13 | GGB | 0 | 0 | 2536 | 3600 | 2520.28 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 26204.91 | GGB | 26205.24 | 2520.28 | 2520.28 |  |  |  | 1 | 1 |  |  |  |  | 130945.13 | 2520.28 | 130945.13 | 2520.28 | 8.3212 | [5 empty] | 91.6718
03.10.2007 16:00 | 3600 | 2 | 757.98 | GGB | 767.766 | 772.359 | 767.766 | 264.33 | GGB | 10935.9 | GGB | 9.93 | GGB | 999.74 | GGB | 61.19 | GGB | 162234.9 | GGB | 130795.61 | GGB | 0 | 0 | 2531 | 3600 | 2515.26 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 26244.06 | GGB | 26244.39 | 2515.26 | 2515.26 |  |  |  | 1 | 1 |  |  |  |  | 130795.61 | 2515.26 | 130795.61 | 2515.26 | 8.4032 | [5 empty] | 91.3847
03.10.2007 17:00 | 3600 | 2 | 757.88 | GGB | 767.766 | 772.359 | 767.766 | 264.12 | GGB | 10914.2 | GGB | 9.92 | GGB | 999.54 | GGB | 61.34 | GGB | 161704.54 | GGB | 130281.14 | GGB | 0 | 0 | 2521 | 3600 | 2505.55 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 26283.01 | GGB | 26283.33 | 2505.55 | 2505.55 |  |  |  | 1 | 1 |  |  |  |  | 130281.14 | 2505.55 | 130281.14 | 2505.55 | 8.3828 | [5 empty] | 90.6739
03.10.2007 18:00 | 3600 | 2 | 758.11 | GGB | 766.667 | 772.359 | 766.667 | 263.91 | GGB | 10903.2 | GGB | 9.93 | GGB | 999.57 | GGB | 61.59 | GGB | 161403.04 | GGB | 129946.8 | GGB | 0 | 0 | 2506 | 3600 | 2491.06 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 26322.38 | GGB | 26322.7 | 2491.06 | 2491.06 |  |  |  | 1 | 1 |  |  |  |  | 129946.8 | 2491.06 | 129946.8 | 2491.06 | 8.2221 | [5 empty] | 89.9181
03.10.2007 19:00 | 3600 | 2 | 757.83 | GGB | 765.201 | 771.211 | 765.201 | 264.27 | GGB | 10901.9 | GGB | 9.92 | GGB | 999.23 | GGB | 61.58 | GGB | 161683.63 | GGB | 130134.26 | GGB | 0 | 0 | 2520 | 3600 | 2504.39 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 26360.89 | GGB | 26361.22 | 2504.39 | 2504.39 |  |  |  | 1 | 1 |  |  |  |  | 130134.26 | 2504.39 | 130134.26 | 2504.39 | 8.4607 | [5 empty] | 90.5297
03.10.2007 20:00 | 3600 | 2 | 757.56 | GGB | 766.3 | 771.445 | 766.3 | 265.55 | GGB | 10935.7 | GGB | 9.91 | GGB | 999.63 | GGB | 61.29 | GGB | 162786.17 | GGB | 131184.01 | GGB | 0 | 0 | 2558 | 3600 | 2543.14 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 26400.43 | GGB | 26400.76 | 2543.14 | 2543.14 |  |  |  | 1 | 1 |  |  |  |  | 131184.01 | 2543.14 | 131184.01 | 2543.14 | 8.4375 | [5 empty] | 92.672
03.10.2007 21:00 | 3600 | 2 | 757.3 | GGB | 765.201 | 770.273 | 765.201 | 266.34 | GGB | 10977.8 | GGB | 9.91 | GGB | 999.99 | GGB | 60.78 | GGB | 164265.02 | GGB | 132628.67 | GGB | 0 | 0 | 2579 | 3600 | 2563.55 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 26439.07 | GGB | 26439.4 | 2563.55 | 2563.55 |  |  |  | 1 | 1 |  |  |  |  | 132628.67 | 2563.55 | 132628.67 | 2563.55 | 8.7992 | [5 empty] | 94.4445
03.10.2007 22:00 | 3600 | 2 | 757.51 | GGB | 767.766 | 771.164 | 765.934 | 268.92 | GGB | 10981.4 | GGB | 9.92 | GGB | 1000.51 | GGB | 60.05 | GGB | 166525.12 | GGB | 134818.79 | GGB | 0 | 0 | 2573 | 3600 | 2557.25 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 26478.8 | GGB | 26479.13 | 2557.25 | 2557.25 |  |  |  | 1 | 1 |  |  |  |  | 134818.79 | 2557.25 | 134818.79 | 2557.25 | 8.6777 | [5 empty] | 95.7682
03.10.2007 23:00 | 3600 | 2 | 757.84 | GGB | 767.766 | 773.297 | 767.033 | 269.28 | GGB | 11020.2 | GGB | 9.93 | GGB | 1000.71 | GGB | 59.9 | GGB | 166913.53 | GGB | 135219.03 | GGB | 0 | 0 | 2560 | 3600 | 2545.01 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 26517.94 | GGB | 26518.27 | 2545.01 | 2545.01 |  |  |  | 1 | 1 |  |  |  |  | 135219.03 | 2545.01 | 135219.03 | 2545.01 | 8.7924 | [5 empty] | 95.5927
03.10.2007 24:00 | 3600 | 2 | 757.94 | GGB | 769.963 | 774.398 | 769.597 | 268.95 | GGB | 11051.1 | GGB | 9.93 | GGB | 1000.85 | GGB | 59.95 | GGB | 166419.48 | GGB | 134818.21 | GGB | 0 | 0 | 2580 | 3600 | 2564.21 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 26557.02 | GGB | 26557.35 | 2564.21 | 2564.21 |  |  |  | 1 | 1 |  |  |  |  | 134818.21 | 2564.21 | 134818.21 | 2564.21 | 8.846 | [5 empty] | 96.0284
04.10.2007 01:00 | 3600 | 2 | 757.55 | GGB | 767.766 | 772.852 | 767.033 | 267.9 | GGB | 11064.9 | GGB | 9.92 | GGB | 1000.97 | GGB | 60.43 | GGB | 165199.21 | GGB | 133651.33 | GGB | 0 | 0 | 2612 | 3600 | 2596.2 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 26597.12 | GGB | 26597.45 | 2596.2 | 2596.2 |  |  |  | 1 | 1 |  |  |  |  | 133651.33 | 2596.2 | 133651.33 | 2596.2 | 8.653 | [5 empty] | 96.3849
04.10.2007 02:00 | 3600 | 2 | 757.56 | GGB | 766.667 | 772.008 | 765.934 | 267.88 | GGB | 11067.4 | GGB | 9.92 | GGB | 1000.68 | GGB | 60.41 | GGB | 165563.42 | GGB | 133914.22 | GGB | 0 | 0 | 2615 | 3600 | 2599.52 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 26635.99 | GGB | 26636.32 | 2599.52 | 2599.52 |  |  |  | 1 | 1 |  |  |  |  | 133914.22 | 2599.52 | 133914.22 | 2599.52 | 8.9558 | [5 empty] | 96.698
04.10.2007 03:00 | 3600 | 2 | 757.76 | GGB | 768.864 | 774.094 | 768.498 | 268.76 | GGB | 11044.7 | GGB | 9.93 | GGB | 1000.54 | GGB | 60.04 | GGB | 166132.29 | GGB | 134508.19 | GGB | 0 | 0 | 2588 | 3600 | 2572.71 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 26675.92 | GGB | 26676.25 | 2572.71 | 2572.71 |  |  |  | 1 | 1 |  |  |  |  | 134508.19 | 2572.71 | 134508.19 | 2572.71 | 8.6664 | [5 empty] | 96.1252
04.10.2007 04:00 | 3600 | 2 | 757.3 | GGB | 766.3 | 770.719 | 765.934 | 267.98 | GGB | 11019.1 | GGB | 9.92 | GGB | 1000.32 | GGB | 60.15 | GGB | 165762.58 | GGB | 134132.52 | GGB | 0 | 0 | 2600 | 3600 | 2584.53 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 26715.44 | GGB | 26715.77 | 2584.53 | 2584.53 |  |  |  | 1 | 1 |  |  |  |  | 134132.52 | 2584.53 | 134132.52 | 2584.53 | 8.772 | [5 empty] | 96.2971
04.10.2007 05:00 | 3600 | 2 | 758.29 | GGB | 766.667 | 771.375 | 765.934 | 268.29 | GGB | 11029.7 | GGB | 9.93 | GGB | 1000.29 | GGB | 59.67 | GGB | 165797.79 | GGB | 134352.02 | GGB | 0 | 0 | 2561 | 3600 | 2545.86 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 26754.33 | GGB | 26754.66 | 2545.86 | 2545.86 |  |  |  | 1 | 1 |  |  |  |  | 134352.02 | 2545.86 | 134352.02 | 2545.86 | 8.7951 | [5 empty] | 95.0115
04.10.2007 06:00 | 3600 | 2 | 757.38 | GGB | 766.667 | 771.375 | 767.033 | 267.54 | GGB | 11013.9 | GGB | 9.92 | GGB | 1000.47 | GGB | 59.48 | GGB | 164416.87 | GGB | 133332.95 | GGB | 0 | 0 | 2603 | 3600 | 2587.54 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 26794.37 | GGB | 26794.7 | 2587.54 | 2587.54 |  |  |  | 1 | 1 |  |  |  |  | 133332.95 | 2587.54 | 133332.95 | 2587.54 | 8.6165 | [5 empty] | 95.8345
04.10.2007 07:00 | 3600 | 2 | 757.31 | GGB | 767.766 | 772.453 | 768.132 | 269.45 | GGB | 10978.2 | GGB | 9.92 | GGB | 1000.31 | GGB | 59.48 | GGB | 165955.14 | GGB | 134558.67 | GGB | 0 | 0 | 2581 | 3600 | 2566.01 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 26832.95 | GGB | 26833.28 | 2566.01 | 2566.01 |  |  |  | 1 | 1 |  |  |  |  | 134558.67 | 2566.01 | 134558.67 | 2566.01 | 8.9497 | [5 empty] | 95.9108
04.10.2007 08:00 | 3600 | 2 | 758.05 | GGB | 765.201 | 770.18 | 764.835 | 267.56 | GGB | 10994.8 | GGB | 9.93 | GGB | 999.81 | GGB | 59.69 | GGB | 164095.57 | GGB | 132901.51 | GGB | 0 | 0 | 2555 | 3600 | 2539.75 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 26872.61 | GGB | 26872.95 | 2539.75 | 2539.75 |  |  |  | 1 | 1 |  |  |  |  | 132901.51 | 2539.75 | 132901.51 | 2539.75 | 8.5086 | [5 empty] | 93.7602
04.10.2007 09:00 | 3600 | 2 | 756.89 | GGB | 766.3 | 771.328 | 767.033 | 268.66 | GGB | 10955.8 | GGB | 9.91 | GGB | 999.56 | GGB | 59.71 | GGB | 164666.64 | GGB | 133322.25 | GGB | 0 | 0 | 2598 | 3600 | 2582.87 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 26911.97 | GGB | 26912.3 | 2582.87 | 2582.87 |  |  |  | 1 | 1 |  |  |  |  | 133322.25 | 2582.87 | 133322.25 | 2582.87 | 8.7511 | [5 empty] | 95.6539
04.10.2007 10:00 | 3600 | 2 | 757.8 | GGB | 767.766 | 773.297 | 768.132 | 268.83 | GGB | 10972 | GGB | 9.93 | GGB | 999.46 | GGB | 60.37 | GGB | 164779.98 | GGB | 133136.74 | GGB | 0 | 0 | 2558 | 3600 | 2542.72 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 26950.84 | GGB | 26951.18 | 2542.72 | 2542.72 |  |  |  | 1 | 1 |  |  |  |  | 133136.74 | 2542.72 | 133136.74 | 2542.72 | 8.707 | [5 empty] | 94.036
04.10.2007 11:00 | 3600 | 2 | 757.56 | GGB | 765.201 | 771.211 | 765.934 | 267.55 | GGB | 10957.2 | GGB | 9.92 | GGB | 999.77 | GGB | 60.92 | GGB | 163127.27 | GGB | 131623.19 | GGB | 0 | 0 | 2570 | 3600 | 2555.13 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 26990.15 | GGB | 26990.49 | 2555.13 | 2555.13 |  |  |  | 1 | 1 |  |  |  |  | 131623.19 | 2555.13 | 131623.19 | 2555.13 | 8.5554 | [5 empty] | 93.4207
04.10.2007 12:00 | 3600 | 2 | 757.33 | GGB | 766.667 | 772.453 | 767.033 | 267.93 | GGB | 10941.6 | GGB | 9.93 | GGB | 999.78 | GGB | 60.92 | GGB | 163687.34 | GGB | 132078.01 | GGB | 0 | 0 | 2539 | 3600 | 2523.25 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 27028.59 | GGB | 27028.94 | 2523.25 | 2523.25 |  |  |  | 1 | 1 |  |  |  |  | 132078.01 | 2523.25 | 132078.01 | 2523.25 | 8.6675 | [5 empty] | 92.5738
04.10.2007 13:00 | 3600 | 2 | 756.74 | GGB | 766.667 | 772.43 | 767.033 | 267.93 | GGB | 10904.7 | GGB | 9.92 | GGB | 999.67 | GGB | 61.09 | GGB | 163734.66 | GGB | 132035.06 | GGB | 0 | 0 | 2550 | 3600 | 2534.94 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 27068.08 | GGB | 27068.43 | 2534.94 | 2534.94 |  |  |  | 1 | 1 |  |  |  |  | 132035.06 | 2534.94 | 132035.06 | 2534.94 | 8.4756 | [5 empty] | 92.9725
04.10.2007 14:00 | 3600 | 2 | 757.43 | GGB | 765.201 | 770.414 | 765.934 | 267.97 | GGB | 10895.5 | GGB | 9.92 | GGB | 999.74 | GGB | 61.09 | GGB | 164054.86 | GGB | 132299.72 | GGB | 0 | 0 | 2515 | 3600 | 2499.45 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 27105.94 | GGB | 27106.29 | 2499.45 | 2499.45 |  |  |  | 1 | 1 |  |  |  |  | 132299.72 | 2499.45 | 132299.72 | 2499.45 | 8.7342 | [5 empty] | 91.8546
04.10.2007 15:00 | 3600 | 2 | 757.43 | GGB | 766.3 | 771.633 | 765.934 | 266.71 | GGB | 10928.2 | GGB | 9.93 | GGB | 999.79 | GGB | 61.8 | GGB | 162294.32 | GGB | 130609.22 | GGB | 0 | 0 | 2546 | 3600 | 2531 | GGB | 100 | GGB | 38.41 | GGB | 38.41 | GGB | 27144.35 | GGB | 27144.7 | 2531 | 2531 |  |  |  | 1 | 1 |  |  |  |  | 130609.22 | 2531 | 130609.22 | 2531 | 8.6064 | [5 empty] | 91.8255
04.10.2007 16:00 | 3600 | 2 | 756.99 | GGB | 765.201 | 770.531 | 764.835 | 267.29 | GGB | 10901.3 | GGB | 9.92 | GGB | 999.89 | GGB | 61.99 | GGB | 162459.37 | GGB | 130682.58 | GGB | 0 | 0 | 2561 | 3600 | 2545.96 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 27183.38 | GGB | 27183.73 | 2545.96 | 2545.96 |  |  |  | 1 | 1 |  |  |  |  | 130682.58 | 2545.96 | 130682.58 | 2545.96 | 8.5245 | [5 empty] | 92.4202
04.10.2007 17:00 | 3600 | 2 | 757.56 | GGB | 766.3 | 771.633 | 767.033 | 268.41 | GGB | 10891.7 | GGB | 9.92 | GGB | 999.43 | GGB | 61.46 | GGB | 163696.15 | GGB | 131826.2 | GGB | 0 | 0 | 2527 | 3600 | 2511.51 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 27221.52 | GGB | 27221.87 | 2511.51 | 2511.51 |  |  |  | 1 | 1 |  |  |  |  | 131826.2 | 2511.51 | 131826.2 | 2511.51 | 8.6807 | [5 empty] | 91.9674
04.10.2007 18:00 | 3600 | 2 | 758.06 | GGB | 765.201 | 771.633 | 765.934 | 267.12 | GGB | 10909.8 | GGB | 9.93 | GGB | 999.44 | GGB | 62.19 | GGB | 162151.27 | GGB | 130298.53 | GGB | 0 | 0 | 2516 | 3600 | 2500.39 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 27260.27 | GGB | 27260.62 | 2500.39 | 2500.39 |  |  |  | 1 | 1 |  |  |  |  | 130298.53 | 2500.39 | 130298.53 | 2500.39 | 8.4077 | [5 empty] | 90.4992
04.10.2007 19:00 | 3600 | 2 | 757.44 | GGB | 765.201 | 771.656 | 765.934 | 266.96 | GGB | 10892.5 | GGB | 9.92 | GGB | 999.33 | GGB | 62.59 | GGB | 161478.97 | GGB | 129590.01 | GGB | 0 | 0 | 2540 | 3600 | 2525.08 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 27299.17 | GGB | 27299.52 | 2525.08 | 2525.08 |  |  |  | 1 | 1 |  |  |  |  | 129590.01 | 2525.08 | 129590.01 | 2525.08 | 8.412 | [5 empty] | 90.8959
04.10.2007 20:00 | 3600 | 2 | 757.48 | GGB | 767.766 | 771.656 | 767.033 | 268.26 | GGB | 10877.4 | GGB | 9.92 | GGB | 999.7 | GGB | 62.08 | GGB | 162935.81 | GGB | 131005.88 | GGB | 0 | 0 | 2530 | 3600 | 2514.93 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 27337.51 | GGB | 27337.86 | 2514.93 | 2514.93 |  |  |  | 1 | 1 |  |  |  |  | 131005.88 | 2514.93 | 131005.88 | 2514.93 | 8.5934 | [5 empty] | 91.5196
04.10.2007 21:00 | 3600 | 2 | 758.02 | GGB | 766.667 | 771.727 | 767.033 | 266.84 | GGB | 10917.2 | GGB | 9.93 | GGB | 999.6 | GGB | 62.64 | GGB | 161327.12 | GGB | 129481.3 | GGB | 0 | 0 | 2533 | 3600 | 2517.91 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 27376.77 | GGB | 27377.12 | 2517.91 | 2517.91 |  |  |  | 1 | 1 |  |  |  |  | 129481.3 | 2517.91 | 129481.3 | 2517.91 | 8.3042 | [5 empty] | 90.5617
04.10.2007 22:00 | 3600 | 2 | 757.55 | GGB | 766.667 | 771.727 | 767.033 | 266.57 | GGB | 10906.8 | GGB | 9.93 | GGB | 999.6 | GGB | 62.65 | GGB | 161191.78 | GGB | 129369.71 | GGB | 0 | 0 | 2548 | 3600 | 2533.07 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 27415.31 | GGB | 27415.66 | 2533.07 | 2533.07 |  |  |  | 1 | 1 |  |  |  |  | 129369.71 | 2533.07 | 129369.71 | 2533.07 | 8.5029 | [5 empty] | 91.0285
04.10.2007 23:00 | 3600 | 2 | 757.12 | GGB | 766.667 | 771.867 | 767.033 | 267.16 | GGB | 10912.2 | GGB | 9.91 | GGB | 999.64 | GGB | 62.6 | GGB | 161900.4 | GGB | 129963.92 | GGB | 0 | 0 | 2570 | 3600 | 2555.18 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 27454.58 | GGB | 27454.94 | 2555.18 | 2555.18 |  |  |  | 1 | 1 |  |  |  |  | 129963.92 | 2555.18 | 129963.92 | 2555.18 | 8.4542 | [5 empty] | 92.2448
04.10.2007 24:00 | 3600 | 2 | 757.52 | GGB | 766.667 | 771.797 | 767.033 | 267.38 | GGB | 10953.1 | GGB | 9.93 | GGB | 999.63 | GGB | 62.17 | GGB | 162204.09 | GGB | 130373.16 | GGB | 0 | 0 | 2570 | 3600 | 2554.5 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 27493.72 | GGB | 27494.08 | 2554.5 | 2554.5 |  |  |  | 1 | 1 |  |  |  |  | 130373.16 | 2554.5 | 130373.16 | 2554.5 | 8.5089 | [5 empty] | 92.5106
05.10.2007 01:00 | 3600 | 2 | 756.99 | GGB | 766.3 | 770.742 | 767.033 | 267.37 | GGB | 10946.8 | GGB | 9.92 | GGB | 999.89 | GGB | 62.27 | GGB | 162404.35 | GGB | 130530.72 | GGB | 0 | 0 | 2592 | 3600 | 2576.8 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 27533.16 | GGB | 27533.51 | 2576.8 | 2576.8 |  |  |  | 1 | 1 |  |  |  |  | 130530.72 | 2576.8 | 130530.72 | 2576.8 | 8.5303 | [5 empty] | 93.431
05.10.2007 02:00 | 3600 | 2 | 757.1 | GGB | 768.864 | 774.117 | 768.864 | 267.62 | GGB | 10956.5 | GGB | 9.93 | GGB | 999.94 | GGB | 62.14 | GGB | 162342.73 | GGB | 130537.6 | GGB | 0 | 0 | 2588 | 3600 | 2572.83 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 27572.5 | GGB | 27572.86 | 2572.83 | 2572.83 |  |  |  | 1 | 1 |  |  |  |  | 130537.6 | 2572.83 | 130537.6 | 2572.83 | 8.535 | [5 empty] | 93.292
05.10.2007 03:00 | 3600 | 2 | 757.11 | GGB | 766.667 | 771.82 | 766.667 | 267.35 | GGB | 10949.3 | GGB | 9.92 | GGB | 999.88 | GGB | 62.1 | GGB | 162080.85 | GGB | 130334.5 | GGB | 0 | 0 | 2578 | 3600 | 2562.7 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 27611.61 | GGB | 27611.97 | 2562.7 | 2562.7 |  |  |  | 1 | 1 |  |  |  |  | 130334.5 | 2562.7 | 130334.5 | 2562.7 | 8.5402 | [5 empty] | 92.7801
05.10.2007 04:00 | 3600 | 2 | 756.86 | GGB | 766.667 | 771.75 | 767.033 | 268.58 | GGB | 10937.8 | GGB | 9.91 | GGB | 1000.14 | GGB | 61.7 | GGB | 163581.71 | GGB | 131732.72 | GGB | 0 | 0 | 2588 | 3600 | 2572.81 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 27650.9 | GGB | 27651.26 | 2572.81 | 2572.81 |  |  |  | 1 | 1 |  |  |  |  | 131732.72 | 2572.81 | 131732.72 | 2572.81 | 8.6262 | [5 empty] | 94.1453
05.10.2007 05:00 | 3600 | 2 | 757.52 | GGB | 767.766 | 771.727 | 768.132 | 269.26 | GGB | 10957 | GGB | 9.93 | GGB | 1000.34 | GGB | 61.08 | GGB | 164255.12 | GGB | 132548.88 | GGB | 0 | 0 | 2558 | 3600 | 2542.58 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 27689.98 | GGB | 27690.34 | 2542.58 | 2542.58 |  |  |  | 1 | 1 |  |  |  |  | 132548.88 | 2542.58 | 132548.88 | 2542.58 | 8.6237 | [5 empty] | 93.6156
05.10.2007 06:00 | 3600 | 2 | 757.35 | GGB | 765.201 | 770.648 | 765.934 | 268.38 | GGB | 10975.1 | GGB | 9.92 | GGB | 1000.25 | GGB | 61.73 | GGB | 163156.98 | GGB | 131393.52 | GGB | 0 | 0 | 2589 | 3600 | 2573.9 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 27729 | GGB | 27729.36 | 2573.9 | 2573.9 |  |  |  | 1 | 1 |  |  |  |  | 131393.52 | 2573.9 | 131393.52 | 2573.9 | 8.6672 | [5 empty] | 93.9427
05.10.2007 07:00 | 3600 | 2 | 756.98 | GGB | 765.201 | 770.602 | 765.934 | 270.12 | GGB | 10971.5 | GGB | 9.91 | GGB | 1000.42 | GGB | 61.09 | GGB | 164863.61 | GGB | 133043.28 | GGB | 0 | 0 | 2590 | 3600 | 2574.82 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 27768.35 | GGB | 27768.71 | 2574.82 | 2574.82 |  |  |  | 1 | 1 |  |  |  |  | 133043.28 | 2574.82 | 133043.28 | 2574.82 | 8.7055 | [5 empty] | 95.1562
05.10.2007 08:00 | 3600 | 2 | 757.6 | GGB | 768.864 | 773.719 | 768.498 | 270.13 | GGB | 11017.2 | GGB | 9.94 | GGB | 1000.42 | GGB | 60.83 | GGB | 165359.86 | GGB | 133548.85 | GGB | 0 | 0 | 2579 | 3600 | 2563.6 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 27807.14 | GGB | 27807.5 | 2563.6 | 2563.6 |  |  |  | 1 | 1 |  |  |  |  | 133548.85 | 2563.6 | 133548.85 | 2563.6 | 8.8261 | [5 empty] | 95.1016
05.10.2007 09:00 | 3600 | 2 | 757.03 | GGB | 765.201 | 769.828 | 764.835 | 269.57 | GGB | 11014.7 | GGB | 9.92 | GGB | 1000.92 | GGB | 61.26 | GGB | 164628.13 | GGB | 132855.79 | GGB | 0 | 0 | 2617 | 3206 | 2601.61 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 27846.46 | GGB | 27846.82 | 2601.61 | 2601.61 |  |  |  | 1 | 1 |  |  |  |  | 132855.79 | 2601.61 | 132855.79 | 2601.61 | 8.7904 | [5 empty] | 96.0108
05.10.2007 10:00 | 3600 | 2 | 756.85 | GGB | 766.3 | 770.836 | 765.934 | 271.13 | GGB | 10999.3 | GGB | 9.92 | GGB | 1001.08 | GGB | 60.55 | GGB | 166440.39 | GGB | 134621.82 | GGB | 0 | 0 | 2619 | 3600 | 2604.11 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 27885.19 | GGB | 27885.55 | 2604.11 | 2604.11 |  |  |  | 1 | 1 |  |  |  |  | 134621.82 | 2604.11 | 134621.82 | 2604.11 | 9.0516 | [5 empty] | 97.3806
05.10.2007 11:00 | 3600 | 2 | 758.02 | GGB | 766.667 | 771.586 | 767.033 | 269.63 | GGB | 11046.2 | GGB | 9.94 | GGB | 1001.32 | GGB | 60.92 | GGB | 164859.2 | GGB | 133229.77 | GGB | 0 | 0 | 2576 | 3600 | 2560.8 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 27924.27 | GGB | 27924.63 | 2560.8 | 2560.8 |  |  |  | 1 | 1 |  |  |  |  | 133229.77 | 2560.8 | 133229.77 | 2560.8 | 8.7302 | [5 empty] | 94.7708
05.10.2007 12:00 | 3600 | 2 | 756.45 | GGB | 767.766 | 772.828 | 768.132 | 269.13 | GGB | 11027 | GGB | 9.92 | GGB | 1001.58 | GGB | 60.98 | GGB | 164206.7 | GGB | 132710.5 | GGB | 0 | 0 | 2632 | 3600 | 2616.22 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 27963.67 | GGB | 27964.03 | 2616.22 | 2616.22 |  |  |  | 1 | 1 |  |  |  |  | 132710.5 | 2616.22 | 132710.5 | 2616.22 | 8.8122 | [5 empty] | 96.4444
05.10.2007 13:00 | 3600 | 2 | 757.52 | GGB | 766.667 | 772.828 | 767.033 | 268.36 | GGB | 11018.7 | GGB | 9.93 | GGB | 1001.62 | GGB | 61.24 | GGB | 163608.12 | GGB | 132132.03 | GGB | 0 | 0 | 2579 | 3600 | 2563.64 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 28002.61 | GGB | 28002.97 | 2563.64 | 2563.64 |  |  |  | 1 | 1 |  |  |  |  | 132132.03 | 2563.64 | 132132.03 | 2563.64 | 8.699 | [5 empty] | 94.0942
05.10.2007 14:00 | 3600 | 2 | 756.99 | GGB | 766.667 | 771.773 | 767.033 | 269.62 | GGB | 10954 | GGB | 9.92 | GGB | 1001.5 | GGB | 60.94 | GGB | 165162.9 | GGB | 133490.56 | GGB | 0 | 0 | 2578 | 3600 | 2563.11 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 28043.36 | GGB | 28043.72 | 2563.11 | 2563.11 |  |  |  | 1 | 1 |  |  |  |  | 133490.56 | 2563.11 | 133490.56 | 2563.11 | 8.3963 | [5 empty] | 95.0419
05.10.2007 15:00 | 3600 | 2 | 757.76 | GGB | 766.3 | 770.672 | 765.934 | 268.77 | GGB | 10967.2 | GGB | 9.93 | GGB | 1001.2 | GGB | 61.06 | GGB | 164711.76 | GGB | 133038.46 | GGB | 0 | 0 | 2544 | 3600 | 2528.85 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 28082.12 | GGB | 28082.48 | 2528.85 | 2528.85 |  |  |  | 1 | 1 |  |  |  |  | 133038.46 | 2528.85 | 133038.46 | 2528.85 | 8.6799 | [5 empty] | 93.454
05.10.2007 16:00 | 3600 | 2 | 757.59 | GGB | 766.3 | 770.719 | 765.934 | 267.3 | GGB | 10964.6 | GGB | 9.93 | GGB | 1000.94 | GGB | 61.58 | GGB | 163289.02 | GGB | 131651.02 | GGB | 0 | 0 | 2549 | 3600 | 2534.04 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 28121.33 | GGB | 28121.69 | 2534.04 | 2534.04 |  |  |  | 1 | 1 |  |  |  |  | 131651.02 | 2534.04 | 131651.02 | 2534.04 | 8.5083 | [5 empty] | 92.6692
05.10.2007 17:00 | 3600 | 2 | 757.39 | GGB | 765.201 | 770.836 | 765.934 | 266.91 | GGB | 10942 | GGB | 9.93 | GGB | 1000.94 | GGB | 61.82 | GGB | 162879.7 | GGB | 131227.29 | GGB | 0 | 0 | 2550 | 3600 | 2534.4 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 28160.34 | GGB | 28160.7 | 2534.4 | 2534.4 |  |  |  | 1 | 1 |  |  |  |  | 131227.29 | 2534.4 | 131227.29 | 2534.4 | 8.5256 | [5 empty] | 92.384
05.10.2007 18:00 | 3600 | 2 | 757.44 | GGB | 766.3 | 771.914 | 767.033 | 266.87 | GGB | 10929.3 | GGB | 9.92 | GGB | 1000.83 | GGB | 62.14 | GGB | 162770.76 | GGB | 130995.95 | GGB | 0 | 0 | 2553 | 3600 | 2537.29 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 28199.19 | GGB | 28199.56 | 2537.29 | 2537.29 |  |  |  | 1 | 1 |  |  |  |  | 130995.95 | 2537.29 | 130995.95 | 2537.29 | 8.5531 | [5 empty] | 92.3263
05.10.2007 19:00 | 3600 | 2 | 757.27 | GGB | 766.3 | 771.633 | 765.934 | 267.3 | GGB | 10942.7 | GGB | 9.92 | GGB | 1000.39 | GGB | 62.07 | GGB | 163107.47 | GGB | 131238.43 | GGB | 0 | 0 | 2563 | 3600 | 2547.42 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 28238.56 | GGB | 28238.92 | 2547.42 | 2547.42 |  |  |  | 1 | 1 |  |  |  |  | 131238.43 | 2547.42 | 131238.43 | 2547.42 | 8.4939 | [5 empty] | 92.8665
05.10.2007 20:00 | 3600 | 2 | 756.47 | GGB | 764.102 | 769.031 | 764.835 | 268.41 | GGB | 10957.1 | GGB | 9.91 | GGB | 1000.54 | GGB | 61.76 | GGB | 164175.89 | GGB | 132240.02 | GGB | 0 | 0 | 2619 | 3600 | 2603.39 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 28277.22 | GGB | 28277.59 | 2603.39 | 2603.39 |  |  |  | 1 | 1 |  |  |  |  | 132240.02 | 2603.39 | 132240.02 | 2603.39 | 8.9028 | [5 empty] | 95.6312
05.10.2007 21:00 | 3600 | 2 | 757.29 | GGB | 766.667 | 771.352 | 767.033 | 268.7 | GGB | 10996.4 | GGB | 9.93 | GGB | 1000.77 | GGB | 61.55 | GGB | 164301.33 | GGB | 132454.25 | GGB | 0 | 0 | 2608 | 3600 | 2592.34 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 28316.72 | GGB | 28317.09 | 2592.34 | 2592.34 |  |  |  | 1 | 1 |  |  |  |  | 132454.25 | 2592.34 | 132454.25 | 2592.34 | 8.6928 | [5 empty] | 95.3796
05.10.2007 22:00 | 3600 | 2 | 757.68 | GGB | 767.766 | 772.43 | 768.132 | 267.35 | GGB | 10984.5 | GGB | 9.94 | GGB | 1000.79 | GGB | 61.58 | GGB | 162953.42 | GGB | 131359 | GGB | 0 | 0 | 2574 | 3600 | 2559.06 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 28355.88 | GGB | 28356.26 | 2559.06 | 2559.06 |  |  |  | 1 | 1 |  |  |  |  | 131359 | 2559.06 | 131359 | 2559.06 | 8.582 | [5 empty] | 93.3765
05.10.2007 23:00 | 3600 | 2 | 757.48 | GGB | 766.667 | 772.523 | 767.033 | 266.69 | GGB | 10942.2 | GGB | 9.93 | GGB | 1000.67 | GGB | 61.41 | GGB | 162381.24 | GGB | 130949.92 | GGB | 0 | 0 | 2564 | 3600 | 2548.95 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 28394.8 | GGB | 28395.17 | 2548.95 | 2548.95 |  |  |  | 1 | 1 |  |  |  |  | 130949.92 | 2548.95 | 130949.92 | 2548.95 | 8.5784 | [5 empty] | 92.718
05.10.2007 24:00 | 3600 | 2 | 757.57 | GGB | 767.766 | 772.477 | 768.132 | 266.54 | GGB | 10928.3 | GGB | 9.93 | GGB | 1000.32 | GGB | 61.7 | GGB | 162706.94 | GGB | 131051.78 | GGB | 0 | 0 | 2557 | 3600 | 2541.5 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 28434.22 | GGB | 28434.6 | 2541.5 | 2541.5 |  |  |  | 1 | 1 |  |  |  |  | 131051.78 | 2541.5 | 131051.78 | 2541.5 | 8.4471 | [5 empty] | 92.5189
06.10.2007 01:00 | 3600 | 2 | 757.46 | GGB | 766.667 | 771.375 | 767.033 | 266.35 | GGB | 10914.5 | GGB | 9.92 | GGB | 1000.07 | GGB | 61.8 | GGB | 162775.16 | GGB | 131033.32 | GGB | 0 | 0 | 2554 | 3600 | 2538.59 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 28473.18 | GGB | 28473.56 | 2538.59 | 2538.59 |  |  |  | 1 | 1 |  |  |  |  | 131033.32 | 2538.59 | 131033.32 | 2538.59 | 8.538 | [5 empty] | 92.4
06.10.2007 02:00 | 3600 | 2 | 757.53 | GGB | 766.667 | 771.469 | 767.033 | 266.39 | GGB | 10919 | GGB | 9.93 | GGB | 999.84 | GGB | 61.78 | GGB | 162793.87 | GGB | 131026.99 | GGB | 0 | 0 | 2555 | 3600 | 2539.52 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 28511.85 | GGB | 28512.23 | 2539.52 | 2539.52 |  |  |  | 1 | 1 |  |  |  |  | 131026.99 | 2539.52 | 131026.99 | 2539.52 | 8.6047 | [5 empty] | 92.4294
06.10.2007 03:00 | 3600 | 2 | 757.38 | GGB | 766.3 | 771.234 | 765.934 | 266.52 | GGB | 10889.9 | GGB | 9.92 | GGB | 1000.06 | GGB | 61.95 | GGB | 162649.73 | GGB | 130875.76 | GGB | 0 | 0 | 2554 | 3600 | 2538.72 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 28551.24 | GGB | 28551.61 | 2538.72 | 2538.72 |  |  |  | 1 | 1 |  |  |  |  | 130875.76 | 2538.72 | 130875.76 | 2538.72 | 8.4372 | [5 empty] | 92.2936
06.10.2007 04:00 | 3600 | 2 | 756.87 | GGB | 766.3 | 770.297 | 765.934 | 267.07 | GGB | 10906.7 | GGB | 9.91 | GGB | 1000.23 | GGB | 62.06 | GGB | 162481.37 | GGB | 130715.97 | GGB | 0 | 0 | 2585 | 3600 | 2569.96 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 28589.55 | GGB | 28589.93 | 2569.96 | 2569.96 |  |  |  | 1 | 1 |  |  |  |  | 130715.97 | 2569.96 | 130715.97 | 2569.96 | 8.7666 | [5 empty] | 93.3152
06.10.2007 05:00 | 3600 | 2 | 756.83 | GGB | 766.667 | 772.242 | 767.033 | 270.42 | GGB | 10926.5 | GGB | 9.91 | GGB | 1000.17 | GGB | 61.07 | GGB | 165610.73 | GGB | 133621.61 | GGB | 0 | 0 | 2578 | 3600 | 2562.54 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 28628.84 | GGB | 28629.22 | 2562.54 | 2562.54 |  |  |  | 1 | 1 |  |  |  |  | 133621.61 | 2562.54 | 133621.61 | 2562.54 | 8.715 | [5 empty] | 95.1141
06.10.2007 06:00 | 3600 | 2 | 757.19 | GGB | 766.3 | 770.109 | 765.934 | 269.82 | GGB | 11007.6 | GGB | 9.92 | GGB | 1000.66 | GGB | 61.24 | GGB | 165145.29 | GGB | 133244.82 | GGB | 0 | 0 | 2600 | 3600 | 2584.45 | GGB | 100 | GGB | 36.98 | GGB | 36.98 | GGB | 28665.82 | GGB | 28666.2 | 2584.45 | 2584.45 |  |  |  | 1 | 1 |  |  |  |  | 133244.82 | 2584.45 | 133244.82 | 2584.45 | 9.3122 | [5 empty] | 95.6568
06.10.2007 07:00 | 3600 | 2 | 757.12 | GGB | 766.667 | 771.656 | 767.033 | 269.94 | GGB | 11042.3 | GGB | 9.92 | GGB | 1000.85 | GGB | 61.06 | GGB | 165493 | GGB | 133621.98 | GGB | 0 | 0 | 2619 | 3600 | 2604.07 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 28705.69 | GGB | 28706.07 | 2604.07 | 2604.07 |  |  |  | 1 | 1 |  |  |  |  | 133621.98 | 2604.07 | 133621.98 | 2604.07 | 8.7274 | [5 empty] | 96.6558
06.10.2007 08:00 | 3600 | 2 | 756.89 | GGB | 766.3 | 770.648 | 765.934 | 270.48 | GGB | 11063.6 | GGB | 9.92 | GGB | 1000.88 | GGB | 60.79 | GGB | 166151 | GGB | 134267.99 | GGB | 0 | 0 | 2648 | 3600 | 2632.37 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 28745.18 | GGB | 28745.56 | 2632.37 | 2632.37 |  |  |  | 1 | 1 |  |  |  |  | 134267.99 | 2632.37 | 134267.99 | 2632.37 | 8.9502 | [5 empty] | 98.1786
06.10.2007 09:00 | 3600 | 2 | 757.27 | GGB | 765.201 | 770.766 | 766.667 | 271.61 | GGB | 11038.1 | GGB | 9.93 | GGB | 1001.33 | GGB | 60.42 | GGB | 167726.68 | GGB | 135750.45 | GGB | 0 | 0 | 2604 | 3600 | 2589.08 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 28784.72 | GGB | 28785.1 | 2589.08 | 2589.08 |  |  |  | 1 | 1 |  |  |  |  | 135750.45 | 2589.08 | 135750.45 | 2589.08 | 8.8889 | [5 empty] | 97.6302
06.10.2007 10:00 | 3600 | 2 | 757.71 | GGB | 766.667 | 771.938 | 766.667 | 269.4 | GGB | 11051.6 | GGB | 9.93 | GGB | 1001.6 | GGB | 60.96 | GGB | 165752.68 | GGB | 133971.28 | GGB | 0 | 0 | 2594 | 3600 | 2578.67 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 28823.98 | GGB | 28824.36 | 2578.67 | 2578.67 |  |  |  | 1 | 1 |  |  |  |  | 133971.28 | 2578.67 | 133971.28 | 2578.67 | 8.7995 | [5 empty] | 95.9633
06.10.2007 11:00 | 3600 | 2 | 757.32 | GGB | 765.201 | 770.953 | 766.667 | 268.85 | GGB | 11019.6 | GGB | 9.92 | GGB | 1001.55 | GGB | 61.14 | GGB | 165209.11 | GGB | 133452.53 | GGB | 0 | 0 | 2599 | 3600 | 2583.89 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 28863.88 | GGB | 28864.26 | 2583.89 | 2583.89 |  |  |  | 1 | 1 |  |  |  |  | 133452.53 | 2583.89 | 133452.53 | 2583.89 | 8.6423 | [5 empty] | 95.7852
06.10.2007 12:00 | 3600 | 2 | 757.47 | GGB | 766.667 | 772.031 | 767.033 | 269.09 | GGB | 10974.5 | GGB | 9.93 | GGB | 1001.61 | GGB | 60.87 | GGB | 165691.06 | GGB | 133960.58 | GGB | 0 | 0 | 2547 | 3600 | 2531.45 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 28903.24 | GGB | 28903.61 | 2531.45 | 2531.45 |  |  |  | 1 | 1 |  |  |  |  | 133960.58 | 2531.45 | 133960.58 | 2531.45 | 8.6179 | [5 empty] | 94.1985
06.10.2007 13:00 | 3600 | 2 | 757.79 | GGB | 766.3 | 772.125 | 767.033 | 266.9 | GGB | 10968.7 | GGB | 9.93 | GGB | 1001.21 | GGB | 61.7 | GGB | 163602.62 | GGB | 131890.14 | GGB | 0 | 0 | 2541 | 3600 | 2525.93 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 28942.3 | GGB | 28942.67 | 2525.93 | 2525.93 |  |  |  | 1 | 1 |  |  |  |  | 131890.14 | 2525.93 | 131890.14 | 2525.93 | 8.5291 | [5 empty] | 92.5404
06.10.2007 14:00 | 3600 | 2 | 758.01 | GGB | 766.667 | 773.25 | 767.033 | 266.42 | GGB | 10933.1 | GGB | 9.93 | GGB | 1001.21 | GGB | 62.09 | GGB | 162777.36 | GGB | 131073.13 | GGB | 0 | 0 | 2520 | 3600 | 2504.97 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 28981.29 | GGB | 28981.66 | 2504.97 | 2504.97 |  |  |  | 1 | 1 |  |  |  |  | 131073.13 | 2504.97 | 131073.13 | 2504.97 | 8.421 | [5 empty] | 91.204
06.10.2007 15:00 | 3600 | 2 | 757.11 | GGB | 766.3 | 771.234 | 767.033 | 266.84 | GGB | 10903.7 | GGB | 9.92 | GGB | 1000.94 | GGB | 62.19 | GGB | 162783.97 | GGB | 131004.39 | GGB | 0 | 0 | 2552 | 3600 | 2536.61 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 29020.54 | GGB | 29020.91 | 2536.61 | 2536.61 |  |  |  | 1 | 1 |  |  |  |  | 131004.39 | 2536.61 | 131004.39 | 2536.61 | 8.4664 | [5 empty] | 92.3075
06.10.2007 16:00 | 3600 | 2 | 757.45 | GGB | 766.3 | 771.117 | 765.934 | 267.39 | GGB | 10919.8 | GGB | 9.92 | GGB | 1000.96 | GGB | 62.12 | GGB | 162858.79 | GGB | 131093.15 | GGB | 0 | 0 | 2547 | 3600 | 2531.92 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 29059.04 | GGB | 29059.42 | 2531.92 | 2531.92 |  |  |  | 1 | 1 |  |  |  |  | 131093.15 | 2531.92 | 131093.15 | 2531.92 | 8.619 | [5 empty] | 92.1993
06.10.2007 17:00 | 3600 | 2 | 757.45 | GGB | 766.667 | 772.219 | 767.033 | 269.36 | GGB | 10895 | GGB | 9.92 | GGB | 1000.52 | GGB | 61.54 | GGB | 164624.83 | GGB | 132686.73 | GGB | 0 | 0 | 2534 | 3600 | 2518.96 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 29098.34 | GGB | 29098.72 | 2518.96 | 2518.96 |  |  |  | 1 | 1 |  |  |  |  | 132686.73 | 2518.96 | 132686.73 | 2518.96 | 8.5046 | [5 empty] | 92.8424
06.10.2007 18:00 | 3600 | 2 | 758.02 | GGB | 768.864 | 774.633 | 769.597 | 268.78 | GGB | 10921.3 | GGB | 9.93 | GGB | 1000.44 | GGB | 61.62 | GGB | 164247.42 | GGB | 132338.55 | GGB | 0 | 0 | 2518 | 3600 | 2502.86 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 29137.17 | GGB | 29137.55 | 2502.86 | 2502.86 |  |  |  | 1 | 1 |  |  |  |  | 132338.55 | 2502.86 | 132338.55 | 2502.86 | 8.5301 | [5 empty] | 92.0069
06.10.2007 19:00 | 3600 | 2 | 757.39 | GGB | 767.766 | 772.477 | 768.132 | 267.6 | GGB | 10934.5 | GGB | 9.92 | GGB | 1000.58 | GGB | 62.35 | GGB | 162973.23 | GGB | 131044.83 | GGB | 0 | 0 | 2569 | 3600 | 2554.2 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 29176.13 | GGB | 29176.51 | 2554.2 | 2554.2 |  |  |  | 1 | 1 |  |  |  |  | 131044.83 | 2554.2 | 131044.83 | 2554.2 | 8.5912 | [5 empty] | 92.9763
06.10.2007 20:00 | 3600 | 2 | 757.57 | GGB | 766.667 | 771.445 | 767.033 | 267.52 | GGB | 10939.3 | GGB | 9.92 | GGB | 1000.45 | GGB | 62.3 | GGB | 163065.65 | GGB | 131122.84 | GGB | 0 | 0 | 2567 | 3600 | 2552.06 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 29215.47 | GGB | 29215.85 | 2552.06 | 2552.06 |  |  |  | 1 | 1 |  |  |  |  | 131122.84 | 2552.06 | 131122.84 | 2552.06 | 8.5062 | [5 empty] | 92.9537
06.10.2007 21:00 | 3600 | 2 | 756.88 | GGB | 766.3 | 771.352 | 767.033 | 268.95 | GGB | 10930.6 | GGB | 9.91 | GGB | 1000.7 | GGB | 61.86 | GGB | 164259.52 | GGB | 132289.28 | GGB | 0 | 0 | 2601 | 3600 | 2585.28 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 29254.27 | GGB | 29254.65 | 2585.28 | 2585.28 |  |  |  | 1 | 1 |  |  |  |  | 132289.28 | 2585.28 | 132289.28 | 2585.28 | 8.8146 | [5 empty] | 95.0013
06.10.2007 22:00 | 3600 | 2 | 757.87 | GGB | 764.102 | 768.961 | 763.37 | 268.97 | GGB | 10970.9 | GGB | 9.93 | GGB | 1000.6 | GGB | 61.6 | GGB | 164688.65 | GGB | 132725.17 | GGB | 0 | 0 | 2564 | 3600 | 2548.25 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 29293.1 | GGB | 29293.49 | 2548.25 | 2548.25 |  |  |  | 1 | 1 |  |  |  |  | 132725.17 | 2548.25 | 132725.17 | 2548.25 | 8.708 | [5 empty] | 93.9491
06.10.2007 23:00 | 3600 | 2 | 757.13 | GGB | 766.667 | 772.008 | 767.033 | 268.19 | GGB | 10983.5 | GGB | 9.93 | GGB | 1000.48 | GGB | 61.58 | GGB | 164600.62 | GGB | 132645.64 | GGB | 0 | 0 | 2607 | 3600 | 2591.59 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 29332.32 | GGB | 29332.71 | 2591.59 | 2591.59 |  |  |  | 1 | 1 |  |  |  |  | 132645.64 | 2591.59 | 132645.64 | 2591.59 | 8.765 | [5 empty] | 95.4898
06.10.2007 24:00 | 3600 | 2 | 756.89 | GGB | 766.667 | 771.961 | 767.033 | 270.34 | GGB | 10946.8 | GGB | 9.92 | GGB | 1000.22 | GGB | 60.99 | GGB | 165822 | GGB | 133831.81 | GGB | 0 | 0 | 2597 | 3600 | 2581.69 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 29371.86 | GGB | 29372.25 | 2581.69 | 2581.69 |  |  |  | 1 | 1 |  |  |  |  | 133831.81 | 2581.69 | 133831.81 | 2581.69 | 8.7383 | [5 empty] | 95.9756
07.10.2007 01:00 | 3600 | 2 | 757.69 | GGB | 765.201 | 769.828 | 765.201 | 269.45 | GGB | 10982.9 | GGB | 9.93 | GGB | 1000.02 | GGB | 61.23 | GGB | 164789.88 | GGB | 132874.82 | GGB | 0 | 0 | 2577 | 3600 | 2561.84 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 29410.6 | GGB | 29411 | 2561.84 | 2561.84 |  |  |  | 1 | 1 |  |  |  |  | 132874.82 | 2561.84 | 132874.82 | 2561.84 | 8.7846 | [5 empty] | 94.5567
07.10.2007 02:00 | 3600 | 2 | 757.06 | GGB | 766.3 | 771.094 | 767.766 | 268.89 | GGB | 10999.5 | GGB | 9.93 | GGB | 999.79 | GGB | 61.49 | GGB | 164318.94 | GGB | 132363.34 | GGB | 0 | 0 | 2620 | 3600 | 2604.54 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 29450.01 | GGB | 29450.41 | 2604.54 | 2604.54 |  |  |  | 1 | 1 |  |  |  |  | 132363.34 | 2604.54 | 132363.34 | 2604.54 | 8.7477 | [5 empty] | 95.7627
07.10.2007 03:00 | 3600 | 2 | 756.66 | GGB | 765.201 | 770.391 | 766.3 | 269.59 | GGB | 10974.5 | GGB | 9.91 | GGB | 999.91 | GGB | 61.31 | GGB | 164821.79 | GGB | 132856.47 | GGB | 0 | 0 | 2624 | 3600 | 2608.64 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 29489.39 | GGB | 29489.8 | 2608.64 | 2608.64 |  |  |  | 1 | 1 |  |  |  |  | 132856.47 | 2608.64 | 132856.47 | 2608.64 | 8.7985 | [5 empty] | 96.2708
07.10.2007 04:00 | 3600 | 2 | 757.25 | GGB | 764.102 | 770.203 | 764.835 | 269.64 | GGB | 11002.9 | GGB | 9.93 | GGB | 999.54 | GGB | 61.12 | GGB | 165257.53 | GGB | 133231.61 | GGB | 0 | 0 | 2608 | 3600 | 2593.11 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 29528.12 | GGB | 29528.53 | 2593.11 | 2593.11 |  |  |  | 1 | 1 |  |  |  |  | 133231.61 | 2593.11 | 133231.61 | 2593.11 | 8.9203 | [5 empty] | 95.9678
07.10.2007 05:00 | 3600 | 2 | 757.39 | GGB | 766.667 | 772.406 | 767.033 | 270.54 | GGB | 10980.2 | GGB | 9.93 | GGB | 999.34 | GGB | 60.69 | GGB | 166376.57 | GGB | 134279.33 | GGB | 0 | 0 | 2585 | 3600 | 2570.02 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 29567.79 | GGB | 29568.2 | 2570.02 | 2570.02 |  |  |  | 1 | 1 |  |  |  |  | 134279.33 | 2570.02 | 134279.33 | 2570.02 | 8.6993 | [5 empty] | 95.8613
07.10.2007 06:00 | 3600 | 2 | 757.38 | GGB | 766.667 | 771.211 | 767.033 | 269.41 | GGB | 10994.1 | GGB | 9.93 | GGB | 998.91 | GGB | 60.86 | GGB | 165192.61 | GGB | 133199.75 | GGB | 0 | 0 | 2593 | 3600 | 2578.15 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 29606.53 | GGB | 29606.94 | 2578.15 | 2578.15 |  |  |  | 1 | 1 |  |  |  |  | 133199.75 | 2578.15 | 133199.75 | 2578.15 | 8.8645 | [5 empty] | 95.3914
07.10.2007 07:00 | 3600 | 2 | 757.24 | GGB | 765.201 | 771.141 | 765.934 | 268.69 | GGB | 10997.9 | GGB | 9.92 | GGB | 998.73 | GGB | 61.24 | GGB | 164318.94 | GGB | 132322.97 | GGB | 0 | 0 | 2612 | 3600 | 2597.06 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 29645.77 | GGB | 29646.18 | 2597.06 | 2597.06 |  |  |  | 1 | 1 |  |  |  |  | 132322.97 | 2597.06 | 132322.97 | 2597.06 | 8.7577 | [5 empty] | 95.4585
07.10.2007 08:00 | 3600 | 2 | 757.01 | GGB | 765.201 | 771.117 | 765.934 | 269.15 | GGB | 10974.9 | GGB | 9.92 | GGB | 998.53 | GGB | 60.95 | GGB | 164764.57 | GGB | 132767.79 | GGB | 0 | 0 | 2604 | 3600 | 2588.5 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 29685.38 | GGB | 29685.79 | 2588.5 | 2588.5 |  |  |  | 1 | 1 |  |  |  |  | 132767.79 | 2588.5 | 132767.79 | 2588.5 | 8.6763 | [5 empty] | 95.4637
07.10.2007 09:00 | 3600 | 2 | 757.71 | GGB | 765.201 | 771.141 | 766.3 | 268.58 | GGB | 11002.5 | GGB | 9.93 | GGB | 998.98 | GGB | 60.96 | GGB | 164517 | GGB | 132624.34 | GGB | 0 | 0 | 2587 | 3600 | 2571.62 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 29723.98 | GGB | 29724.39 | 2571.62 | 2571.62 |  |  |  | 1 | 1 |  |  |  |  | 132624.34 | 2571.62 | 132624.34 | 2571.62 | 8.8357 | [5 empty] | 94.7387
07.10.2007 10:00 | 3600 | 2 | 757.29 | GGB | 766.3 | 772.5 | 766.667 | 268.29 | GGB | 10996.5 | GGB | 9.93 | GGB | 999.15 | GGB | 61.35 | GGB | 164123.08 | GGB | 132177.14 | GGB | 0 | 0 | 2611 | 3600 | 2595.41 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 29763.61 | GGB | 29764.02 | 2595.41 | 2595.41 |  |  |  | 1 | 1 |  |  |  |  | 132177.14 | 2595.41 | 132177.14 | 2595.41 | 8.6564 | [5 empty] | 95.2927
07.10.2007 11:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 771.539 | 766.667 | 269.51 | GGB | 10958.8 | GGB | 9.92 | GGB | 998.86 | GGB | 61.09 | GGB | 164992.34 | GGB | 132939.92 | GGB | 0 | 0 | 2608 | 3600 | 2593.09 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 29802.63 | GGB | 29803.04 | 2593.09 | 2593.09 |  |  |  | 1 | 1 |  |  |  |  | 132939.92 | 2593.09 | 132939.92 | 2593.09 | 8.8346 | [5 empty] | 95.757
07.10.2007 12:00 | 3600 | 2 | 757.79 | GGB | 766.667 | 772.57 | 766.667 | 269.52 | GGB | 10943.6 | GGB | 9.93 | GGB | 998.41 | GGB | 60.91 | GGB | 164854.8 | GGB | 132842.91 | GGB | 0 | 0 | 2548 | 3600 | 2532.31 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 29841.7 | GGB | 29842.12 | 2532.31 | 2532.31 |  |  |  | 1 | 1 |  |  |  |  | 132842.91 | 2532.31 | 132842.91 | 2532.31 | 8.608 | [5 empty] | 93.4443
07.10.2007 13:00 | 3600 | 2 | 757.86 | GGB | 766.3 | 771.164 | 766.3 | 267.69 | GGB | 10957.8 | GGB | 9.93 | GGB | 997.75 | GGB | 61.61 | GGB | 163038.14 | GGB | 131017.62 | GGB | 0 | 0 | 2563 | 3600 | 2547.22 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 29880.78 | GGB | 29881.2 | 2547.22 | 2547.22 |  |  |  | 1 | 1 |  |  |  |  | 131017.62 | 2547.22 | 131017.62 | 2547.22 | 8.5397 | [5 empty] | 92.703
07.10.2007 14:00 | 3600 | 2 | 757.51 | GGB | 767.766 | 772.125 | 767.766 | 267.82 | GGB | 10964.2 | GGB | 9.93 | GGB | 997.82 | GGB | 61.76 | GGB | 163199.89 | GGB | 131096.87 | GGB | 0 | 0 | 2587 | 3600 | 2571.71 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 29919.74 | GGB | 29920.16 | 2571.71 | 2571.71 |  |  |  | 1 | 1 |  |  |  |  | 131096.87 | 2571.71 | 131096.87 | 2571.71 | 8.6536 | [5 empty] | 93.6509
07.10.2007 15:00 | 3600 | 2 | 757.46 | GGB | 767.766 | 772.031 | 767.766 | 267.36 | GGB | 10943.9 | GGB | 9.92 | GGB | 997.98 | GGB | 62.01 | GGB | 162982.03 | GGB | 130846.1 | GGB | 0 | 0 | 2577 | 3600 | 2562.07 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 29959.04 | GGB | 29959.46 | 2562.07 | 2562.07 |  |  |  | 1 | 1 |  |  |  |  | 130846.1 | 2562.07 | 130846.1 | 2562.07 | 8.5302 | [5 empty] | 93.1214
07.10.2007 16:00 | 3600 | 2 | 757.39 | GGB | 766.3 | 772.031 | 766.667 | 267.49 | GGB | 10947.8 | GGB | 9.93 | GGB | 998.07 | GGB | 61.9 | GGB | 163319.83 | GGB | 131169.53 | GGB | 0 | 0 | 2585 | 3600 | 2569.67 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 29997.84 | GGB | 29998.26 | 2569.67 | 2569.67 |  |  |  | 1 | 1 |  |  |  |  | 131169.53 | 2569.67 | 131169.53 | 2569.67 | 8.6872 | [5 empty] | 93.6284
07.10.2007 17:00 | 3600 | 2 | 757.04 | GGB | 766.3 | 772.031 | 766.667 | 268.23 | GGB | 10927.6 | GGB | 9.92 | GGB | 997.84 | GGB | 61.72 | GGB | 164047.15 | GGB | 131795.42 | GGB | 0 | 0 | 2595 | 3600 | 2579.92 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 30037.22 | GGB | 30037.64 | 2579.92 | 2579.92 |  |  |  | 1 | 1 |  |  |  |  | 131795.42 | 2579.92 | 131795.42 | 2579.92 | 8.6344 | [5 empty] | 94.4505
07.10.2007 18:00 | 3600 | 2 | 757.45 | GGB | 766.3 | 772.477 | 766.667 | 269.32 | GGB | 10904.7 | GGB | 9.92 | GGB | 997.9 | GGB | 61.29 | GGB | 164998.95 | GGB | 132738.68 | GGB | 0 | 0 | 2560 | 3600 | 2545.17 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 30075.98 | GGB | 30076.4 | 2545.17 | 2545.17 |  |  |  | 1 | 1 |  |  |  |  | 132738.68 | 2545.17 | 132738.68 | 2545.17 | 8.7163 | [5 empty] | 93.8451
07.10.2007 19:00 | 3600 | 2 | 757.59 | GGB | 765.201 | 769.453 | 765.201 | 268.12 | GGB | 10937.4 | GGB | 9.93 | GGB | 997.7 | GGB | 61.61 | GGB | 163542.1 | GGB | 131416.43 | GGB | 0 | 0 | 2570 | 3600 | 2555.15 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 30114.71 | GGB | 30115.14 | 2555.15 | 2555.15 |  |  |  | 1 | 1 |  |  |  |  | 131416.43 | 2555.15 | 131416.43 | 2555.15 | 8.6678 | [5 empty] | 93.2746
07.10.2007 20:00 | 3600 | 2 | 757.38 | GGB | 765.201 | 771.164 | 766.667 | 268.33 | GGB | 10944.8 | GGB | 9.92 | GGB | 997.84 | GGB | 61.81 | GGB | 163384.75 | GGB | 131228.46 | GGB | 0 | 0 | 2598 | 3600 | 2582.9 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 30154 | GGB | 30154.43 | 2582.9 | 2582.9 |  |  |  | 1 | 1 |  |  |  |  | 131228.46 | 2582.9 | 131228.46 | 2582.9 | 8.6269 | [5 empty] | 94.1528
07.10.2007 21:00 | 3600 | 2 | 757.27 | GGB | 765.934 | 772.195 | 766.667 | 269.05 | GGB | 10960.2 | GGB | 9.92 | GGB | 997.74 | GGB | 61.6 | GGB | 163871.1 | GGB | 131688.86 | GGB | 0 | 0 | 2606 | 3600 | 2591.16 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 30192.66 | GGB | 30193.09 | 2591.16 | 2591.16 |  |  |  | 1 | 1 |  |  |  |  | 131688.86 | 2591.16 | 131688.86 | 2591.16 | 8.8264 | [5 empty] | 94.7853
07.10.2007 22:00 | 3600 | 2 | 757.36 | GGB | 767.033 | 771.164 | 767.766 | 269.33 | GGB | 10974.9 | GGB | 9.92 | GGB | 998.07 | GGB | 61.6 | GGB | 164204.5 | GGB | 131998.19 | GGB | 0 | 0 | 2614 | 3600 | 2598.65 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 30231.75 | GGB | 30232.18 | 2598.65 | 2598.65 |  |  |  | 1 | 1 |  |  |  |  | 131998.19 | 2598.65 | 131998.19 | 2598.65 | 8.7751 | [5 empty] | 95.2825
07.10.2007 23:00 | 3600 | 2 | 757.03 | GGB | 765.934 | 771.141 | 766.3 | 268.99 | GGB | 10991.4 | GGB | 9.92 | GGB | 998.07 | GGB | 61.4 | GGB | 164423.47 | GGB | 132256.94 | GGB | 0 | 0 | 2630 | 3600 | 2614.53 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 30270.24 | GGB | 30270.66 | 2614.53 | 2614.53 |  |  |  | 1 | 1 |  |  |  |  | 132256.94 | 2614.53 | 132256.94 | 2614.53 | 8.9862 | [5 empty] | 96.0527
07.10.2007 24:00 | 3600 | 2 | 757.31 | GGB | 767.033 | 771.047 | 766.667 | 269.93 | GGB | 11005.3 | GGB | 9.92 | GGB | 998.29 | GGB | 61.45 | GGB | 164686.45 | GGB | 132477.16 | GGB | 0 | 0 | 2631 | 3600 | 2615.72 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 30310.09 | GGB | 30310.51 | 2615.72 | 2615.72 |  |  |  | 1 | 1 |  |  |  |  | 132477.16 | 2615.72 | 132477.16 | 2615.72 | 8.6957 | [5 empty] | 96.2564
08.10.2007 01:00 | 3600 | 2 | 757 | GGB | 767.033 | 772.172 | 767.766 | 270.42 | GGB | 11017.6 | GGB | 9.92 | GGB | 998.21 | GGB | 61.22 | GGB | 165164 | GGB | 132938.94 | GGB | 0 | 0 | 2649 | 3600 | 2634.03 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 30349.49 | GGB | 30349.91 | 2634.03 | 2634.03 |  |  |  | 1 | 1 |  |  |  |  | 132938.94 | 2634.03 | 132938.94 | 2634.03 | 8.8874 | [5 empty] | 97.2681
08.10.2007 02:00 | 3600 | 2 | 757.32 | GGB | 765.934 | 770.906 | 766.667 | 270.62 | GGB | 11037.7 | GGB | 9.92 | GGB | 998.34 | GGB | 61.09 | GGB | 165415.97 | GGB | 133214.13 | GGB | 0 | 0 | 2646 | 3600 | 2630.46 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 30388.49 | GGB | 30388.92 | 2630.46 | 2630.46 |  |  |  | 1 | 1 |  |  |  |  | 133214.13 | 2630.46 | 133214.13 | 2630.46 | 8.9827 | [5 empty] | 97.3373
08.10.2007 03:00 | 3600 | 2 | 757.09 | GGB | 764.835 | 769.852 | 765.201 | 270.84 | GGB | 11047.8 | GGB | 9.92 | GGB | 997.76 | GGB | 60.81 | GGB | 165521.61 | GGB | 133331.97 | GGB | 0 | 0 | 2659 | 3600 | 2643.92 | GGB | 100 | GGB | 42.46 | GGB | 42.46 | GGB | 30430.95 | GGB | 30431.38 | 2643.92 | 2643.92 |  |  |  | 1 | 1 |  |  |  |  | 133331.97 | 2643.92 | 133331.97 | 2643.92 | 8.3024 | [5 empty] | 97.922
08.10.2007 04:00 | 3600 | 2 | 749.78 | GNB | 748.718 | 753.234 | 748.352 | 258.09 | GGB | 10302.5 | GGB | 9.87 | GGB | 997.5 | GGB | 63.28 | GGB | 150514.1 | GGB | 120319.5 | GGB | 0 | 0 | 2760 | 3600 | 2745.03 | GGB | 100 | GGB | 43.08 | GGB | 43.08 | GGB | 30474.03 | GGB | 30474.46 | 2745.03 | 2745.03 |  |  |  | 0 | 1 | [14 empty] | 91.7446
08.10.2007 05:00 | 0 | 1 | 374.63 | XNN | 259.341 | 256.758 | 253.846 | 16.87 | XNN | 2076.91 | XNN | 18.38 | XNN | 997.32 | XNN | 69.18 | XNN | 7897.19 | XNN | 6203.05 | XNN | 0 | 0 | 1141 | 3600 | 1126.45 | GGB | 100 | XNN | 3.59 | XNN | 3.59 | XNN | 0 | UUU | 30474.46 | 1126.45 | 1126.45 |  |  |  | 0 | 0 | [14 empty] | 1.941
08.10.2007 06:00 | 0 | 1 | 206.14 | XNN | 209.157 | 211.688 | 210.989 | 3.81 | XNN | 2758.67 | XNN | 19.98 | XNN | 997.09 | XNN | 42.17 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 183 | 3600 | 169.58 | GGB | 100 | XNN | 3.01 | XNN | 3.01 | XNN | 0 | UUU | 30474.46 | 169.58 | 169.58 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 07:00 | 0 | 1 | 160.33 | XNN | 184.615 | 187.664 | 190.11 | 3.8 | XNN | 2266.96 | XNN | 19.98 | XNN | 996.51 | XNN | 41.78 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 11 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 08:00 | 0 | 1 | 135.25 | XNN | 162.637 | 164.789 | 165.934 | 3.81 | XNN | 117.57 | XNN | 6.09 | XNN | 996.21 | XNN | 40.36 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 09:00 | 0 | 1 | 119.73 | XNN | 145.788 | 147.469 | 147.619 | 3.82 | XNN | 8.52 | XNN | 0 | XNN | 996.14 | XNN | 39.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -4 | 3600 | 0 | GGB | 100 | XNN | 4.42 | XNN | 4.42 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 10:00 | 0 | 1 | 109.18 | XNN | 135.897 | 136.711 | 132.967 | 3.85 | XNN | 8.71 | XNN | 0 | XNN | 996 | XNN | 26.31 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 5.63 | XNN | 5.63 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 11:00 | 0 | 1 | 101.27 | XNN | 127.473 | 126.938 | 121.978 | 3.79 | XNN | 8.78 | XNN | 0 | XNN | 996.09 | XNN | 15.81 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 52 | 3600 | 39.09 | GGB | 100 | XNN | 5.66 | XNN | 5.66 | XNN | 0 | UUU | 30474.46 | 39.09 | 39.09 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 12:00 | 0 | 1 | 94.48 | XNN | 118.681 | 119.578 | 110.989 | 3.77 | XNN | 8.82 | XNN | 0 | XNN | 995.87 | XNN | 13.98 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 39 | 3600 | 25.92 | GGB | 100 | XNN | 4.89 | XNN | 4.89 | XNN | 0 | UUU | 30474.46 | 25.92 | 25.92 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 13:00 | 0 | 1 | 88.53 | XNN | 113.919 | 114.258 | 98.5348 | 3.76 | XNN | 8.83 | XNN | 0 | XNN | 995.64 | XNN | 13.56 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 22 | 3600 | 8.97 | GGB | 100 | XNN | 3.63 | XNN | 3.63 | XNN | 0 | UUU | 30474.46 | 8.97 | 8.97 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 14:00 | 0 | 1 | 83.08 | XNN | 109.157 | 110.789 | 90.1099 | 3.77 | XNN | 8.79 | XNN | 0 | XNN | 995.38 | XNN | 13.41 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 16 | 3600 | 3.18 | GGB | 100 | XNN | 2.73 | XNN | 2.73 | XNN | 0 | UUU | 30474.46 | 3.18 | 3.18 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 15:00 | 0 | 1 | 77.56 | XNN | 105.494 | 107.695 | 83.8828 | 3.81 | XNN | 8.85 | XNN | 0 | XNN | 994.95 | XNN | 14.12 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 12 | 3600 | 0 | GGB | 100 | XNN | 2.41 | XNN | 2.41 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 16:00 | 0 | 1 | 72.85 | XNN | 104.029 | 104.555 | 78.022 | 3.82 | XNN | 8.79 | XNN | 0 | XNN | 994.61 | XNN | 14.54 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 11 | 3600 | 0 | GGB | 100 | XNN | 2.41 | XNN | 2.41 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 17:00 | 0 | 1 | 69.06 | XNN | 101.831 | 102.398 | 72.8938 | 3.79 | XNN | 8.86 | XNN | 0 | XNN | 994.73 | XNN | 13.3 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 13 | 3600 | 0 | GGB | 100 | XNN | 2.42 | XNN | 2.42 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 18:00 | 0 | 1 | 66.3 | XNN | 99.2674 | 100.383 | 68.1318 | 3.74 | XNN | 8.88 | XNN | 0 | XNN | 995.37 | XNN | 12.37 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 10 | 3600 | 0 | GGB | 100 | XNN | 2.39 | XNN | 2.39 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 19:00 | 0 | 1 | 63.46 | XNN | 98.1685 | 99.375 | 65.5677 | 3.76 | XNN | 8.88 | XNN | 0 | XNN | 996.03 | XNN | 12.28 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 11 | 3600 | 0 | GGB | 100 | XNN | 2.25 | XNN | 2.25 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 20:00 | 0 | 1 | 61.3 | XNN | 95.6044 | 97.2188 | 61.9047 | 3.74 | XNN | 8.89 | XNN | 0 | XNN | 996.55 | XNN | 11.21 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 8 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 21:00 | 0 | 1 | 59.33 | XNN | 94.5055 | 95.0391 | 59.7069 | 3.74 | XNN | 8.9 | XNN | 0 | XNN | 997.43 | XNN | 11.07 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 22:00 | 0 | 1 | 57.2 | XNN | 91.9414 | 92.9297 | 58.2417 | 3.74 | XNN | 8.89 | XNN | 0 | XNN | 997.87 | XNN | 11.04 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 23:00 | 0 | 1 | 55.66 | XNN | 90.8425 | 90.7734 | 56.0439 | 3.73 | XNN | 8.87 | XNN | 0 | XNN | 998.41 | XNN | 11.01 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
08.10.2007 24:00 | 0 | 1 | 54.26 | XNN | 88.2784 | 89.7188 | 54.5787 | 3.73 | XNN | 8.86 | XNN | 0 | XNN | 998.72 | XNN | 10.8 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 01:00 | 0 | 1 | 52.74 | XNN | 87.1795 | 87.6563 | 53.4798 | 3.73 | XNN | 8.89 | XNN | 0 | XNN | 999.64 | XNN | 10.5 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 02:00 | 0 | 1 | 51.43 | XNN | 84.6154 | 85.6406 | 52.3809 | 3.74 | XNN | 8.89 | XNN | 0 | XNN | 999.84 | XNN | 10.48 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 03:00 | 0 | 1 | 50.21 | XNN | 83.5165 | 84.4922 | 50.9157 | 3.74 | XNN | 8.91 | XNN | 0 | XNN | 999.92 | XNN | 10.14 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 04:00 | 0 | 1 | 49.11 | XNN | 80.9524 | 82.4063 | 48.7179 | 3.74 | XNN | 8.91 | XNN | 0 | XNN | 1000.35 | XNN | 9.86 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 05:00 | 0 | 1 | 48.26 | XNN | 79.8535 | 80.3203 | 47.2527 | 3.75 | XNN | 8.91 | XNN | 0 | XNN | 1000.85 | XNN | 9.64 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 06:00 | 0 | 1 | 47.28 | XNN | 78.3883 | 79.3125 | 47.2527 | 3.74 | XNN | 8.92 | XNN | 0 | XNN | 1000.85 | XNN | 9.07 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 07:00 | 0 | 1 | 46.07 | XNN | 76.1905 | 77.0391 | 46.1538 | 3.74 | XNN | 8.88 | XNN | 0 | XNN | 1001.17 | XNN | 8.73 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 0 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 08:00 | 0 | 1 | 44.93 | XNN | 74.7253 | 76.0313 | 45.0549 | 3.74 | XNN | 8.9 | XNN | 0 | XNN | 1001.69 | XNN | 8.5 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -1 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 09:00 | 0 | 1 | 43.91 | XNN | 73.6264 | 74.0156 | 43.5897 | 3.76 | XNN | 8.89 | XNN | 0 | XNN | 1002.04 | XNN | 9.08 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -1 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 10:00 | 0 | 1 | 42.77 | XNN | 71.0622 | 72.9375 | 42.4908 | 3.81 | XNN | 8.89 | XNN | 0 | XNN | 1002.7 | XNN | 10.27 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 11:00 | 0 | 1 | 41.93 | XNN | 69.9633 | 71.8359 | 41.7582 | 3.89 | XNN | 8.89 | XNN | 0 | XNN | 1002.78 | XNN | 10.9 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 12:00 | 0 | 1 | 41.25 | XNN | 68.8644 | 69.7266 | 40.6593 | 3.91 | XNN | 8.88 | XNN | 0 | XNN | 1002.77 | XNN | 11.4 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 13:00 | 0 | 1 | 40.77 | XNN | 67.3992 | 68.625 | 40.6593 | 4.02 | XNN | 8.86 | XNN | 0 | XNN | 1002.82 | XNN | 12.25 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 14:00 | 0 | 1 | 40.29 | XNN | 66.3003 | 67.6172 | 40.6593 | 4.07 | XNN | 8.87 | XNN | 0 | XNN | 1002.26 | XNN | 12.87 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 15:00 | 0 | 1 | 39.8 | XNN | 65.2014 | 65.5547 | 39.9267 | 4.07 | XNN | 8.89 | XNN | 0 | XNN | 1002.44 | XNN | 12.99 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 16:00 | 0 | 1 | 39.24 | XNN | 63.7362 | 64.5234 | 38.8278 | 4.06 | XNN | 8.82 | XNN | 0 | XNN | 1002.94 | XNN | 13.59 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 17:00 | 0 | 1 | 38.54 | XNN | 62.6373 | 63.375 | 38.8278 | 4.06 | XNN | 8.85 | XNN | 0 | XNN | 1003.19 | XNN | 14.04 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 18:00 | 0 | 1 | 38.03 | XNN | 61.5384 | 62.3438 | 38.0952 | 4.05 | XNN | 8.83 | XNN | 0 | XNN | 1003.48 | XNN | 14.92 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 19:00 | 0 | 1 | 37.48 | XNN | 60.0732 | 61.2891 | 38.0952 | 4.02 | XNN | 8.8 | XNN | 0 | XNN | 1004.05 | XNN | 14.18 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 20:00 | 0 | 1 | 36.94 | XNN | 57.8754 | 59.2031 | 36.9963 | 3.97 | XNN | 8.8 | XNN | 0 | XNN | 1004.93 | XNN | 12.54 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 21:00 | 0 | 1 | 36.4 | XNN | 57.8754 | 58.1953 | 35.8974 | 3.92 | XNN | 8.86 | XNN | 0 | XNN | 1005.56 | XNN | 11.28 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 22:00 | 0 | 1 | 35.41 | XNN | 56.4102 | 57.1875 | 35.8974 | 3.91 | XNN | 8.86 | XNN | 0 | XNN | 1006.32 | XNN | 10.44 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 23:00 | 0 | 1 | 34.73 | XNN | 55.3113 | 56.0859 | 34.4322 | 3.9 | XNN | 8.88 | XNN | 0 | XNN | 1007.11 | XNN | 9.78 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
09.10.2007 24:00 | 0 | 1 | 34.03 | XNN | 54.2124 | 55.0781 | 33.3333 | 3.89 | XNN | 8.89 | XNN | 0 | XNN | 1007.64 | XNN | 8.9 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 01:00 | 0 | 1 | 33.35 | XNN | 52.7472 | 54.0469 | 33.3333 | 3.87 | XNN | 8.91 | XNN | 0 | XNN | 1008.63 | XNN | 8.26 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 02:00 | 0 | 1 | 32.57 | XNN | 51.6483 | 52.9922 | 32.2344 | 3.84 | XNN | 8.9 | XNN | 0 | XNN | 1009.2 | XNN | 7.38 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 03:00 | 0 | 1 | 31.13 | XNN | 50.5494 | 51.9375 | 31.8681 | 3.8 | XNN | 8.89 | XNN | 0 | XNN | 1009.78 | XNN | 6.29 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 04:00 | 0 | 1 | 30.43 | XNN | 49.0842 | 50.8125 | 30.7692 | 3.78 | XNN | 8.91 | XNN | 0 | XNN | 1010.09 | XNN | 5.4 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 05:00 | 0 | 1 | 29.77 | XNN | 49.0842 | 49.6875 | 29.6703 | 3.79 | XNN | 8.82 | XNN | 0 | XNN | 1010.5 | XNN | 4.89 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 06:00 | 0 | 1 | 28.99 | XNN | 47.9853 | 48.6328 | 29.6703 | 3.79 | XNN | 8.88 | XNN | 0 | XNN | 1010.82 | XNN | 4.48 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 07:00 | 0 | 1 | 27.99 | XNN | 46.8864 | 47.6016 | 28.5714 | 3.78 | XNN | 8.88 | XNN | 0 | XNN | 1011.15 | XNN | 3.94 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 08:00 | 0 | 1 | 27.36 | XNN | 45.4212 | 46.5703 | 27.1062 | 3.78 | XNN | 8.88 | XNN | 0 | XNN | 1011.49 | XNN | 3.47 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 09:00 | 0 | 1 | 26.69 | XNN | 45.4212 | 45.5625 | 27.1062 | 3.78 | XNN | 8.84 | XNN | 0 | XNN | 1011.85 | XNN | 3.7 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 10:00 | 0 | 1 | 26.13 | XNN | 44.3223 | 44.5313 | 26.0073 | 3.82 | XNN | 8.87 | XNN | 0 | XNN | 1012.15 | XNN | 5.02 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 11:00 | 0 | 1 | 25.27 | XNN | 43.5897 | 44.5313 | 26.0073 | 3.91 | XNN | 8.86 | XNN | 0 | XNN | 1011.81 | XNN | 7.37 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 12:00 | 0 | 1 | 24.6 | XNN | 42.4908 | 43.5234 | 24.9084 | 4.03 | XNN | 8.85 | XNN | 0 | XNN | 1011.2 | XNN | 9.69 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 13:00 | 0 | 1 | 24.45 | XNN | 41.3919 | 42.4453 | 24.9084 | 4.1 | XNN | 8.85 | XNN | 0 | XNN | 1010.44 | XNN | 11.25 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 14:00 | 0 | 1 | 24.25 | XNN | 41.3919 | 42.4453 | 24.9084 | 4.14 | XNN | 8.83 | XNN | 0 | XNN | 1009.43 | XNN | 12.24 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 15:00 | 0 | 1 | 24 | XNN | 39.9267 | 41.2031 | 24.9084 | 4.16 | XNN | 8.87 | XNN | 0 | XNN | 1008.11 | XNN | 13.37 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 16:00 | 0 | 1 | 24.01 | XNN | 39.9267 | 41.2031 | 24.9084 | 4.16 | XNN | 8.83 | XNN | 0 | XNN | 1006.9 | XNN | 13.48 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 17:00 | 0 | 1 | 23.91 | XNN | 38.8278 | 40.1953 | 24.9084 | 4.15 | XNN | 8.84 | XNN | 0 | XNN | 1006.47 | XNN | 12.84 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 18:00 | 0 | 1 | 23.55 | XNN | 37.7289 | 39.1172 | 24.9084 | 4.14 | XNN | 8.82 | XNN | 0 | XNN | 1006.1 | XNN | 12.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 19:00 | 0 | 1 | 23.48 | XNN | 36.2637 | 38.0156 | 24.9084 | 4.13 | XNN | 8.81 | XNN | 0 | XNN | 1005.8 | XNN | 14.58 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 20:00 | 0 | 1 | 41.86 | XNN | 80.2198 | 76.6172 | 70.3297 | 4.12 | XNN | 8.84 | XNN | 0 | XNN | 1005.99 | XNN | 14.41 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 21:00 | 0 | 1 | 94.77 | XNN | 130.403 | 127.57 | 121.612 | 4.12 | XNN | 8.9 | XNN | 0 | XNN | 1005.96 | XNN | 13.27 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 22:00 | 0 | 1 | 168.11 | XNN | 237.729 | 232.453 | 190.11 | 4.14 | XNN | 8.88 | XNN | 0 | XNN | 1005.8 | XNN | 14.83 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 23:00 | 0 | 1 | 214.93 | XNN | 262.271 | 257.672 | 200 | 4.15 | XNN | 8.89 | XNN | 0 | XNN | 1005.91 | XNN | 17.25 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0.01 | XNN | 0.01 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
10.10.2007 24:00 | 0 | 1 | 218.77 | XNN | 267.033 | 263.25 | 200 | 4.16 | XNN | 8.9 | XNN | 0 | XNN | 1005.58 | XNN | 19.76 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 01:00 | 0 | 1 | 221.37 | XNN | 270.696 | 266.391 | 203.663 | 4.17 | XNN | 8.91 | XNN | 0 | XNN | 1005.28 | XNN | 20.37 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 02:00 | 0 | 1 | 222.04 | XNN | 271.795 | 268.5 | 205.861 | 4.17 | XNN | 8.9 | XNN | 0 | XNN | 1004.89 | XNN | 20.19 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 03:00 | 0 | 1 | 211.77 | XNN | 267.033 | 230.648 | 168.864 | 7.9 | XNN | 8.89 | XNN | 0 | XNN | 1004.92 | XNN | 23.53 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 04:00 | 0 | 1 | 157.74 | XNN | 149.817 | 147.539 | 147.985 | 22.36 | XNN | 8.56 | XNN | 0 | XNN | 1004.62 | XNN | 52.7 | XNN | 429.09 | XNN | 356.68 | XNN | 0 | 0 | -6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 05:00 | 0 | 1 | 102.6 | XNN | 108.791 | 110.086 | 108.425 | 105.99 | XNN | 24.32 | XNN | 0.02 | XNN | 1004.45 | XNN | 36.36 | XNN | 43992.16 | XNN | 38493.99 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 06:00 | 0 | 1 | 116.94 | XNN | 117.582 | 117.609 | 116.85 | 160.38 | XNN | 1555.3 | XNN | 2.04 | XNN | 1004.63 | XNN | 18.98 | XNN | 83314.6 | XNN | 77254.49 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 07:00 | 0 | 1 | 124 | XNN | 127.106 | 128.32 | 127.106 | 192.02 | XNN | 1661.39 | XNN | 1.98 | XNN | 1005.08 | XNN | 15.78 | XNN | 98682.03 | XNN | 92559.14 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 08:00 | 0 | 1 | 134.5 | XNN | 134.432 | 135.984 | 134.432 | 226.28 | XNN | 1659.1 | XNN | 1.81 | XNN | 1005.64 | XNN | 11.43 | XNN | 118759.45 | XNN | 113160.06 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 09:00 | 0 | 1 | 138.31 | XNN | 136.996 | 138.094 | 136.996 | 231.03 | XNN | 1641.43 | XNN | 1.92 | XNN | 1006.1 | XNN | 8.96 | XNN | 129728.72 | XNN | 124752.2 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 10:00 | 0 | 1 | 139.7 | XNN | 136.996 | 138.094 | 136.996 | 232.75 | XNN | 4527.06 | XNN | 5.28 | XNN | 1006.6 | XNN | 7.8 | XNN | 136287.83 | XNN | 131666.01 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 11:00 | 0 | 1 | 139.57 | XNN | 138.095 | 139.266 | 138.095 | 232.08 | XNN | 7545.88 | XNN | 8.65 | XNN | 1007.05 | XNN | 7.5 | XNN | 137563.13 | XNN | 133100.55 | XNN | 0 | 0 | -7 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
11.10.2007 12:00 | 0 | 1 | 415.95 | XNN | 727.472 | 730.336 | 726.007 | 223.09 | XNN | 7664.42 | XNN | 9.07 | XNN | 1007.17 | XNN | 27.63 | XNN | 122972.65 | XNN | 111025.77 | XNN | 0 | 0 | 1572 | 3600 | 1557.71 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 30474.46 | 1557.71 | 1557.71 |  |  |  | 0 | 0 | [14 empty] | 48.0405
11.10.2007 13:00 | 3600 | 2 | 736.73 | GNB | 751.648 | 753.539 | 750.549 | 237.46 | GNB | 8802.92 | GGB | 9.81 | GGB | 1007.06 | GGB | 70.38 | GGB | 127716.2 | GGB | 100942.17 | GGB | 0 | 0 | 2880 | 3600 | 2864.62 | GGB | 100 | GGB | 0 | GGB | 0 | GGB | 30474.03 | GGB | 30474.46 | 2864.62 | 2864.62 |  |  |  | 0 | 1 | [14 empty] | 80.3225
11.10.2007 14:00 | 3600 | 2 | 747.26 | GNB | 758.974 | 761.977 | 758.974 | 253.5 | GGB | 9628.95 | GGB | 9.86 | GGB | 1006.19 | GGB | 67.11 | GGB | 151307.44 | GGB | 120635.64 | GGB | 0 | 0 | 2836 | 3600 | 2820.98 | GGB | 100 | GGB | 4.04 | GGB | 4.04 | GGB | 30478.07 | GGB | 30478.5 | 2820.98 | 2820.98 |  |  |  | 0 | 1 | [14 empty] | 94.5308
11.10.2007 15:00 | 3600 | 2 | 751.4 | GNB | 755.678 | 759.82 | 754.212 | 259.68 | GGB | 10017.9 | GGB | 9.86 | GGB | 1005.7 | GGB | 65.26 | GGB | 159744.83 | GGB | 127997.66 | GGB | 0 | 0 | 2664 | 3600 | 2648.67 | GGB | 100 | GGB | 1.11 | GGB | 1.11 | GGB | 30479.18 | GGB | 30479.61 | 2648.67 | 2648.67 |  |  |  | 0 | 1 | [14 empty] | 94.1732
11.10.2007 16:00 | 3600 | 2 | 751.45 | GNB | 754.212 | 758.203 | 754.212 | 259.53 | GGB | 10188.3 | GGB | 9.85 | GGB | 1005.33 | GGB | 65.16 | GGB | 160754.94 | GGB | 128798.67 | GGB | 0 | 0 | 2746 | 3600 | 2730.48 | GGB | 100 | GGB | 9.97 | GGB | 9.97 | GGB | 30489.15 | GGB | 30489.58 | 2730.48 | 2730.48 |  |  |  | 0 | 1 | [14 empty] | 97.6895
11.10.2007 17:00 | 3600 | 2 | 754.4 | GNB | 768.864 | 773.367 | 768.864 | 261.92 | GGB | 10455.5 | GGB | 9.9 | GGB | 1004.87 | GGB | 63.11 | GGB | 166386.47 | GGB | 134058.18 | GGB | 0 | 0 | 2664 | 3600 | 2649.06 | GGB | 100 | GGB | 44.06 | GGB | 44.06 | GGB | 30533.21 | GGB | 30533.64 | 2649.06 | 2649.06 |  |  |  | 0 | 1 | [14 empty] | 98.6467
11.10.2007 18:00 | 3600 | 2 | 756.63 | GGB | 759.341 | 764.555 | 759.341 | 261.4 | GGB | 10471.3 | GGB | 9.92 | GGB | 1004.27 | GGB | 63.39 | GGB | 165486.4 | GGB | 133143.24 | GGB | 0 | 0 | 2509 | 3600 | 2494.09 | GGB | 100 | GGB | 44.87 | GGB | 44.87 | GGB | 30578.08 | GGB | 30578.51 | 2494.09 | 2494.09 |  |  |  | 0 | 1 | [14 empty] | 92.242
11.10.2007 19:00 | 3600 | 2 | 753.22 | GNB | 759.341 | 764.719 | 760.44 | 261.35 | GGB | 10459.6 | GGB | 9.87 | GGB | 1003.87 | GGB | 62.88 | GGB | 165572.22 | GGB | 133363.35 | GGB | 0 | 0 | 2674 | 3600 | 2658.46 | GGB | 100 | GGB | 45.48 | GGB | 45.48 | GGB | 30623.56 | GGB | 30623.99 | 2658.46 | 2658.46 |  |  |  | 0 | 1 | [14 empty] | 98.4836
11.10.2007 20:00 | 3600 | 2 | 752.77 | GNB | 759.341 | 763.617 | 759.341 | 260.64 | GGB | 10503.7 | GGB | 9.86 | GGB | 1003.59 | GGB | 62.9 | GGB | 165389.57 | GGB | 133170.91 | GGB | 0 | 0 | 2709 | 3600 | 2693.33 | GGB | 100 | GGB | 45.44 | GGB | 45.44 | GGB | 30669 | GGB | 30669.43 | 2693.33 | 2693.33 |  |  |  | 0 | 1 | [14 empty] | 99.6314
11.10.2007 21:00 | 3600 | 2 | 752.51 | GNB | 760.44 | 765.656 | 760.44 | 262.53 | GGB | 10471.3 | GGB | 9.86 | GGB | 1002.7 | GGB | 62.05 | GGB | 167172.11 | GGB | 134828.43 | GGB | 0 | 0 | 2695 | 3600 | 2679.17 | GGB | 100 | GGB | 44.12 | GGB | 44.12 | GGB | 30713.11 | GGB | 30713.55 | 2679.17 | 2679.17 |  |  |  | 0 | 1 | [14 empty] | 100.3412
11.10.2007 22:00 | 3600 | 2 | 752.78 | GNB | 760.44 | 765.609 | 761.538 | 261.27 | GGB | 10498.1 | GGB | 9.87 | GGB | 1001.66 | GGB | 62.02 | GGB | 165913.33 | GGB | 133684.7 | GGB | 0 | 0 | 2678 | 3600 | 2662.67 | GGB | 100 | GGB | 43.78 | GGB | 43.78 | GGB | 30756.89 | GGB | 30757.33 | 2662.67 | 2662.67 |  |  |  | 0 | 1 | [14 empty] | 98.8773
11.10.2007 23:00 | 3600 | 2 | 752.76 | GNB | 760.44 | 765.609 | 760.44 | 260.59 | GGB | 10481.1 | GGB | 9.87 | GGB | 1000.85 | GGB | 62.15 | GGB | 165119.98 | GGB | 132889.24 | GGB | 0 | 0 | 2676 | 3600 | 2661.05 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 30796.89 | GGB | 30797.33 | 2661.05 | 2661.05 |  |  |  | 0 | 1 | [14 empty] | 98.2291
11.10.2007 24:00 | 3600 | 2 | 752.73 | GNB | 759.341 | 764.531 | 760.44 | 260.02 | GGB | 10464.7 | GGB | 9.87 | GGB | 999.79 | GGB | 61.82 | GGB | 164331.04 | GGB | 132240.8 | GGB | 0 | 0 | 2674 | 3600 | 2658.71 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 30836.91 | GGB | 30837.35 | 2658.71 | 2658.71 |  |  |  | 0 | 1 | [14 empty] | 97.6639
12.10.2007 01:00 | 3600 | 2 | 752.49 | GNB | 760.44 | 764.742 | 760.44 | 260.15 | GGB | 10422.7 | GGB | 9.86 | GGB | 998.57 | GGB | 61.29 | GGB | 164498.29 | GGB | 132426.38 | GGB | 0 | 0 | 2669 | 3600 | 2653.15 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 30877.1 | GGB | 30877.55 | 2653.15 | 2653.15 |  |  |  | 0 | 1 | [14 empty] | 97.5964
12.10.2007 02:00 | 3600 | 2 | 752.73 | GNB | 759.341 | 763.688 | 759.341 | 258.95 | GGB | 10442.7 | GGB | 9.87 | GGB | 997.85 | GGB | 61.38 | GGB | 162942.42 | GGB | 131044.78 | GGB | 0 | 0 | 2661 | 3600 | 2645.44 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 30916.77 | GGB | 30917.22 | 2645.44 | 2645.44 |  |  |  | 0 | 1 | [14 empty] | 96.2975
12.10.2007 03:00 | 3600 | 2 | 752.22 | GNB | 760.44 | 764.695 | 760.44 | 259.05 | GGB | 10435.7 | GGB | 9.86 | GGB | 996.87 | GGB | 61.76 | GGB | 162956.72 | GGB | 130776.41 | GGB | 0 | 0 | 2677 | 3600 | 2661.45 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 30956.25 | GGB | 30956.69 | 2661.45 | 2661.45 |  |  |  | 0 | 1 | [14 empty] | 96.6819
12.10.2007 04:00 | 3600 | 2 | 752.39 | GNB | 760.44 | 764.695 | 760.44 | 259.09 | GGB | 10445.7 | GGB | 9.87 | GGB | 995.71 | GGB | 61.59 | GGB | 163220.8 | GGB | 130902.41 | GGB | 0 | 0 | 2669 | 3600 | 2653.6 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 30995.76 | GGB | 30996.2 | 2653.6 | 2653.6 |  |  |  | 0 | 1 | [14 empty] | 96.4896
12.10.2007 05:00 | 3600 | 2 | 752.4 | GNB | 760.44 | 764.695 | 760.44 | 258.49 | GGB | 10439.8 | GGB | 9.87 | GGB | 994.5 | GGB | 61.39 | GGB | 162955.62 | GGB | 130611.02 | GGB | 0 | 0 | 2663 | 3600 | 2647.39 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 31035.24 | GGB | 31035.68 | 2647.39 | 2647.39 |  |  |  | 0 | 1 | [14 empty] | 96.0495
12.10.2007 06:00 | 3600 | 2 | 752.09 | GNB | 759.341 | 764.695 | 760.44 | 258.68 | GGB | 10446.3 | GGB | 9.86 | GGB | 993.22 | GGB | 61.14 | GGB | 163523.39 | GGB | 130993.45 | GGB | 0 | 0 | 2678 | 3600 | 2662.47 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 31074.66 | GGB | 31075.1 | 2662.47 | 2662.47 |  |  |  | 0 | 1 | [14 empty] | 96.8795
12.10.2007 07:00 | 3600 | 2 | 752.35 | GNB | 759.341 | 764.719 | 760.44 | 259.15 | GGB | 10487.6 | GGB | 9.86 | GGB | 992.21 | GGB | 60.8 | GGB | 164612.73 | GGB | 131867.3 | GGB | 0 | 0 | 2683 | 3600 | 2667.52 | GGB | 100 | GGB | 42.59 | GGB | 42.59 | GGB | 31117.25 | GGB | 31117.69 | 2667.52 | 2667.52 |  |  |  | 0 | 1 | [14 empty] | 97.7107
12.10.2007 08:00 | 3600 | 2 | 752.27 | GNB | 760.44 | 764.719 | 760.44 | 259.06 | GGB | 10487.5 | GGB | 9.87 | GGB | 991.09 | GGB | 60.76 | GGB | 164682.05 | GGB | 131789.88 | GGB | 0 | 0 | 2685 | 3600 | 2669.4 | GGB | 100 | GGB | 45.08 | GGB | 45.08 | GGB | 31162.33 | GGB | 31162.77 | 2669.4 | 2669.4 |  |  |  | 0 | 1 | [14 empty] | 97.7222
12.10.2007 09:00 | 3600 | 2 | 752.21 | GNB | 760.44 | 764.719 | 760.44 | 258.78 | GGB | 10479.2 | GGB | 9.87 | GGB | 990.43 | GGB | 60.71 | GGB | 164535.7 | GGB | 131602.72 | GGB | 0 | 0 | 2679 | 3207 | 2663.76 | GGB | 100 | GGB | 42.03 | GGB | 42.03 | GGB | 31204.36 | GGB | 31204.8 | 2663.76 | 2663.76 |  |  |  | 0 | 1 | [14 empty] | 97.3772
12.10.2007 10:00 | 3600 | 2 | 752.2 | GNB | 760.44 | 764.719 | 760.44 | 258.44 | GGB | 10462.2 | GGB | 9.87 | GGB | 989.76 | GGB | 60.68 | GGB | 164090.07 | GGB | 131169.45 | GGB | 0 | 0 | 2668 | 3600 | 2653.12 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 31244.79 | GGB | 31245.23 | 2653.12 | 2653.12 |  |  |  | 0 | 1 | [14 empty] | 96.669
12.10.2007 11:00 | 3600 | 2 | 752.13 | GNB | 761.538 | 765.914 | 761.538 | 257.99 | GGB | 10449.9 | GGB | 9.87 | GGB | 988.73 | GGB | 60.94 | GGB | 163867.8 | GGB | 130754.49 | GGB | 0 | 0 | 2663 | 3600 | 2647.8 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 31284.43 | GGB | 31284.88 | 2647.8 | 2647.8 |  |  |  | 0 | 1 | [14 empty] | 96.1699
12.10.2007 12:00 | 3600 | 2 | 753.46 | GNB | 763.004 | 768.094 | 763.004 | 260.8 | GGB | 10654.9 | GGB | 9.87 | GGB | 987.99 | GGB | 60.23 | GGB | 169312.27 | GGB | 135283.87 | GGB | 0 | 0 | 2640 | 3600 | 2624.83 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 31324.6 | GGB | 31325.05 | 2624.83 | 2624.83 |  |  |  | 0 | 1 | [14 empty] | 98.6381
12.10.2007 13:00 | 3600 | 2 | 755.73 | GNB | 763.004 | 768.141 | 763.37 | 261.92 | GGB | 10714.8 | GGB | 9.91 | GGB | 987.26 | GGB | 60.42 | GGB | 171334.69 | GGB | 136722.29 | GGB | 0 | 0 | 2558 | 3600 | 2542.64 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 31364.91 | GGB | 31365.36 | 2542.64 | 2542.64 |  |  |  | 0 | 1 | [14 empty] | 96.5654
12.10.2007 14:00 | 3600 | 2 | 755.72 | GNB | 767.766 | 772.406 | 767.033 | 265.86 | GGB | 10859.7 | GGB | 9.88 | GGB | 986.29 | GGB | 58.85 | GGB | 178703.65 | GGB | 143137.64 | GGB | 0 | 0 | 2583 | 3600 | 2567.25 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 31405.85 | GGB | 31406.3 | 2567.25 | 2567.25 |  |  |  | 0 | 1 | [14 empty] | 102.075
12.10.2007 15:00 | 3600 | 2 | 758.67 | GGB | 768.864 | 774.445 | 769.597 | 265.77 | GGB | 10958 | GGB | 9.93 | GGB | 985.78 | GGB | 59.24 | GGB | 178910.52 | GGB | 143059.17 | GGB | 0 | 0 | 2485 | 3600 | 2470.24 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 31446.82 | GGB | 31447.26 | 2470.24 | 2470.24 |  |  |  | 1 | 1 |  |  |  |  | 143059.17 | 2470.24 | 143059.17 | 2470.24 | 8.6277 | [5 empty] | 98.164
12.10.2007 16:00 | 3600 | 2 | 757.98 | GGB | 766.667 | 771.211 | 767.033 | 264.16 | GGB | 10936.3 | GGB | 9.92 | GGB | 984.67 | GGB | 60.38 | GGB | 177037.74 | GGB | 140921.42 | GGB | 0 | 0 | 2512 | 3600 | 2496.91 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 31487.64 | GGB | 31488.09 | 2496.91 | 2496.91 |  |  |  | 1 | 1 |  |  |  |  | 140921.42 | 2496.91 | 140921.42 | 2496.91 | 8.6179 | [5 empty] | 97.7411
12.10.2007 17:00 | 3600 | 2 | 758.1 | GGB | 766.667 | 771.164 | 767.033 | 263.5 | GGB | 10905.4 | GGB | 9.92 | GGB | 983.56 | GGB | 60.58 | GGB | 176014.43 | GGB | 139863.12 | GGB | 0 | 0 | 2495 | 3600 | 2479.34 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 31528.51 | GGB | 31528.95 | 2479.34 | 2479.34 |  |  |  | 1 | 1 |  |  |  |  | 139863.12 | 2479.34 | 139863.12 | 2479.34 | 8.4867 | [5 empty] | 96.3245
12.10.2007 18:00 | 3600 | 2 | 757.87 | GGB | 767.766 | 772.313 | 767.033 | 262.93 | GGB | 10889.2 | GGB | 9.92 | GGB | 982.71 | GGB | 59.96 | GGB | 175331.12 | GGB | 139460.77 | GGB | 0 | 0 | 2498 | 3600 | 2482.86 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 31570.06 | GGB | 31570.5 | 2482.86 | 2482.86 |  |  |  | 1 | 1 |  |  |  |  | 139460.77 | 2482.86 | 139460.77 | 2482.86 | 8.3336 | [5 empty] | 96.1838
12.10.2007 19:00 | 3600 | 2 | 757.32 | GGB | 766.667 | 771.281 | 765.934 | 262.91 | GGB | 10881.6 | GGB | 9.9 | GGB | 983.1 | GGB | 59.94 | GGB | 175322.32 | GGB | 139516.16 | GGB | 0 | 0 | 2493 | 3600 | 2478.04 | GGB | 100 | GGB | 42.2 | GGB | 42.2 | GGB | 31612.25 | GGB | 31612.7 | 2478.04 | 2478.04 |  |  |  | 1 | 1 |  |  |  |  | 139516.16 | 2478.04 | 139516.16 | 2478.04 | 8.1926 | [5 empty] | 96.0352
12.10.2007 20:00 | 3600 | 2 | 755.07 | GNB | 761.538 | 765.703 | 761.172 | 264.39 | GGB | 10868.9 | GGB | 9.86 | GGB | 983.78 | GGB | 59.95 | GGB | 177498.78 | GGB | 141342.19 | GGB | 0 | 0 | 2602 | 3600 | 2587.09 | GGB | 100 | GGB | 37.45 | GGB | 37.45 | GGB | 31649.71 | GGB | 31650.15 | 2587.09 | 2587.09 |  |  |  | 0 | 1 | [14 empty] | 101.5736
12.10.2007 21:00 | 3600 | 2 | 753.84 | GNB | 761.538 | 767.461 | 762.271 | 266.41 | GGB | 10937.6 | GGB | 9.84 | GGB | 984.48 | GGB | 58.72 | GGB | 180283.74 | GGB | 144192.5 | GGB | 0 | 0 | 2679 | 3600 | 2663.78 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 31689.41 | GGB | 31689.85 | 2663.78 | 2663.78 |  |  |  | 0 | 1 | [14 empty] | 106.6936 | 2620.9962
12.10.2007 22:00 | 3600 | 2 | 753.63 | GNB | 762.637 | 768.703 | 763.37 | 267.75 | GGB | 11026.6 | GGB | 9.84 | GGB | 985.86 | GGB | 57.23 | GGB | 182686.88 | GGB | 146981.38 | GGB | 0 | 0 | 2699 | 3600 | 2683.13 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 31729.6 | GGB | 31730.05 | 2683.13 | 2683.13 |  |  |  | 0 | 1 | [14 empty] | 109.5473 | 2571.2645
12.10.2007 23:00 | 3600 | 2 | 754.22 | GNB | 761.538 | 766.594 | 762.271 | 268.2 | GGB | 11055.9 | GGB | 9.85 | GGB | 987.34 | GGB | 56.56 | GGB | 183958.87 | GGB | 148527.04 | GGB | 0 | 0 | 2685 | 3600 | 2669.26 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 31770.68 | GGB | 31771.12 | 2669.26 | 2669.26 |  |  |  | 0 | 1 | [14 empty] | 110.127 | 2544.5064
12.10.2007 24:00 | 3600 | 2 | 754.6 | GNB | 763.004 | 768.656 | 763.37 | 268.46 | GGB | 11072.5 | GGB | 9.86 | GGB | 988.44 | GGB | 55.51 | GGB | 185463.03 | GGB | 150386.58 | GGB | 0 | 0 | 2664 | 3600 | 2648.76 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 31811.36 | GGB | 31811.8 | 2648.76 | 2648.76 |  |  |  | 0 | 1 | [14 empty] | 110.6494 | 2513.0434
13.10.2007 01:00 | 3600 | 2 | 754.25 | GNB | 763.004 | 767.602 | 762.271 | 267.37 | GGB | 11080.2 | GGB | 9.86 | GGB | 990.02 | GGB | 56 | GGB | 182478.91 | GGB | 147983.5 | GGB | 0 | 0 | 2692 | 3600 | 2676.46 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 31852.45 | GGB | 31852.89 | 2676.46 | 2676.46 |  |  |  | 0 | 1 | [14 empty] | 110.02 | 2553.8523
13.10.2007 02:00 | 3600 | 2 | 753.04 | GNB | 762.637 | 766.57 | 762.271 | 269.7 | GGB | 11062.6 | GGB | 9.83 | GGB | 991.74 | GGB | 55.14 | GGB | 185548.85 | GGB | 151131.17 | GGB | 0 | 0 | 2746 | 3600 | 2730.46 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 31892.36 | GGB | 31892.8 | 2730.46 | 2730.46 |  |  |  | 0 | 1 | [14 empty] | 114.6271 | 2500.6622
13.10.2007 03:00 | 3600 | 2 | 753.94 | GNB | 761.538 | 766.711 | 762.271 | 269.65 | GGB | 11140 | GGB | 9.86 | GGB | 992.94 | GGB | 55.26 | GGB | 185256.16 | GGB | 151020.45 | GGB | 0 | 0 | 2730 | 3600 | 2714.97 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 31931.87 | GGB | 31932.32 | 2714.97 | 2714.97 |  |  |  | 0 | 1 | [14 empty] | 113.8933 | 2502.4955
13.10.2007 04:00 | 3600 | 2 | 753.31 | GNB | 762.637 | 766.453 | 762.271 | 270.08 | GGB | 11127.1 | GGB | 9.84 | GGB | 993.88 | GGB | 55.08 | GGB | 186162.84 | GGB | 151984.59 | GGB | 0 | 0 | 2764 | 3600 | 2748.43 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 31972.06 | GGB | 31972.51 | 2748.43 | 2748.43 |  |  |  | 0 | 1 | [14 empty] | 116.0331 | 2486.6205
13.10.2007 05:00 | 3600 | 2 | 754.1 | GNB | 762.637 | 767.273 | 763.37 | 271.28 | GGB | 11143.4 | GGB | 9.85 | GGB | 994.77 | GGB | 54.6 | GGB | 188139.05 | GGB | 153959.8 | GGB | 0 | 0 | 2721 | 3600 | 2705.85 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 32011.06 | GGB | 32011.51 | 2705.85 | 2705.85 |  |  |  | 0 | 1 | [14 empty] | 115.72 | 2454.7187
13.10.2007 06:00 | 3600 | 2 | 754.46 | GNB | 762.637 | 767.555 | 763.37 | 269.73 | GGB | 11190.1 | GGB | 9.87 | GGB | 995.65 | GGB | 55.16 | GGB | 186064.91 | GGB | 152137.87 | GGB | 0 | 0 | 2725 | 3600 | 2709.21 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 32050.92 | GGB | 32051.36 | 2709.21 | 2709.21 |  |  |  | 0 | 1 | [14 empty] | 114.4926 | 2484.1152
13.10.2007 07:00 | 3600 | 2 | 753.65 | GNB | 761.538 | 766.383 | 762.271 | 269.92 | GGB | 11194.4 | GGB | 9.85 | GGB | 996.2 | GGB | 55.09 | GGB | 186348.8 | GGB | 152486.24 | GGB | 0 | 0 | 2766 | 3600 | 2751.03 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 32090.6 | GGB | 32091.04 | 2751.03 | 2751.03 |  |  |  | 0 | 1 | [14 empty] | 116.5262 | 2478.44
13.10.2007 08:00 | 3600 | 2 | 753.71 | GNB | 763.004 | 768.539 | 763.004 | 271.97 | GGB | 11202.6 | GGB | 9.84 | GGB | 996.99 | GGB | 54.37 | GGB | 189354.92 | GGB | 155409.06 | GGB | 0 | 0 | 2770 | 3600 | 2754.07 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 32129.75 | GGB | 32130.19 | 2754.07 | 2754.07 |  |  |  | 0 | 1 | [14 empty] | 118.891 | 2431.8273
13.10.2007 09:00 | 3600 | 2 | 754.38 | GNB | 764.102 | 769.383 | 764.102 | 272.53 | GGB | 11237.5 | GGB | 9.86 | GGB | 997.95 | GGB | 54.31 | GGB | 189815.96 | GGB | 155967.54 | GGB | 0 | 0 | 2743 | 3600 | 2727.46 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 32169.29 | GGB | 32169.73 | 2727.46 | 2727.46 |  |  |  | 0 | 1 | [14 empty] | 118.1653 | 2423.1196
13.10.2007 10:00 | 3600 | 2 | 754.56 | GNB | 764.102 | 769.453 | 765.201 | 271.3 | GGB | 11260.6 | GGB | 9.86 | GGB | 999.05 | GGB | 55.13 | GGB | 187733.03 | GGB | 154040.38 | GGB | 0 | 0 | 2753 | 3600 | 2737.77 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 32209.34 | GGB | 32209.79 | 2737.77 | 2737.77 |  |  |  | 0 | 1 | [14 empty] | 117.1464 | 2453.4346
13.10.2007 11:00 | 3600 | 2 | 754.87 | GNB | 763.004 | 768.609 | 764.102 | 272.03 | GGB | 11209.6 | GGB | 9.85 | GGB | 1000.16 | GGB | 55.05 | GGB | 188619.9 | GGB | 154977.1 | GGB | 0 | 0 | 2718 | 3600 | 2702.43 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 32249.12 | GGB | 32249.56 | 2702.43 | 2702.43 |  |  |  | 0 | 1 | [14 empty] | 116.3374 | 2438.6054
13.10.2007 12:00 | 3600 | 2 | 755.8 | GNB | 765.201 | 770.625 | 765.201 | 271.19 | GGB | 11197.9 | GGB | 9.87 | GGB | 1000.93 | GGB | 55.36 | GGB | 187200.46 | GGB | 153785.47 | GGB | 0 | 0 | 2665 | 3600 | 2649.52 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 32289.1 | GGB | 32289.55 | 2649.52 | 2649.52 |  |  |  | 0 | 1 | [14 empty] | 113.1827 | 2457.5013
13.10.2007 13:00 | 3600 | 2 | 754.95 | GNB | 760.44 | 766.102 | 761.538 | 270.11 | GGB | 11134.1 | GGB | 9.85 | GGB | 1001.47 | GGB | 56.34 | GGB | 184889.75 | GGB | 151515.8 | GGB | 0 | 0 | 2691 | 3600 | 2676.06 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 32329.15 | GGB | 32329.59 | 2676.06 | 2676.06 |  |  |  | 0 | 1 | [14 empty] | 112.6293 | 2494.3141
13.10.2007 14:00 | 3600 | 2 | 755.26 | GNB | 766.3 | 770.859 | 766.3 | 271.56 | GGB | 11111.3 | GGB | 9.86 | GGB | 1001.5 | GGB | 55.95 | GGB | 186593.08 | GGB | 153098.57 | GGB | 0 | 0 | 2672 | 3600 | 2656.81 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 32368.68 | GGB | 32369.12 | 2656.81 | 2656.81 |  |  |  | 0 | 1 | [14 empty] | 112.9872 | 2468.5273
13.10.2007 15:00 | 3600 | 2 | 756.6 | GGB | 764.102 | 768.633 | 764.102 | 270.44 | GGB | 11125 | GGB | 9.88 | GGB | 1002.03 | GGB | 57.05 | GGB | 183758.61 | GGB | 150348.18 | GGB | 0 | 0 | 2619 | 3600 | 2603.54 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 32408.35 | GGB | 32408.8 | 2603.54 | 2603.54 |  |  |  | 1 | 1 |  |  |  |  | 150348.18 | 2603.54 | 150348.18 | 2603.54 | 9.8649 | [5 empty] | 108.7326 | 2513.6852
13.10.2007 16:00 | 3600 | 2 | 755.33 | GNB | 764.102 | 768.75 | 763.004 | 270.35 | GGB | 11089.5 | GGB | 9.85 | GGB | 1002.46 | GGB | 57.66 | GGB | 183111.61 | GGB | 149607.61 | GGB | 0 | 0 | 2673 | 3600 | 2657.51 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 32448.04 | GGB | 32448.49 | 2657.51 | 2657.51 |  |  |  | 0 | 1 | [14 empty] | 110.4399 | 2526.1282
13.10.2007 17:00 | 3600 | 2 | 755.44 | GNB | 765.201 | 769.828 | 765.201 | 271.85 | GGB | 11053.2 | GGB | 9.85 | GGB | 1003.15 | GGB | 57.43 | GGB | 184708.2 | GGB | 151122.3 | GGB | 0 | 0 | 2655 | 3600 | 2640.05 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 32487.35 | GGB | 32487.8 | 2640.05 | 2640.05 |  |  |  | 0 | 1 | [14 empty] | 110.8251 | 2500.8089
13.10.2007 18:00 | 3600 | 2 | 756.13 | GGB | 764.102 | 768.727 | 764.102 | 270.22 | GGB | 11075.2 | GGB | 9.86 | GGB | 1003.57 | GGB | 58.03 | GGB | 182606.55 | GGB | 149193.05 | GGB | 0 | 0 | 2635 | 3600 | 2619.59 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 32526.86 | GGB | 32527.31 | 2619.59 | 2619.59 |  |  |  | 1 | 1 |  |  |  |  | 149193.05 | 2619.59 | 149193.05 | 2619.59 | 9.8918 | [5 empty] | 108.5624 | 2533.1475
13.10.2007 19:00 | 3600 | 2 | 755.36 | GNB | 764.102 | 768.727 | 764.102 | 270.49 | GGB | 11074.4 | GGB | 9.85 | GGB | 1004.21 | GGB | 58.23 | GGB | 182599.95 | GGB | 149192.93 | GGB | 0 | 0 | 2676 | 3600 | 2660.42 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 32566.23 | GGB | 32566.68 | 2660.42 | 2660.42 |  |  |  | 0 | 1 | [14 empty] | 110.2544 | 2533.1495
13.10.2007 20:00 | 3600 | 2 | 754.95 | GNB | 764.102 | 768.656 | 764.102 | 272.53 | GGB | 11067.4 | GGB | 9.84 | GGB | 1004.68 | GGB | 57.92 | GGB | 184713.7 | GGB | 151131.32 | GGB | 0 | 0 | 2694 | 3600 | 2678.26 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 32606.16 | GGB | 32606.61 | 2678.26 | 2678.26 |  |  |  | 0 | 1 | [14 empty] | 112.4358 | 2500.6597
13.10.2007 21:00 | 3600 | 2 | 754.91 | GNB | 763.004 | 768.656 | 764.102 | 273.68 | GGB | 11097.1 | GGB | 9.84 | GGB | 1005.24 | GGB | 57.3 | GGB | 185885.56 | GGB | 152461.35 | GGB | 0 | 0 | 2700 | 3600 | 2684.74 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 32645.37 | GGB | 32645.82 | 2684.74 | 2684.74 |  |  |  | 0 | 1 | [14 empty] | 113.6997 | 2478.8446
13.10.2007 22:00 | 3600 | 2 | 755.39 | GNB | 761.538 | 766.477 | 761.538 | 272.93 | GGB | 11189.3 | GGB | 9.86 | GGB | 1005.95 | GGB | 57.45 | GGB | 184974.48 | GGB | 151750.26 | GGB | 0 | 0 | 2729 | 3600 | 2713.73 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 32684.92 | GGB | 32685.37 | 2713.73 | 2713.73 |  |  |  | 0 | 1 | [14 empty] | 114.3915 | 2490.4603
13.10.2007 23:00 | 3600 | 2 | 754.48 | GNB | 764.102 | 768.656 | 764.102 | 274.41 | GGB | 11206.7 | GGB | 9.85 | GGB | 1006.61 | GGB | 57.31 | GGB | 186057.21 | GGB | 152803.7 | GGB | 0 | 0 | 2791 | 3600 | 2775.47 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 32725.5 | GGB | 32725.95 | 2775.47 | 2775.47 |  |  |  | 0 | 1 | [14 empty] | 117.8061 | 2473.2909
13.10.2007 24:00 | 3600 | 2 | 754.13 | GNB | 761.538 | 767.273 | 761.538 | 276.07 | GGB | 11217.5 | GGB | 9.83 | GGB | 1006.97 | GGB | 57.14 | GGB | 187815.55 | GGB | 154385.64 | GGB | 0 | 0 | 2817 | 3600 | 2801.37 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 32764.62 | GGB | 32765.07 | 2801.37 | 2801.37 |  |  |  | 0 | 1 | [14 empty] | 120.1365 | 2447.9479
14.10.2007 01:00 | 3600 | 2 | 754.43 | GNB | 764.102 | 768.539 | 764.102 | 278.4 | GGB | 11254.1 | GGB | 9.84 | GGB | 1007.13 | GGB | 56.11 | GGB | 191081.35 | GGB | 157586.1 | GGB | 0 | 0 | 2817 | 3600 | 2801.14 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 32804.74 | GGB | 32805.2 | 2801.14 | 2801.14 |  |  |  | 0 | 1 | [14 empty] | 122.6169 | 2398.2318
14.10.2007 02:00 | 3600 | 2 | 755.42 | GNB | 764.102 | 769.734 | 764.102 | 277.97 | GGB | 11317.2 | GGB | 9.87 | GGB | 1007.73 | GGB | 56.27 | GGB | 190743.55 | GGB | 157324.1 | GGB | 0 | 0 | 2795 | 3600 | 2779.77 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 32844.78 | GGB | 32845.24 | 2779.77 | 2779.77 |  |  |  | 0 | 1 | [14 empty] | 121.4791 | 2402.2257
14.10.2007 03:00 | 3600 | 2 | 754.36 | GNB | 764.102 | 767.672 | 764.102 | 277.09 | GGB | 11332.8 | GGB | 9.85 | GGB | 1008.79 | GGB | 56.65 | GGB | 189563.99 | GGB | 156334.98 | GGB | 0 | 0 | 2866 | 3600 | 2850.35 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 32884.62 | GGB | 32885.08 | 2850.35 | 2850.35 |  |  |  | 0 | 1 | [14 empty] | 123.7804 | 2417.4244
14.10.2007 04:00 | 3600 | 2 | 754.06 | GNB | 762.637 | 766.758 | 762.637 | 278.24 | GGB | 11315.3 | GGB | 9.84 | GGB | 1009.05 | GGB | 56.55 | GGB | 190685.23 | GGB | 157348.6 | GGB | 0 | 0 | 2886 | 3600 | 2869.98 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 32925.42 | GGB | 32925.87 | 2869.98 | 2869.98 |  |  |  | 0 | 1 | [14 empty] | 125.4409 | 2401.8517
14.10.2007 05:00 | 3600 | 2 | 754.36 | GNB | 764.102 | 767.953 | 763.37 | 279.6 | GGB | 11320.3 | GGB | 9.85 | GGB | 1009.29 | GGB | 56 | GGB | 192607.52 | GGB | 159238.97 | GGB | 0 | 0 | 2861 | 3600 | 2845.47 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 32965.19 | GGB | 32965.64 | 2845.47 | 2845.47 |  |  |  | 0 | 1 | [14 empty] | 125.8638 | 2373.3386
14.10.2007 06:00 | 3600 | 2 | 755.17 | GNB | 763.004 | 766.688 | 762.271 | 278.77 | GGB | 11369.7 | GGB | 9.87 | GGB | 1009.72 | GGB | 56.34 | GGB | 191416.96 | GGB | 158156.66 | GGB | 0 | 0 | 2844 | 3600 | 2828.86 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 33005.5 | GGB | 33005.96 | 2828.86 | 2828.86 |  |  |  | 0 | 1 | [14 empty] | 124.2786 | 2389.5801
14.10.2007 07:00 | 3600 | 2 | 754.6 | GNB | 764.102 | 768.797 | 764.469 | 277.97 | GGB | 11360.5 | GGB | 9.86 | GGB | 1009.89 | GGB | 56.69 | GGB | 190131.76 | GGB | 156956.58 | GGB | 0 | 0 | 2880 | 3600 | 2864.37 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 33046.4 | GGB | 33046.86 | 2864.37 | 2864.37 |  |  |  | 0 | 1 | [14 empty] | 124.8838 | 2407.8506
14.10.2007 08:00 | 3600 | 2 | 754.1 | GNB | 762.637 | 766.195 | 762.271 | 278.5 | GGB | 11326.8 | GGB | 9.84 | GGB | 1009.99 | GGB | 56.52 | GGB | 191057.15 | GGB | 157815.48 | GGB | 0 | 0 | 2882 | 3600 | 2866.69 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 33086.96 | GGB | 33087.42 | 2866.69 | 2866.69 |  |  |  | 0 | 1 | [14 empty] | 125.6689 | 2394.7461
14.10.2007 09:00 | 3600 | 2 | 754.33 | GNB | 763.004 | 767.555 | 763.37 | 280.04 | GGB | 11340.3 | GGB | 9.85 | GGB | 1010.36 | GGB | 55.95 | GGB | 193013.55 | GGB | 159767.45 | GGB | 0 | 0 | 2867 | 3600 | 2851.94 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 33127.76 | GGB | 33128.23 | 2851.94 | 2851.94 |  |  |  | 0 | 1 | [14 empty] | 126.5687 | 2365.4881
14.10.2007 10:00 | 3600 | 2 | 755.47 | GNB | 764.102 | 769.734 | 764.835 | 278.82 | GGB | 11374.2 | GGB | 9.88 | GGB | 1010.72 | GGB | 56.3 | GGB | 191366.34 | GGB | 158290.19 | GGB | 0 | 0 | 2825 | 3600 | 2809.94 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 33168.08 | GGB | 33168.55 | 2809.94 | 2809.94 |  |  |  | 0 | 1 | [14 empty] | 123.5516 | 2387.5643
14.10.2007 11:00 | 3600 | 2 | 755.31 | GNB | 764.102 | 768.727 | 764.469 | 276.65 | GGB | 11315.7 | GGB | 9.87 | GGB | 1010.79 | GGB | 57.15 | GGB | 188442.74 | GGB | 155482.59 | GGB | 0 | 0 | 2818 | 3600 | 2802.32 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 33208.72 | GGB | 33209.19 | 2802.32 | 2802.32 |  |  |  | 0 | 1 | [14 empty] | 121.0311 | 2430.6773
14.10.2007 12:00 | 3600 | 2 | 756.03 | GGB | 765.201 | 769.828 | 764.835 | 275.19 | GGB | 11258.4 | GGB | 9.87 | GGB | 1010.68 | GGB | 57.76 | GGB | 186455.53 | GGB | 153543.11 | GNB | 0 | 0 | 2755 | 3600 | 2739.2 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 33249.15 | GGB | 33249.63 | 2739.2 | 2739.2 |  |  |  | 1 | 1 |  |  |  |  | 153543.11 | 2739.2 |  | 2739.2 | 10.4002 | [5 empty] | 116.8292 | 2461.3804
14.10.2007 13:00 | 3600 | 2 | 756.01 | GGB | 765.201 | 769.125 | 764.835 | 274.01 | GGB | 11202.2 | GGB | 9.86 | GGB | 1010.54 | GGB | 57.95 | GGB | 185368.4 | GGB | 152537.35 | GGB | 0 | 0 | 2726 | 3600 | 2710.79 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 33288.84 | GGB | 33289.31 | 2710.79 | 2710.79 |  |  |  | 1 | 1 |  |  |  |  | 152537.35 | 2710.79 | 152537.35 | 2710.79 | 10.4208 | [5 empty] | 114.8602 | 2477.6096
14.10.2007 14:00 | 3600 | 2 | 756.15 | GGB | 765.201 | 770.32 | 764.835 | 273.06 | GGB | 11156.1 | GGB | 9.86 | GGB | 1009.81 | GGB | 58.31 | GGB | 184095.31 | GGB | 151218.25 | GGB | 0 | 0 | 2695 | 3600 | 2679.54 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 33328.61 | GGB | 33329.08 | 2679.54 | 2679.54 |  |  |  | 1 | 1 |  |  |  |  | 151218.25 | 2679.54 | 151218.25 | 2679.54 | 10.1885 | [5 empty] | 112.5543 | 2499.2222
14.10.2007 15:00 | 3600 | 2 | 756.41 | GGB | 765.201 | 770.742 | 764.835 | 272.28 | GGB | 11124.8 | GGB | 9.87 | GGB | 1009.41 | GGB | 58.72 | GGB | 183484.62 | GGB | 150470.81 | GGB | 0 | 0 | 2670 | 3600 | 2654.93 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 33368.44 | GGB | 33368.92 | 2654.93 | 2654.93 |  |  |  | 1 | 1 |  |  |  |  | 150470.81 | 2654.93 | 150470.81 | 2654.93 | 10.0273 | [5 empty] | 110.9693 | 2511.6366
14.10.2007 16:00 | 3600 | 2 | 756.02 | GGB | 764.102 | 768.703 | 764.835 | 272.32 | GGB | 11072.6 | GGB | 9.85 | GGB | 1008.59 | GGB | 58.84 | GGB | 183434.01 | GGB | 150251.86 | GGB | 0 | 0 | 2660 | 3600 | 2644.68 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 33408.25 | GGB | 33408.73 | 2644.68 | 2644.68 |  |  |  | 1 | 1 |  |  |  |  | 150251.86 | 2644.68 | 150251.86 | 2644.68 | 9.9816 | [5 empty] | 110.38 | 2515.2966
14.10.2007 17:00 | 3600 | 2 | 756.32 | GGB | 766.3 | 770.766 | 767.033 | 272.76 | GGB | 11052 | GGB | 9.86 | GGB | 1007.74 | GGB | 58.66 | GGB | 183908.25 | GGB | 150594.56 | GGB | 0 | 0 | 2638 | 3600 | 2622.79 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 33447.25 | GGB | 33447.72 | 2622.79 | 2622.79 |  |  |  | 1 | 1 |  |  |  |  | 150594.56 | 2622.79 | 150594.56 | 2622.79 | 10.1302 | [5 empty] | 109.7161 | 2509.5727
14.10.2007 18:00 | 3600 | 2 | 756.19 | GGB | 764.102 | 768.867 | 764.835 | 271.5 | GGB | 11057.6 | GGB | 9.86 | GGB | 1007.31 | GGB | 59.27 | GGB | 181926.54 | GGB | 148637.06 | GGB | 0 | 0 | 2651 | 3600 | 2635.16 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 33487.11 | GGB | 33487.58 | 2635.16 | 2635.16 |  |  |  | 1 | 1 |  |  |  |  | 148637.06 | 2635.16 | 148637.06 | 2635.16 | 9.8265 | [5 empty] | 108.8007 | 2542.623
14.10.2007 19:00 | 3600 | 2 | 755.5 | GNB | 764.102 | 768.844 | 764.469 | 271.99 | GGB | 11054 | GGB | 9.84 | GGB | 1007.39 | GGB | 59.13 | GGB | 182180.72 | GGB | 148916.55 | GGB | 0 | 0 | 2687 | 3600 | 2671.55 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 33526.32 | GGB | 33526.78 | 2671.55 | 2671.55 |  |  |  | 0 | 1 | [14 empty] | 110.5106 | 2537.8509
14.10.2007 20:00 | 3600 | 2 | 754.88 | GNB | 761.538 | 765.609 | 762.271 | 274.03 | GGB | 11067.8 | GGB | 9.83 | GGB | 1008.35 | GGB | 58.69 | GGB | 183953.36 | GGB | 150710.85 | GGB | 0 | 0 | 2724 | 3600 | 2708.45 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 33565.82 | GGB | 33566.28 | 2708.45 | 2708.45 |  |  |  | 0 | 1 | [14 empty] | 113.3869 | 2507.6363
14.10.2007 21:00 | 3600 | 2 | 755.52 | GNB | 762.637 | 767.648 | 763.37 | 274.42 | GGB | 11143.4 | GGB | 9.86 | GGB | 1008.59 | GGB | 58.93 | GGB | 183946.76 | GGB | 150631.46 | GGB | 0 | 0 | 2729 | 3600 | 2713.66 | GGB | 100 | GGB | 37.51 | GGB | 37.51 | GGB | 33603.33 | GGB | 33603.79 | 2713.66 | 2713.66 |  |  |  | 0 | 1 | [14 empty] | 113.5452 | 2508.958
14.10.2007 22:00 | 3600 | 2 | 755.35 | GNB | 764.102 | 768.797 | 764.469 | 275.27 | GGB | 11152.8 | GGB | 9.85 | GGB | 1008.38 | GGB | 58.89 | GGB | 184800.62 | GGB | 151318.87 | GGB | 0 | 0 | 2749 | 3600 | 2733.09 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 33643.63 | GGB | 33644.09 | 2733.09 | 2733.09 |  |  |  | 0 | 1 | [14 empty] | 114.88 | 2497.5603
14.10.2007 23:00 | 3600 | 2 | 755.4 | GNB | 761.538 | 765.891 | 762.271 | 274.71 | GGB | 11157.6 | GGB | 9.86 | GGB | 1007.62 | GGB | 58.79 | GGB | 185391.51 | GGB | 151731.24 | GGB | 0 | 0 | 2742 | 3600 | 2726.52 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 33682.88 | GGB | 33683.34 | 2726.52 | 2726.52 |  |  |  | 0 | 1 | [14 empty] | 114.9162 | 2490.7725
14.10.2007 24:00 | 3600 | 2 | 755.03 | GNB | 764.102 | 768.234 | 764.469 | 276.82 | GGB | 11116.7 | GGB | 9.85 | GGB | 1007.36 | GGB | 58.01 | GGB | 187071.72 | GGB | 153427.68 | GGB | 0 | 0 | 2748 | 3600 | 2732.9 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 33722.84 | GGB | 33723.3 | 2732.9 | 2732.9 |  |  |  | 0 | 1 | [14 empty] | 116.4729 | 2463.2322
15.10.2007 01:00 | 3600 | 2 | 756.15 | GGB | 763.004 | 768.258 | 763.37 | 275.25 | GGB | 11159.5 | GGB | 9.87 | GGB | 1006.77 | GGB | 58.45 | GGB | 185149.43 | GGB | 151560.02 | GGB | 0 | 0 | 2712 | 3600 | 2696.92 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 33761.75 | GGB | 33762.21 | 2696.92 | 2696.92 |  |  |  | 0 | 1 | [14 empty] | 113.5403 | 2493.5864
15.10.2007 02:00 | 3600 | 2 | 755.32 | GNB | 763.004 | 768.445 | 763.37 | 274.4 | GGB | 11135.8 | GGB | 9.86 | GGB | 1006.41 | GGB | 58.72 | GGB | 183859.84 | GGB | 150329.53 | GGB | 0 | 0 | 2742 | 3600 | 2726.94 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 33801.34 | GGB | 33801.8 | 2726.94 | 2726.94 |  |  |  | 0 | 1 | [14 empty] | 113.8721 | 2513.9971
15.10.2007 03:00 | 3600 | 2 | 755.61 | GNB | 764.102 | 768.891 | 764.835 | 274.68 | GGB | 11123.3 | GGB | 9.86 | GGB | 1006.07 | GGB | 58.69 | GGB | 184192.14 | GGB | 150563.16 | GGB | 0 | 0 | 2732 | 3600 | 2716.64 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 33841.5 | GGB | 33841.96 | 2716.64 | 2716.64 |  |  |  | 0 | 1 | [14 empty] | 113.6183 | 2510.0961
15.10.2007 04:00 | 3600 | 2 | 754.94 | GNB | 765.201 | 770.25 | 765.934 | 275.43 | GGB | 11076.8 | GGB | 9.85 | GGB | 1005.22 | GGB | 58.2 | GGB | 185312.28 | GGB | 151575.42 | GGB | 0 | 0 | 2742 | 3600 | 2726.45 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 33880.5 | GGB | 33880.96 | 2726.45 | 2726.45 |  |  |  | 0 | 1 | [14 empty] | 114.7952 | 2493.333
15.10.2007 05:00 | 3600 | 2 | 755.71 | GNB | 765.201 | 770.344 | 765.934 | 275.06 | GGB | 11101.1 | GGB | 9.86 | GGB | 1004.9 | GGB | 58.38 | GGB | 184568.45 | GGB | 150838.44 | GGB | 0 | 0 | 2718 | 3600 | 2702.81 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 33920.43 | GGB | 33920.89 | 2702.81 | 2702.81 |  |  |  | 0 | 1 | [14 empty] | 113.2466 | 2505.5152
15.10.2007 06:00 | 3600 | 2 | 755.4 | GNB | 764.102 | 768.141 | 764.469 | 273.97 | GGB | 11101.9 | GGB | 9.86 | GGB | 1004.58 | GGB | 59.23 | GGB | 183018.08 | GGB | 149139.77 | GGB | 0 | 0 | 2741 | 3600 | 2725.71 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 33959.85 | GGB | 33960.31 | 2725.71 | 2725.71 |  |  |  | 0 | 1 | [14 empty] | 112.9199 | 2534.0525
15.10.2007 07:00 | 3600 | 2 | 755.16 | GNB | 764.102 | 768.914 | 764.469 | 273.91 | GGB | 11073.9 | GGB | 9.85 | GGB | 1003.57 | GGB | 59.22 | GGB | 183443.91 | GGB | 149340.77 | GGB | 0 | 0 | 2740 | 3600 | 2724.63 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 33999.18 | GGB | 33999.64 | 2724.63 | 2724.63 |  |  |  | 0 | 1 | [14 empty] | 113.0273 | 2530.6418
15.10.2007 08:00 | 3600 | 2 | 756.01 | GGB | 765.201 | 770.039 | 764.835 | 273.99 | GGB | 11069.8 | GGB | 9.86 | GGB | 1002.57 | GGB | 58.35 | GGB | 184778.62 | GGB | 150671.14 | GGB | 0 | 0 | 2688 | 3600 | 2672.63 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 34038.9 | GGB | 34039.36 | 2672.63 | 2672.63 |  |  |  | 1 | 1 |  |  |  |  | 150671.14 | 2672.63 | 150671.14 | 2672.63 | 10.1382 | [5 empty] | 111.8578 | 2508.2972
15.10.2007 09:00 | 3600 | 2 | 755.89 | GNB | 764.102 | 769.031 | 764.469 | 271.94 | GGB | 11104.2 | GGB | 9.87 | GGB | 1002.29 | GGB | 58.88 | GGB | 182646.16 | GGB | 148656.06 | GGB | 0 | 0 | 2689 | 3600 | 2673.32 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 34078.35 | GGB | 34078.82 | 2673.32 | 2673.32 |  |  |  | 0 | 1 | [14 empty] | 110.3903 | 2542.298
15.10.2007 10:00 | 3600 | 2 | 756.01 | GGB | 764.102 | 769.219 | 764.835 | 271.52 | GGB | 11068.4 | GGB | 9.86 | GGB | 1002.03 | GGB | 58.74 | GGB | 182485.51 | GGB | 148546.63 | GGB | 0 | 0 | 2677 | 3600 | 2661.18 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 34118 | GGB | 34118.46 | 2661.18 | 2661.18 |  |  |  | 1 | 1 |  |  |  |  | 148546.63 | 2661.18 | 148546.63 | 2661.18 | 9.9725 | [5 empty] | 109.8081 | 2544.1708
15.10.2007 11:00 | 3600 | 2 | 755.33 | GNB | 763.004 | 768.352 | 764.469 | 270.45 | GGB | 11048.3 | GGB | 9.86 | GGB | 1001.43 | GGB | 58.58 | GGB | 181697.67 | GGB | 147887.23 | GGB | 0 | 0 | 2663 | 3600 | 2647.64 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 34157.39 | GGB | 34157.85 | 2647.64 | 2647.64 |  |  |  | 0 | 1 | [14 empty] | 108.7645 | 2555.5148
15.10.2007 12:00 | 3600 | 2 | 755.32 | GNB | 764.102 | 769.617 | 764.835 | 270.94 | GGB | 10988.4 | GGB | 9.86 | GGB | 1000.92 | GGB | 58.34 | GGB | 182843.12 | GGB | 148853.17 | GGB | 0 | 0 | 2620 | 3600 | 2604.78 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 34196.59 | GGB | 34197.06 | 2604.78 | 2604.78 |  |  |  | 0 | 1 | [14 empty] | 107.7027 | 2538.9315
15.10.2007 13:00 | 3600 | 2 | 755.99 | GNB | 765.201 | 770.648 | 765.934 | 268.29 | GGB | 11002.1 | GGB | 9.88 | GGB | 1000.63 | GGB | 59.16 | GGB | 179545.41 | GGB | 145766.21 | GGB | 0 | 0 | 2604 | 3600 | 2588.99 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 34236.05 | GGB | 34236.52 | 2588.99 | 2588.99 |  |  |  | 0 | 1 | [14 empty] | 104.8298
15.10.2007 14:00 | 3600 | 2 | 754.9 | GNB | 764.102 | 768.445 | 764.469 | 267.93 | GGB | 10900.6 | GGB | 9.85 | GGB | 1000.04 | GGB | 59.07 | GGB | 179326.44 | GGB | 145539.65 | GGB | 0 | 0 | 2613 | 3600 | 2597.19 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 34275.23 | GGB | 34275.71 | 2597.19 | 2597.19 |  |  |  | 0 | 1 | [14 empty] | 104.9984 | 2596.7357
15.10.2007 15:00 | 3600 | 2 | 755.6 | GNB | 763.004 | 768.352 | 764.469 | 268.31 | GGB | 10878.1 | GGB | 9.86 | GGB | 999.61 | GGB | 59.04 | GGB | 179638.94 | GGB | 145745.35 | GGB | 0 | 0 | 2573 | 3600 | 2557.6 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 34314.17 | GGB | 34314.64 | 2557.6 | 2557.6 |  |  |  | 0 | 1 | [14 empty] | 103.544
15.10.2007 16:00 | 3600 | 2 | 755.63 | GNB | 763.004 | 768.164 | 763.37 | 267.08 | GGB | 10918.4 | GGB | 9.86 | GGB | 998.91 | GGB | 59.55 | GGB | 177472.38 | GGB | 143664.32 | GGB | 0 | 0 | 2606 | 3600 | 2590.7 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 34353.08 | GGB | 34353.56 | 2590.7 | 2590.7 |  |  |  | 0 | 1 | [14 empty] | 103.3864
15.10.2007 17:00 | 3600 | 2 | 754.56 | GNB | 763.004 | 768.164 | 763.37 | 267.92 | GGB | 10915.3 | GGB | 9.84 | GGB | 998.72 | GGB | 59.64 | GGB | 178103.97 | GGB | 144110.3 | GGB | 0 | 0 | 2668 | 3600 | 2652.41 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 34392.08 | GGB | 34392.55 | 2652.41 | 2652.41 |  |  |  | 0 | 1 | [14 empty] | 106.1777 | 2622.4912
15.10.2007 18:00 | 3600 | 2 | 754.98 | GNB | 765.201 | 769.289 | 764.835 | 269.89 | GGB | 10904.2 | GGB | 9.84 | GGB | 998.81 | GGB | 58.91 | GGB | 180740.38 | GGB | 146579.56 | GGB | 0 | 0 | 2640 | 3600 | 2624.15 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 34431.05 | GGB | 34431.52 | 2624.15 | 2624.15 |  |  |  | 0 | 1 | [14 empty] | 106.8463 | 2578.3131
15.10.2007 19:00 | 3600 | 2 | 755.56 | GNB | 763.004 | 768.211 | 764.469 | 268.94 | GGB | 10956.2 | GGB | 9.86 | GGB | 998.97 | GGB | 59.23 | GGB | 179456.28 | GGB | 145421.51 | GGB | 0 | 0 | 2626 | 3600 | 2610.68 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 34470.31 | GGB | 34470.79 | 2610.68 | 2610.68 |  |  |  | 0 | 1 | [14 empty] | 105.4581 | 2598.8452
15.10.2007 20:00 | 3600 | 2 | 754.97 | GNB | 764.102 | 769.477 | 764.469 | 268.65 | GGB | 10942.5 | GGB | 9.86 | GGB | 998.87 | GGB | 59.45 | GGB | 179126.18 | GGB | 145042.11 | GGB | 0 | 0 | 2651 | 3600 | 2635.5 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 34509.48 | GGB | 34509.96 | 2635.5 | 2635.5 |  |  |  | 0 | 1 | [14 empty] | 106.1829 | 2605.6433
15.10.2007 21:00 | 3600 | 2 | 754.87 | GNB | 764.102 | 768.281 | 764.469 | 269.94 | GGB | 10917.3 | GGB | 9.85 | GGB | 998.81 | GGB | 58.81 | GGB | 180846.01 | GGB | 146709.85 | GGB | 0 | 0 | 2643 | 3600 | 2628.05 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 34548.38 | GGB | 34548.86 | 2628.05 | 2628.05 |  |  |  | 0 | 1 | [14 empty] | 107.1002 | 2576.0234
15.10.2007 22:00 | 3600 | 2 | 755 | GNB | 763.004 | 768.234 | 763.37 | 269.36 | GGB | 10954.5 | GGB | 9.85 | GGB | 998.83 | GGB | 59.14 | GGB | 179599.33 | GGB | 145554.67 | GGB | 0 | 0 | 2660 | 3600 | 2644.3 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 34587.27 | GGB | 34587.75 | 2644.3 | 2644.3 |  |  |  | 0 | 1 | [14 empty] | 106.9139 | 2596.4677
15.10.2007 23:00 | 3600 | 2 | 754.92 | GNB | 761.538 | 766.852 | 763.004 | 270.92 | GGB | 10959.5 | GGB | 9.85 | GGB | 999.32 | GGB | 58.25 | GGB | 182485.51 | GGB | 148364.5 | GGB | 0 | 0 | 2660 | 3600 | 2644.94 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 34625.9 | GGB | 34626.38 | 2644.94 | 2644.94 |  |  |  | 0 | 1 | [14 empty] | 109.0042 | 2547.294
15.10.2007 24:00 | 3600 | 2 | 754.86 | GNB | 764.102 | 768.938 | 764.835 | 271.21 | GGB | 10993.2 | GGB | 9.85 | GGB | 999.68 | GGB | 58.41 | GGB | 181738.39 | GGB | 147737.07 | GGB | 0 | 0 | 2691 | 3600 | 2675.15 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 34665.45 | GGB | 34665.93 | 2675.15 | 2675.15 |  |  |  | 0 | 1 | [14 empty] | 109.783 | 2558.1122
16.10.2007 01:00 | 3600 | 2 | 754.21 | GNB | 761.538 | 766.688 | 762.271 | 271.28 | GGB | 11024.7 | GGB | 9.84 | GGB | 999.87 | GGB | 58.84 | GGB | 181540.32 | GGB | 147416.1 | GGB | 0 | 0 | 2732 | 3600 | 2716.66 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 34704.22 | GGB | 34704.7 | 2716.66 | 2716.66 |  |  |  | 0 | 1 | [14 empty] | 111.2443 | 2563.682
16.10.2007 02:00 | 3600 | 2 | 753.76 | GNB | 764.102 | 768.891 | 764.469 | 274.51 | GGB | 11062.3 | GGB | 9.83 | GGB | 1000.17 | GGB | 57.89 | GGB | 185449.82 | GGB | 151065.53 | GGB | 0 | 0 | 2783 | 3600 | 2767.88 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 34742.22 | GGB | 34742.7 | 2767.88 | 2767.88 |  |  |  | 0 | 1 | [14 empty] | 116.1476 | 2501.7487
16.10.2007 03:00 | 3600 | 2 | 754.37 | GNB | 763.004 | 767.695 | 763.37 | 275.64 | GGB | 11103.9 | GGB | 9.84 | GGB | 1000.46 | GGB | 57.42 | GGB | 186920.98 | GGB | 152528.35 | GGB | 0 | 0 | 2765 | 3600 | 2749.14 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 34780.84 | GGB | 34781.31 | 2749.14 | 2749.14 |  |  |  | 0 | 1 | [14 empty] | 116.4783 | 2477.7558
16.10.2007 04:00 | 3600 | 2 | 754.72 | GNB | 761.538 | 765.445 | 761.172 | 274.37 | GGB | 11174 | GGB | 9.86 | GGB | 1000.2 | GGB | 57.69 | GGB | 185457.53 | GGB | 151168.72 | GGB | 0 | 0 | 2784 | 3600 | 2768.15 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 34820.67 | GGB | 34821.15 | 2768.15 | 2768.15 |  |  |  | 0 | 1 | [14 empty] | 116.2382 | 2500.041
16.10.2007 05:00 | 3600 | 2 | 753.48 | GNB | 761.538 | 766.477 | 762.271 | 276.12 | GGB | 11231.6 | GGB | 9.84 | GGB | 1000.33 | GGB | 57.05 | GGB | 188348.11 | GGB | 153841.36 | GGB | 0 | 0 | 2866 | 3600 | 2850.31 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 34859.69 | GGB | 34860.17 | 2850.31 | 2850.31 |  |  |  | 0 | 1 | [14 empty] | 121.8043 | 2456.6085
16.10.2007 06:00 | 3600 | 2 | 753.77 | GNB | 762.637 | 766.523 | 762.271 | 277.86 | GGB | 11241.7 | GGB | 9.84 | GGB | 1000.27 | GGB | 56.14 | GGB | 191507.18 | GGB | 156847.96 | GGB | 0 | 0 | 2853 | 3600 | 2837.26 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 34899.71 | GGB | 34900.19 | 2837.26 | 2837.26 |  |  |  | 0 | 1 | [14 empty] | 123.6162 | 2409.5181
16.10.2007 07:00 | 3600 | 2 | 753.7 | GNB | 762.637 | 766.219 | 762.271 | 277.8 | GGB | 11331.9 | GGB | 9.85 | GGB | 1000.45 | GGB | 56.38 | GGB | 190427.75 | GGB | 155879.16 | GGB | 0 | 0 | 2904 | 3600 | 2887.92 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 34939.37 | GGB | 34939.85 | 2887.92 | 2887.92 |  |  |  | 0 | 1 | [14 empty] | 125.0463 | 2424.4934
16.10.2007 08:00 | 3600 | 2 | 753.47 | GNB | 761.538 | 766.219 | 762.271 | 278.99 | GGB | 11365.3 | GGB | 9.84 | GGB | 1000.74 | GGB | 55.74 | GGB | 192834.19 | GGB | 158198 | GGB | 0 | 0 | 2929 | 3600 | 2913.84 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 34979.16 | GGB | 34979.64 | 2913.84 | 2913.84 |  |  |  | 0 | 1 | [14 empty] | 128.0455 | 2388.9556
16.10.2007 09:00 | 3600 | 2 | 754.6 | GNB | 765.201 | 769.453 | 765.934 | 279.62 | GGB | 11396.9 | GGB | 9.87 | GGB | 1001.3 | GGB | 55.17 | GGB | 193916.92 | GGB | 159452.91 | GGB | 0 | 0 | 2880 | 3600 | 2864.06 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 35019.45 | GGB | 35019.93 | 2864.06 | 2864.06 |  |  |  | 0 | 1 | [14 empty] | 126.8563 | 2370.1543
16.10.2007 10:00 | 3600 | 2 | 755.12 | GNB | 766.3 | 770.578 | 767.033 | 276.49 | GGB | 11372.6 | GGB | 9.88 | GGB | 1001.47 | GGB | 56.2 | GGB | 189922.7 | GGB | 155709.28 | GGB | 0 | 0 | 2841 | 3600 | 2825.02 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 35060.1 | GGB | 35060.58 | 2825.02 | 2825.02 |  |  |  | 0 | 1 | [14 empty] | 122.1894 | 2427.1386
16.10.2007 11:00 | 3600 | 2 | 756.14 | GGB | 766.3 | 771.68 | 767.033 | 273.2 | GGB | 11202.2 | GGB | 9.89 | GGB | 1001.11 | GGB | 56.93 | GGB | 186442.33 | GGB | 152459.67 | GGB | 0 | 0 | 2712 | 3600 | 2696.72 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 35099.54 | GGB | 35100.02 | 2696.72 | 2696.72 |  |  |  | 1 | 1 |  |  |  |  | 152459.67 | 2696.72 | 152459.67 | 2696.72 | 10.4245 | [5 empty] | 114.2058 | 2478.872
16.10.2007 12:00 | 3600 | 2 | 757.84 | GGB | 766.3 | 771.516 | 767.033 | 267.41 | GGB | 10986.9 | GGB | 9.91 | GGB | 1000.62 | GGB | 58.5 | GGB | 179933.83 | GGB | 146369.6 | GGB | 0 | 0 | 2509 | 3600 | 2493.6 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 35139.49 | GGB | 35139.98 | 2493.6 | 2493.6 |  |  |  | 1 | 1 |  |  |  |  | 146369.6 | 2493.6 | 146369.6 | 2493.6 | 9.1338 | [5 empty] | 101.3853
16.10.2007 13:00 | 3600 | 2 | 756.75 | GGB | 765.201 | 770.484 | 765.934 | 262.62 | GGB | 10825.9 | GGB | 9.87 | GGB | 999.68 | GGB | 59.92 | GGB | 173965.6 | GGB | 140779.38 | GGB | 0 | 0 | 2486 | 2981 | 2470.35 | GGB | 100 | GGB | 38.26 | GGB | 38.26 | GGB | 35177.75 | GGB | 35178.24 | 2470.35 | 2470.35 |  |  |  | 1 | 1 |  |  |  |  | 140779.38 | 2470.35 | 140779.38 | 2470.35 | 9.0898 | [5 empty] | 96.604
16.10.2007 14:00 | 3600 | 2 | 756.98 | GGB | 765.201 | 770.297 | 765.934 | 261.26 | GGB | 10733.3 | GGB | 9.86 | GGB | 998.84 | GGB | 60.68 | GGB | 172037.81 | GGB | 138787.75 | GGB | 0 | 0 | 2456 | 3600 | 2440.85 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 35215.85 | GGB | 35216.34 | 2440.85 | 2440.85 |  |  |  | 1 | 1 |  |  |  |  | 138787.75 | 2440.85 | 138787.75 | 2440.85 | 8.8913 | [5 empty] | 94.1
16.10.2007 15:00 | 3600 | 2 | 756.87 | GGB | 764.102 | 770.203 | 764.835 | 261.76 | GGB | 10636 | GGB | 9.85 | GGB | 998.36 | GGB | 60.84 | GGB | 172520.86 | GGB | 139040.45 | GGB | 0 | 0 | 2422 | 3600 | 2407.2 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 35254.28 | GGB | 35254.76 | 2407.2 | 2407.2 |  |  |  | 1 | 1 |  |  |  |  | 139040.45 | 2407.2 | 139040.45 | 2407.2 | 8.7116 | [5 empty] | 92.9717
16.10.2007 16:00 | 3600 | 2 | 757.28 | GGB | 765.201 | 770.297 | 765.201 | 260.6 | GGB | 10668.5 | GGB | 9.86 | GGB | 997.91 | GGB | 61.15 | GGB | 171729.71 | GGB | 138212.13 | GGB | 0 | 0 | 2429 | 3600 | 2413.84 | GGB | 100 | GGB | 37.61 | GGB | 37.61 | GGB | 35291.89 | GGB | 35292.37 | 2413.84 | 2413.84 |  |  |  | 1 | 1 |  |  |  |  | 138212.13 | 2413.84 | 138212.13 | 2413.84 | 8.8706 | [5 empty] | 92.6728
16.10.2007 17:00 | 3600 | 2 | 757.03 | GGB | 764.102 | 770.531 | 765.201 | 261.1 | GGB | 10641.3 | GGB | 9.85 | GGB | 997.52 | GGB | 60.5 | GGB | 173260.28 | GGB | 139659.91 | GGB | 0 | 0 | 2421 | 3600 | 2405.47 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 35329.88 | GGB | 35330.37 | 2405.47 | 2405.47 |  |  |  | 1 | 1 |  |  |  |  | 139659.91 | 2405.47 | 139659.91 | 2405.47 | 8.8407 | [5 empty] | 93.3188
16.10.2007 18:00 | 3600 | 2 | 756.69 | GGB | 764.102 | 770.508 | 765.201 | 259.77 | GGB | 10689.7 | GGB | 9.85 | GGB | 997.55 | GGB | 60.8 | GGB | 171444.73 | GGB | 138078.64 | GGB | 0 | 0 | 2456 | 3600 | 2440.94 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 35368.27 | GGB | 35368.76 | 2440.94 | 2440.94 |  |  |  | 1 | 1 |  |  |  |  | 138078.64 | 2440.94 | 138078.64 | 2440.94 | 8.7794 | [5 empty] | 93.6227
16.10.2007 19:00 | 3600 | 2 | 755.8 | GNB | 764.102 | 769.43 | 765.201 | 261.86 | GGB | 10721.5 | GGB | 9.84 | GGB | 998.04 | GGB | 60.49 | GGB | 173364.81 | GGB | 139825.23 | GGB | 0 | 0 | 2515 | 3600 | 2499.28 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 35406.39 | GGB | 35406.87 | 2499.28 | 2499.28 |  |  |  | 0 | 1 | [14 empty] | 97.0729
16.10.2007 20:00 | 3600 | 2 | 756.39 | GGB | 764.102 | 769.148 | 765.201 | 263.77 | GGB | 10742.8 | GGB | 9.85 | GGB | 998.59 | GGB | 59.66 | GGB | 175587.5 | GGB | 142045.88 | GGB | 0 | 0 | 2505 | 3600 | 2489.39 | GGB | 100 | GGB | 37.78 | GGB | 37.78 | GGB | 35444.17 | GGB | 35444.65 | 2489.39 | 2489.39 |  |  |  | 1 | 1 |  |  |  |  | 142045.88 | 2489.39 | 142045.88 | 2489.39 | 9.3597 | [5 empty] | 98.2243
16.10.2007 21:00 | 3600 | 2 | 756.42 | GGB | 766.3 | 770.344 | 765.934 | 263.11 | GGB | 10775.6 | GGB | 9.86 | GGB | 998.64 | GGB | 59.87 | GGB | 174659.91 | GGB | 141212.96 | GGB | 0 | 0 | 2514 | 3600 | 2498.79 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 35483.03 | GGB | 35483.52 | 2498.79 | 2498.79 |  |  |  | 1 | 1 |  |  |  |  | 141212.96 | 2498.79 | 141212.96 | 2498.79 | 9.078 | [5 empty] | 98.0171
16.10.2007 22:00 | 3600 | 2 | 756.16 | GGB | 765.201 | 770.367 | 765.934 | 261.95 | GGB | 10774.8 | GGB | 9.85 | GGB | 998.81 | GGB | 60.3 | GGB | 173101.83 | GGB | 139798.41 | GGB | 0 | 0 | 2536 | 3600 | 2520.59 | GGB | 100 | GGB | 37.96 | GGB | 37.96 | GGB | 35520.99 | GGB | 35521.48 | 2520.59 | 2520.59 |  |  |  | 1 | 1 |  |  |  |  | 139798.41 | 2520.59 | 139798.41 | 2520.59 | 9.2828 | [5 empty] | 97.8818
16.10.2007 23:00 | 3600 | 2 | 756.15 | GGB | 764.102 | 770.344 | 765.934 | 261.75 | GGB | 10770.7 | GGB | 9.86 | GGB | 998.83 | GGB | 60.41 | GGB | 172888.37 | GGB | 139585.4 | GGB | 0 | 0 | 2537 | 3600 | 2521.39 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 35558.99 | GGB | 35559.48 | 2521.39 | 2521.39 |  |  |  | 1 | 1 |  |  |  |  | 139585.4 | 2521.39 | 139585.4 | 2521.39 | 9.2618 | [5 empty] | 97.7637
16.10.2007 24:00 | 3600 | 2 | 756.19 | GGB | 765.201 | 770.367 | 765.201 | 261.58 | GGB | 10771.5 | GGB | 9.86 | GGB | 998.94 | GGB | 60.46 | GGB | 172658.4 | GGB | 139394.21 | GGB | 0 | 0 | 2540 | 3600 | 2524.25 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 35597.81 | GGB | 35598.29 | 2524.25 | 2524.25 |  |  |  | 1 | 1 |  |  |  |  | 139394.21 | 2524.25 | 139394.21 | 2524.25 | 9.0664 | [5 empty] | 97.7405
17.10.2007 01:00 | 3600 | 2 | 756.12 | GGB | 765.201 | 769.336 | 765.201 | 261.16 | GGB | 10758.9 | GGB | 9.85 | GGB | 998.69 | GGB | 60.43 | GGB | 172262.28 | GGB | 139049.3 | GGB | 0 | 0 | 2543 | 3600 | 2528.19 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 35636.9 | GGB | 35637.39 | 2528.19 | 2528.19 |  |  |  | 1 | 1 |  |  |  |  | 139049.3 | 2528.19 | 139049.3 | 2528.19 | 8.9909 | [5 empty] | 97.6508
17.10.2007 02:00 | 3600 | 2 | 755.79 | GNB | 764.102 | 769.242 | 765.201 | 261.24 | GGB | 10753 | GGB | 9.85 | GGB | 998.6 | GGB | 60.46 | GGB | 172124.73 | GGB | 138914.79 | GGB | 0 | 0 | 2552 | 3600 | 2536.8 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 35675.41 | GGB | 35675.9 | 2536.8 | 2536.8 |  |  |  | 0 | 1 | [14 empty] | 97.8886
17.10.2007 03:00 | 3600 | 2 | 756.11 | GGB | 764.102 | 769.242 | 765.201 | 261.4 | GGB | 10759.7 | GGB | 9.86 | GGB | 998.47 | GGB | 60.47 | GGB | 172392.12 | GGB | 139107.36 | GGB | 0 | 0 | 2553 | 3600 | 2537.85 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 35713.59 | GGB | 35714.08 | 2537.85 | 2537.85 |  |  |  | 1 | 1 |  |  |  |  | 139107.36 | 2537.85 | 139107.36 | 2537.85 | 9.2466 | [5 empty] | 98.0649
17.10.2007 04:00 | 3600 | 2 | 756.1 | GGB | 764.102 | 770.32 | 765.201 | 261.63 | GGB | 10760.6 | GGB | 9.85 | GGB | 998.47 | GGB | 60.55 | GGB | 172414.12 | GGB | 139091.66 | GGB | 0 | 0 | 2555 | 3600 | 2539.72 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 35752.24 | GGB | 35752.72 | 2539.72 | 2539.72 |  |  |  | 1 | 1 |  |  |  |  | 139091.66 | 2539.72 | 139091.66 | 2539.72 | 9.1422 | [5 empty] | 98.1261
17.10.2007 05:00 | 3600 | 2 | 756.14 | GGB | 764.102 | 769.148 | 765.201 | 261.57 | GGB | 10758.1 | GGB | 9.85 | GGB | 998.35 | GGB | 60.54 | GGB | 172351.4 | GGB | 139027.58 | GGB | 0 | 0 | 2555 | 3600 | 2540.17 | GGB | 100 | GGB | 38.09 | GGB | 38.09 | GGB | 35790.33 | GGB | 35790.81 | 2540.17 | 2540.17 |  |  |  | 1 | 1 |  |  |  |  | 139027.58 | 2540.17 | 139027.58 | 2540.17 | 9.2716 | [5 empty] | 98.0982
17.10.2007 06:00 | 3600 | 2 | 755.93 | GNB | 764.102 | 769.125 | 764.102 | 262 | GGB | 10764.5 | GGB | 9.85 | GGB | 998.26 | GGB | 60.54 | GGB | 172450.43 | GGB | 139094.88 | GGB | 0 | 0 | 2566 | 3600 | 2550.28 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 35828.82 | GGB | 35829.3 | 2550.28 | 2550.28 |  |  |  | 0 | 1 | [14 empty] | 98.5364
17.10.2007 07:00 | 3600 | 2 | 755.69 | GNB | 765.201 | 769.125 | 765.201 | 263.06 | GGB | 10788.2 | GGB | 9.85 | GGB | 997.87 | GGB | 60.45 | GGB | 173396.72 | GGB | 139844 | GGB | 0 | 0 | 2591 | 3600 | 2575.37 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 35867.19 | GGB | 35867.67 | 2575.37 | 2575.37 |  |  |  | 0 | 1 | [14 empty] | 100.0417
17.10.2007 08:00 | 3600 | 2 | 755.97 | GNB | 765.201 | 770.156 | 766.3 | 263.29 | GGB | 10811 | GGB | 9.86 | GGB | 997.89 | GGB | 60.38 | GGB | 173688.31 | GGB | 140111.4 | GGB | 0 | 0 | 2587 | 3600 | 2571.78 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 35905.7 | GGB | 35906.18 | 2571.78 | 2571.78 |  |  |  | 0 | 1 | [14 empty] | 100.0932
17.10.2007 09:00 | 3600 | 2 | 755.53 | GNB | 764.102 | 769.102 | 765.201 | 263.3 | GGB | 10809.3 | GGB | 9.85 | GGB | 997.97 | GGB | 60.29 | GGB | 173975.5 | GGB | 140390.6 | GGB | 0 | 0 | 2602 | 3600 | 2586.95 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 35944.06 | GGB | 35944.54 | 2586.95 | 2586.95 |  |  |  | 0 | 1 | [14 empty] | 100.8843
17.10.2007 10:00 | 3600 | 2 | 755.91 | GNB | 764.102 | 769.125 | 764.102 | 263.34 | GGB | 10814.5 | GGB | 9.86 | GGB | 997.95 | GGB | 60.02 | GGB | 174376.03 | GGB | 140825.22 | GGB | 0 | 0 | 2587 | 3600 | 2571.2 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 35982.85 | GGB | 35983.33 | 2571.2 | 2571.2 |  |  |  | 0 | 1 | [14 empty] | 100.5805
17.10.2007 11:00 | 3600 | 2 | 756.03 | GGB | 765.201 | 770.25 | 766.3 | 263.01 | GGB | 10753.3 | GGB | 9.86 | GGB | 997.65 | GGB | 59.57 | GGB | 174723.73 | GGB | 141251.65 | GGB | 0 | 0 | 2532 | 3600 | 2516.31 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 36020.99 | GGB | 36021.47 | 2516.31 | 2516.31 |  |  |  | 1 | 1 |  |  |  |  | 141251.65 | 2516.31 | 141251.65 | 2516.31 | 9.3192 | [5 empty] | 98.7314
17.10.2007 12:00 | 3600 | 2 | 756.54 | GGB | 764.102 | 770.32 | 765.201 | 261.01 | GGB | 10715.2 | GGB | 9.86 | GGB | 997.32 | GGB | 60.08 | GGB | 172293.09 | GGB | 139031.29 | GGB | 0 | 0 | 2494 | 3600 | 2478.77 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 36059.59 | GGB | 36060.07 | 2478.77 | 2478.77 |  |  |  | 1 | 1 |  |  |  |  | 139031.29 | 2478.77 | 139031.29 | 2478.77 | 8.9282 | [5 empty] | 95.7296
17.10.2007 13:00 | 3600 | 2 | 756.48 | GGB | 765.201 | 770.367 | 766.3 | 259.74 | GGB | 10688.3 | GGB | 9.86 | GGB | 997.13 | GGB | 60.46 | GGB | 170808.73 | GGB | 137647.45 | GGB | 0 | 0 | 2493 | 3600 | 2477.54 | GGB | 100 | GGB | 37.92 | GGB | 37.92 | GGB | 36097.51 | GGB | 36097.99 | 2477.54 | 2477.54 |  |  |  | 1 | 1 |  |  |  |  | 137647.45 | 2477.54 | 137647.45 | 2477.54 | 8.9933 | [5 empty] | 94.7297
17.10.2007 14:00 | 3600 | 2 | 756.53 | GGB | 765.201 | 770.367 | 766.3 | 258.29 | GGB | 10649.4 | GGB | 9.86 | GGB | 996.63 | GGB | 60.99 | GGB | 169022.88 | GGB | 135926.88 | GGB | 0 | 0 | 2476 | 3600 | 2460.34 | GGB | 100 | GGB | 38.21 | GGB | 38.21 | GGB | 36135.72 | GGB | 36136.2 | 2460.34 | 2460.34 |  |  |  | 1 | 1 |  |  |  |  | 135926.88 | 2460.34 | 135926.88 | 2460.34 | 8.7523 | [5 empty] | 92.8962
17.10.2007 15:00 | 3600 | 2 | 756.36 | GGB | 764.102 | 769.242 | 765.201 | 258.43 | GGB | 10591 | GGB | 9.85 | GGB | 996.33 | GGB | 60.95 | GGB | 169350.78 | GGB | 136162.3 | GGB | 0 | 0 | 2454 | 3600 | 2438.82 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 36174.09 | GGB | 36174.57 | 2438.82 | 2438.82 |  |  |  | 1 | 1 |  |  |  |  | 136162.3 | 2438.82 | 136162.3 | 2438.82 | 8.6546 | [5 empty] | 92.2432
17.10.2007 16:00 | 3600 | 2 | 756.72 | GGB | 765.201 | 770.367 | 766.3 | 259.23 | GGB | 10584.7 | GGB | 9.86 | GGB | 995.92 | GGB | 60.6 | GGB | 170444.52 | GGB | 137131.79 | GGB | 0 | 0 | 2433 | 3600 | 2417.83 | GGB | 100 | GGB | 37.48 | GGB | 37.48 | GGB | 36211.58 | GGB | 36212.05 | 2417.83 | 2417.83 |  |  |  | 1 | 1 |  |  |  |  | 137131.79 | 2417.83 | 137131.79 | 2417.83 | 8.8464 | [5 empty] | 92.1004
17.10.2007 17:00 | 3600 | 2 | 756.92 | GGB | 765.201 | 770.367 | 766.667 | 257.52 | GGB | 10607.3 | GGB | 9.86 | GGB | 995.57 | GGB | 61.07 | GGB | 168209.73 | GGB | 135096.7 | GGB | 0 | 0 | 2436 | 3600 | 2420.41 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 36249.61 | GGB | 36250.09 | 2420.41 | 2420.41 |  |  |  | 1 | 1 |  |  |  |  | 135096.7 | 2420.41 | 135096.7 | 2420.41 | 8.5959 | [5 empty] | 90.8304
17.10.2007 18:00 | 3600 | 2 | 756.2 | GGB | 764.102 | 770.555 | 766.3 | 257.53 | GGB | 10598 | GGB | 9.85 | GGB | 995.21 | GGB | 61.08 | GGB | 168216.33 | GGB | 135046.33 | GGB | 0 | 0 | 2464 | 3600 | 2448.73 | GGB | 100 | GGB | 37.71 | GGB | 37.71 | GGB | 36287.32 | GGB | 36287.8 | 2448.73 | 2448.73 |  |  |  | 1 | 1 |  |  |  |  | 135046.33 | 2448.73 | 135046.33 | 2448.73 | 8.7693 | [5 empty] | 91.8589
17.10.2007 19:00 | 3600 | 2 | 755.79 | GNB | 764.102 | 770.438 | 765.201 | 258.61 | GGB | 10627.9 | GGB | 9.85 | GGB | 994.85 | GGB | 61.07 | GGB | 169255.05 | GGB | 135835.4 | GGB | 0 | 0 | 2498 | 3600 | 2482.4 | GGB | 100 | GGB | 37.96 | GGB | 37.96 | GGB | 36325.28 | GGB | 36325.76 | 2482.4 | 2482.4 |  |  |  | 0 | 1 | [14 empty] | 93.6661
17.10.2007 20:00 | 3600 | 2 | 755.86 | GNB | 764.102 | 770.367 | 765.201 | 258.95 | GGB | 10647.4 | GGB | 9.85 | GGB | 994.78 | GGB | 60.89 | GGB | 169677.58 | GGB | 136238.69 | GGB | 0 | 0 | 2504 | 3600 | 2488.7 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 36363.33 | GGB | 36363.81 | 2488.7 | 2488.7 |  |  |  | 0 | 1 | [14 empty] | 94.1826
17.10.2007 21:00 | 3600 | 2 | 756.05 | GGB | 765.201 | 770.484 | 765.201 | 259.17 | GGB | 10649.3 | GGB | 9.86 | GGB | 994.15 | GGB | 60.72 | GGB | 170225.55 | GGB | 136663.48 | GGB | 0 | 0 | 2494 | 3600 | 2478.63 | GGB | 100 | GGB | 37.26 | GGB | 37.26 | GGB | 36400.58 | GGB | 36401.07 | 2478.63 | 2478.63 |  |  |  | 1 | 1 |  |  |  |  | 136663.48 | 2478.63 | 136663.48 | 2478.63 | 9.0912 | [5 empty] | 94.0939
17.10.2007 22:00 | 3600 | 2 | 756.59 | GGB | 765.201 | 771.398 | 766.667 | 258.69 | GGB | 10652.5 | GGB | 9.86 | GGB | 993.64 | GGB | 60.29 | GGB | 171262.07 | GGB | 137602.11 | GGB | 0 | 0 | 2465 | 3600 | 2449.55 | GGB | 100 | GGB | 37.66 | GGB | 37.66 | GGB | 36438.24 | GGB | 36438.73 | 2449.55 | 2449.55 |  |  |  | 1 | 1 |  |  |  |  | 137602.11 | 2449.55 | 137602.11 | 2449.55 | 8.9502 | [5 empty] | 93.6287
17.10.2007 23:00 | 3600 | 2 | 755.88 | GNB | 764.102 | 770.25 | 765.201 | 258.58 | GGB | 10650 | GGB | 9.85 | GGB | 993.29 | GGB | 60.53 | GGB | 170059.4 | GGB | 136488.01 | GGB | 0 | 0 | 2498 | 3600 | 2482.76 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 36476.8 | GGB | 36477.29 | 2482.76 | 2482.76 |  |  |  | 0 | 1 | [14 empty] | 94.1297
17.10.2007 24:00 | 3600 | 2 | 755.49 | GNB | 764.102 | 769.219 | 765.201 | 260.02 | GGB | 10632.4 | GGB | 9.84 | GGB | 993.03 | GGB | 60.12 | GGB | 171733.01 | GGB | 137962.83 | GGB | 0 | 0 | 2507 | 3600 | 2492.19 | GGB | 100 | GGB | 38.21 | GGB | 38.21 | GGB | 36515 | GGB | 36515.5 | 2492.19 | 2492.19 |  |  |  | 0 | 1 | [14 empty] | 95.5082
18.10.2007 01:00 | 3600 | 2 | 756.02 | GGB | 764.102 | 770.297 | 765.201 | 260.88 | GGB | 10643.3 | GGB | 9.86 | GGB | 992.43 | GGB | 59.74 | GGB | 172714.52 | GGB | 138828.09 | GGB | 0 | 0 | 2483 | 3600 | 2468.12 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 36553.11 | GGB | 36553.61 | 2468.12 | 2468.12 |  |  |  | 1 | 1 |  |  |  |  | 138828.09 | 2468.12 | 138828.09 | 2468.12 | 8.9909 | [5 empty] | 95.179
18.10.2007 02:00 | 3600 | 2 | 755.77 | GNB | 764.102 | 769.5 | 765.201 | 259.68 | GGB | 10679.3 | GGB | 9.86 | GGB | 991.82 | GGB | 60.35 | GGB | 171040.9 | GGB | 137148.03 | GGB | 0 | 0 | 2517 | 3600 | 2501.61 | GGB | 100 | GGB | 37.82 | GGB | 37.82 | GGB | 36590.93 | GGB | 36591.43 | 2501.61 | 2501.61 |  |  |  | 0 | 1 | [14 empty] | 95.303
18.10.2007 03:00 | 3600 | 2 | 755.34 | GNB | 764.102 | 769.43 | 765.201 | 260.16 | GGB | 10701 | GGB | 9.85 | GGB | 991.02 | GGB | 60.33 | GGB | 171470.03 | GGB | 137389.35 | GGB | 0 | 0 | 2548 | 3600 | 2532.29 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 36629.27 | GGB | 36629.77 | 2532.29 | 2532.29 |  |  |  | 0 | 1 | [14 empty] | 96.6416
18.10.2007 04:00 | 3600 | 2 | 755.29 | GNB | 764.102 | 769.383 | 765.201 | 260.34 | GGB | 10708 | GGB | 9.85 | GGB | 990.28 | GGB | 60.24 | GGB | 171791.33 | GGB | 137579.25 | GGB | 0 | 0 | 2555 | 3600 | 2540 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 36667.32 | GGB | 36667.82 | 2540 | 2540 |  |  |  | 0 | 1 | [14 empty] | 97.0698
18.10.2007 05:00 | 3600 | 2 | 755.47 | GNB | 764.102 | 769.406 | 765.201 | 260.42 | GGB | 10715.8 | GGB | 9.86 | GGB | 989.12 | GGB | 60.14 | GGB | 171808.94 | GGB | 137474.97 | GGB | 0 | 0 | 2551 | 3600 | 2535.49 | GGB | 100 | GGB | 37.83 | GGB | 37.83 | GGB | 36705.15 | GGB | 36705.65 | 2535.49 | 2535.49 |  |  |  | 0 | 1 | [14 empty] | 96.824
18.10.2007 06:00 | 3600 | 2 | 755.47 | GNB | 764.102 | 768.352 | 765.201 | 260.2 | GGB | 10709.8 | GGB | 9.85 | GGB | 988.39 | GGB | 59.95 | GGB | 171790.23 | GGB | 137437.99 | GGB | 0 | 0 | 2551 | 3600 | 2535.4 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 36743.58 | GGB | 36744.08 | 2535.4 | 2535.4 |  |  |  | 0 | 1 | [14 empty] | 96.7945
18.10.2007 07:00 | 3600 | 2 | 755.39 | GNB | 764.102 | 768.234 | 765.201 | 260.37 | GGB | 10712.2 | GGB | 9.85 | GGB | 987.98 | GGB | 59.72 | GGB | 171940.98 | GGB | 137594.55 | GGB | 0 | 0 | 2554 | 3600 | 2538.26 | GGB | 100 | GGB | 37.87 | GGB | 37.87 | GGB | 36781.45 | GGB | 36781.95 | 2538.26 | 2538.26 |  |  |  | 0 | 1 | [14 empty] | 97.0141
18.10.2007 08:00 | 3600 | 2 | 755.41 | GNB | 764.102 | 769.383 | 765.201 | 260.75 | GGB | 10725.4 | GGB | 9.85 | GGB | 987.75 | GGB | 59.48 | GGB | 172316.19 | GGB | 137962.32 | GGB | 0 | 0 | 2559 | 3600 | 2543.57 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 36820.03 | GGB | 36820.52 | 2543.57 | 2543.57 |  |  |  | 0 | 1 | [14 empty] | 97.4769
18.10.2007 09:00 | 3600 | 2 | 755.33 | GNB | 764.102 | 769.359 | 765.201 | 261.52 | GGB | 10706.9 | GGB | 9.85 | GGB | 987.87 | GGB | 58.84 | GGB | 173836.86 | GGB | 139465.62 | GGB | 0 | 0 | 2537 | 3600 | 2522.17 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 36858.1 | GGB | 36858.6 | 2522.17 | 2522.17 |  |  |  | 0 | 1 | [14 empty] | 97.71
18.10.2007 10:00 | 3600 | 2 | 754.93 | GNB | 764.102 | 768.258 | 764.102 | 262.05 | GGB | 10703.1 | GGB | 9.85 | GGB | 987.93 | GGB | 58.39 | GGB | 174314.41 | GGB | 140046.25 | GGB | 0 | 0 | 2543 | 3600 | 2527.74 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 36896.16 | GGB | 36896.66 | 2527.74 | 2527.74 |  |  |  | 0 | 1 | [14 empty] | 98.3335
18.10.2007 11:00 | 3600 | 2 | 755.55 | GNB | 765.201 | 770.391 | 766.3 | 261.61 | GGB | 10720.6 | GGB | 9.86 | GGB | 988.3 | GGB | 58.51 | GGB | 173601.39 | GGB | 139474.64 | GGB | 0 | 0 | 2536 | 3600 | 2520.37 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 36934.7 | GGB | 36935.2 | 2520.37 | 2520.37 |  |  |  | 0 | 1 | [14 empty] | 97.6466
18.10.2007 12:00 | 3600 | 2 | 755.38 | GNB | 764.102 | 769.383 | 765.201 | 259.59 | GGB | 10703.8 | GGB | 9.86 | GGB | 988.39 | GGB | 59.33 | GGB | 170584.26 | GGB | 136724.88 | GGB | 0 | 0 | 2550 | 3600 | 2534.4 | GGB | 100 | GGB | 38.07 | GGB | 38.07 | GGB | 36972.77 | GGB | 36973.27 | 2534.4 | 2534.4 |  |  |  | 0 | 1 | [14 empty] | 96.2543
18.10.2007 13:00 | 3600 | 2 | 754.44 | GNB | 762.637 | 767.063 | 763.004 | 260.21 | GGB | 10675 | GGB | 9.84 | GGB | 988.63 | GGB | 59.51 | GGB | 170856.04 | GGB | 136902.64 | GGB | 0 | 0 | 2583 | 3600 | 2567.41 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 37011.13 | GGB | 37011.63 | 2567.41 | 2567.41 |  |  |  | 0 | 1 | [14 empty] | 97.6348
18.10.2007 14:00 | 3600 | 2 | 754.81 | GNB | 763.004 | 769.148 | 764.102 | 263.37 | GGB | 10721.6 | GGB | 9.85 | GGB | 989.62 | GGB | 58.24 | GGB | 175095.65 | GGB | 140980.85 | GGB | 0 | 0 | 2578 | 3600 | 2562.23 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 37049.44 | GGB | 37049.94 | 2562.23 | 2562.23 |  |  |  | 0 | 1 | [14 empty] | 100.3404
18.10.2007 15:00 | 3600 | 2 | 755.72 | GNB | 764.102 | 769.383 | 765.201 | 262.58 | GGB | 10746 | GGB | 9.86 | GGB | 990.51 | GGB | 58.28 | GGB | 174407.93 | GGB | 140534.44 | GGB | 0 | 0 | 2540 | 3600 | 2525.14 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 37087.48 | GGB | 37087.98 | 2525.14 | 2525.14 |  |  |  | 0 | 1 | [14 empty] | 98.5748
18.10.2007 16:00 | 3600 | 2 | 755.69 | GNB | 764.102 | 769.289 | 765.201 | 260.63 | GGB | 10749.1 | GGB | 9.86 | GGB | 990.98 | GGB | 58.84 | GGB | 171981.69 | GGB | 138412.76 | GGB | 0 | 0 | 2542 | 3600 | 2526.88 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 37125.84 | GGB | 37126.34 | 2526.88 | 2526.88 |  |  |  | 0 | 1 | [14 empty] | 97.1535
18.10.2007 17:00 | 3600 | 2 | 755.43 | GNB | 763.004 | 768.211 | 764.102 | 260.72 | GGB | 10724.6 | GGB | 9.85 | GGB | 991.68 | GGB | 58.9 | GGB | 172210.56 | GGB | 138669.84 | GGB | 0 | 0 | 2541 | 3600 | 2525.24 | GGB | 100 | GGB | 37.92 | GGB | 37.92 | GGB | 37163.76 | GGB | 37164.26 | 2525.24 | 2525.24 |  |  |  | 0 | 1 | [14 empty] | 97.2707
18.10.2007 18:00 | 3600 | 2 | 755.81 | GNB | 764.102 | 769.547 | 765.201 | 261.07 | GGB | 10732.1 | GGB | 9.85 | GGB | 991.66 | GGB | 58.83 | GGB | 172452.63 | GGB | 138888.79 | GGB | 0 | 0 | 2531 | 3600 | 2515.76 | GGB | 100 | GGB | 38.21 | GGB | 38.21 | GGB | 37201.97 | GGB | 37202.47 | 2515.76 | 2515.76 |  |  |  | 0 | 1 | [14 empty] | 97.0586
18.10.2007 19:00 | 3600 | 2 | 755.33 | GNB | 764.102 | 769.5 | 765.201 | 263.31 | GGB | 10723.8 | GGB | 9.84 | GGB | 992.57 | GGB | 58.11 | GGB | 175076.94 | GGB | 141440.02 | GGB | 0 | 0 | 2547 | 3600 | 2531.93 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 37240.16 | GGB | 37240.66 | 2531.93 | 2531.93 |  |  |  | 0 | 1 | [14 empty] | 99.4767
18.10.2007 20:00 | 3600 | 2 | 755.14 | GNB | 765.201 | 770.484 | 766.3 | 263.94 | GGB | 10805 | GGB | 9.85 | GGB | 993.67 | GGB | 57.1 | GGB | 176541.49 | GGB | 143219.72 | GGB | 0 | 0 | 2584 | 3600 | 2569.13 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 37278.34 | GGB | 37278.84 | 2569.13 | 2569.13 |  |  |  | 0 | 1 | [14 empty] | 102.2084
18.10.2007 21:00 | 3600 | 2 | 755.12 | GNB | 763.004 | 768.352 | 764.102 | 263.87 | GGB | 10837.7 | GGB | 9.85 | GGB | 994.58 | GGB | 58.23 | GGB | 174754.54 | GGB | 141415.62 | GGB | 0 | 0 | 2623 | 3600 | 2607.57 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 37317.6 | GGB | 37318.1 | 2607.57 | 2607.57 |  |  |  | 0 | 1 | [14 empty] | 102.4309
18.10.2007 22:00 | 3600 | 2 | 754.91 | GNB | 763.004 | 769.453 | 764.102 | 266.19 | GGB | 10819.9 | GGB | 9.84 | GGB | 995.11 | GGB | 57.63 | GGB | 177474.58 | GGB | 143950.01 | GGB | 0 | 0 | 2624 | 3600 | 2608.6 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 37356.26 | GGB | 37356.76 | 2608.6 | 2608.6 |  |  |  | 0 | 1 | [14 empty] | 104.3078
18.10.2007 23:00 | 3600 | 2 | 755.92 | GNB | 764.102 | 768.539 | 765.201 | 265.7 | GGB | 10866.3 | GGB | 9.86 | GGB | 995.72 | GGB | 57.45 | GGB | 177195.09 | GGB | 143891.63 | GGB | 0 | 0 | 2599 | 3600 | 2583.6 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 37394.34 | GGB | 37394.84 | 2583.6 | 2583.6 |  |  |  | 0 | 1 | [14 empty] | 103.2662
18.10.2007 24:00 | 3600 | 2 | 755.15 | GNB | 763.004 | 768.539 | 764.102 | 264.9 | GGB | 10895.9 | GGB | 9.85 | GGB | 995.94 | GGB | 57.85 | GGB | 176255.4 | GGB | 142986.72 | GGB | 0 | 0 | 2643 | 3600 | 2627.5 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 37433.72 | GGB | 37434.22 | 2627.5 | 2627.5 |  |  |  | 0 | 1 | [14 empty] | 104.3604
19.10.2007 01:00 | 3600 | 2 | 754.68 | GNB | 763.004 | 767.203 | 764.102 | 266.02 | GGB | 10930.4 | GGB | 9.84 | GGB | 996.34 | GGB | 57.56 | GGB | 177659.43 | GGB | 144312.33 | GGB | 0 | 0 | 2682 | 3600 | 2666.9 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 37472.3 | GGB | 37472.8 | 2666.9 | 2666.9 |  |  |  | 0 | 1 | [14 empty] | 106.9074 | 2618.8199
19.10.2007 02:00 | 3600 | 2 | 754.04 | GNB | 761.538 | 767.203 | 762.637 | 268.25 | GGB | 10936.5 | GGB | 9.83 | GGB | 997 | GGB | 56.97 | GGB | 180464.19 | GGB | 146947.27 | GGB | 0 | 0 | 2716 | 3600 | 2700.75 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 37511.42 | GGB | 37511.92 | 2700.75 | 2700.75 |  |  |  | 0 | 1 | [14 empty] | 110.2411 | 2571.8613
19.10.2007 03:00 | 3600 | 2 | 755.49 | GNB | 762.637 | 768.398 | 763.004 | 268.46 | GGB | 11041.1 | GGB | 9.86 | GGB | 997.36 | GGB | 56.35 | GGB | 180947.24 | GGB | 147672.78 | GGB | 0 | 0 | 2681 | 3600 | 2665.25 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 37550.58 | GGB | 37551.08 | 2665.25 | 2665.25 |  |  |  | 0 | 1 | [14 empty] | 109.3291 | 2559.2259
19.10.2007 04:00 | 3600 | 2 | 754.42 | GNB | 763.004 | 768.258 | 764.102 | 270.44 | GGB | 11034.4 | GGB | 9.84 | GGB | 997.86 | GGB | 55.63 | GGB | 183723.39 | GGB | 150342.38 | GGB | 0 | 0 | 2728 | 3600 | 2712.21 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 37589.53 | GGB | 37590.03 | 2712.21 | 2712.21 |  |  |  | 0 | 1 | [14 empty] | 113.2667 | 2513.7822
19.10.2007 05:00 | 3600 | 2 | 755.21 | GNB | 762.637 | 767.109 | 763.004 | 270.35 | GGB | 11113.7 | GGB | 9.86 | GGB | 998.3 | GGB | 55.69 | GGB | 183586.95 | GGB | 150270.59 | GGB | 0 | 0 | 2719 | 3600 | 2703.58 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 37629.23 | GGB | 37629.73 | 2703.58 | 2703.58 |  |  |  | 0 | 1 | [14 empty] | 112.8524 | 2514.9831
19.10.2007 06:00 | 3600 | 2 | 755.99 | GNB | 762.637 | 767.602 | 764.102 | 269.6 | GGB | 11057.6 | GGB | 9.87 | GGB | 999.19 | GGB | 55.71 | GGB | 183004.87 | GGB | 149916.31 | GGB | 0 | 0 | 2659 | 3600 | 2643.46 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 37668.37 | GGB | 37668.87 | 2643.46 | 2643.46 |  |  |  | 0 | 1 | [14 empty] | 110.0827 | 2520.9265
19.10.2007 07:00 | 3600 | 2 | 756.6 | GGB | 765.201 | 769.805 | 766.3 | 269.07 | GGB | 11016.7 | GGB | 9.87 | GGB | 999.56 | GGB | 56.3 | GGB | 181483.11 | GGB | 148457.6 | GGB | 0 | 0 | 2603 | 3600 | 2587.25 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 37706.99 | GGB | 37707.49 | 2587.25 | 2587.25 |  |  |  | 1 | 1 |  |  |  |  | 148457.6 | 2587.25 | 148457.6 | 2587.25 | 9.9455 | [5 empty] | 106.6936 | 2545.6965
19.10.2007 08:00 | 3600 | 2 | 756.49 | GGB | 765.201 | 770.109 | 766.667 | 266.7 | GGB | 10965.7 | GGB | 9.87 | GGB | 1000.12 | GGB | 57.2 | GGB | 178757.57 | GGB | 145910.83 | GGB | 0 | 0 | 2577 | 3600 | 2561.38 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 37746.52 | GGB | 37747.02 | 2561.38 | 2561.38 |  |  |  | 1 | 1 |  |  |  |  | 145910.83 | 2561.38 | 145910.83 | 2561.38 | 9.4544 | [5 empty] | 103.8147
19.10.2007 09:00 | 3600 | 2 | 756.51 | GGB | 764.102 | 768.82 | 765.201 | 265.7 | GGB | 10879.9 | GGB | 9.86 | GGB | 1001.07 | GGB | 56.76 | GGB | 178712.46 | GGB | 146209.68 | GGB | 0 | 0 | 2526 | 3207 | 2511.03 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 37785.45 | GGB | 37785.95 | 2511.03 | 2511.03 |  |  |  | 1 | 1 |  |  |  |  | 146209.68 | 2511.03 | 146209.68 | 2511.03 | 9.4307 | [5 empty] | 101.9825
19.10.2007 10:00 | 3600 | 2 | 756.93 | GGB | 765.201 | 769.758 | 766.3 | 263.27 | GGB | 10876.2 | GGB | 9.87 | GGB | 1009.44 | GGB | 56.97 | GGB | 174412.34 | GGB | 143792.64 | GGB | 0 | 0 | 2520 | 2526 | 2504.76 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 37824.42 | GGB | 37824.92 | 2504.76 | 2504.76 |  |  |  | 1 | 1 |  |  |  |  | 143792.64 | 2504.76 | 143792.64 | 2504.76 | 9.2421 | [5 empty] | 100.0461
19.10.2007 11:00 | 3600 | 2 | 756.74 | GGB | 766.3 | 771.891 | 766.667 | 262.94 | GGB | 10809.2 | GGB | 9.85 | GGB | 1014.41 | GGB | 57.77 | GGB | 175341.02 | GGB | 144920.49 | GGB | 0 | 0 | 2495 | 3600 | 2479.8 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 37863.46 | GGB | 37863.95 | 2479.8 | 2479.8 |  |  |  | 1 | 1 |  |  |  |  | 144920.49 | 2479.8 | 144920.49 | 2479.8 | 9.2076 | [5 empty] | 99.8261
19.10.2007 12:00 | 3600 | 2 | 757.2 | GGB | 766.3 | 771.094 | 767.766 | 263.86 | GGB | 10746.7 | GGB | 9.86 | GGB | 1014.78 | GGB | 58.07 | GGB | 174526.77 | GGB | 144170.04 | GGB | 0 | 0 | 2457 | 3600 | 2442.07 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 37901.65 | GGB | 37902.15 | 2442.07 | 2442.07 |  |  |  | 1 | 1 |  |  |  |  | 144170.04 | 2442.07 | 144170.04 | 2442.07 | 9.2166 | [5 empty] | 97.7981
19.10.2007 13:00 | 3600 | 2 | 757.93 | GGB | 766.3 | 771.328 | 767.766 | 261.12 | GGB | 10687.2 | GGB | 9.87 | GGB | 1014.58 | GGB | 59.61 | GGB | 169783.22 | GGB | 139573.46 | GGB | 0 | 0 | 2418 | 3600 | 2403.09 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 37940.03 | GGB | 37940.53 | 2403.09 | 2403.09 |  |  |  | 1 | 1 |  |  |  |  | 139573.46 | 2403.09 | 139573.46 | 2403.09 | 8.7391 | [5 empty] | 93.1688
19.10.2007 14:00 | 3600 | 2 | 757.63 | GGB | 765.201 | 770.25 | 766.667 | 261.08 | GGB | 10610.9 | GGB | 9.86 | GGB | 1014.88 | GGB | 59.94 | GGB | 169526.84 | GGB | 139266.04 | GGB | 0 | 0 | 2400 | 3600 | 2385 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 37977.89 | GGB | 37978.39 | 2385 | 2385 |  |  |  | 1 | 1 |  |  |  |  | 139266.04 | 2385 | 139266.04 | 2385 | 8.7731 | [5 empty] | 92.2638
19.10.2007 15:00 | 3600 | 2 | 757.67 | GGB | 766.3 | 771.234 | 767.766 | 261.56 | GGB | 10595.3 | GGB | 9.85 | GGB | 1014.88 | GGB | 59.47 | GGB | 171101.42 | GGB | 140758.51 | GGB | 0 | 0 | 2383 | 3600 | 2368.04 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 38016 | GGB | 38016.5 | 2368.04 | 2368.04 |  |  |  | 1 | 1 |  |  |  |  | 140758.51 | 2368.04 | 140758.51 | 2368.04 | 8.7463 | [5 empty] | 92.5894
19.10.2007 16:00 | 3600 | 2 | 758.06 | GGB | 765.201 | 769.969 | 765.201 | 259.33 | GGB | 10603.7 | GGB | 9.86 | GGB | 1015.05 | GGB | 60.17 | GGB | 168883.14 | GGB | 138664.16 | GGB | 0 | 0 | 2366 | 3600 | 2351.35 | GGB | 100 | GGB | 37.8 | GGB | 37.8 | GGB | 38053.8 | GGB | 38054.3 | 2351.35 | 2351.35 |  |  |  | 1 | 1 |  |  |  |  | 138664.16 | 2351.35 | 138664.16 | 2351.35 | 8.6256 | [5 empty] | 90.5689
19.10.2007 17:00 | 3600 | 2 | 757.67 | GGB | 764.102 | 770.063 | 765.201 | 259.04 | GGB | 10600.8 | GGB | 9.85 | GGB | 1015.47 | GGB | 60.63 | GGB | 168668.57 | GGB | 138352.07 | GGB | 0 | 0 | 2391 | 3600 | 2375.57 | GGB | 100 | GGB | 37.83 | GGB | 37.83 | GGB | 38091.63 | GGB | 38092.13 | 2375.57 | 2375.57 |  |  |  | 1 | 1 |  |  |  |  | 138352.07 | 2375.57 | 138352.07 | 2375.57 | 8.6879 | [5 empty] | 91.2958
19.10.2007 18:00 | 3600 | 2 | 757.47 | GGB | 765.201 | 771.023 | 766.667 | 261.11 | GGB | 10614.8 | GGB | 9.85 | GGB | 1016.22 | GGB | 59.72 | GGB | 171560.26 | GGB | 141215.12 | GGB | 0 | 0 | 2404 | 3600 | 2388.44 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 38129.75 | GGB | 38130.26 | 2388.44 | 2388.44 |  |  |  | 1 | 1 |  |  |  |  | 141215.12 | 2388.44 | 141215.12 | 2388.44 | 8.8456 | [5 empty] | 93.69
19.10.2007 19:00 | 3600 | 2 | 757.75 | GGB | 765.201 | 770.953 | 766.667 | 259.43 | GGB | 10661.4 | GGB | 9.86 | GGB | 1017.1 | GGB | 59.78 | GGB | 169806.32 | GGB | 139865.68 | GGB | 0 | 0 | 2400 | 3600 | 2384.62 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 38167.75 | GGB | 38168.26 | 2384.62 | 2384.62 |  |  |  | 1 | 1 |  |  |  |  | 139865.68 | 2384.62 | 139865.68 | 2384.62 | 8.777 | [5 empty] | 92.6462
19.10.2007 20:00 | 3600 | 2 | 757.26 | GGB | 765.201 | 770.906 | 767.033 | 261.88 | GGB | 10673.8 | GGB | 9.85 | GGB | 1018.07 | GGB | 58.89 | GGB | 173065.52 | GGB | 143068.21 | GGB | 0 | 0 | 2423 | 3600 | 2408.3 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 38205.95 | GGB | 38206.46 | 2408.3 | 2408.3 |  |  |  | 1 | 1 |  |  |  |  | 143068.21 | 2408.3 | 143068.21 | 2408.3 | 9.0197 | [5 empty] | 95.7087
19.10.2007 21:00 | 3600 | 2 | 757 | GGB | 766.3 | 770.602 | 767.033 | 260.6 | GGB | 10756.9 | GGB | 9.86 | GGB | 1018.53 | GGB | 58.59 | GGB | 172986.3 | GGB | 143197.98 | GGB | 0 | 0 | 2460 | 3600 | 2444.68 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 38244.25 | GGB | 38244.76 | 2444.68 | 2444.68 |  |  |  | 1 | 1 |  |  |  |  | 143197.98 | 2444.68 | 143197.98 | 2444.68 | 9.1403 | [5 empty] | 97.2426
19.10.2007 22:00 | 3600 | 2 | 756.76 | GGB | 765.201 | 770.508 | 765.934 | 262.48 | GGB | 10777.8 | GGB | 9.84 | GGB | 1019.25 | GGB | 58.41 | GGB | 174273.69 | GGB | 144444.42 | GGB | 0 | 0 | 2491 | 3600 | 2475.75 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 38283.42 | GGB | 38283.92 | 2475.75 | 2475.75 |  |  |  | 1 | 1 |  |  |  |  | 144444.42 | 2475.75 | 144444.42 | 2475.75 | 9.132 | [5 empty] | 99.3356
19.10.2007 23:00 | 3600 | 2 | 756.97 | GGB | 766.3 | 771.609 | 768.132 | 263.79 | GGB | 10818.9 | GGB | 9.85 | GGB | 1019.86 | GGB | 58.07 | GGB | 176274.11 | GGB | 146340.05 | GGB | 0 | 0 | 2494 | 3600 | 2478.92 | GGB | 100 | GGB | 37.7 | GGB | 37.7 | GGB | 38321.11 | GGB | 38321.62 | 2478.92 | 2478.92 |  |  |  | 1 | 1 |  |  |  |  | 146340.05 | 2478.92 | 146340.05 | 2478.92 | 9.6224 | [5 empty] | 100.7681
19.10.2007 24:00 | 3600 | 2 | 756.65 | GGB | 764.102 | 769.5 | 765.934 | 263.63 | GGB | 10880.8 | GGB | 9.85 | GGB | 1020.44 | GGB | 58.35 | GGB | 176004.53 | GGB | 146077.15 | GGB | 0 | 0 | 2539 | 3600 | 2524.13 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 38360.36 | GGB | 38360.86 | 2524.13 | 2524.13 |  |  |  | 1 | 1 |  |  |  |  | 146077.15 | 2524.13 | 146077.15 | 2524.13 | 9.3965 | [5 empty] | 102.4216
20.10.2007 01:00 | 3600 | 2 | 757.27 | GGB | 765.201 | 770.555 | 766.3 | 264.79 | GGB | 10897 | GGB | 9.86 | GGB | 1020.73 | GGB | 57.95 | GGB | 177958.72 | GGB | 147918.67 | GGB | 0 | 0 | 2519 | 3600 | 2503.49 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 38399.05 | GGB | 38399.56 | 2503.49 | 2503.49 |  |  |  | 1 | 1 |  |  |  |  | 147918.67 | 2503.49 | 147918.67 | 2503.49 | 9.5688 | [5 empty] | 102.8647
20.10.2007 02:00 | 3600 | 2 | 756.53 | GGB | 764.102 | 768.422 | 764.102 | 264.15 | GGB | 10886.6 | GGB | 9.84 | GGB | 1020.33 | GGB | 57.68 | GGB | 177586.81 | GGB | 147672.03 | GGB | 0 | 0 | 2550 | 3600 | 2534.46 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 38438.42 | GGB | 38438.93 | 2534.46 | 2534.46 |  |  |  | 1 | 1 |  |  |  |  | 147672.03 | 2534.46 | 147672.03 | 2534.46 | 9.5064 | [5 empty] | 103.9636
20.10.2007 03:00 | 3600 | 2 | 757.22 | GGB | 766.667 | 772.688 | 767.033 | 264.74 | GGB | 10919.7 | GGB | 9.87 | GGB | 1020.2 | GGB | 57.22 | GGB | 178588.12 | GGB | 148694.71 | GGB | 0 | 0 | 2523 | 3600 | 2508.06 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 38476.97 | GGB | 38477.48 | 2508.06 | 2508.06 |  |  |  | 1 | 1 |  |  |  |  | 148694.71 | 2508.06 | 148694.71 | 2508.06 | 9.6741 | [5 empty] | 103.5931
20.10.2007 04:00 | 3600 | 2 | 756.49 | GGB | 764.102 | 769.266 | 765.201 | 263.4 | GGB | 10923 | GGB | 9.85 | GGB | 1020 | GGB | 57.96 | GGB | 176894.7 | GGB | 146921.55 | GGB | 0 | 0 | 2569 | 3600 | 2553.24 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 38516.5 | GGB | 38517.01 | 2553.24 | 2553.24 |  |  |  | 1 | 1 |  |  |  |  | 146921.55 | 2553.24 | 146921.55 | 2553.24 | 9.4897 | [5 empty] | 104.2017
20.10.2007 05:00 | 3600 | 2 | 756.88 | GGB | 765.201 | 770.414 | 766.667 | 263.18 | GGB | 10933.6 | GGB | 9.86 | GGB | 1020.25 | GGB | 58.05 | GGB | 176661.43 | GGB | 146727.95 | GGB | 0 | 0 | 2555 | 3600 | 2539.79 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 38555.3 | GGB | 38555.81 | 2539.79 | 2539.79 |  |  |  | 1 | 1 |  |  |  |  | 146727.95 | 2539.79 | 146727.95 | 2539.79 | 9.6046 | [5 empty] | 103.5162
20.10.2007 06:00 | 3600 | 2 | 756.72 | GGB | 764.102 | 769.336 | 765.201 | 263.09 | GGB | 10898.6 | GGB | 9.85 | GGB | 1020.29 | GGB | 58.12 | GGB | 176154.17 | GGB | 146279.52 | GGB | 0 | 0 | 2555 | 3600 | 2539.61 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 38594.46 | GGB | 38594.97 | 2539.61 | 2539.61 |  |  |  | 1 | 1 |  |  |  |  | 146279.52 | 2539.61 | 146279.52 | 2539.61 | 9.4865 | [5 empty] | 103.1925
20.10.2007 07:00 | 3600 | 2 | 757.09 | GGB | 764.102 | 769.453 | 765.201 | 264.11 | GGB | 10855.4 | GGB | 9.85 | GGB | 1020.4 | GGB | 57.71 | GGB | 177749.66 | GGB | 147806.23 | GGB | 0 | 0 | 2514 | 3600 | 2498.94 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 38633.43 | GGB | 38633.93 | 2498.94 | 2498.94 |  |  |  | 1 | 1 |  |  |  |  | 147806.23 | 2498.94 | 147806.23 | 2498.94 | 9.4805 | [5 empty] | 102.5997
20.10.2007 08:00 | 3600 | 2 | 757.11 | GGB | 764.102 | 769.5 | 766.3 | 263.6 | GGB | 10902.3 | GGB | 9.86 | GGB | 1020.75 | GGB | 57.88 | GGB | 176838.58 | GGB | 147018.91 | GGB | 0 | 0 | 2534 | 3600 | 2518.36 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 38671.73 | GGB | 38672.23 | 2518.36 | 2518.36 |  |  |  | 1 | 1 |  |  |  |  | 147018.91 | 2518.36 | 147018.91 | 2518.36 | 9.667 | [5 empty] | 102.8463
20.10.2007 09:00 | 3600 | 2 | 756.56 | GGB | 767.766 | 771.633 | 767.766 | 264.94 | GGB | 10920 | GGB | 9.85 | GGB | 1021.19 | GGB | 57.55 | GGB | 178401.06 | GGB | 148534.41 | GGB | 0 | 0 | 2567 | 3600 | 2551.23 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 38710.87 | GGB | 38711.38 | 2551.23 | 2551.23 |  |  |  | 1 | 1 |  |  |  |  | 148534.41 | 2551.23 | 148534.41 | 2551.23 | 9.6793 | [5 empty] | 105.2626 | 2544.3801
20.10.2007 10:00 | 3600 | 2 | 757.23 | GGB | 767.766 | 771.891 | 767.766 | 264.88 | GGB | 10923.7 | GGB | 9.86 | GGB | 1021.61 | GGB | 57.48 | GGB | 178439.57 | GGB | 148654.76 | GGB | 0 | 0 | 2539 | 3600 | 2524.08 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 38750.25 | GGB | 38750.75 | 2524.08 | 2524.08 |  |  |  | 1 | 1 |  |  |  |  | 148654.76 | 2524.08 | 148654.76 | 2524.08 | 9.5305 | [5 empty] | 104.2268
20.10.2007 11:00 | 3600 | 2 | 757.31 | GGB | 765.201 | 769.992 | 766.667 | 264.89 | GGB | 10897.6 | GGB | 9.86 | GGB | 1021.94 | GGB | 57.14 | GGB | 178679.45 | GGB | 149058.55 | GGB | 0 | 0 | 2514 | 3600 | 2498.26 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 38788.63 | GGB | 38789.13 | 2498.26 | 2498.26 |  |  |  | 1 | 1 |  |  |  |  | 149058.55 | 2498.26 | 149058.55 | 2498.26 | 9.7026 | [5 empty] | 103.4408
20.10.2007 12:00 | 3600 | 2 | 757.21 | GGB | 766.3 | 771.352 | 766.667 | 263.08 | GGB | 10907.8 | GGB | 9.86 | GGB | 1021.84 | GGB | 57.88 | GGB | 176204.79 | GGB | 146650 | GGB | 0 | 0 | 2523 | 3600 | 2507.88 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 38828.14 | GGB | 38828.64 | 2507.88 | 2507.88 |  |  |  | 1 | 1 |  |  |  |  | 146650 | 2507.88 | 146650 | 2507.88 | 9.3085 | [5 empty] | 102.1613
20.10.2007 13:00 | 3600 | 2 | 757.48 | GGB | 766.3 | 772.008 | 766.667 | 262.91 | GGB | 10839.2 | GGB | 9.86 | GGB | 1021.58 | GGB | 58.01 | GGB | 176115.66 | GGB | 146479.45 | GGB | 0 | 0 | 2472 | 3600 | 2456.43 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 38866.87 | GGB | 38867.37 | 2456.43 | 2456.43 |  |  |  | 1 | 1 |  |  |  |  | 146479.45 | 2456.43 | 146479.45 | 2456.43 | 9.2904 | [5 empty] | 99.949
20.10.2007 14:00 | 3600 | 2 | 757.82 | GGB | 766.667 | 772.195 | 767.766 | 262.52 | GGB | 10809.7 | GGB | 9.86 | GGB | 1021.34 | GGB | 57.79 | GGB | 176071.65 | GGB | 146506.45 | GGB | 0 | 0 | 2430 | 3600 | 2414.57 | GGB | 100 | GGB | 38.02 | GGB | 38.02 | GGB | 38904.88 | GGB | 38905.39 | 2414.57 | 2414.57 |  |  |  | 1 | 1 |  |  |  |  | 146506.45 | 2414.57 | 146506.45 | 2414.57 | 9.3043 | [5 empty] | 98.2639
20.10.2007 15:00 | 3600 | 2 | 757.78 | GGB | 765.201 | 770.297 | 766.667 | 261.1 | GGB | 10800.3 | GGB | 9.86 | GGB | 1020.72 | GGB | 58.4 | GGB | 174545.48 | GGB | 144880.41 | GGB | 0 | 0 | 2428 | 3600 | 2413.29 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 38944.31 | GGB | 38944.81 | 2413.29 | 2413.29 |  |  |  | 1 | 1 |  |  |  |  | 144880.41 | 2413.29 | 144880.41 | 2413.29 | 8.8696 | [5 empty] | 97.1218
20.10.2007 16:00 | 3600 | 2 | 757.91 | GGB | 766.667 | 771.375 | 767.766 | 262.61 | GGB | 10795.9 | GGB | 9.86 | GGB | 1020.41 | GGB | 57.79 | GGB | 176846.28 | GGB | 147018.19 | GGB | 0 | 0 | 2416 | 3600 | 2400.57 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 38982.3 | GGB | 38982.8 | 2400.57 | 2400.57 |  |  |  | 1 | 1 |  |  |  |  | 147018.19 | 2400.57 | 147018.19 | 2400.57 | 9.29 | [5 empty] | 98.0354
20.10.2007 17:00 | 3600 | 2 | 757.55 | GGB | 765.201 | 771.07 | 766.3 | 261.89 | GGB | 10855.7 | GGB | 9.85 | GGB | 1020.46 | GGB | 58 | GGB | 175732.74 | GGB | 146009.27 | GGB | 0 | 0 | 2465 | 3600 | 2450.29 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 39021.11 | GGB | 39021.61 | 2450.29 | 2450.29 |  |  |  | 1 | 1 |  |  |  |  | 146009.27 | 2450.29 | 146009.27 | 2450.29 | 9.2184 | [5 empty] | 99.3792
20.10.2007 18:00 | 3600 | 2 | 757 | GGB | 766.3 | 771 | 767.766 | 263.17 | GGB | 10891.7 | GGB | 9.85 | GGB | 1021.19 | GGB | 57.84 | GGB | 176940.91 | GGB | 147187.76 | GGB | 0 | 0 | 2513 | 3600 | 2497.61 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 39060.01 | GGB | 39060.51 | 2497.61 | 2497.61 |  |  |  | 1 | 1 |  |  |  |  | 147187.76 | 2497.61 | 147187.76 | 2497.61 | 9.4503 | [5 empty] | 102.116
20.10.2007 19:00 | 3600 | 2 | 756.68 | GGB | 766.3 | 770.953 | 766.3 | 265.36 | GGB | 10891.9 | GGB | 9.84 | GGB | 1022.36 | GGB | 57.05 | GGB | 179850.21 | GGB | 150138.48 | GGB | 0 | 0 | 2519 | 3600 | 2504.03 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 39099.08 | GGB | 39099.58 | 2504.03 | 2504.03 |  |  |  | 1 | 1 |  |  |  |  | 150138.48 | 2504.03 | 150138.48 | 2504.03 | 9.6225 | [5 empty] | 104.4309
20.10.2007 20:00 | 3600 | 2 | 756.8 | GGB | 765.201 | 769.805 | 766.3 | 264.8 | GGB | 10959 | GGB | 9.85 | GGB | 1022.78 | GGB | 57.41 | GGB | 178374.65 | GGB | 148805.25 | GGB | 0 | 0 | 2551 | 3600 | 2536.15 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 39138.17 | GGB | 39138.68 | 2536.15 | 2536.15 |  |  |  | 1 | 1 |  |  |  |  | 148805.25 | 2536.15 | 148805.25 | 2536.15 | 9.652 | [5 empty] | 104.8312
20.10.2007 21:00 | 3600 | 2 | 756.24 | GGB | 764.102 | 769.781 | 766.3 | 267.11 | GGB | 10964.7 | GGB | 9.84 | GGB | 1023.33 | GGB | 56.26 | GGB | 181505.11 | GGB | 152028.92 | GGB | 0 | 0 | 2581 | 3600 | 2565.4 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 39177.19 | GGB | 39177.69 | 2565.4 | 2565.4 |  |  |  | 1 | 1 |  |  |  |  | 152028.92 | 2565.4 | 152028.92 | 2565.4 | 9.9978 | [5 empty] | 108.3375 | 2485.8954
20.10.2007 22:00 | 3600 | 2 | 756.94 | GGB | 765.201 | 769.734 | 766.3 | 265.67 | GGB | 11035.2 | GGB | 9.87 | GGB | 1023.06 | GGB | 56.38 | GGB | 180257.33 | GGB | 150884.3 | GGB | 0 | 0 | 2583 | 3600 | 2568.05 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 39216.91 | GGB | 39217.42 | 2568.05 | 2568.05 |  |  |  | 1 | 1 |  |  |  |  | 150884.3 | 2568.05 | 150884.3 | 2568.05 | 9.7528 | [5 empty] | 107.6329 | 2504.7536
20.10.2007 23:00 | 3600 | 2 | 756.49 | GGB | 765.201 | 769.688 | 766.3 | 265.54 | GGB | 10953.9 | GGB | 9.86 | GGB | 1023.38 | GGB | 56.4 | GGB | 179462.89 | GGB | 150257.9 | GGB | 0 | 0 | 2577 | 3600 | 2561.99 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 39256.06 | GGB | 39256.56 | 2561.99 | 2561.99 |  |  |  | 1 | 1 |  |  |  |  | 150257.9 | 2561.99 | 150257.9 | 2561.99 | 9.8354 | [5 empty] | 106.9331 | 2515.1955
20.10.2007 24:00 | 3600 | 2 | 756.93 | GGB | 765.201 | 769.711 | 765.201 | 265.28 | GGB | 10962.2 | GGB | 9.86 | GGB | 1023.55 | GGB | 56.68 | GGB | 178566.11 | GGB | 149406.91 | GGB | 0 | 0 | 2574 | 3600 | 2558.54 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 39294.78 | GGB | 39295.29 | 2558.54 | 2558.54 |  |  |  | 1 | 1 |  |  |  |  | 149406.91 | 2558.54 | 149406.91 | 2558.54 | 9.87 | [5 empty] | 106.1843 | 2529.5216
21.10.2007 01:00 | 3600 | 2 | 756.3 | GGB | 764.102 | 768.492 | 764.102 | 264.98 | GGB | 10927.3 | GGB | 9.85 | GGB | 1023.63 | GGB | 57.23 | GGB | 178201.9 | GGB | 148867.28 | GGB | 0 | 0 | 2598 | 3600 | 2582.58 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 39334.97 | GGB | 39335.48 | 2582.58 | 2582.58 |  |  |  | 1 | 1 |  |  |  |  | 148867.28 | 2582.58 | 148867.28 | 2582.58 | 9.5661 | [5 empty] | 106.7949 | 2538.6908
21.10.2007 02:00 | 3600 | 2 | 756.47 | GGB | 763.004 | 767.648 | 764.102 | 265.29 | GGB | 10954.8 | GGB | 9.86 | GGB | 1024 | GGB | 57.24 | GGB | 178451.68 | GGB | 149120.78 | GGB | 0 | 0 | 2598 | 3600 | 2582.49 | GGB | 100 | GGB | 38.07 | GGB | 38.07 | GGB | 39373.04 | GGB | 39373.55 | 2582.49 | 2582.49 |  |  |  | 0 | 1 | [14 empty] | 106.973 | 2534.3752
21.10.2007 03:00 | 3600 | 2 | 756.47 | GGB | 765.201 | 770.742 | 766.667 | 266.63 | GGB | 10944.1 | GGB | 9.85 | GGB | 1024.67 | GGB | 56.61 | GGB | 179763.28 | GGB | 150603.87 | GGB | 0 | 0 | 2597 | 3600 | 2581.57 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 39412.86 | GGB | 39413.37 | 2581.57 | 2581.57 |  |  |  | 1 | 1 |  |  |  |  | 150603.87 | 2581.57 | 150603.87 | 2581.57 | 9.7638 | [5 empty] | 107.9985 | 2509.4176
21.10.2007 04:00 | 3600 | 2 | 756.89 | GGB | 764.102 | 768.68 | 765.201 | 264.69 | GGB | 10962.2 | GGB | 9.86 | GGB | 1024.72 | GGB | 57.38 | GGB | 177412.96 | GGB | 148297.17 | GGB | 0 | 0 | 2591 | 3600 | 2575.91 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 39452.07 | GGB | 39452.58 | 2575.91 | 2575.91 |  |  |  | 1 | 1 |  |  |  |  | 148297.17 | 2575.91 | 148297.17 | 2575.91 | 9.7424 | [5 empty] | 106.1112 | 2548.4505
21.10.2007 05:00 | 3600 | 2 | 756.1 | GGB | 765.201 | 769.898 | 766.3 | 265.78 | GGB | 10927.7 | GGB | 9.85 | GGB | 1024.9 | GGB | 57.22 | GGB | 178556.21 | GGB | 149351.85 | GGB | 0 | 0 | 2611 | 3600 | 2595.7 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 39490.8 | GGB | 39491.31 | 2595.7 | 2595.7 |  |  |  | 1 | 1 |  |  |  |  | 149351.85 | 2595.7 | 149351.85 | 2595.7 | 10.0096 | [5 empty] | 107.6868 | 2530.4541
21.10.2007 06:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 770.977 | 766.667 | 265.77 | GGB | 10956.4 | GGB | 9.87 | GGB | 1025.08 | GGB | 57.25 | GGB | 178447.27 | GGB | 149272.76 | GGB | 0 | 0 | 2581 | 3600 | 2565.26 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 39530.35 | GGB | 39530.87 | 2565.26 | 2565.26 |  |  |  | 1 | 1 |  |  |  |  | 149272.76 | 2565.26 | 149272.76 | 2565.26 | 9.6796 | [5 empty] | 106.3676 | 2531.7948
21.10.2007 07:00 | 3600 | 2 | 755.95 | GNB | 763.004 | 767.789 | 764.102 | 265.3 | GGB | 10927.5 | GGB | 9.84 | GGB | 1025.12 | GGB | 57.64 | GGB | 177741.96 | GGB | 148512.31 | GGB | 0 | 0 | 2624 | 3600 | 2608.34 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 39569.4 | GGB | 39569.91 | 2608.34 | 2608.34 |  |  |  | 0 | 1 | [14 empty] | 107.6029 | 2544.7587
21.10.2007 08:00 | 3600 | 2 | 756.71 | GGB | 765.201 | 769.898 | 766.3 | 267.06 | GGB | 10942 | GGB | 9.85 | GGB | 1025.63 | GGB | 57.04 | GGB | 179814.99 | GGB | 150592.75 | GGB | 0 | 0 | 2595 | 3600 | 2579.63 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 39608.18 | GGB | 39608.7 | 2579.63 | 2579.63 |  |  |  | 1 | 1 |  |  |  |  | 150592.75 | 2579.63 | 150592.75 | 2579.63 | 10.0148 | [5 empty] | 107.9093 | 2509.6029
21.10.2007 09:00 | 3600 | 2 | 757.04 | GGB | 764.102 | 768.867 | 765.201 | 265.77 | GGB | 10966 | GGB | 9.86 | GGB | 1026.04 | GGB | 57.64 | GGB | 178139.18 | GGB | 148977.94 | GGB | 0 | 0 | 2595 | 3600 | 2580.16 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 39647.53 | GGB | 39648.04 | 2580.16 | 2580.16 |  |  |  | 1 | 1 |  |  |  |  | 148977.94 | 2580.16 | 148977.94 | 2580.16 | 9.7709 | [5 empty] | 106.7741 | 2536.8051
21.10.2007 10:00 | 3600 | 2 | 756.04 | GGB | 765.201 | 770.133 | 766.3 | 266.79 | GGB | 10963.5 | GGB | 9.84 | GGB | 1026.72 | GGB | 57.52 | GGB | 179248.32 | GGB | 150060.9 | GGB | 0 | 0 | 2643 | 3600 | 2627.28 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 39686.56 | GGB | 39687.08 | 2627.28 | 2627.28 |  |  |  | 1 | 1 |  |  |  |  | 150060.9 | 2627.28 | 150060.9 | 2627.28 | 10.0987 | [5 empty] | 109.5144 | 2518.4975
21.10.2007 11:00 | 3600 | 2 | 757.11 | GGB | 765.201 | 770.133 | 766.3 | 267.5 | GGB | 10962.3 | GGB | 9.86 | GGB | 1027.26 | GGB | 57.1 | GGB | 180156.1 | GGB | 151092.38 | GGB | 0 | 0 | 2589 | 3600 | 2573.66 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 39726.04 | GGB | 39726.56 | 2573.66 | 2573.66 |  |  |  | 1 | 1 |  |  |  |  | 151092.38 | 2573.66 | 151092.38 | 2573.66 | 9.8496 | [5 empty] | 108.0168 | 2501.3042
21.10.2007 12:00 | 3600 | 2 | 757.37 | GGB | 765.201 | 770.18 | 766.3 | 265.84 | GGB | 10980.8 | GGB | 9.87 | GGB | 1027.24 | GGB | 57.82 | GGB | 178354.85 | GGB | 149252.57 | GGB | 0 | 0 | 2582 | 3600 | 2566.85 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 39764.69 | GGB | 39765.21 | 2566.85 | 2566.85 |  |  |  | 1 | 1 |  |  |  |  | 149252.57 | 2566.85 | 149252.57 | 2566.85 | 9.9123 | [5 empty] | 106.4192 | 2532.1373
21.10.2007 13:00 | 3600 | 2 | 757.33 | GGB | 764.102 | 769.008 | 765.201 | 264.21 | GGB | 10934.8 | GGB | 9.86 | GGB | 1027.14 | GGB | 58.47 | GGB | 176205.89 | GGB | 147149.85 | GGB | 0 | 0 | 2572 | 3600 | 2556.72 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 39804.12 | GGB | 39804.64 | 2556.72 | 2556.72 |  |  |  | 1 | 1 |  |  |  |  | 147149.85 | 2556.72 | 147149.85 | 2556.72 | 9.5415 | [5 empty] | 104.5058
21.10.2007 14:00 | 3600 | 2 | 757.35 | GGB | 765.201 | 770.203 | 766.3 | 263.4 | GGB | 10906.8 | GGB | 9.86 | GGB | 1026.97 | GGB | 58.73 | GGB | 175495.07 | GGB | 146416.61 | GGB | 0 | 0 | 2554 | 3600 | 2538.86 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 39843.07 | GGB | 39843.59 | 2538.86 | 2538.86 |  |  |  | 1 | 1 |  |  |  |  | 146416.61 | 2538.86 | 146416.61 | 2538.86 | 9.5438 | [5 empty] | 103.2587
21.10.2007 15:00 | 3600 | 2 | 756.89 | GGB | 764.102 | 769.172 | 765.201 | 263.98 | GGB | 10875.4 | GGB | 9.85 | GGB | 1026.75 | GGB | 58.45 | GGB | 176282.91 | GGB | 147167.82 | GGB | 0 | 0 | 2564 | 3600 | 2548.34 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 39881.96 | GGB | 39882.48 | 2548.34 | 2548.34 |  |  |  | 1 | 1 |  |  |  |  | 147167.82 | 2548.34 | 147167.82 | 2548.34 | 9.6434 | [5 empty] | 104.176
21.10.2007 16:00 | 3600 | 2 | 757.39 | GGB | 766.3 | 771.375 | 767.766 | 265.46 | GGB | 10879.2 | GGB | 9.86 | GGB | 1027.58 | GGB | 58.02 | GGB | 177765.07 | GGB | 148717.74 | GGB | 0 | 0 | 2533 | 3600 | 2517.69 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 39921.05 | GGB | 39921.57 | 2517.69 | 2517.69 |  |  |  | 1 | 1 |  |  |  |  | 148717.74 | 2517.69 | 148717.74 | 2517.69 | 9.5785 | [5 empty] | 104.007
21.10.2007 17:00 | 3600 | 2 | 757.24 | GGB | 766.3 | 770.156 | 766.3 | 264.48 | GGB | 10920.6 | GGB | 9.86 | GGB | 1027.45 | GGB | 58.46 | GGB | 176544.79 | GGB | 147478.98 | GGB | 0 | 0 | 2563 | 3600 | 2547.59 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 39959.78 | GGB | 39960.3 | 2547.59 | 2547.59 |  |  |  | 1 | 1 |  |  |  |  | 147478.98 | 2547.59 | 147478.98 | 2547.59 | 9.7009 | [5 empty] | 104.3655
21.10.2007 18:00 | 3600 | 2 | 757.12 | GGB | 766.3 | 771.211 | 767.766 | 265.15 | GGB | 10885.5 | GGB | 9.85 | GGB | 1027.83 | GGB | 58.3 | GGB | 177293.02 | GGB | 148235.54 | GGB | 0 | 0 | 2558 | 3600 | 2543.19 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 39999.01 | GGB | 39999.53 | 2543.19 | 2543.19 |  |  |  | 1 | 1 |  |  |  |  | 148235.54 | 2543.19 | 148235.54 | 2543.19 | 9.6098 | [5 empty] | 104.7198
21.10.2007 19:00 | 3600 | 2 | 757.14 | GGB | 765.201 | 770.18 | 766.3 | 266.02 | GGB | 10882 | GGB | 9.85 | GGB | 1028.54 | GGB | 58.12 | GGB | 177829.99 | GGB | 148864.43 | GGB | 0 | 0 | 2550 | 3600 | 2534.48 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 40037.81 | GGB | 40038.33 | 2534.48 | 2534.48 |  |  |  | 1 | 1 |  |  |  |  | 148864.43 | 2534.48 | 148864.43 | 2534.48 | 9.7241 | [5 empty] | 104.8039
21.10.2007 20:00 | 3600 | 2 | 757.3 | GGB | 765.201 | 770.133 | 766.3 | 265.01 | GGB | 10933.5 | GGB | 9.86 | GGB | 1029.26 | GGB | 58.69 | GGB | 176199.28 | GGB | 147349.26 | GGB | 0 | 0 | 2573 | 3600 | 2557.4 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 40076.52 | GGB | 40077.04 | 2557.4 | 2557.4 |  |  |  | 1 | 1 |  |  |  |  | 147349.26 | 2557.4 | 147349.26 | 2557.4 | 9.7347 | [5 empty] | 104.6753
21.10.2007 21:00 | 3600 | 2 | 756.42 | GGB | 765.201 | 770.133 | 765.201 | 266.53 | GGB | 10905.4 | GGB | 9.84 | GGB | 1029.37 | GGB | 58.37 | GGB | 178024.75 | GGB | 149036.95 | GGB | 0 | 0 | 2606 | 3600 | 2590.4 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 40116.27 | GGB | 40116.79 | 2590.4 | 2590.4 |  |  |  | 1 | 1 |  |  |  |  | 149036.95 | 2590.4 | 149036.95 | 2590.4 | 9.7123 | [5 empty] | 107.2404 | 2535.8007
21.10.2007 22:00 | 3600 | 2 | 757.12 | GGB | 765.201 | 770.508 | 766.3 | 267.32 | GGB | 10938.9 | GGB | 9.86 | GGB | 1029.67 | GGB | 58 | GGB | 179278.03 | GGB | 150297.54 | GGB | 0 | 0 | 2581 | 3600 | 2565.29 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 40154.41 | GGB | 40154.93 | 2565.29 | 2565.29 |  |  |  | 1 | 1 |  |  |  |  | 150297.54 | 2565.29 | 150297.54 | 2565.29 | 10.109 | [5 empty] | 107.0991 | 2514.5322
21.10.2007 23:00 | 3600 | 2 | 757.4 | GGB | 765.201 | 770.32 | 766.667 | 265.49 | GGB | 10962.5 | GGB | 9.86 | GGB | 1029.69 | GGB | 58.72 | GGB | 176912.3 | GGB | 147995.59 | GGB | 0 | 0 | 2584 | 3600 | 2568.76 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 40193.66 | GGB | 40194.18 | 2568.76 | 2568.76 |  |  |  | 1 | 1 |  |  |  |  | 147995.59 | 2568.76 | 147995.59 | 2568.76 | 9.6857 | [5 empty] | 105.6014 | 2553.6437
21.10.2007 24:00 | 3600 | 2 | 756.84 | GGB | 766.3 | 771.492 | 767.766 | 264.95 | GGB | 10942.3 | GGB | 9.85 | GGB | 1029.48 | GGB | 58.34 | GGB | 176915.6 | GGB | 148137.43 | GGB | 0 | 0 | 2599 | 3600 | 2584.1 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 40232.64 | GGB | 40233.16 | 2584.1 | 2584.1 |  |  |  | 1 | 1 |  |  |  |  | 148137.43 | 2584.1 | 148137.43 | 2584.1 | 9.8205 | [5 empty] | 106.3339 | 2551.1986
22.10.2007 01:00 | 3600 | 2 | 756.82 | GGB | 765.201 | 770.578 | 766.3 | 267.99 | GGB | 10928.6 | GGB | 9.84 | GGB | 1029.69 | GGB | 58.01 | GGB | 179794.09 | GGB | 150727.46 | GGB | 0 | 0 | 2596 | 3600 | 2580.61 | GGB | 100 | GGB | 38.68 | GGB | 38.68 | GGB | 40271.33 | GGB | 40271.84 | 2580.61 | 2580.61 |  |  |  | 1 | 1 |  |  |  |  | 150727.46 | 2580.61 | 150727.46 | 2580.61 | 10.0561 | [5 empty] | 108.0469 | 2507.36
22.10.2007 02:00 | 3600 | 2 | 757.31 | GGB | 765.201 | 769.57 | 766.3 | 267.1 | GGB | 10969.7 | GGB | 9.86 | GGB | 1029.92 | GGB | 58.63 | GGB | 177770.57 | GGB | 148788.59 | GGB | 0 | 0 | 2603 | 3600 | 2588.11 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 40311.14 | GGB | 40311.66 | 2588.11 | 2588.11 |  |  |  | 1 | 1 |  |  |  |  | 148788.59 | 2588.11 | 148788.59 | 2588.11 | 9.6705 | [5 empty] | 106.967 | 2540.0335
22.10.2007 03:00 | 3600 | 2 | 757.45 | GGB | 765.201 | 770.602 | 766.3 | 268.1 | GGB | 10931.8 | GGB | 9.85 | GGB | 1030.14 | GGB | 58.19 | GGB | 179449.68 | GGB | 150421.95 | GGB | 0 | 0 | 2570 | 3600 | 2554.59 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 40349.48 | GGB | 40349.99 | 2554.59 | 2554.59 |  |  |  | 1 | 1 |  |  |  |  | 150421.95 | 2554.59 | 150421.95 | 2554.59 | 10.0252 | [5 empty] | 106.7407 | 2512.4525
22.10.2007 04:00 | 3600 | 2 | 757.49 | GGB | 765.201 | 770.461 | 766.3 | 266.57 | GGB | 10954.8 | GGB | 9.86 | GGB | 1030.05 | GGB | 58.82 | GGB | 177376.65 | GGB | 148390.41 | GGB | 0 | 0 | 2580 | 3600 | 2565.12 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 40389.26 | GGB | 40389.77 | 2565.12 | 2565.12 |  |  |  | 1 | 1 |  |  |  |  | 148390.41 | 2565.12 | 148390.41 | 2565.12 | 9.5686 | [5 empty] | 105.7331 | 2546.8492
22.10.2007 05:00 | 3600 | 2 | 756.96 | GGB | 764.102 | 769.313 | 766.3 | 267.42 | GGB | 10946.7 | GGB | 9.85 | GGB | 1029.91 | GGB | 58.51 | GGB | 178302.03 | GGB | 149282.25 | GGB | 0 | 0 | 2601 | 3600 | 2586.06 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 40427.75 | GGB | 40428.26 | 2586.06 | 2586.06 |  |  |  | 1 | 1 |  |  |  |  | 149282.25 | 2586.06 | 149282.25 | 2586.06 | 10.03 | [5 empty] | 107.2369 | 2531.6339
22.10.2007 06:00 | 3600 | 2 | 757.32 | GGB | 766.667 | 771.445 | 767.766 | 267.14 | GGB | 10973.6 | GGB | 9.86 | GGB | 1030.13 | GGB | 58.4 | GGB | 178135.88 | GGB | 149224.61 | GGB | 0 | 0 | 2595 | 3600 | 2579.43 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 40467.27 | GGB | 40467.78 | 2579.43 | 2579.43 |  |  |  | 1 | 1 |  |  |  |  | 149224.61 | 2579.43 | 149224.61 | 2579.43 | 9.7397 | [5 empty] | 106.9207 | 2532.6117
22.10.2007 07:00 | 3600 | 2 | 756.51 | GGB | 764.102 | 769.266 | 765.201 | 267.47 | GGB | 10962.7 | GGB | 9.84 | GGB | 1030 | GGB | 58.22 | GGB | 178980.94 | GGB | 149994.53 | GGB | 0 | 0 | 2628 | 3600 | 2612.37 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 40506.53 | GGB | 40507.04 | 2612.37 | 2612.37 |  |  |  | 1 | 1 |  |  |  |  | 149994.53 | 2612.37 | 149994.53 | 2612.37 | 9.9807 | [5 empty] | 108.8448 | 2519.6119
22.10.2007 08:00 | 3600 | 2 | 756.78 | GGB | 766.3 | 771.281 | 767.766 | 267.55 | GGB | 11019.7 | GGB | 9.86 | GGB | 1030.24 | GGB | 58.19 | GGB | 179079.97 | GGB | 150129.46 | GGB | 0 | 0 | 2650 | 3600 | 2634.8 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 40545.84 | GGB | 40546.35 | 2634.8 | 2634.8 |  |  |  | 1 | 1 |  |  |  |  | 150129.46 | 2634.8 | 150129.46 | 2634.8 | 10.0626 | [5 empty] | 109.8781 | 2517.3474
22.10.2007 09:00 | 3600 | 2 | 757.11 | GGB | 766.3 | 771.445 | 766.667 | 267.29 | GGB | 11021.2 | GGB | 9.86 | GGB | 1030.63 | GGB | 58.34 | GGB | 178746.57 | GGB | 149836.31 | GGB | 0 | 0 | 2628 | 3600 | 2612.89 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 40585.33 | GGB | 40585.85 | 2612.89 | 2612.89 |  |  |  | 1 | 1 |  |  |  |  | 149836.31 | 2612.89 | 149836.31 | 2612.89 | 9.9115 | [5 empty] | 108.7516 | 2522.2725
22.10.2007 10:00 | 3600 | 2 | 756.54 | GGB | 765.201 | 770.555 | 767.033 | 268.53 | GGB | 10966.4 | GGB | 9.84 | GGB | 1031.17 | GGB | 57.92 | GGB | 180232.02 | GGB | 151351.86 | GGB | 0 | 0 | 2635 | 3600 | 2619.77 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 40624.57 | GGB | 40625.08 | 2619.77 | 2619.77 |  |  |  | 1 | 1 |  |  |  |  | 151351.86 | 2619.77 | 151351.86 | 2619.77 | 10.1072 | [5 empty] | 110.1409 | 2497.0159
22.10.2007 11:00 | 3600 | 2 | 757.31 | GGB | 766.3 | 770.32 | 767.033 | 268.58 | GGB | 10973.4 | GGB | 9.86 | GGB | 1031.44 | GGB | 57.66 | GGB | 180351.96 | GGB | 151611.02 | GGB | 0 | 0 | 2592 | 3600 | 2576.64 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 40664 | GGB | 40664.51 | 2576.64 | 2576.64 |  |  |  | 1 | 1 |  |  |  |  | 151611.02 | 2576.64 | 151611.02 | 2576.64 | 9.9074 | [5 empty] | 108.5131 | 2492.7476
22.10.2007 12:00 | 3600 | 2 | 757.41 | GGB | 765.201 | 770.156 | 765.934 | 268.13 | GGB | 10956.8 | GGB | 9.86 | GGB | 1031.47 | GGB | 57.92 | GGB | 179898.62 | GGB | 151116.95 | GGB | 0 | 0 | 2579 | 3600 | 2564.02 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 40703.28 | GGB | 40703.8 | 2564.02 | 2564.02 |  |  |  | 1 | 1 |  |  |  |  | 151116.95 | 2564.02 | 151116.95 | 2564.02 | 9.8617 | [5 empty] | 107.6297 | 2500.8975
22.10.2007 13:00 | 3600 | 2 | 758 | GGB | 766.667 | 771.281 | 767.033 | 267.05 | GGB | 10918.4 | GGB | 9.87 | GGB | 1030.88 | GGB | 58.27 | GGB | 178692.65 | GGB | 149858.79 | GGB | 0 | 0 | 2534 | 3600 | 2519.16 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 40742.17 | GGB | 40742.69 | 2519.16 | 2519.16 |  |  |  | 1 | 1 |  |  |  |  | 149858.79 | 2519.16 | 149858.79 | 2519.16 | 9.7073 | [5 empty] | 104.8662
22.10.2007 14:00 | 3600 | 2 | 757.89 | GGB | 765.201 | 771.047 | 767.033 | 265.68 | GGB | 10863.3 | GGB | 9.86 | GGB | 1030.19 | GGB | 58.54 | GGB | 177331.53 | GGB | 148499.45 | GGB | 0 | 0 | 2507 | 3600 | 2492.09 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 40781.08 | GGB | 40781.61 | 2492.09 | 2492.09 |  |  |  | 1 | 1 |  |  |  |  | 148499.45 | 2492.09 | 148499.45 | 2492.09 | 9.5086 | [5 empty] | 102.7983
22.10.2007 15:00 | 3600 | 2 | 758.13 | GGB | 766.667 | 772.43 | 768.132 | 265.17 | GGB | 10838.2 | GGB | 9.86 | GGB | 1029.39 | GGB | 58.66 | GGB | 176618.51 | GGB | 147734.37 | GGB | 0 | 0 | 2488 | 3600 | 2472.3 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 40820.11 | GGB | 40820.63 | 2472.3 | 2472.3 |  |  |  | 1 | 1 |  |  |  |  | 147734.37 | 2472.3 | 147734.37 | 2472.3 | 9.3604 | [5 empty] | 101.4566
22.10.2007 16:00 | 3600 | 2 | 758.28 | GGB | 767.766 | 772.383 | 768.132 | 264.65 | GGB | 10824.2 | GGB | 9.86 | GGB | 1029.14 | GGB | 58.89 | GGB | 175929.7 | GGB | 147020.91 | GGB | 0 | 0 | 2480 | 3600 | 2464.33 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 40858.74 | GGB | 40859.26 | 2464.33 | 2464.33 |  |  |  | 1 | 1 |  |  |  |  | 147020.91 | 2464.33 | 147020.91 | 2464.33 | 9.3789 | [5 empty] | 100.6411
22.10.2007 17:00 | 3600 | 2 | 758.06 | GGB | 766.3 | 770.836 | 767.033 | 262.8 | GGB | 10817.7 | GGB | 9.86 | GGB | 1028.64 | GGB | 59.85 | GGB | 173417.63 | GGB | 144430.96 | GGB | 0 | 0 | 2494 | 3600 | 2478.94 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 40897.37 | GGB | 40897.89 | 2478.94 | 2478.94 |  |  |  | 1 | 1 |  |  |  |  | 144430.96 | 2478.94 | 144430.96 | 2478.94 | 9.2683 | [5 empty] | 99.4544
22.10.2007 18:00 | 3600 | 2 | 757.73 | GGB | 765.201 | 770.859 | 767.033 | 262.93 | GGB | 10810.4 | GGB | 9.85 | GGB | 1028.38 | GGB | 59.8 | GGB | 173314.2 | GGB | 144330.05 | GGB | 0 | 0 | 2510 | 3600 | 2494.8 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 40936.2 | GGB | 40936.72 | 2494.8 | 2494.8 |  |  |  | 1 | 1 |  |  |  |  | 144330.05 | 2494.8 | 144330.05 | 2494.8 | 9.2731 | [5 empty] | 100.0207
22.10.2007 19:00 | 3600 | 2 | 757.61 | GGB | 765.201 | 770.93 | 767.033 | 263.44 | GGB | 10835.4 | GGB | 9.85 | GGB | 1028.02 | GGB | 59.48 | GGB | 173780.74 | GGB | 144807.87 | GGB | 0 | 0 | 2527 | 3600 | 2511.66 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 40974.91 | GGB | 40975.43 | 2511.66 | 2511.66 |  |  |  | 1 | 1 |  |  |  |  | 144807.87 | 2511.66 | 144807.87 | 2511.66 | 9.3957 | [5 empty] | 101.03
22.10.2007 20:00 | 3600 | 2 | 757.5 | GGB | 764.102 | 769.828 | 765.934 | 264 | GGB | 10856.7 | GGB | 9.85 | GGB | 1028.75 | GGB | 59.64 | GGB | 174491.56 | GGB | 145432.36 | GGB | 0 | 0 | 2541 | 3600 | 2525.61 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 41013.78 | GGB | 41014.3 | 2525.61 | 2525.61 |  |  |  | 1 | 1 |  |  |  |  | 145432.36 | 2525.61 | 145432.36 | 2525.61 | 9.4496 | [5 empty] | 102.0293
22.10.2007 21:00 | 3600 | 2 | 757.14 | GGB | 765.201 | 769.852 | 765.934 | 264.96 | GGB | 10850.5 | GGB | 9.85 | GGB | 1028.99 | GGB | 59.61 | GGB | 175286 | GGB | 146142.89 | GGB | 0 | 0 | 2563 | 3600 | 2547.52 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 41052.42 | GGB | 41052.94 | 2547.52 | 2547.52 |  |  |  | 1 | 1 |  |  |  |  | 146142.89 | 2547.52 | 146142.89 | 2547.52 | 9.6351 | [5 empty] | 103.4172
22.10.2007 22:00 | 3600 | 2 | 758.24 | GGB | 765.201 | 770.859 | 765.934 | 265.35 | GGB | 10867.7 | GGB | 9.87 | GGB | 1028.92 | GGB | 59.31 | GGB | 175792.16 | GGB | 146687.16 | GGB | 0 | 0 | 2521 | 3600 | 2505.71 | GGB | 100 | GGB | 37.22 | GGB | 37.22 | GGB | 41089.64 | GGB | 41090.16 | 2505.71 | 2505.71 |  |  |  | 1 | 1 |  |  |  |  | 146687.16 | 2505.71 | 146687.16 | 2505.71 | 9.8752 | [5 empty] | 102.0987
22.10.2007 23:00 | 3600 | 2 | 757.31 | GGB | 766.3 | 771.984 | 767.033 | 264.75 | GGB | 10861.4 | GGB | 9.85 | GGB | 1029 | GGB | 59.55 | GGB | 175587.5 | GGB | 146420.96 | GGB | 0 | 0 | 2559 | 3600 | 2543.38 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 41130 | GGB | 41130.53 | 2543.38 | 2543.38 |  |  |  | 1 | 1 |  |  |  |  | 146420.96 | 2543.38 | 146420.96 | 2543.38 | 9.2248 | [5 empty] | 103.4456
22.10.2007 24:00 | 3600 | 2 | 757.51 | GGB | 767.766 | 771.914 | 768.132 | 266.06 | GGB | 10830.3 | GGB | 9.85 | GGB | 1028.76 | GGB | 58.95 | GGB | 176511.78 | GGB | 147422.6 | GGB | 0 | 0 | 2530 | 3600 | 2514.97 | GGB | 100 | GGB | 38.68 | GGB | 38.68 | GGB | 41168.68 | GGB | 41169.21 | 2514.97 | 2514.97 |  |  |  | 1 | 1 |  |  |  |  | 147422.6 | 2514.97 | 147422.6 | 2514.97 | 9.5854 | [5 empty] | 102.9898
23.10.2007 01:00 | 3600 | 2 | 757.97 | GGB | 765.201 | 770.906 | 765.934 | 265.64 | GGB | 10817.9 | GGB | 9.86 | GGB | 1028.74 | GGB | 59.28 | GGB | 176188.28 | GGB | 147003.81 | GGB | 0 | 0 | 2503 | 3600 | 2487.61 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 41207.01 | GGB | 41207.55 | 2487.61 | 2487.61 |  |  |  | 1 | 1 |  |  |  |  | 147003.81 | 2487.61 | 147003.81 | 2487.61 | 9.538 | [5 empty] | 101.58
23.10.2007 02:00 | 3600 | 2 | 757.9 | GGB | 766.3 | 771.984 | 766.667 | 264.84 | GGB | 10842.2 | GGB | 9.86 | GGB | 1028.75 | GGB | 59.5 | GGB | 175061.54 | GGB | 145970.5 | GGB | 0 | 0 | 2508 | 3600 | 2492.66 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 41245.95 | GGB | 41246.49 | 2492.66 | 2492.66 |  |  |  | 1 | 1 |  |  |  |  | 145970.5 | 2492.66 | 145970.5 | 2492.66 | 9.344 | [5 empty] | 101.0708
23.10.2007 03:00 | 3600 | 2 | 757.57 | GGB | 766.667 | 772.219 | 768.864 | 264.12 | GGB | 10851.7 | GGB | 9.86 | GGB | 1028.48 | GGB | 59.86 | GGB | 173972.2 | GGB | 144864.75 | GGB | 0 | 0 | 2537 | 3600 | 2521.85 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 41285.01 | GGB | 41285.54 | 2521.85 | 2521.85 |  |  |  | 1 | 1 |  |  |  |  | 144864.75 | 2521.85 | 144864.75 | 2521.85 | 9.3554 | [5 empty] | 101.4798
23.10.2007 04:00 | 3600 | 2 | 757.14 | GGB | 765.201 | 770.086 | 766.667 | 264.57 | GGB | 10847.2 | GGB | 9.85 | GGB | 1028.48 | GGB | 59.84 | GGB | 174592.79 | GGB | 145392.52 | GGB | 0 | 0 | 2565 | 3600 | 2549.35 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 41323.72 | GGB | 41324.25 | 2549.35 | 2549.35 |  |  |  | 1 | 1 |  |  |  |  | 145392.52 | 2549.35 | 145392.52 | 2549.35 | 9.5752 | [5 empty] | 102.9601
23.10.2007 05:00 | 3600 | 2 | 757.15 | GGB | 765.201 | 769.852 | 766.3 | 265.79 | GGB | 10837.3 | GGB | 9.85 | GGB | 1028.36 | GGB | 59.39 | GGB | 176123.36 | GGB | 146849.34 | GGB | 0 | 0 | 2558 | 3600 | 2543.21 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 41363.2 | GGB | 41363.73 | 2543.21 | 2543.21 |  |  |  | 1 | 1 |  |  |  |  | 146849.34 | 2543.21 | 146849.34 | 2543.21 | 9.4597 | [5 empty] | 103.7413
23.10.2007 06:00 | 3600 | 2 | 757.77 | GGB | 765.201 | 769.898 | 766.3 | 266.35 | GGB | 10842.3 | GGB | 9.86 | GGB | 1028.27 | GGB | 58.95 | GGB | 176928.81 | GGB | 147701.19 | GGB | 0 | 0 | 2524 | 3600 | 2508.3 | GGB | 100 | GGB | 38.35 | GGB | 38.35 | GGB | 41401.54 | GGB | 41402.08 | 2508.3 | 2508.3 |  |  |  | 1 | 1 |  |  |  |  | 147701.19 | 2508.3 | 147701.19 | 2508.3 | 9.6605 | [5 empty] | 102.9108
23.10.2007 07:00 | 3600 | 2 | 757.58 | GGB | 766.3 | 771.305 | 767.766 | 265.91 | GGB | 10850.8 | GGB | 9.86 | GGB | 1028.12 | GGB | 59 | GGB | 176535.99 | GGB | 147328.21 | GGB | 0 | 0 | 2532 | 3600 | 2516.96 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 41440.66 | GGB | 41441.2 | 2516.96 | 2516.96 |  |  |  | 1 | 1 |  |  |  |  | 147328.21 | 2516.96 | 147328.21 | 2516.96 | 9.479 | [5 empty] | 103.0053
23.10.2007 08:00 | 3600 | 2 | 757.52 | GGB | 765.201 | 770.273 | 766.3 | 264.49 | GGB | 10869.4 | GGB | 9.86 | GGB | 1027.96 | GGB | 59.65 | GGB | 174695.12 | GGB | 145485.38 | GGB | 0 | 0 | 2554 | 3600 | 2538.32 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 41479.45 | GGB | 41479.99 | 2538.32 | 2538.32 |  |  |  | 1 | 1 |  |  |  |  | 145485.38 | 2538.32 | 145485.38 | 2538.32 | 9.5202 | [5 empty] | 102.5801
23.10.2007 09:00 | 3600 | 2 | 757.46 | GGB | 764.102 | 769.359 | 765.201 | 264.7 | GGB | 10852.6 | GGB | 9.85 | GGB | 1028.01 | GGB | 59.45 | GGB | 175069.24 | GGB | 145890.97 | GGB | 0 | 0 | 2547 | 3600 | 2531.5 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 41518.25 | GGB | 41518.79 | 2531.5 | 2531.5 |  |  |  | 1 | 1 |  |  |  |  | 145890.97 | 2531.5 | 145890.97 | 2531.5 | 9.5186 | [5 empty] | 102.5897
23.10.2007 10:00 | 3600 | 2 | 757.66 | GGB | 766.3 | 771.539 | 767.033 | 266.03 | GGB | 10835.3 | GGB | 9.85 | GGB | 1028.11 | GGB | 58.77 | GGB | 176964.02 | GGB | 147790.68 | GGB | 0 | 0 | 2526 | 3600 | 2511.17 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 41557.2 | GGB | 41557.74 | 2511.17 | 2511.17 |  |  |  | 1 | 1 |  |  |  |  | 147790.68 | 2511.17 | 147790.68 | 2511.17 | 9.5283 | [5 empty] | 103.091
23.10.2007 11:00 | 3600 | 2 | 758.4 | GGB | 766.667 | 771.867 | 767.766 | 264.77 | GGB | 10854.7 | GGB | 9.87 | GGB | 1028 | GGB | 59.39 | GGB | 175444.45 | GGB | 146229.65 | GGB | 0 | 0 | 2497 | 3600 | 2482.16 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 41595.69 | GGB | 41596.23 | 2482.16 | 2482.16 |  |  |  | 1 | 1 |  |  |  |  | 146229.65 | 2482.16 | 146229.65 | 2482.16 | 9.4301 | [5 empty] | 100.8237
23.10.2007 12:00 | 3600 | 2 | 757.67 | GGB | 766.3 | 771.914 | 767.766 | 262.9 | GGB | 10828 | GGB | 9.86 | GGB | 1028.21 | GGB | 60.2 | GGB | 173565.08 | GGB | 144343.53 | GGB | 0 | 0 | 2522 | 3600 | 2507.09 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 41634.55 | GGB | 41635.09 | 2507.09 | 2507.09 |  |  |  | 1 | 1 |  |  |  |  | 144343.53 | 2507.09 | 144343.53 | 2507.09 | 9.3125 | [5 empty] | 100.5228
23.10.2007 13:00 | 3600 | 2 | 757.91 | GGB | 766.3 | 771.891 | 767.766 | 261.97 | GGB | 10792.9 | GGB | 9.86 | GGB | 1028.04 | GGB | 60.25 | GGB | 172875.16 | GGB | 143721.61 | GGB | 0 | 0 | 2495 | 3600 | 2479.55 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 41673.29 | GGB | 41673.83 | 2479.55 | 2479.55 |  |  |  | 1 | 1 |  |  |  |  | 143721.61 | 2479.55 | 143721.61 | 2479.55 | 9.1989 | [5 empty] | 98.9903
23.10.2007 14:00 | 3600 | 2 | 758.15 | GGB | 766.3 | 771.867 | 767.766 | 262.91 | GGB | 10767.8 | GGB | 9.86 | GGB | 1028.23 | GGB | 59.9 | GGB | 173956.8 | GGB | 144800.19 | GGB | 0 | 0 | 2472 | 3600 | 2456.7 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 41711.69 | GGB | 41712.23 | 2456.7 | 2456.7 |  |  |  | 1 | 1 |  |  |  |  | 144800.19 | 2456.7 | 144800.19 | 2456.7 | 9.2638 | [5 empty] | 98.8141
23.10.2007 15:00 | 3600 | 2 | 758.11 | GGB | 766.3 | 771.703 | 767.766 | 263.41 | GGB | 10744 | GGB | 9.85 | GGB | 1028.02 | GGB | 59.79 | GGB | 174117.45 | GGB | 144953.83 | GGB | 0 | 0 | 2464 | 3600 | 2448.76 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 41750.6 | GGB | 41751.14 | 2448.76 | 2448.76 |  |  |  | 1 | 1 |  |  |  |  | 144953.83 | 2448.76 | 144953.83 | 2448.76 | 9.1225 | [5 empty] | 98.5992
23.10.2007 16:00 | 3600 | 2 | 758.18 | GGB | 765.201 | 770.766 | 767.766 | 262.03 | GGB | 10763.9 | GGB | 9.86 | GGB | 1027.57 | GGB | 60.33 | GGB | 172297.49 | GGB | 143144.75 | GGB | 0 | 0 | 2476 | 3600 | 2460.76 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 41788.55 | GGB | 41789.09 | 2460.76 | 2460.76 |  |  |  | 1 | 1 |  |  |  |  | 143144.75 | 2460.76 | 143144.75 | 2460.76 | 9.2818 | [5 empty] | 97.8458
23.10.2007 17:00 | 3600 | 2 | 757.85 | GGB | 766.3 | 770.742 | 767.766 | 261.63 | GGB | 10761.5 | GGB | 9.85 | GGB | 1027.02 | GGB | 60.55 | GGB | 171685.7 | GGB | 142462.32 | GGB | 0 | 0 | 2498 | 3600 | 2482.62 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 41827.6 | GGB | 41828.14 | 2482.62 | 2482.62 |  |  |  | 1 | 1 |  |  |  |  | 142462.32 | 2482.62 | 142462.32 | 2482.62 | 9.0571 | [5 empty] | 98.2444
23.10.2007 18:00 | 3600 | 2 | 757.9 | GGB | 766.3 | 771.797 | 766.667 | 261.69 | GGB | 10758.4 | GGB | 9.85 | GGB | 1026.76 | GGB | 60.57 | GGB | 171689 | GGB | 142421.21 | GGB | 0 | 0 | 2493 | 3600 | 2477.33 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 41865.99 | GGB | 41866.52 | 2477.33 | 2477.33 |  |  |  | 1 | 1 |  |  |  |  | 142421.21 | 2477.33 | 142421.21 | 2477.33 | 9.1929 | [5 empty] | 98.0068
23.10.2007 19:00 | 3600 | 2 | 757.69 | GGB | 765.201 | 770.953 | 766.667 | 262.35 | GGB | 10741.4 | GGB | 9.85 | GGB | 1027.07 | GGB | 60.58 | GGB | 172272.18 | GGB | 142943.99 | GGB | 0 | 0 | 2496 | 3600 | 2481.25 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 41904.45 | GGB | 41904.99 | 2481.25 | 2481.25 |  |  |  | 1 | 1 |  |  |  |  | 142943.99 | 2481.25 | 142943.99 | 2481.25 | 9.2196 | [5 empty] | 98.5222
23.10.2007 20:00 | 3600 | 2 | 757.77 | GGB | 766.667 | 772.055 | 767.766 | 263.15 | GGB | 10729.4 | GGB | 9.85 | GGB | 1027.36 | GGB | 59.92 | GGB | 173790.65 | GGB | 144532.16 | GGB | 0 | 0 | 2484 | 3600 | 2468.77 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 41942.87 | GGB | 41943.41 | 2468.77 | 2468.77 |  |  |  | 1 | 1 |  |  |  |  | 144532.16 | 2468.77 | 144532.16 | 2468.77 | 9.2873 | [5 empty] | 99.1157
23.10.2007 21:00 | 3600 | 2 | 757.87 | GGB | 766.667 | 772.031 | 767.766 | 261.94 | GGB | 10773 | GGB | 9.86 | GGB | 1027.46 | GGB | 59.33 | GGB | 173616.79 | GGB | 144655.38 | GGB | 0 | 0 | 2487 | 3600 | 2471.5 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 41981.25 | GGB | 41981.78 | 2471.5 | 2471.5 |  |  |  | 1 | 1 |  |  |  |  | 144655.38 | 2471.5 | 144655.38 | 2471.5 | 9.3176 | [5 empty] | 99.3099
23.10.2007 22:00 | 3600 | 2 | 757.46 | GGB | 765.201 | 770.719 | 766.3 | 260.33 | GGB | 10797.4 | GGB | 9.86 | GGB | 1027.27 | GGB | 59.64 | GGB | 172333.8 | GGB | 143429.39 | GGB | 0 | 0 | 2521 | 3600 | 2505.58 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 42019.79 | GGB | 42020.32 | 2505.58 | 2505.58 |  |  |  | 1 | 1 |  |  |  |  | 143429.39 | 2505.58 | 143429.39 | 2505.58 | 9.3247 | [5 empty] | 99.8261
23.10.2007 23:00 | 3600 | 2 | 757.3 | GGB | 765.201 | 769.734 | 765.201 | 259.69 | GGB | 10807.2 | GGB | 9.85 | GGB | 1027.44 | GGB | 59.41 | GGB | 172631.99 | GGB | 143800.26 | GGB | 0 | 0 | 2529 | 3600 | 2513.37 | GGB | 100 | GGB | 36.74 | GGB | 36.74 | GGB | 42056.52 | GGB | 42057.06 | 2513.37 | 2513.37 |  |  |  | 1 | 1 |  |  |  |  | 143800.26 | 2513.37 | 143800.26 | 2513.37 | 9.8373 | [5 empty] | 100.3953
23.10.2007 24:00 | 3600 | 2 | 757.2 | GGB | 765.201 | 770.742 | 766.667 | 261.52 | GGB | 10776.9 | GGB | 9.85 | GGB | 1027.49 | GGB | 59.05 | GGB | 174173.56 | GGB | 145245.41 | GGB | 0 | 0 | 2521 | 3600 | 2505.57 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 42096.02 | GGB | 42096.55 | 2505.57 | 2505.57 |  |  |  | 1 | 1 |  |  |  |  | 145245.41 | 2505.57 | 145245.41 | 2505.57 | 9.2156 | [5 empty] | 101.0896
24.10.2007 01:00 | 3600 | 2 | 757.38 | GGB | 765.201 | 770.695 | 766.3 | 261.76 | GGB | 10771.8 | GGB | 9.85 | GGB | 1027.86 | GGB | 58.91 | GGB | 174600.49 | GGB | 145716 | GGB | 0 | 0 | 2509 | 3600 | 2493.59 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 42135.37 | GGB | 42135.9 | 2493.59 | 2493.59 |  |  |  | 1 | 1 |  |  |  |  | 145716 | 2493.59 | 145716 | 2493.59 | 9.234 | [5 empty] | 100.9322
24.10.2007 02:00 | 3600 | 2 | 757.44 | GGB | 765.201 | 770.695 | 766.3 | 260.46 | GGB | 10798.1 | GGB | 9.86 | GGB | 1027.34 | GGB | 59.21 | GGB | 172683.71 | GGB | 143912.95 | GGB | 0 | 0 | 2520 | 3600 | 2504.71 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 42173.74 | GGB | 42174.28 | 2504.71 | 2504.71 |  |  |  | 1 | 1 |  |  |  |  | 143912.95 | 2504.71 | 143912.95 | 2504.71 | 9.3919 | [5 empty] | 100.1278
24.10.2007 03:00 | 3600 | 2 | 757.12 | GGB | 765.201 | 770.508 | 766.3 | 260.17 | GGB | 10796.2 | GGB | 9.85 | GGB | 1027.06 | GGB | 59.44 | GGB | 172147.84 | GGB | 143331.65 | GGB | 0 | 0 | 2541 | 3600 | 2525.68 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 42212.83 | GGB | 42213.37 | 2525.68 | 2525.68 |  |  |  | 1 | 1 |  |  |  |  | 143331.65 | 2525.68 | 143331.65 | 2525.68 | 9.2609 | [5 empty] | 100.5583
24.10.2007 04:00 | 3600 | 2 | 757.01 | GGB | 765.201 | 769.477 | 765.201 | 260.3 | GGB | 10804.1 | GGB | 9.85 | GGB | 1026.88 | GGB | 59.41 | GGB | 172332.7 | GGB | 143470.78 | GGB | 0 | 0 | 2550 | 3600 | 2534.24 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 42251.62 | GGB | 42252.15 | 2534.24 | 2534.24 |  |  |  | 1 | 1 |  |  |  |  | 143470.78 | 2534.24 | 143470.78 | 2534.24 | 9.3757 | [5 empty] | 100.9971
24.10.2007 05:00 | 3600 | 2 | 757.04 | GGB | 765.201 | 770.555 | 766.3 | 260.34 | GGB | 10809.3 | GGB | 9.85 | GGB | 1026.62 | GGB | 59.49 | GGB | 172526.36 | GGB | 143563.43 | GGB | 0 | 0 | 2558 | 3600 | 2543.04 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 42290.11 | GGB | 42290.64 | 2543.04 | 2543.04 |  |  |  | 1 | 1 |  |  |  |  | 143563.43 | 2543.04 | 143563.43 | 2543.04 | 9.4853 | [5 empty] | 101.4132
24.10.2007 06:00 | 3600 | 2 | 757.12 | GGB | 765.201 | 769.523 | 766.3 | 260.22 | GGB | 10806.3 | GGB | 9.85 | GGB | 1026.34 | GGB | 59.46 | GGB | 172387.71 | GGB | 143420.44 | GGB | 0 | 0 | 2554 | 3600 | 2539.11 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 42329.15 | GGB | 42329.68 | 2539.11 | 2539.11 |  |  |  | 1 | 1 |  |  |  |  | 143420.44 | 2539.11 | 143420.44 | 2539.11 | 9.3279 | [5 empty] | 101.1556
24.10.2007 07:00 | 3600 | 2 | 757.06 | GGB | 765.201 | 769.664 | 766.3 | 260.11 | GGB | 10799.8 | GGB | 9.85 | GGB | 1026.24 | GGB | 59.41 | GGB | 172081.82 | GGB | 143174.91 | GGB | 0 | 0 | 2555 | 3600 | 2540.13 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 42367.62 | GGB | 42368.15 | 2540.13 | 2540.13 |  |  |  | 1 | 1 |  |  |  |  | 143174.91 | 2540.13 | 143174.91 | 2540.13 | 9.4537 | [5 empty] | 101.023
24.10.2007 08:00 | 3600 | 2 | 757.25 | GGB | 765.201 | 769.57 | 766.3 | 260 | GGB | 10800.3 | GGB | 9.86 | GGB | 1026.32 | GGB | 59.46 | GGB | 171890.36 | GGB | 143004.07 | GGB | 0 | 0 | 2546 | 3600 | 2530.59 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 42406.54 | GGB | 42407.07 | 2530.59 | 2530.59 |  |  |  | 1 | 1 |  |  |  |  | 143004.07 | 2530.59 | 143004.07 | 2530.59 | 9.2982 | [5 empty] | 100.5235
24.10.2007 09:00 | 3600 | 2 | 757.06 | GGB | 765.201 | 770.742 | 766.667 | 261.48 | GGB | 10880.9 | GGB | 9.84 | GGB | 1026.98 | GGB | 59.02 | GGB | 174919.59 | GGB | 145810.69 | GGB | 0 | 0 | 2572 | 3600 | 2556.35 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 42445.42 | GGB | 42445.95 | 2556.35 | 2556.35 |  |  |  | 1 | 1 |  |  |  |  | 145810.69 | 2556.35 | 145810.69 | 2556.35 | 9.587 | [5 empty] | 103.5398
24.10.2007 10:00 | 3600 | 2 | 757.69 | GGB | 766.3 | 770.883 | 767.766 | 263.69 | GGB | 10945.1 | GGB | 9.83 | GGB | 1027.35 | GGB | 58.56 | GGB | 178758.67 | GGB | 149272.61 | GGB | 0 | 0 | 2560 | 3600 | 2545.18 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 42484.46 | GGB | 42484.98 | 2545.18 | 2545.18 |  |  |  | 1 | 1 |  |  |  |  | 149272.61 | 2545.18 | 149272.61 | 2545.18 | 9.7342 | [5 empty] | 105.5349 | 2531.7974
24.10.2007 11:00 | 3600 | 2 | 759.52 | GGB | 767.766 | 771.867 | 768.864 | 264.5 | GGB | 10956.5 | GGB | 9.86 | GGB | 1027.62 | GGB | 58.43 | GGB | 180052.67 | GGB | 150451.41 | GGB | 0 | 0 | 2476 | 3600 | 2460.43 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 42523.75 | GGB | 42524.27 | 2460.43 | 2460.43 |  |  |  | 1 | 1 |  |  |  |  | 150451.41 | 2460.43 | 150451.41 | 2460.43 | 9.4216 | [5 empty] | 102.8264
24.10.2007 12:00 | 3600 | 2 | 759.12 | GGB | 767.766 | 771.938 | 768.498 | 263.87 | GGB | 10932.4 | GGB | 9.85 | GGB | 1027.86 | GGB | 58.57 | GGB | 179424.37 | GGB | 149895.31 | GGB | 0 | 0 | 2473 | 3600 | 2458.07 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 42562.75 | GGB | 42563.27 | 2458.07 | 2458.07 |  |  |  | 1 | 1 |  |  |  |  | 149895.31 | 2458.07 | 149895.31 | 2458.07 | 9.4475 | [5 empty] | 102.3481
24.10.2007 13:00 | 3600 | 2 | 759.26 | GGB | 766.667 | 771.586 | 767.033 | 261.84 | GGB | 10948 | GGB | 9.86 | GGB | 1027.83 | GGB | 59.49 | GGB | 176556.89 | GGB | 147087.35 | GGB | 0 | 0 | 2482 | 3600 | 2466.45 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 42601.77 | GGB | 42602.29 | 2466.45 | 2466.45 |  |  |  | 1 | 1 |  |  |  |  | 147087.35 | 2466.45 | 147087.35 | 2466.45 | 9.2974 | [5 empty] | 100.7732
24.10.2007 14:00 | 3600 | 2 | 759.31 | GGB | 767.766 | 773.719 | 768.498 | 261.42 | GGB | 10930 | GGB | 9.87 | GGB | 1027.25 | GGB | 59.61 | GGB | 176183.88 | GGB | 146640.84 | GGB | 0 | 0 | 2469 | 3600 | 2453.68 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 42641.23 | GGB | 42641.74 | 2453.68 | 2453.68 |  |  |  | 1 | 1 |  |  |  |  | 146640.84 | 2453.68 | 146640.84 | 2453.68 | 9.1207 | [5 empty] | 99.9471
24.10.2007 15:00 | 3600 | 2 | 758.79 | GGB | 767.766 | 772.453 | 768.132 | 261.09 | GGB | 10889.5 | GGB | 9.85 | GGB | 1026.24 | GGB | 59.72 | GGB | 175749.25 | GGB | 146086.58 | GGB | 0 | 0 | 2474 | 3600 | 2458.84 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 42680.03 | GGB | 42680.54 | 2458.84 | 2458.84 |  |  |  | 1 | 1 |  |  |  |  | 146086.58 | 2458.84 | 146086.58 | 2458.84 | 9.2578 | [5 empty] | 99.7788
24.10.2007 16:00 | 3600 | 2 | 759.05 | GGB | 767.766 | 772.383 | 768.864 | 262.51 | GGB | 10869.2 | GGB | 9.85 | GGB | 1025.81 | GGB | 59.23 | GGB | 177572.51 | GGB | 147761.24 | GGB | 0 | 0 | 2446 | 3600 | 2431.13 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 42719.32 | GGB | 42719.83 | 2431.13 | 2431.13 |  |  |  | 1 | 1 |  |  |  |  | 147761.24 | 2431.13 | 147761.24 | 2431.13 | 9.143 | [5 empty] | 99.7852
24.10.2007 17:00 | 3600 | 2 | 759.4 | GGB | 767.766 | 772.453 | 767.766 | 261.69 | GGB | 10891.4 | GGB | 9.86 | GGB | 1025.62 | GGB | 59.45 | GGB | 176565.7 | GGB | 146797.09 | GGB | 0 | 0 | 2441 | 3600 | 2425.6 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 42757.81 | GGB | 42758.32 | 2425.6 | 2425.6 |  |  |  | 1 | 1 |  |  |  |  | 146797.09 | 2425.6 | 146797.09 | 2425.6 | 9.251 | [5 empty] | 98.9086
24.10.2007 18:00 | 3600 | 2 | 758.7 | GGB | 766.667 | 771.445 | 767.766 | 261.78 | GGB | 10875.7 | GGB | 9.84 | GGB | 1025.56 | GGB | 59.49 | GGB | 176374.24 | GGB | 146612.91 | GGB | 0 | 0 | 2467 | 3600 | 2452.2 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 42797.37 | GGB | 42797.88 | 2452.2 | 2452.2 |  |  |  | 1 | 1 |  |  |  |  | 146612.91 | 2452.2 | 146612.91 | 2452.2 | 9.0881 | [5 empty] | 99.8678
24.10.2007 19:00 | 3600 | 2 | 759.22 | GGB | 767.766 | 772.641 | 768.864 | 263.51 | GGB | 10887 | GGB | 9.85 | GGB | 1026.04 | GGB | 58.94 | GGB | 178557.31 | GGB | 148740.62 | GGB | 0 | 0 | 2443 | 3600 | 2427.6 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 42835.91 | GGB | 42836.42 | 2427.6 | 2427.6 |  |  |  | 1 | 1 |  |  |  |  | 148740.62 | 2427.6 | 148740.62 | 2427.6 | 9.369 | [5 empty] | 100.3008
24.10.2007 20:00 | 3600 | 2 | 759.36 | GGB | 767.766 | 773.695 | 768.864 | 263.31 | GGB | 10906.6 | GGB | 9.86 | GGB | 1026.58 | GGB | 59.08 | GGB | 178231.61 | GGB | 148486.57 | GGB | 0 | 0 | 2447 | 3600 | 2431.61 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 42875.05 | GGB | 42875.56 | 2431.61 | 2431.61 |  |  |  | 1 | 1 |  |  |  |  | 148486.57 | 2431.61 | 148486.57 | 2431.61 | 9.2249 | [5 empty] | 100.2948
24.10.2007 21:00 | 3600 | 2 | 758.84 | GGB | 766.667 | 771.469 | 767.766 | 262.15 | GGB | 10923.2 | GGB | 9.85 | GGB | 1026.53 | GGB | 59.59 | GGB | 176504.08 | GGB | 146816.5 | GGB | 0 | 0 | 2479 | 3600 | 2463.95 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 42914.19 | GGB | 42914.7 | 2463.95 | 2463.95 |  |  |  | 1 | 1 |  |  |  |  | 146816.5 | 2463.95 | 146816.5 | 2463.95 | 9.2424 | [5 empty] | 100.4857
24.10.2007 22:00 | 3600 | 2 | 758.83 | GGB | 767.766 | 772.336 | 768.864 | 263.18 | GGB | 10901.7 | GGB | 9.85 | GGB | 1026.79 | GGB | 59.21 | GGB | 177942.22 | GGB | 148216.33 | GGB | 0 | 0 | 2480 | 3600 | 2464.3 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 42953.04 | GGB | 42953.55 | 2464.3 | 2464.3 |  |  |  | 1 | 1 |  |  |  |  | 148216.33 | 2464.3 | 148216.33 | 2464.3 | 9.4015 | [5 empty] | 101.4582
24.10.2007 23:00 | 3600 | 2 | 759.32 | GGB | 767.766 | 773.648 | 768.864 | 263.71 | GGB | 10898.9 | GGB | 9.86 | GGB | 1026.83 | GGB | 58.99 | GGB | 178875.31 | GGB | 149098.85 | GGB | 0 | 0 | 2447 | 3600 | 2431.52 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 42992.03 | GGB | 42992.54 | 2431.52 | 2431.52 |  |  |  | 1 | 1 |  |  |  |  | 149098.85 | 2431.52 | 149098.85 | 2431.52 | 9.2982 | [5 empty] | 100.7047
24.10.2007 24:00 | 3600 | 2 | 759 | GGB | 767.766 | 772.57 | 768.864 | 263.43 | GGB | 10899.3 | GGB | 9.86 | GGB | 1026.79 | GGB | 58.99 | GGB | 178048.95 | GGB | 148404.29 | GGB | 0 | 0 | 2459 | 3600 | 2443.46 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 43030.49 | GGB | 43031 | 2443.46 | 2443.46 |  |  |  | 1 | 1 |  |  |  |  | 148404.29 | 2443.46 | 148404.29 | 2443.46 | 9.4285 | [5 empty] | 100.7278
25.10.2007 01:00 | 3600 | 2 | 758.56 | GGB | 766.667 | 771.469 | 767.766 | 262.46 | GGB | 10931.9 | GGB | 9.85 | GGB | 1026.39 | GGB | 59.43 | GGB | 176486.47 | GGB | 146851.08 | GGB | 0 | 0 | 2497 | 3600 | 2481.71 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 43070.13 | GGB | 43070.65 | 2481.71 | 2481.71 |  |  |  | 1 | 1 |  |  |  |  | 146851.08 | 2481.71 | 146851.08 | 2481.71 | 9.1915 | [5 empty] | 101.2338
25.10.2007 02:00 | 3600 | 2 | 758.36 | GGB | 766.3 | 771.469 | 767.033 | 262.29 | GGB | 10931.8 | GGB | 9.85 | GGB | 1026.21 | GGB | 59.48 | GGB | 176681.23 | GGB | 146964.7 | GGB | 0 | 0 | 2507 | 3600 | 2491.79 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 43109.4 | GGB | 43109.92 | 2491.79 | 2491.79 |  |  |  | 1 | 1 |  |  |  |  | 146964.7 | 2491.79 | 146964.7 | 2491.79 | 9.3253 | [5 empty] | 101.7237
25.10.2007 03:00 | 3600 | 2 | 757.96 | GGB | 766.667 | 772.641 | 768.132 | 263.43 | GGB | 10909.6 | GGB | 9.85 | GGB | 1026.64 | GGB | 59.09 | GGB | 178468.18 | GGB | 148689.91 | GGB | 0 | 0 | 2515 | 3600 | 2500.16 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 43149.05 | GGB | 43149.57 | 2500.16 | 2500.16 |  |  |  | 1 | 1 |  |  |  |  | 148689.91 | 2500.16 | 148689.91 | 2500.16 | 9.3758 | [5 empty] | 103.2635
25.10.2007 04:00 | 3600 | 2 | 758.68 | GGB | 766.667 | 771.469 | 767.033 | 264.09 | GGB | 10912.5 | GGB | 9.85 | GGB | 1026.79 | GGB | 58.62 | GGB | 179472.79 | GGB | 149759.12 | GGB | 0 | 0 | 2485 | 3600 | 2470.14 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 43187.86 | GGB | 43188.38 | 2470.14 | 2470.14 |  |  |  | 1 | 1 |  |  |  |  | 149759.12 | 2470.14 | 149759.12 | 2470.14 | 9.5317 | [5 empty] | 102.7572
25.10.2007 05:00 | 3600 | 2 | 758.47 | GGB | 766.667 | 772.523 | 768.132 | 264.16 | GGB | 10919.9 | GGB | 9.85 | GGB | 1026.44 | GGB | 58.57 | GGB | 179513.5 | GGB | 149765.63 | GGB | 0 | 0 | 2495 | 3600 | 2480.1 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 43227.31 | GGB | 43227.83 | 2480.1 | 2480.1 |  |  |  | 1 | 1 |  |  |  |  | 149765.63 | 2480.1 | 149765.63 | 2480.1 | 9.4153 | [5 empty] | 103.176
25.10.2007 06:00 | 3600 | 2 | 758.55 | GGB | 766.3 | 771.492 | 767.033 | 262.34 | GGB | 10953 | GGB | 9.86 | GGB | 1026.05 | GGB | 59.02 | GGB | 177548.3 | GGB | 147868.14 | GGB | 0 | 0 | 2510 | 3600 | 2494.9 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 43266.29 | GGB | 43266.81 | 2494.9 | 2494.9 |  |  |  | 1 | 1 |  |  |  |  | 147868.14 | 2494.9 | 147868.14 | 2494.9 | 9.4642 | [5 empty] | 102.4767
25.10.2007 07:00 | 3600 | 2 | 758.08 | GGB | 765.201 | 770.625 | 765.934 | 262.49 | GGB | 10958 | GGB | 9.86 | GGB | 1025.99 | GGB | 59.03 | GGB | 177227 | GGB | 147587.82 | GGB | 0 | 0 | 2530 | 3600 | 2514.92 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 43305.55 | GGB | 43306.08 | 2514.92 | 2514.92 |  |  |  | 1 | 1 |  |  |  |  | 147587.82 | 2514.92 | 147587.82 | 2514.92 | 9.4518 | [5 empty] | 103.1032
25.10.2007 08:00 | 3600 | 2 | 757.83 | GGB | 766.667 | 772.43 | 768.132 | 262.49 | GGB | 10958.4 | GGB | 9.85 | GGB | 1025.99 | GGB | 58.92 | GGB | 177570.31 | GGB | 147921.44 | GGB | 0 | 0 | 2546 | 3600 | 2530.52 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 43344.98 | GGB | 43345.51 | 2530.52 | 2530.52 |  |  |  | 1 | 1 |  |  |  |  | 147921.44 | 2530.52 | 147921.44 | 2530.52 | 9.4932 | [5 empty] | 103.9773
25.10.2007 09:00 | 3600 | 2 | 757.78 | GGB | 766.3 | 771.445 | 767.033 | 264.38 | GGB | 10947 | GGB | 9.84 | GGB | 1026.75 | GGB | 58.23 | GGB | 180035.06 | GGB | 150400.06 | GGB | 0 | 0 | 2541 | 3600 | 2526.11 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 43383.98 | GGB | 43384.5 | 2526.11 | 2526.11 |  |  |  | 1 | 1 |  |  |  |  | 150400.06 | 2526.11 | 150400.06 | 2526.11 | 9.7442 | [5 empty] | 105.5353 | 2512.8181
25.10.2007 10:00 | 3600 | 2 | 758.53 | GGB | 766.667 | 772.453 | 768.132 | 264.65 | GGB | 10963.5 | GGB | 9.86 | GGB | 1027.8 | GGB | 58.12 | GGB | 180335.45 | GGB | 150853.79 | GGB | 0 | 0 | 2508 | 3600 | 2493.25 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 43424.38 | GGB | 43424.9 | 2493.25 | 2493.25 |  |  |  | 1 | 1 |  |  |  |  | 150853.79 | 2493.25 | 150853.79 | 2493.25 | 9.3098 | [5 empty] | 104.4767
25.10.2007 11:00 | 3600 | 2 | 758.56 | GGB | 767.033 | 772.453 | 768.132 | 264.63 | GGB | 10957.7 | GGB | 9.86 | GGB | 1028.28 | GGB | 58.15 | GGB | 180063.67 | GGB | 150684.39 | GGB | 0 | 0 | 2508 | 3600 | 2492.74 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 43463.82 | GGB | 43464.35 | 2492.74 | 2492.74 |  |  |  | 1 | 1 |  |  |  |  | 150684.39 | 2492.74 | 150684.39 | 2492.74 | 9.5213 | [5 empty] | 104.3381
25.10.2007 12:00 | 3600 | 2 | 759.15 | GGB | 768.132 | 772.805 | 768.498 | 263.07 | GGB | 10934.8 | GGB | 9.87 | GGB | 1028.04 | GGB | 58.45 | GGB | 178688.25 | GGB | 149361.42 | GGB | 0 | 0 | 2463 | 3600 | 2447.71 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 43504.27 | GGB | 43504.8 | 2447.71 | 2447.71 |  |  |  | 1 | 1 |  |  |  |  | 149361.42 | 2447.71 | 149361.42 | 2447.71 | 9.0382 | [5 empty] | 101.5537
25.10.2007 13:00 | 3600 | 2 | 758.74 | GGB | 768.132 | 772.688 | 768.132 | 261.02 | GGB | 10924 | GGB | 9.86 | GGB | 1027.66 | GGB | 59.29 | GGB | 175945.11 | GGB | 146643.69 | GGB | 0 | 0 | 2480 | 3600 | 2464.43 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 43543.8 | GGB | 43544.33 | 2464.43 | 2464.43 |  |  |  | 1 | 1 |  |  |  |  | 146643.69 | 2464.43 | 146643.69 | 2464.43 | 9.1422 | [5 empty] | 100.387
25.10.2007 14:00 | 3600 | 2 | 759.06 | GGB | 768.132 | 774.094 | 769.597 | 260.09 | GGB | 10858.7 | GGB | 9.86 | GGB | 1027.07 | GGB | 59.7 | GGB | 174791.95 | GGB | 145419.07 | GGB | 0 | 0 | 2440 | 3600 | 2424.66 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 43583.78 | GGB | 43584.31 | 2424.66 | 2424.66 |  |  |  | 1 | 1 |  |  |  |  | 145419.07 | 2424.66 | 145419.07 | 2424.66 | 8.8192 | [5 empty] | 97.9422
25.10.2007 15:00 | 3600 | 2 | 759.74 | GGB | 768.132 | 773.039 | 768.498 | 260.09 | GGB | 10776.1 | GGB | 9.86 | GGB | 1026.45 | GGB | 59.59 | GGB | 175291.51 | GGB | 145797.28 | GGB | 0 | 0 | 2372 | 3600 | 2357.11 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 43623.52 | GGB | 43624.05 | 2357.11 | 2357.11 |  |  |  | 1 | 1 |  |  |  |  | 145797.28 | 2357.11 | 145797.28 | 2357.11 | 8.6477 | [5 empty] | 95.4612
25.10.2007 16:00 | 3600 | 2 | 759.81 | GGB | 768.498 | 774.188 | 769.597 | 259.42 | GGB | 10747.4 | GGB | 9.86 | GGB | 1025.84 | GGB | 59.84 | GGB | 174713.83 | GGB | 145119.85 | GGB | 0 | 0 | 2353 | 3600 | 2337.86 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 43662.36 | GGB | 43662.9 | 2337.86 | 2337.86 |  |  |  | 1 | 1 |  |  |  |  | 145119.85 | 2337.86 | 145119.85 | 2337.86 | 8.7328 | [5 empty] | 94.2416
25.10.2007 17:00 | 3600 | 2 | 759.32 | GGB | 767.033 | 773.063 | 768.498 | 258.35 | GGB | 10768.6 | GGB | 9.85 | GGB | 1025.35 | GGB | 60.6 | GGB | 172876.26 | GGB | 143198.7 | GGB | 0 | 0 | 2392 | 3600 | 2376.83 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 43701.85 | GGB | 43702.39 | 2376.83 | 2376.83 |  |  |  | 1 | 1 |  |  |  |  | 143198.7 | 2376.83 | 143198.7 | 2376.83 | 8.6189 | [5 empty] | 94.5442
25.10.2007 18:00 | 3600 | 2 | 759.21 | GGB | 768.132 | 774.164 | 769.597 | 260.01 | GGB | 10771.6 | GGB | 9.85 | GGB | 1025.51 | GGB | 60.27 | GGB | 174366.12 | GGB | 144598.9 | GGB | 0 | 0 | 2400 | 3600 | 2385.03 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 43741.11 | GGB | 43741.65 | 2385.03 | 2385.03 |  |  |  | 1 | 1 |  |  |  |  | 144598.9 | 2385.03 | 144598.9 | 2385.03 | 8.7843 | [5 empty] | 95.798
25.10.2007 19:00 | 3600 | 2 | 758.63 | GGB | 768.132 | 772.898 | 768.498 | 263.02 | GGB | 10815.3 | GGB | 9.84 | GGB | 1026.54 | GGB | 59.46 | GGB | 177220.4 | GGB | 147472.56 | GGB | 0 | 0 | 2442 | 3600 | 2427.24 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 43780.51 | GGB | 43781.05 | 2427.24 | 2427.24 |  |  |  | 1 | 1 |  |  |  |  | 147472.56 | 2427.24 | 147472.56 | 2427.24 | 9.0851 | [5 empty] | 99.4309
25.10.2007 20:00 | 3600 | 2 | 758.99 | GGB | 767.033 | 772.781 | 768.132 | 263.69 | GGB | 10872.5 | GGB | 9.85 | GGB | 1027.19 | GGB | 59.11 | GGB | 178166.69 | GGB | 148507.78 | GGB | 0 | 0 | 2459 | 3600 | 2443.39 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 43819.94 | GGB | 43820.48 | 2443.39 | 2443.39 |  |  |  | 1 | 1 |  |  |  |  | 148507.78 | 2443.39 | 148507.78 | 2443.39 | 9.2027 | [5 empty] | 100.7951
25.10.2007 21:00 | 3600 | 2 | 758.63 | GGB | 767.033 | 772.852 | 767.766 | 262.43 | GGB | 10948.6 | GGB | 9.86 | GGB | 1027.72 | GGB | 59.12 | GGB | 176934.31 | GGB | 147553.68 | GGB | 0 | 0 | 2507 | 3600 | 2492.12 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 43859.52 | GGB | 43860.06 | 2492.12 | 2492.12 |  |  |  | 1 | 1 |  |  |  |  | 147553.68 | 2492.12 | 147553.68 | 2492.12 | 9.2906 | [5 empty] | 102.1449
25.10.2007 22:00 | 3600 | 2 | 758.07 | GGB | 765.934 | 770.789 | 766.667 | 262.31 | GGB | 10949.4 | GGB | 9.85 | GGB | 1028.74 | GGB | 59.03 | GGB | 176894.7 | GGB | 147705.23 | GGB | 0 | 0 | 2526 | 3600 | 2510.42 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 43899.68 | GGB | 43900.21 | 2510.42 | 2510.42 |  |  |  | 1 | 1 |  |  |  |  | 147705.23 | 2510.42 | 147705.23 | 2510.42 | 9.2354 | [5 empty] | 103.0006
25.10.2007 23:00 | 3600 | 2 | 758.18 | GGB | 767.033 | 771.844 | 767.033 | 262.61 | GGB | 10936 | GGB | 9.85 | GGB | 1029.08 | GGB | 59.04 | GGB | 176179.48 | GGB | 147151.57 | GGB | 0 | 0 | 2523 | 3600 | 2507.89 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 43938.99 | GGB | 43939.52 | 2507.89 | 2507.89 |  |  |  | 1 | 1 |  |  |  |  | 147151.57 | 2507.89 | 147151.57 | 2507.89 | 9.3879 | [5 empty] | 102.5111
25.10.2007 24:00 | 3600 | 2 | 758.49 | GGB | 767.033 | 772.852 | 768.132 | 262.94 | GGB | 10908.9 | GGB | 9.86 | GGB | 1029.4 | GGB | 59.21 | GGB | 175291.51 | GGB | 146381.56 | GGB | 0 | 0 | 2508 | 3600 | 2492.89 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 43978.9 | GGB | 43979.43 | 2492.89 | 2492.89 |  |  |  | 1 | 1 |  |  |  |  | 146381.56 | 2492.89 | 146381.56 | 2492.89 | 9.1434 | [5 empty] | 101.3648
26.10.2007 01:00 | 3600 | 2 | 758.68 | GGB | 767.033 | 772.055 | 767.033 | 263.79 | GGB | 10901 | GGB | 9.85 | GGB | 1029.86 | GGB | 58.63 | GGB | 178090.77 | GGB | 149047.89 | GGB | 0 | 0 | 2477 | 3600 | 2461.34 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 44018.85 | GGB | 44019.38 | 2461.34 | 2461.34 |  |  |  | 1 | 1 |  |  |  |  | 149047.89 | 2461.34 | 149047.89 | 2461.34 | 9.1829 | [5 empty] | 101.9049
26.10.2007 02:00 | 3600 | 2 | 758.35 | GGB | 767.033 | 771.867 | 767.033 | 262.82 | GGB | 10943 | GGB | 9.85 | GGB | 1029.89 | GGB | 58.77 | GGB | 177484.48 | GGB | 148480.27 | GGB | 0 | 0 | 2520 | 3600 | 2504.51 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 44059.07 | GGB | 44059.6 | 2504.51 | 2504.51 |  |  |  | 1 | 1 |  |  |  |  | 148480.27 | 2504.51 | 148480.27 | 2504.51 | 9.2459 | [5 empty] | 103.2973
26.10.2007 03:00 | 3600 | 2 | 758.38 | GGB | 767.033 | 772.875 | 767.766 | 262.67 | GGB | 10938.6 | GGB | 9.85 | GGB | 1030.04 | GGB | 59.23 | GGB | 176449.06 | GGB | 147430.82 | GGB | 0 | 0 | 2520 | 3600 | 2504.88 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 44098.27 | GGB | 44098.79 | 2504.88 | 2504.88 |  |  |  | 1 | 1 |  |  |  |  | 147430.82 | 2504.88 | 147430.82 | 2504.88 | 9.4232 | [5 empty] | 102.5824
26.10.2007 04:00 | 3600 | 2 | 758.48 | GGB | 767.033 | 771.656 | 767.766 | 262.86 | GGB | 10933.9 | GGB | 9.85 | GGB | 1029.85 | GGB | 59.38 | GGB | 176434.76 | GGB | 147326.39 | GGB | 0 | 0 | 2517 | 3600 | 2501.26 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 44139.08 | GGB | 44139.6 | 2501.26 | 2501.26 |  |  |  | 1 | 1 |  |  |  |  | 147326.39 | 2501.26 | 147326.39 | 2501.26 | 9.0297 | [5 empty] | 102.3616
26.10.2007 05:00 | 3600 | 2 | 758.29 | GGB | 767.033 | 772.805 | 767.766 | 263.2 | GGB | 10945.2 | GGB | 9.85 | GGB | 1029.75 | GGB | 59.38 | GGB | 176726.35 | GGB | 147554.91 | GGB | 0 | 0 | 2527 | 3600 | 2511.36 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 44178.15 | GGB | 44178.67 | 2511.36 | 2511.36 |  |  |  | 1 | 1 |  |  |  |  | 147554.91 | 2511.36 | 147554.91 | 2511.36 | 9.4846 | [5 empty] | 102.9343
26.10.2007 06:00 | 3600 | 2 | 758.33 | GGB | 765.934 | 771.797 | 767.766 | 263.22 | GGB | 10948.9 | GGB | 9.85 | GGB | 1029.89 | GGB | 59.42 | GGB | 177019.04 | GGB | 147800.8 | GGB | 0 | 0 | 2532 | 3600 | 2516.45 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 44218.45 | GGB | 44218.97 | 2516.45 | 2516.45 |  |  |  | 1 | 1 |  |  |  |  | 147800.8 | 2516.45 | 147800.8 | 2516.45 | 9.2291 | [5 empty] | 103.3148
26.10.2007 07:00 | 3600 | 2 | 758.53 | GGB | 767.033 | 772.852 | 767.766 | 262.77 | GGB | 10936.9 | GGB | 9.86 | GGB | 1029.69 | GGB | 59.47 | GGB | 176181.68 | GGB | 147052.86 | GGB | 0 | 0 | 2520 | 3600 | 2504.25 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 44258.23 | GGB | 44258.75 | 2504.25 | 2504.25 |  |  |  | 1 | 1 |  |  |  |  | 147052.86 | 2504.25 | 147052.86 | 2504.25 | 9.2573 | [5 empty] | 102.2936
26.10.2007 08:00 | 3600 | 2 | 758.43 | GGB | 767.033 | 771.844 | 767.766 | 263.22 | GGB | 10924.3 | GGB | 9.85 | GGB | 1030.09 | GGB | 59.56 | GGB | 175961.61 | GGB | 146886.95 | GGB | 0 | 0 | 2531 | 3600 | 2515.36 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 44298.34 | GGB | 44298.86 | 2515.36 | 2515.36 |  |  |  | 1 | 1 |  |  |  |  | 146886.95 | 2515.36 | 146886.95 | 2515.36 | 9.2115 | [5 empty] | 102.6315
26.10.2007 09:00 | 3600 | 2 | 758.44 | GGB | 765.934 | 772.125 | 767.766 | 265.07 | GGB | 10887.3 | GGB | 9.85 | GGB | 1030.65 | GGB | 59.04 | GGB | 177857.49 | GGB | 148780.75 | GGB | 0 | 0 | 2508 | 3207 | 2492.62 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 44337.85 | GGB | 44338.37 | 2492.62 | 2492.62 |  |  |  | 1 | 1 |  |  |  |  | 148780.75 | 2492.62 | 148780.75 | 2492.62 | 9.3863 | [5 empty] | 103.015
26.10.2007 10:00 | 3600 | 2 | 758.77 | GGB | 767.033 | 772.148 | 767.766 | 265.17 | GGB | 10907.9 | GGB | 9.85 | GGB | 1031.03 | GGB | 58.83 | GGB | 178523.2 | GGB | 149488.89 | GGB | 0 | 0 | 2504 | 3600 | 2488.55 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 44377.91 | GGB | 44378.43 | 2488.55 | 2488.55 |  |  |  | 1 | 1 |  |  |  |  | 149488.89 | 2488.55 | 149488.89 | 2488.55 | 9.2863 | [5 empty] | 103.3363
26.10.2007 11:00 | 3600 | 2 | 759.23 | GGB | 765.934 | 772.125 | 767.766 | 263.59 | GGB | 10940.4 | GGB | 9.87 | GGB | 1031.01 | GGB | 59.17 | GGB | 177092.76 | GGB | 148133.2 | GGB | 0 | 0 | 2492 | 3600 | 2476.78 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 44417.46 | GGB | 44417.98 | 2476.78 | 2476.78 |  |  |  | 1 | 1 |  |  |  |  | 148133.2 | 2476.78 | 148133.2 | 2476.78 | 9.2767 | [5 empty] | 101.9148
26.10.2007 12:00 | 3600 | 2 | 758.75 | GGB | 767.033 | 773.25 | 768.864 | 262.62 | GGB | 10933.4 | GGB | 9.86 | GGB | 1031.08 | GGB | 59.56 | GGB | 176037.54 | GGB | 147091.61 | GGB | 0 | 0 | 2518 | 3600 | 2502.65 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 44457.32 | GGB | 44457.85 | 2502.65 | 2502.65 |  |  |  | 1 | 1 |  |  |  |  | 147091.61 | 2502.65 | 147091.61 | 2502.65 | 9.233 | [5 empty] | 102.2552
26.10.2007 13:00 | 3600 | 2 | 758.84 | GGB | 768.132 | 773.297 | 768.864 | 262.17 | GGB | 10910.1 | GGB | 9.86 | GGB | 1030.75 | GGB | 59.81 | GGB | 175381.73 | GGB | 146384.39 | GGB | 0 | 0 | 2503 | 3600 | 2487.94 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 44497.34 | GGB | 44497.86 | 2487.94 | 2487.94 |  |  |  | 1 | 1 |  |  |  |  | 146384.39 | 2487.94 | 146384.39 | 2487.94 | 9.1026 | [5 empty] | 101.1654
26.10.2007 14:00 | 3600 | 2 | 758.95 | GGB | 767.033 | 773.32 | 767.766 | 261.69 | GGB | 10890.6 | GGB | 9.86 | GGB | 1030.66 | GGB | 59.93 | GGB | 174713.83 | GGB | 145761.9 | GGB | 0 | 0 | 2491 | 3600 | 2475.67 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 44536.89 | GGB | 44537.41 | 2475.67 | 2475.67 |  |  |  | 1 | 1 |  |  |  |  | 145761.9 | 2475.67 | 145761.9 | 2475.67 | 9.1241 | [5 empty] | 100.2384
26.10.2007 15:00 | 3600 | 2 | 758.9 | GGB | 767.033 | 773.273 | 767.766 | 261.67 | GGB | 10885.8 | GGB | 9.86 | GGB | 1030.42 | GGB | 59.98 | GGB | 174597.19 | GGB | 145610.19 | GGB | 0 | 0 | 2493 | 3600 | 2477.79 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 44577.01 | GGB | 44577.54 | 2477.79 | 2477.79 |  |  |  | 1 | 1 |  |  |  |  | 145610.19 | 2477.79 | 145610.19 | 2477.79 | 8.9906 | [5 empty] | 100.2199
26.10.2007 16:00 | 3600 | 2 | 758.93 | GGB | 767.033 | 772.242 | 767.766 | 261.47 | GGB | 10870.2 | GGB | 9.85 | GGB | 1030.37 | GGB | 60.1 | GGB | 174203.27 | GGB | 145218.57 | GGB | 0 | 0 | 2486 | 3600 | 2471.17 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 44616.58 | GGB | 44617.11 | 2471.17 | 2471.17 |  |  |  | 1 | 1 |  |  |  |  | 145218.57 | 2471.17 | 145218.57 | 2471.17 | 9.069 | [5 empty] | 99.6833
26.10.2007 17:00 | 3600 | 2 | 759.07 | GGB | 765.934 | 771.258 | 766.667 | 261.4 | GGB | 10840.4 | GGB | 9.85 | GGB | 1029.8 | GGB | 60.37 | GGB | 173708.12 | GGB | 144610.02 | GGB | 0 | 0 | 2465 | 3600 | 2450.24 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 44656.52 | GGB | 44657.05 | 2450.24 | 2450.24 |  |  |  | 1 | 1 |  |  |  |  | 144610.02 | 2450.24 | 144610.02 | 2450.24 | 8.8715 | [5 empty] | 98.4248
26.10.2007 18:00 | 3600 | 2 | 759.16 | GGB | 765.934 | 771.422 | 767.766 | 262.39 | GGB | 10873 | GGB | 9.85 | GGB | 1029.89 | GGB | 60.23 | GGB | 174631.3 | GGB | 145452.5 | GGB | 0 | 0 | 2483 | 3600 | 2468.25 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 44695.96 | GGB | 44696.49 | 2468.25 | 2468.25 |  |  |  | 1 | 1 |  |  |  |  | 145452.5 | 2468.25 | 145452.5 | 2468.25 | 9.1028 | [5 empty] | 99.7259
26.10.2007 19:00 | 3600 | 2 | 759.27 | GGB | 767.033 | 772.453 | 767.766 | 262.36 | GGB | 10891.7 | GGB | 9.86 | GGB | 1029.6 | GGB | 60.17 | GGB | 174964.71 | GGB | 145714.01 | GGB | 0 | 0 | 2484 | 3600 | 2469.02 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 44735.56 | GGB | 44736.09 | 2469.02 | 2469.02 |  |  |  | 1 | 1 |  |  |  |  | 145714.01 | 2469.02 | 145714.01 | 2469.02 | 9.0851 | [5 empty] | 99.9363
26.10.2007 20:00 | 3600 | 2 | 758.07 | GGB | 764.835 | 770.227 | 766.667 | 262.76 | GGB | 10923.4 | GGB | 9.84 | GGB | 1029.38 | GGB | 59.6 | GGB | 176902.4 | GGB | 147552.25 | GGB | 0 | 0 | 2544 | 3600 | 2528.82 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 44775.28 | GGB | 44775.82 | 2528.82 | 2528.82 |  |  |  | 1 | 1 |  |  |  |  | 147552.25 | 2528.82 | 147552.25 | 2528.82 | 9.3917 | [5 empty] | 103.6481
26.10.2007 21:00 | 3600 | 2 | 758.92 | GGB | 765.934 | 771.68 | 767.766 | 263.65 | GGB | 10934.4 | GGB | 9.86 | GGB | 1029.66 | GGB | 59.32 | GGB | 177505.39 | GGB | 148219.28 | GGB | 0 | 0 | 2510 | 3600 | 2495.16 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 44815.13 | GGB | 44815.67 | 2495.16 | 2495.16 |  |  |  | 1 | 1 |  |  |  |  | 148219.28 | 2495.16 | 148219.28 | 2495.16 | 9.2806 | [5 empty] | 102.7308
26.10.2007 22:00 | 3600 | 2 | 758.36 | GGB | 765.934 | 771.703 | 766.667 | 263.41 | GGB | 10911.1 | GGB | 9.85 | GGB | 1030.01 | GGB | 59.62 | GGB | 175780.06 | GGB | 146697.28 | GGB | 0 | 0 | 2534 | 3600 | 2518.56 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 44855.42 | GGB | 44855.96 | 2518.56 | 2518.56 |  |  |  | 1 | 1 |  |  |  |  | 146697.28 | 2518.56 | 146697.28 | 2518.56 | 9.1702 | [5 empty] | 102.6294
26.10.2007 23:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 771.75 | 767.766 | 264.41 | GGB | 10930.6 | GGB | 9.85 | GGB | 1030.34 | GGB | 59.56 | GGB | 176363.24 | GGB | 147257.25 | GGB | 0 | 0 | 2545 | 3600 | 2529.99 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 44894.6 | GGB | 44895.14 | 2529.99 | 2529.99 |  |  |  | 1 | 1 |  |  |  |  | 147257.25 | 2529.99 | 147257.25 | 2529.99 | 9.5089 | [5 empty] | 103.4887
26.10.2007 24:00 | 3600 | 2 | 758.38 | GGB | 764.835 | 770.672 | 766.3 | 264.36 | GGB | 10950.5 | GGB | 9.85 | GGB | 1030.47 | GGB | 59.43 | GGB | 176798.97 | GGB | 147694.38 | GGB | 0 | 0 | 2548 | 3600 | 2533.22 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 44934.96 | GGB | 44935.5 | 2533.22 | 2533.22 |  |  |  | 1 | 1 |  |  |  |  | 147694.38 | 2533.22 | 147694.38 | 2533.22 | 9.2701 | [5 empty] | 103.9284
27.10.2007 01:00 | 3600 | 2 | 758.13 | GGB | 764.835 | 770.531 | 766.3 | 265.38 | GGB | 10968.4 | GGB | 9.85 | GGB | 1030.33 | GGB | 58.97 | GGB | 178271.22 | GGB | 149110 | GGB | 0 | 0 | 2569 | 3600 | 2553.56 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 44974.44 | GGB | 44974.98 | 2553.56 | 2553.56 |  |  |  | 1 | 1 |  |  |  |  | 149110 | 2553.56 | 149110 | 2553.56 | 9.6444 | [5 empty] | 105.767 | 2534.5584
27.10.2007 02:00 | 3600 | 2 | 758.5 | GGB | 765.934 | 771.891 | 767.766 | 264.59 | GGB | 10992.3 | GGB | 9.86 | GGB | 1030.64 | GGB | 59.03 | GGB | 177532.89 | GGB | 148510.46 | GGB | 0 | 0 | 2558 | 3600 | 2543.1 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 45014.67 | GGB | 45015.2 | 2543.1 | 2543.1 |  |  |  | 1 | 1 |  |  |  |  | 148510.46 | 2543.1 | 148510.46 | 2543.1 | 9.3903 | [5 empty] | 104.9103
27.10.2007 03:00 | 3600 | 2 | 757.89 | GGB | 765.934 | 771.844 | 766.667 | 265.06 | GGB | 10996 | GGB | 9.85 | GGB | 1030.48 | GGB | 58.82 | GGB | 177915.81 | GGB | 148905.2 | GGB | 0 | 0 | 2587 | 3600 | 2571.87 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 45054.79 | GGB | 45055.32 | 2571.87 | 2571.87 |  |  |  | 1 | 1 |  |  |  |  | 148905.2 | 2571.87 | 148905.2 | 2571.87 | 9.5455 | [5 empty] | 106.3791 | 2538.0443
27.10.2007 04:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 771.586 | 767.033 | 264.59 | GGB | 10994.4 | GGB | 9.86 | GGB | 1030.52 | GGB | 58.82 | GGB | 177604.42 | GGB | 148647.03 | GGB | 0 | 0 | 2567 | 3600 | 2552.03 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 45094.88 | GGB | 45095.41 | 2552.03 | 2552.03 |  |  |  | 1 | 1 |  |  |  |  | 148647.03 | 2552.03 | 148647.03 | 2552.03 | 9.4625 | [5 empty] | 105.3755 | 2542.4524
27.10.2007 05:00 | 3600 | 2 | 758.21 | GGB | 765.934 | 771.586 | 766.667 | 264.11 | GGB | 10972 | GGB | 9.85 | GGB | 1030.19 | GGB | 58.95 | GGB | 177213.8 | GGB | 148214.8 | GGB | 0 | 0 | 2565 | 3600 | 2549.44 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 45135.27 | GGB | 45135.8 | 2549.44 | 2549.44 |  |  |  | 1 | 1 |  |  |  |  | 148214.8 | 2549.44 | 148214.8 | 2549.44 | 9.3554 | [5 empty] | 104.9624
27.10.2007 06:00 | 3600 | 2 | 758.43 | GGB | 765.934 | 772.828 | 767.033 | 263.67 | GGB | 10967.3 | GGB | 9.86 | GGB | 1030.2 | GGB | 59.08 | GGB | 176894.7 | GGB | 147893.19 | GGB | 0 | 0 | 2552 | 3600 | 2537.12 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 45175 | GGB | 45175.54 | 2537.12 | 2537.12 |  |  |  | 1 | 1 |  |  |  |  | 147893.19 | 2537.12 | 147893.19 | 2537.12 | 9.4419 | [5 empty] | 104.2285
27.10.2007 07:00 | 3600 | 2 | 758.21 | GGB | 765.934 | 771.914 | 767.033 | 263.54 | GGB | 10956.3 | GGB | 9.85 | GGB | 1030.26 | GGB | 59.17 | GGB | 176584.4 | GGB | 147603.84 | GGB | 0 | 0 | 2557 | 3600 | 2542.03 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 45215.39 | GGB | 45215.92 | 2542.03 | 2542.03 |  |  |  | 1 | 1 |  |  |  |  | 147603.84 | 2542.03 | 147603.84 | 2542.03 | 9.2921 | [5 empty] | 104.2259
27.10.2007 08:00 | 3600 | 2 | 758.44 | GGB | 765.934 | 771.914 | 767.033 | 263.41 | GGB | 10962.2 | GGB | 9.86 | GGB | 1030.09 | GGB | 59.05 | GGB | 176962.92 | GGB | 147948.68 | GGB | 0 | 0 | 2548 | 3600 | 2533.03 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 45255.13 | GGB | 45255.67 | 2533.03 | 2533.03 |  |  |  | 1 | 1 |  |  |  |  | 147948.68 | 2533.03 | 147948.68 | 2533.03 | 9.4279 | [5 empty] | 104.0996
27.10.2007 09:00 | 3600 | 2 | 758.26 | GGB | 767.033 | 771.914 | 768.132 | 263.28 | GGB | 10954.4 | GGB | 9.85 | GGB | 1030.19 | GGB | 58.9 | GGB | 176724.15 | GGB | 147827.31 | GGB | 0 | 0 | 2551 | 3600 | 2535.97 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 45294.9 | GGB | 45295.44 | 2535.97 | 2535.97 |  |  |  | 1 | 1 |  |  |  |  | 147827.31 | 2535.97 | 147827.31 | 2535.97 | 9.4263 | [5 empty] | 104.1349
27.10.2007 10:00 | 3600 | 2 | 758.4 | GGB | 765.934 | 771.82 | 767.033 | 263.21 | GGB | 10946.7 | GGB | 9.86 | GGB | 1030.76 | GGB | 59.08 | GGB | 176067.24 | GGB | 147280.56 | GGB | 0 | 0 | 2544 | 3600 | 2528.26 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 45335.38 | GGB | 45335.92 | 2528.26 | 2528.26 |  |  |  | 1 | 1 |  |  |  |  | 147280.56 | 2528.26 | 147280.56 | 2528.26 | 9.1987 | [5 empty] | 103.4343
27.10.2007 11:00 | 3600 | 2 | 757.93 | GGB | 764.835 | 771.609 | 766.667 | 262.8 | GGB | 10937.6 | GGB | 9.86 | GGB | 1030.82 | GGB | 59.35 | GGB | 175871.38 | GGB | 147005.59 | GGB | 0 | 0 | 2529 | 3600 | 2514.15 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 45374.66 | GGB | 45375.2 | 2514.15 | 2514.15 |  |  |  | 1 | 1 |  |  |  |  | 147005.59 | 2514.15 | 147005.59 | 2514.15 | 9.4092 | [5 empty] | 102.665
27.10.2007 12:00 | 3600 | 2 | 757.74 | GGB | 765.934 | 771.422 | 767.033 | 261.93 | GGB | 10905.2 | GGB | 9.86 | GGB | 1030.54 | GGB | 59.61 | GGB | 175036.23 | GGB | 146153.61 | GGB | 0 | 0 | 2508 | 3600 | 2492.44 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 45413.26 | GGB | 45413.8 | 2492.44 | 2492.44 |  |  |  | 1 | 1 |  |  |  |  | 146153.61 | 2492.44 | 146153.61 | 2492.44 | 9.4373 | [5 empty] | 101.1886
27.10.2007 13:00 | 3600 | 2 | 758.06 | GGB | 765.934 | 772.57 | 767.766 | 261.21 | GGB | 10878.8 | GGB | 9.86 | GGB | 1030.39 | GGB | 59.91 | GGB | 174141.65 | GGB | 145252.88 | GGB | 0 | 0 | 2487 | 3600 | 2471.37 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 45454.16 | GGB | 45454.7 | 2471.37 | 2471.37 |  |  |  | 1 | 1 |  |  |  |  | 145252.88 | 2471.37 | 145252.88 | 2471.37 | 8.7769 | [5 empty] | 99.7149
27.10.2007 14:00 | 3600 | 2 | 758.05 | GGB | 765.934 | 772.664 | 767.766 | 260.78 | GGB | 10843.3 | GGB | 9.86 | GGB | 1029.43 | GGB | 60.1 | GGB | 173433.04 | GGB | 144446.97 | GGB | 0 | 0 | 2468 | 3600 | 2452.72 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 45493.42 | GGB | 45493.96 | 2452.72 | 2452.72 |  |  |  | 1 | 1 |  |  |  |  | 144446.97 | 2452.72 | 144446.97 | 2452.72 | 9.0241 | [5 empty] | 98.4133
27.10.2007 15:00 | 3600 | 2 | 758.33 | GGB | 767.033 | 772.664 | 767.766 | 260.19 | GGB | 10816.5 | GGB | 9.86 | GGB | 1029.05 | GGB | 60.44 | GGB | 172707.91 | GGB | 143642.51 | GGB | 0 | 0 | 2449 | 3600 | 2433.75 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 45533.31 | GGB | 45533.85 | 2433.75 | 2433.75 |  |  |  | 1 | 1 |  |  |  |  | 143642.51 | 2433.75 | 143642.51 | 2433.75 | 8.7638 | [5 empty] | 97.1083
27.10.2007 16:00 | 3600 | 2 | 758.78 | GGB | 767.033 | 772.664 | 768.864 | 259.12 | GGB | 10771 | GGB | 9.86 | GGB | 1027.93 | GGB | 60.84 | GGB | 171700 | GGB | 142478.78 | GGB | 0 | 0 | 2416 | 3600 | 2400.9 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 45572.9 | GGB | 45573.44 | 2400.9 | 2400.9 |  |  |  | 1 | 1 |  |  |  |  | 142478.78 | 2400.9 | 142478.78 | 2400.9 | 8.6405 | [5 empty] | 95.0215
27.10.2007 17:00 | 3600 | 2 | 758.62 | GGB | 767.033 | 772.664 | 767.766 | 258.18 | GGB | 10726.4 | GGB | 9.85 | GGB | 1026.9 | GGB | 61.13 | GGB | 170850.54 | GGB | 141508.2 | GGB | 0 | 0 | 2395 | 3600 | 2379.86 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 45611.98 | GGB | 45612.52 | 2379.86 | 2379.86 |  |  |  | 1 | 1 |  |  |  |  | 141508.2 | 2379.86 | 141508.2 | 2379.86 | 8.6174 | [5 empty] | 93.5471
27.10.2007 18:00 | 3600 | 2 | 758.59 | GGB | 765.934 | 771.68 | 766.667 | 258.49 | GGB | 10719.1 | GGB | 9.85 | GGB | 1026.88 | GGB | 61.21 | GGB | 170632.68 | GGB | 141292.43 | GGB | 0 | 0 | 2400 | 3600 | 2385.24 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 45651.54 | GGB | 45652.08 | 2385.24 | 2385.24 |  |  |  | 1 | 1 |  |  |  |  | 141292.43 | 2385.24 | 141292.43 | 2385.24 | 8.5191 | [5 empty] | 93.6157
27.10.2007 19:00 | 3600 | 2 | 758.34 | GGB | 767.033 | 772.688 | 768.864 | 259.79 | GGB | 10766.5 | GGB | 9.85 | GGB | 1027.36 | GGB | 61.01 | GGB | 172118.13 | GGB | 142673.32 | GGB | 0 | 0 | 2431 | 3600 | 2416.22 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 45690.27 | GGB | 45690.81 | 2416.22 | 2416.22 |  |  |  | 1 | 1 |  |  |  |  | 142673.32 | 2416.22 | 142673.32 | 2416.22 | 8.9009 | [5 empty] | 95.7584
27.10.2007 20:00 | 3600 | 2 | 758.3 | GGB | 767.033 | 771.469 | 767.033 | 260.58 | GGB | 10795.5 | GGB | 9.85 | GGB | 1027.52 | GGB | 60.68 | GGB | 173183.26 | GGB | 143719.4 | GGB | 0 | 0 | 2450 | 3600 | 2434.38 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 45730.08 | GGB | 45730.62 | 2434.38 | 2434.38 |  |  |  | 1 | 1 |  |  |  |  | 143719.4 | 2434.38 | 143719.4 | 2434.38 | 8.7884 | [5 empty] | 97.1855
27.10.2007 21:00 | 3600 | 2 | 757.87 | GGB | 764.835 | 770.367 | 765.934 | 261.68 | GGB | 10843.4 | GGB | 9.85 | GGB | 1027.89 | GGB | 60.41 | GGB | 174224.18 | GGB | 144753.91 | GGB | 0 | 0 | 2487 | 3600 | 2471.49 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 45769.15 | GGB | 45769.68 | 2471.49 | 2471.49 |  |  |  | 1 | 1 |  |  |  |  | 144753.91 | 2471.49 | 144753.91 | 2471.49 | 9.1592 | [5 empty] | 99.3772
27.10.2007 22:00 | 3600 | 2 | 757.57 | GGB | 763.37 | 769.477 | 764.835 | 261.97 | GGB | 10906.9 | GGB | 9.85 | GGB | 1028.59 | GGB | 59.68 | GGB | 176038.64 | GGB | 146683.13 | GGB | 0 | 0 | 2527 | 3600 | 2512.01 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 45808.75 | GGB | 45809.29 | 2512.01 | 2512.01 |  |  |  | 0 | 1 | [14 empty] | 102.3526
27.10.2007 23:00 | 3600 | 2 | 757.25 | GGB | 765.934 | 771.68 | 767.033 | 263.7 | GGB | 10915.9 | GGB | 9.84 | GGB | 1028.76 | GGB | 59.4 | GGB | 176946.41 | GGB | 147586.23 | GGB | 0 | 0 | 2549 | 3600 | 2533.97 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 45849.36 | GGB | 45849.9 | 2533.97 | 2533.97 |  |  |  | 1 | 1 |  |  |  |  | 147586.23 | 2533.97 | 147586.23 | 2533.97 | 9.209 | [5 empty] | 103.8831
27.10.2007 24:00 | 3600 | 2 | 758.06 | GGB | 764.835 | 770.602 | 765.934 | 264.62 | GGB | 10952.4 | GGB | 9.87 | GGB | 1028.91 | GGB | 58.77 | GGB | 178347.14 | GGB | 149060.5 | GGB | 0 | 0 | 2521 | 3600 | 2506.11 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 45888.11 | GGB | 45888.65 | 2506.11 | 2506.11 |  |  |  | 1 | 1 |  |  |  |  | 149060.5 | 2506.11 | 149060.5 | 2506.11 | 9.6403 | [5 empty] | 103.7672
28.10.2007 01:00 | 3600 | 2 | 757.38 | GGB | 764.469 | 769.594 | 767.033 | 263.79 | GGB | 10954.6 | GGB | 9.85 | GGB | 1028.59 | GGB | 59.11 | GGB | 177309.53 | GGB | 147994.68 | GGB | 0 | 0 | 2563 | 3600 | 2547.78 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 45928.97 | GGB | 45929.51 | 2547.78 | 2547.78 |  |  |  | 1 | 1 |  |  |  |  | 147994.68 | 2547.78 | 147994.68 | 2547.78 | 9.228 | [5 empty] | 104.7383
28.10.2007 02:00 | 3600 | 2 | 756.91 | GGB | 764.835 | 769.547 | 765.201 | 265.38 | GGB | 10974.2 | GGB | 9.84 | GGB | 1028.79 | GGB | 58.92 | GGB | 178239.31 | GGB | 148883.8 | GGB | 0 | 0 | 2600 | 3599 | 2584.19 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 45968.18 | GGB | 45968.72 | 2584.19 | 2584.19 |  |  |  | 1 | 1 |  |  |  |  | 148883.8 | 2584.19 | 148883.8 | 2584.19 | 9.8124 | [5 empty] | 106.8733 | 2538.4091
28.10.2007 03:00 | 3600 | 2 | 756.92 | GGB | 765.934 | 771.891 | 767.033 | 265.62 | GGB | 10966.3 | GGB | 9.82 | GGB | 1028.55 | GGB | 58.68 | GGB | 178855.5 | GGB | 149474.04 | GGB | 0 | 0 | 2593 | 3600 | 2577.38 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 46007.64 | GGB | 46008.18 | 2577.38 | 2577.38 |  |  |  | 1 | 1 |  |  |  |  | 149474.04 | 2577.38 | 149474.04 | 2577.38 | 9.7631 | [5 empty] | 107.0143 | 2528.3855
28.10.2007 04:00 | 3600 | 2 | 757.34 | GGB | 764.835 | 770.719 | 765.934 | 265.28 | GGB | 11026.6 | GGB | 9.86 | GGB | 1028.44 | GGB | 58.44 | GGB | 179160.29 | GGB | 149820.67 | GGB | 0 | 0 | 2592 | 3470 | 2576.64 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 46048.1 | GGB | 46048.64 | 2576.64 | 2576.64 |  |  |  | 1 | 1 |  |  |  |  | 149820.67 | 2576.64 | 149820.67 | 2576.64 | 9.5411 | [5 empty] | 107.2316 | 2522.5358
28.10.2007 05:00 | 3600 | 2 | 757.45 | GGB | 765.934 | 771.82 | 768.132 | 265.13 | GGB | 10977.8 | GGB | 9.85 | GGB | 1028.27 | GGB | 58.38 | GGB | 179007.35 | GGB | 149693.38 | GGB | 0 | 0 | 2569 | 3600 | 2553.55 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 46088.45 | GGB | 46088.99 | 2553.55 | 2553.55 |  |  |  | 1 | 1 |  |  |  |  | 149693.38 | 2553.55 | 149693.38 | 2553.55 | 9.4733 | [5 empty] | 106.1804 | 2524.6808
28.10.2007 06:00 | 3600 | 2 | 758.63 | GGB | 765.934 | 771.703 | 767.033 | 263.26 | GGB | 10967.8 | GGB | 9.87 | GGB | 1027.84 | GGB | 58.8 | GGB | 177189.59 | GGB | 147925.28 | GGB | 0 | 0 | 2511 | 3600 | 2495.56 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 46128.01 | GGB | 46128.55 | 2495.56 | 2495.56 |  |  |  | 1 | 1 |  |  |  |  | 147925.28 | 2495.56 | 147925.28 | 2495.56 | 9.3316 | [5 empty] | 102.5434
28.10.2007 07:00 | 3600 | 2 | 757.96 | GGB | 765.934 | 771.703 | 767.033 | 262.52 | GGB | 10923.5 | GGB | 9.86 | GGB | 1027.66 | GGB | 59.2 | GGB | 175685.43 | GGB | 146467.21 | GGB | 0 | 0 | 2527 | 3600 | 2511.47 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 46168.77 | GGB | 46169.31 | 2511.47 | 2511.47 |  |  |  | 1 | 1 |  |  |  |  | 146467.21 | 2511.47 | 146467.21 | 2511.47 | 9.0247 | [5 empty] | 102.18
28.10.2007 08:00 | 3600 | 2 | 757.77 | GGB | 765.934 | 771.656 | 767.766 | 262.52 | GGB | 10898.7 | GGB | 9.85 | GGB | 1027.45 | GGB | 59.44 | GGB | 175418.04 | GGB | 146106.59 | GGB | 0 | 0 | 2530 | 3600 | 2514.42 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 46208.12 | GGB | 46208.66 | 2514.42 | 2514.42 |  |  |  | 1 | 1 |  |  |  |  | 146106.59 | 2514.42 | 146106.59 | 2514.42 | 9.336 | [5 empty] | 102.0481
28.10.2007 09:00 | 3600 | 2 | 757.97 | GGB | 765.934 | 771.68 | 767.766 | 261.61 | GGB | 10891.6 | GGB | 9.86 | GGB | 1027.49 | GGB | 59.64 | GGB | 174948.2 | GGB | 145637.06 | GGB | 0 | 0 | 2514 | 3600 | 2499.12 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 46248.29 | GGB | 46248.83 | 2499.12 | 2499.12 |  |  |  | 1 | 1 |  |  |  |  | 145637.06 | 2499.12 | 145637.06 | 2499.12 | 9.0606 | [5 empty] | 101.1012
28.10.2007 10:00 | 3600 | 2 | 757.92 | GGB | 767.033 | 772.805 | 767.766 | 261.38 | GGB | 10867 | GGB | 9.86 | GGB | 1027.62 | GGB | 59.91 | GGB | 174393.63 | GGB | 145074.96 | GGB | 0 | 0 | 2506 | 3600 | 2490.92 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 46287.89 | GGB | 46288.43 | 2490.92 | 2490.92 |  |  |  | 1 | 1 |  |  |  |  | 145074.96 | 2490.92 | 145074.96 | 2490.92 | 9.1255 | [5 empty] | 100.3806
28.10.2007 11:00 | 3600 | 2 | 757.98 | GGB | 767.033 | 772.852 | 768.864 | 261.74 | GGB | 10831.2 | GGB | 9.85 | GGB | 1027.49 | GGB | 60.03 | GGB | 174637.91 | GGB | 145207.98 | GGB | 0 | 0 | 2485 | 3600 | 2470.12 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 46327.5 | GGB | 46328.04 | 2470.12 | 2470.12 |  |  |  | 1 | 1 |  |  |  |  | 145207.98 | 2470.12 | 145207.98 | 2470.12 | 9.0553 | [5 empty] | 99.6336
28.10.2007 12:00 | 3600 | 2 | 758.35 | GGB | 767.033 | 772.898 | 768.864 | 261.84 | GGB | 10804.2 | GGB | 9.86 | GGB | 1027.13 | GGB | 59.69 | GGB | 175387.24 | GGB | 145927.33 | GGB | 0 | 0 | 2435 | 3600 | 2419.83 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 46367.02 | GGB | 46367.56 | 2419.83 | 2419.83 |  |  |  | 1 | 1 |  |  |  |  | 145927.33 | 2419.83 | 145927.33 | 2419.83 | 8.9352 | [5 empty] | 98.0887
28.10.2007 13:00 | 3600 | 2 | 758.81 | GGB | 767.033 | 772.898 | 768.864 | 260.37 | GGB | 10789.5 | GGB | 9.87 | GGB | 1026.12 | GGB | 60.11 | GGB | 173887.48 | GGB | 144353.94 | GGB | 0 | 0 | 2418 | 3600 | 2403.06 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 46405.91 | GGB | 46406.45 | 2403.06 | 2403.06 |  |  |  | 1 | 1 |  |  |  |  | 144353.94 | 2403.06 | 144353.94 | 2403.06 | 8.9198 | [5 empty] | 96.3587
28.10.2007 14:00 | 3600 | 2 | 758.34 | GGB | 765.934 | 772.898 | 767.766 | 258.62 | GGB | 10769.1 | GGB | 9.86 | GGB | 1025.03 | GGB | 60.91 | GGB | 171869.46 | GGB | 142185.8 | GGB | 0 | 0 | 2432 | 3600 | 2416.36 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 46445.61 | GGB | 46446.15 | 2416.36 | 2416.36 |  |  |  | 1 | 1 |  |  |  |  | 142185.8 | 2416.36 | 142185.8 | 2416.36 | 8.6542 | [5 empty] | 95.4367
28.10.2007 15:00 | 3600 | 2 | 758.43 | GGB | 765.934 | 771.82 | 767.766 | 258 | GGB | 10740.9 | GGB | 9.86 | GGB | 1024.09 | GGB | 61.15 | GGB | 171368.8 | GGB | 141539.26 | GGB | 0 | 0 | 2420 | 3600 | 2404.71 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 46484.23 | GGB | 46484.77 | 2404.71 | 2404.71 |  |  |  | 1 | 1 |  |  |  |  | 141539.26 | 2404.71 | 141539.26 | 2404.71 | 8.8131 | [5 empty] | 94.5447
28.10.2007 16:00 | 3600 | 2 | 758.35 | GGB | 767.033 | 772.898 | 768.864 | 257.67 | GGB | 10720.7 | GGB | 9.86 | GGB | 1023.32 | GGB | 61.29 | GGB | 170760.32 | GGB | 140874.74 | GGB | 0 | 0 | 2413 | 3600 | 2397.72 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 46523.95 | GGB | 46524.49 | 2397.72 | 2397.72 |  |  |  | 1 | 1 |  |  |  |  | 140874.74 | 2397.72 | 140874.74 | 2397.72 | 8.504 | [5 empty] | 93.8273
28.10.2007 17:00 | 3600 | 2 | 758.48 | GGB | 767.033 | 771.82 | 767.766 | 257.79 | GGB | 10710.6 | GGB | 9.85 | GGB | 1023.17 | GGB | 61.47 | GGB | 170519.34 | GGB | 140576.3 | GGB | 0 | 0 | 2411 | 3600 | 2395.94 | GGB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 46562.48 | GGB | 46563.02 | 2395.94 | 2395.94 |  |  |  | 1 | 1 |  |  |  |  | 140576.3 | 2395.94 | 140576.3 | 2395.94 | 8.7416 | [5 empty] | 93.559
28.10.2007 18:00 | 3600 | 2 | 758.43 | GGB | 765.934 | 771.797 | 767.766 | 258.21 | GGB | 10716.2 | GGB | 9.85 | GGB | 1023.22 | GGB | 61.56 | GGB | 171003.49 | GGB | 140946.07 | GGB | 0 | 0 | 2418 | 3600 | 2402.4 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 46601.88 | GGB | 46602.43 | 2402.4 | 2402.4 |  |  |  | 1 | 1 |  |  |  |  | 140946.07 | 2402.4 | 140946.07 | 2402.4 | 8.592 | [5 empty] | 94.058
28.10.2007 19:00 | 3600 | 2 | 758.39 | GGB | 767.033 | 773.109 | 767.766 | 258.54 | GGB | 10728.7 | GGB | 9.85 | GGB | 1022.91 | GGB | 61.37 | GGB | 171274.17 | GGB | 141207.24 | GGB | 0 | 0 | 2424 | 3600 | 2408.65 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 46640.97 | GGB | 46641.51 | 2408.65 | 2408.65 |  |  |  | 1 | 1 |  |  |  |  | 141207.24 | 2408.65 | 141207.24 | 2408.65 | 8.7031 | [5 empty] | 94.4774
28.10.2007 20:00 | 3600 | 2 | 758.51 | GGB | 765.934 | 773.039 | 767.766 | 258.6 | GGB | 10737.2 | GGB | 9.85 | GGB | 1023.01 | GGB | 61.35 | GGB | 171597.67 | GGB | 141496.68 | GGB | 0 | 0 | 2427 | 3600 | 2411.44 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 46679.99 | GGB | 46680.53 | 2411.44 | 2411.44 |  |  |  | 1 | 1 |  |  |  |  | 141496.68 | 2411.44 | 141496.68 | 2411.44 | 8.7445 | [5 empty] | 94.7808
28.10.2007 21:00 | 3600 | 2 | 758.42 | GGB | 765.934 | 771.984 | 767.766 | 258.45 | GGB | 10737 | GGB | 9.85 | GGB | 1022.9 | GGB | 61.3 | GGB | 171723.11 | GGB | 141606.71 | GGB | 0 | 0 | 2430 | 3600 | 2415.22 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 46719.53 | GGB | 46720.07 | 2415.22 | 2415.22 |  |  |  | 1 | 1 |  |  |  |  | 141606.71 | 2415.22 | 141606.71 | 2415.22 | 8.6498 | [5 empty] | 95.0032
28.10.2007 22:00 | 3600 | 2 | 757.99 | GGB | 765.934 | 771.867 | 767.766 | 258.76 | GGB | 10748.9 | GGB | 9.85 | GGB | 1022.4 | GGB | 60.91 | GGB | 172279.88 | GGB | 142163.18 | GGB | 0 | 0 | 2448 | 3600 | 2432.54 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 46758.36 | GGB | 46758.9 | 2432.54 | 2432.54 |  |  |  | 1 | 1 |  |  |  |  | 142163.18 | 2432.54 | 142163.18 | 2432.54 | 8.9059 | [5 empty] | 96.0605
28.10.2007 23:00 | 3600 | 2 | 757.95 | GGB | 765.934 | 771.914 | 767.766 | 258.91 | GGB | 10784.4 | GGB | 9.85 | GGB | 1022.34 | GGB | 60.52 | GGB | 172876.26 | GGB | 142812.73 | GGB | 0 | 0 | 2467 | 3600 | 2451.74 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 46797.8 | GGB | 46798.35 | 2451.74 | 2451.74 |  |  |  | 1 | 1 |  |  |  |  | 142812.73 | 2451.74 | 142812.73 | 2451.74 | 8.8755 | [5 empty] | 97.261
28.10.2007 24:00 | 3600 | 2 | 757.72 | GGB | 765.934 | 772.008 | 767.766 | 260.42 | GGB | 10809.7 | GGB | 9.85 | GGB | 1022.78 | GGB | 60.55 | GGB | 173781.84 | GGB | 143609.97 | GGB | 0 | 0 | 2494 | 3600 | 2478.45 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 46836.55 | GGB | 46837.1 | 2478.45 | 2478.45 |  |  |  | 1 | 1 |  |  |  |  | 143609.97 | 2478.45 | 143609.97 | 2478.45 | 9.1853 | [5 empty] | 98.8695
29.10.2007 01:00 | 3600 | 2 | 757.89 | GGB | 765.934 | 771.773 | 766.667 | 261.15 | GGB | 10849.4 | GGB | 9.85 | GGB | 1022.43 | GGB | 60.27 | GGB | 174843.67 | GGB | 144556.57 | GGB | 0 | 0 | 2503 | 3600 | 2487.67 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 46876.64 | GGB | 46877.2 | 2487.67 | 2487.67 |  |  |  | 1 | 1 |  |  |  |  | 144556.57 | 2487.67 | 144556.57 | 2487.67 | 8.9678 | [5 empty] | 99.8914
29.10.2007 02:00 | 3600 | 2 | 757.47 | GGB | 764.835 | 770.789 | 766.667 | 263 | GGB | 10850.6 | GGB | 9.84 | GGB | 1022.1 | GGB | 59.34 | GGB | 177685.84 | GGB | 147268.95 | GGB | 0 | 0 | 2517 | 3600 | 2501.52 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 46915.91 | GGB | 46916.46 | 2501.52 | 2501.52 |  |  |  | 1 | 1 |  |  |  |  | 147268.95 | 2501.52 | 147268.95 | 2501.52 | 9.3835 | [5 empty] | 102.3323
29.10.2007 03:00 | 3600 | 2 | 757.8 | GGB | 765.934 | 770.742 | 767.766 | 264.25 | GGB | 10903.6 | GGB | 9.86 | GGB | 1021.99 | GGB | 58.75 | GGB | 179287.93 | GGB | 148848.49 | GGB | 0 | 0 | 2523 | 3600 | 2508.23 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 46955.4 | GGB | 46955.96 | 2508.23 | 2508.23 |  |  |  | 1 | 1 |  |  |  |  | 148848.49 | 2508.23 | 148848.49 | 2508.23 | 9.4518 | [5 empty] | 103.7073
29.10.2007 04:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 770.836 | 766.667 | 260.56 | GGB | 10892.4 | GGB | 9.87 | GGB | 1021.51 | GGB | 59.65 | GGB | 175451.06 | GGB | 145201.02 | GGB | 0 | 0 | 2496 | 3600 | 2480.96 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 46995.57 | GGB | 46996.13 | 2480.96 | 2480.96 |  |  |  | 1 | 1 |  |  |  |  | 145201.02 | 2480.96 | 145201.02 | 2480.96 | 8.9678 | [5 empty] | 100.0661
29.10.2007 05:00 | 3600 | 2 | 757.81 | GGB | 764.835 | 770.766 | 766.667 | 259.68 | GGB | 10842 | GGB | 9.85 | GGB | 1020.9 | GGB | 59.77 | GGB | 174544.38 | GGB | 144309.21 | GGB | 0 | 0 | 2493 | 3600 | 2478.21 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 47034.6 | GGB | 47035.16 | 2478.21 | 2478.21 |  |  |  | 1 | 1 |  |  |  |  | 144309.21 | 2478.21 | 144309.21 | 2478.21 | 9.1629 | [5 empty] | 99.3413
29.10.2007 06:00 | 3600 | 2 | 757.93 | GGB | 765.934 | 771.844 | 767.766 | 259.58 | GGB | 10831.7 | GGB | 9.86 | GGB | 1020.33 | GGB | 59.89 | GGB | 174166.96 | GGB | 143868.45 | GGB | 0 | 0 | 2489 | 3600 | 2473.47 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 47075.02 | GGB | 47075.58 | 2473.47 | 2473.47 |  |  |  | 1 | 1 |  |  |  |  | 143868.45 | 2473.47 | 143868.45 | 2473.47 | 8.8039 | [5 empty] | 98.8484
29.10.2007 07:00 | 3600 | 2 | 757.89 | GGB | 765.934 | 771.844 | 767.766 | 258.72 | GGB | 10793.4 | GGB | 9.85 | GGB | 1020.01 | GGB | 60.28 | GGB | 173336.21 | GGB | 142969.02 | GGB | 0 | 0 | 2465 | 3600 | 2450.16 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 47113.72 | GGB | 47114.28 | 2450.16 | 2450.16 |  |  |  | 1 | 1 |  |  |  |  | 142969.02 | 2450.16 | 142969.02 | 2450.16 | 9.0516 | [5 empty] | 97.3047
29.10.2007 08:00 | 3600 | 2 | 757.95 | GGB | 767.033 | 771.844 | 767.766 | 258.51 | GGB | 10784.1 | GGB | 9.86 | GGB | 1020.32 | GGB | 60.42 | GGB | 173131.54 | GGB | 142784.66 | GGB | 0 | 0 | 2458 | 3600 | 2442.43 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 47153.57 | GGB | 47154.12 | 2442.43 | 2442.43 |  |  |  | 1 | 1 |  |  |  |  | 142784.66 | 2442.43 | 142784.66 | 2442.43 | 8.7536 | [5 empty] | 96.8726
29.10.2007 09:00 | 3600 | 2 | 758.06 | GGB | 767.033 | 772.875 | 768.864 | 258.42 | GGB | 10769.9 | GGB | 9.85 | GGB | 1020.66 | GGB | 60.53 | GGB | 172788.24 | GGB | 142500.5 | GGB | 0 | 0 | 2453 | 3600 | 2438.04 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 47192.75 | GGB | 47193.31 | 2438.04 | 2438.04 |  |  |  | 1 | 1 |  |  |  |  | 142500.5 | 2438.04 | 142500.5 | 2438.04 | 8.8651 | [5 empty] | 96.5061
29.10.2007 10:00 | 3600 | 2 | 758.32 | GGB | 765.934 | 771.773 | 767.766 | 257.63 | GGB | 10748.4 | GGB | 9.86 | GGB | 1020.34 | GGB | 60.65 | GGB | 172176.45 | GGB | 141901.96 | GGB | 0 | 0 | 2430 | 3600 | 2415 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 47231.92 | GGB | 47232.47 | 2415 | 2415 |  |  |  | 1 | 1 |  |  |  |  | 141901.96 | 2415 | 141901.96 | 2415 | 8.7511 | [5 empty] | 95.1926
29.10.2007 11:00 | 3600 | 2 | 758.12 | GGB | 767.033 | 771.867 | 767.766 | 257.14 | GGB | 10732.8 | GGB | 9.86 | GGB | 1019.84 | GGB | 60.69 | GGB | 171816.64 | GGB | 141514.96 | GGB | 0 | 0 | 2424 | 3600 | 2408.81 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 47271.42 | GGB | 47271.97 | 2408.81 | 2408.81 |  |  |  | 1 | 1 |  |  |  |  | 141514.96 | 2408.81 | 141514.96 | 2408.81 | 8.6299 | [5 empty] | 94.6896
29.10.2007 12:00 | 3600 | 2 | 757.92 | GGB | 765.934 | 772.852 | 767.766 | 256.85 | GGB | 10722.8 | GGB | 9.86 | GGB | 1019.69 | GGB | 60.85 | GGB | 171730.81 | GGB | 141356.38 | GGB | 0 | 0 | 2413 | 3600 | 2398.27 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 47310.25 | GGB | 47310.8 | 2398.27 | 2398.27 |  |  |  | 1 | 1 |  |  |  |  | 141356.38 | 2398.27 | 141356.38 | 2398.27 | 8.7306 | [5 empty] | 94.1697
29.10.2007 13:00 | 3600 | 2 | 758.27 | GGB | 767.033 | 772.875 | 767.766 | 257.9 | GGB | 10685.4 | GGB | 9.85 | GGB | 1019.34 | GGB | 60.47 | GGB | 172881.77 | GGB | 142419.27 | GGB | 0 | 0 | 2383 | 3600 | 2367.55 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 47350.06 | GGB | 47350.6 | 2367.55 | 2367.55 |  |  |  | 1 | 1 |  |  |  |  | 142419.27 | 2367.55 | 142419.27 | 2367.55 | 8.472 | [5 empty] | 93.6624
29.10.2007 14:00 | 3600 | 2 | 758.78 | GGB | 767.033 | 774.117 | 769.963 | 257.43 | GGB | 10672.4 | GGB | 9.86 | GGB | 1018.78 | GGB | 60.41 | GGB | 172487.85 | GGB | 142039.35 | GGB | 0 | 0 | 2357 | 3600 | 2341.67 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 47388.35 | GGB | 47388.89 | 2341.67 | 2341.67 |  |  |  | 1 | 1 |  |  |  |  | 142039.35 | 2341.67 | 142039.35 | 2341.67 | 8.6866 | [5 empty] | 92.3915
29.10.2007 15:00 | 3600 | 2 | 758.27 | GGB | 765.934 | 771.891 | 767.766 | 255.25 | GGB | 10651.3 | GGB | 9.85 | GGB | 1018.02 | GGB | 61.26 | GGB | 170048.4 | GGB | 139571.79 | GGB | 0 | 0 | 2371 | 3600 | 2355.73 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 47427.75 | GGB | 47428.3 | 2355.73 | 2355.73 |  |  |  | 1 | 1 |  |  |  |  | 139571.79 | 2355.73 | 139571.79 | 2355.73 | 8.3429 | [5 empty] | 91.3315
29.10.2007 16:00 | 3600 | 2 | 758.28 | GGB | 767.033 | 772.969 | 768.864 | 255.99 | GGB | 10665.6 | GGB | 9.85 | GGB | 1017.79 | GGB | 61.22 | GGB | 170670.09 | GGB | 140068.67 | GGB | 0 | 0 | 2374 | 3600 | 2359.06 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 47466.36 | GGB | 47466.91 | 2359.06 | 2359.06 |  |  |  | 1 | 1 |  |  |  |  | 140068.67 | 2359.06 | 140068.67 | 2359.06 | 8.5582 | [5 empty] | 91.7862
29.10.2007 17:00 | 3600 | 2 | 757.88 | GGB | 765.934 | 771.961 | 767.766 | 256.93 | GGB | 10700.4 | GGB | 9.85 | GGB | 1017.54 | GGB | 60.89 | GGB | 171702.2 | GGB | 141017.72 | GGB | 0 | 0 | 2405 | 3600 | 2389.67 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 47505.41 | GGB | 47505.95 | 2389.67 | 2389.67 |  |  |  | 1 | 1 |  |  |  |  | 141017.72 | 2389.67 | 141017.72 | 2389.67 | 8.6318 | [5 empty] | 93.6072
29.10.2007 18:00 | 3600 | 2 | 757.64 | GGB | 765.934 | 772.195 | 766.667 | 258.37 | GGB | 10752.3 | GGB | 9.85 | GGB | 1017.72 | GGB | 60.52 | GGB | 172919.18 | GGB | 142199.01 | GGB | 0 | 0 | 2443 | 3600 | 2427.94 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 47544.68 | GGB | 47545.23 | 2427.94 | 2427.94 |  |  |  | 1 | 1 |  |  |  |  | 142199.01 | 2427.94 | 142199.01 | 2427.94 | 8.7895 | [5 empty] | 95.903
29.10.2007 19:00 | 3600 | 2 | 757.48 | GGB | 764.835 | 771.023 | 766.667 | 259.19 | GGB | 10787.7 | GGB | 9.85 | GGB | 1017.49 | GGB | 60.23 | GGB | 173907.28 | GGB | 143107.55 | GGB | 0 | 0 | 2473 | 3600 | 2458.25 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 47583.52 | GGB | 47584.07 | 2458.25 | 2458.25 |  |  |  | 1 | 1 |  |  |  |  | 143107.55 | 2458.25 | 143107.55 | 2458.25 | 9.0575 | [5 empty] | 97.7206
29.10.2007 20:00 | 3600 | 2 | 757.8 | GGB | 765.934 | 772.102 | 767.766 | 258.67 | GGB | 10791.6 | GGB | 9.86 | GGB | 1017.64 | GGB | 60.25 | GGB | 173393.42 | GGB | 142694.02 | GGB | 0 | 0 | 2458 | 3600 | 2442.75 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 47623.4 | GGB | 47623.94 | 2442.75 | 2442.75 |  |  |  | 1 | 1 |  |  |  |  | 142694.02 | 2442.75 | 142694.02 | 2442.75 | 8.7426 | [5 empty] | 96.8238
29.10.2007 21:00 | 3600 | 2 | 757.93 | GGB | 765.934 | 771.984 | 767.766 | 257.62 | GGB | 10736.4 | GGB | 9.85 | GGB | 1017.75 | GGB | 60.49 | GGB | 172512.05 | GGB | 141882.38 | GGB | 0 | 0 | 2427 | 3600 | 2412.12 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 47661.59 | GGB | 47662.13 | 2412.12 | 2412.12 |  |  |  | 1 | 1 |  |  |  |  | 141882.38 | 2412.12 | 141882.38 | 2412.12 | 8.9614 | [5 empty] | 95.0659
29.10.2007 22:00 | 3600 | 2 | 758.21 | GGB | 765.934 | 772.008 | 767.766 | 258.87 | GGB | 10709.5 | GGB | 9.85 | GGB | 1017.17 | GGB | 59.84 | GGB | 174006.31 | GGB | 143311.84 | GGB | 0 | 0 | 2399 | 3600 | 2383.87 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 47701.34 | GGB | 47701.88 | 2383.87 | 2383.87 |  |  |  | 1 | 1 |  |  |  |  | 143311.84 | 2383.87 | 143311.84 | 2383.87 | 8.5946 | [5 empty] | 94.8991
29.10.2007 23:00 | 3600 | 2 | 758.16 | GGB | 765.934 | 772.031 | 767.766 | 256.86 | GGB | 10730.7 | GGB | 9.86 | GGB | 1016.7 | GGB | 60.54 | GGB | 171679.1 | GGB | 141032.16 | GGB | 0 | 0 | 2416 | 3600 | 2401.26 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 47740.04 | GGB | 47740.58 | 2401.26 | 2401.26 |  |  |  | 1 | 1 |  |  |  |  | 141032.16 | 2401.26 | 141032.16 | 2401.26 | 8.7508 | [5 empty] | 94.0708
29.10.2007 24:00 | 3600 | 2 | 757.86 | GGB | 765.934 | 772.031 | 767.766 | 256.55 | GGB | 10724.3 | GGB | 9.85 | GGB | 1016.36 | GGB | 60.48 | GGB | 171741.82 | GGB | 141059.58 | GGB | 0 | 0 | 2426 | 3600 | 2411.32 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 47778.38 | GGB | 47778.92 | 2411.32 | 2411.32 |  |  |  | 1 | 1 |  |  |  |  | 141059.58 | 2411.32 | 141059.58 | 2411.32 | 8.8717 | [5 empty] | 94.4833
30.10.2007 01:00 | 3600 | 2 | 757.91 | GGB | 765.934 | 772.031 | 766.667 | 257.81 | GGB | 10730.4 | GGB | 9.85 | GGB | 1015.79 | GGB | 60.65 | GGB | 172051.01 | GGB | 141165.43 | GGB | 0 | 0 | 2435 | 3600 | 2419.98 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 47818.69 | GGB | 47819.23 | 2419.98 | 2419.98 |  |  |  | 1 | 1 |  |  |  |  | 141165.43 | 2419.98 | 141165.43 | 2419.98 | 8.4748 | [5 empty] | 94.8938
30.10.2007 02:00 | 3600 | 2 | 757.78 | GGB | 765.934 | 772.031 | 767.033 | 258.52 | GGB | 10757.6 | GGB | 9.85 | GGB | 1015.06 | GGB | 60.43 | GGB | 173010.51 | GGB | 141941.77 | GGB | 0 | 0 | 2454 | 3600 | 2438.69 | GGB | 100 | GGB | 38.02 | GGB | 38.02 | GGB | 47856.71 | GGB | 47857.25 | 2438.69 | 2438.69 |  |  |  | 1 | 1 |  |  |  |  | 141941.77 | 2438.69 | 141941.77 | 2438.69 | 9.1045 | [5 empty] | 96.1533
30.10.2007 03:00 | 3600 | 2 | 757.81 | GGB | 765.934 | 772.031 | 767.766 | 258.39 | GGB | 10765.9 | GGB | 9.85 | GGB | 1014.84 | GGB | 60.36 | GGB | 173018.21 | GGB | 141947.11 | GGB | 0 | 0 | 2449 | 3600 | 2434.25 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 47897.39 | GGB | 47897.94 | 2434.25 | 2434.25 |  |  |  | 1 | 1 |  |  |  |  | 141947.11 | 2434.25 | 141947.11 | 2434.25 | 8.4919 | [5 empty] | 95.9819
30.10.2007 04:00 | 3600 | 2 | 757.72 | GGB | 765.934 | 772.031 | 766.667 | 258.33 | GGB | 10763.8 | GGB | 9.85 | GGB | 1014.31 | GGB | 60.28 | GGB | 173270.19 | GGB | 142113.23 | GGB | 0 | 0 | 2453 | 3600 | 2437.45 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 47935.58 | GGB | 47936.13 | 2437.45 | 2437.45 |  |  |  | 1 | 1 |  |  |  |  | 142113.23 | 2437.45 | 142113.23 | 2437.45 | 9.0703 | [5 empty] | 96.2205
30.10.2007 05:00 | 3600 | 2 | 757.57 | GGB | 764.835 | 770.789 | 766.667 | 259.1 | GGB | 10793.1 | GGB | 9.85 | GGB | 1014.3 | GGB | 59.99 | GGB | 174257.19 | GGB | 143049.18 | GGB | 0 | 0 | 2481 | 3600 | 2466.18 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 47975.43 | GGB | 47975.98 | 2466.18 | 2466.18 |  |  |  | 1 | 1 |  |  |  |  | 143049.18 | 2466.18 | 143049.18 | 2466.18 | 8.8528 | [5 empty] | 97.9958
30.10.2007 06:00 | 3600 | 2 | 757.34 | GGB | 765.934 | 770.789 | 766.667 | 259.97 | GGB | 10796.9 | GGB | 9.85 | GGB | 1014.19 | GGB | 59.49 | GGB | 175563.29 | GGB | 144322.66 | GGB | 0 | 0 | 2485 | 3600 | 2469.7 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 48014.93 | GGB | 48015.48 | 2469.7 | 2469.7 |  |  |  | 1 | 1 |  |  |  |  | 144322.66 | 2469.7 | 144322.66 | 2469.7 | 9.0236 | [5 empty] | 99.0094
30.10.2007 07:00 | 3600 | 2 | 757.49 | GGB | 765.934 | 770.813 | 767.766 | 260.52 | GGB | 10796.1 | GGB | 9.85 | GGB | 1014.07 | GGB | 58.99 | GGB | 176385.24 | GGB | 145197.6 | GGB | 0 | 0 | 2465 | 3600 | 2449.69 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 48053.89 | GGB | 48054.44 | 2449.69 | 2449.69 |  |  |  | 1 | 1 |  |  |  |  | 145197.6 | 2449.69 | 145197.6 | 2449.69 | 9.1296 | [5 empty] | 98.8025
30.10.2007 08:00 | 3600 | 2 | 757.62 | GGB | 765.934 | 770.789 | 767.766 | 261.09 | GGB | 10801.6 | GGB | 9.85 | GGB | 1014.02 | GGB | 58.69 | GGB | 177236.9 | GGB | 146024.32 | GGB | 0 | 0 | 2457 | 3600 | 2441.4 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 48093.5 | GGB | 48094.06 | 2441.4 | 2441.4 |  |  |  | 1 | 1 |  |  |  |  | 146024.32 | 2441.4 | 146024.32 | 2441.4 | 8.9981 | [5 empty] | 99.0288
30.10.2007 09:00 | 3600 | 2 | 758.21 | GGB | 767.033 | 772.945 | 767.766 | 260.22 | GGB | 10795.3 | GGB | 9.87 | GGB | 1013.98 | GGB | 58.75 | GGB | 176664.73 | GGB | 145521.07 | GGB | 0 | 0 | 2430 | 3600 | 2415.32 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 48132.8 | GGB | 48133.36 | 2415.32 | 2415.32 |  |  |  | 1 | 1 |  |  |  |  | 145521.07 | 2415.32 | 145521.07 | 2415.32 | 8.9435 | [5 empty] | 97.6333
30.10.2007 10:00 | 3600 | 2 | 758.23 | GGB | 767.033 | 773.016 | 767.766 | 258.95 | GGB | 10744.8 | GGB | 9.86 | GGB | 1014.49 | GGB | 59.09 | GGB | 175322.32 | GGB | 144339.3 | GGB | 0 | 0 | 2402 | 3600 | 2387.17 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 48172.04 | GGB | 48172.6 | 2387.17 | 2387.17 |  |  |  | 1 | 1 |  |  |  |  | 144339.3 | 2387.17 | 144339.3 | 2387.17 | 8.7809 | [5 empty] | 95.7118
30.10.2007 11:00 | 3600 | 2 | 758.4 | GGB | 768.132 | 772.969 | 769.963 | 257.14 | GGB | 10709.8 | GGB | 9.86 | GGB | 1013.95 | GGB | 59.34 | GGB | 173503.46 | GGB | 142659.51 | GGB | 0 | 0 | 2376 | 3600 | 2360.54 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 48211.34 | GGB | 48211.9 | 2360.54 | 2360.54 |  |  |  | 1 | 1 |  |  |  |  | 142659.51 | 2360.54 | 142659.51 | 2360.54 | 8.5688 | [5 empty] | 93.5426
30.10.2007 12:00 | 3600 | 2 | 758.39 | GGB | 765.934 | 773.016 | 768.864 | 254.15 | GGB | 10653.6 | GGB | 9.86 | GGB | 1013.32 | GGB | 60.6 | GGB | 169581.85 | GGB | 138819 | GGB | 0 | 0 | 2351 | 3600 | 2335.86 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 48249.99 | GGB | 48250.55 | 2335.86 | 2335.86 |  |  |  | 1 | 1 |  |  |  |  | 138819 | 2335.86 | 138819 | 2335.86 | 8.3897 | [5 empty] | 90.0727
30.10.2007 13:00 | 3600 | 2 | 758.54 | GGB | 767.033 | 773.016 | 768.864 | 253.37 | GGB | 10584.8 | GGB | 9.86 | GGB | 1012.69 | GGB | 61.11 | GGB | 168509.02 | GGB | 137648.37 | GGB | 0 | 0 | 2323 | 3600 | 2308.27 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 48289.07 | GGB | 48289.63 | 2308.27 | 2308.27 |  |  |  | 1 | 1 |  |  |  |  | 137648.37 | 2308.27 | 137648.37 | 2308.27 | 8.1302 | [5 empty] | 88.2582
30.10.2007 14:00 | 3600 | 2 | 759.4 | GGB | 768.132 | 774.07 | 769.963 | 254.01 | GGB | 10524.3 | GGB | 9.86 | GGB | 1012.02 | GGB | 61.14 | GGB | 169341.98 | GGB | 138221.15 | GGB | 0 | 0 | 2266 | 3600 | 2250.61 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 48327.65 | GGB | 48328.22 | 2250.61 | 2250.61 |  |  |  | 1 | 1 |  |  |  |  | 138221.15 | 2250.61 | 138221.15 |  | 8.0612 | [5 empty] | 86.4116
30.10.2007 15:00 | 3600 | 2 | 759.07 | GGB | 767.033 | 773.039 | 768.864 | 252.72 | GGB | 10537.5 | GGB | 9.85 | GGB | 1011.48 | GGB | 61.74 | GGB | 167699.18 | GGB | 136563.78 | GGB | 0 | 0 | 2293 | 3600 | 2277.58 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 48365.99 | GGB | 48366.55 | 2277.58 | 2277.58 |  |  |  | 1 | 1 |  |  |  |  | 136563.78 | 2277.58 | 136563.78 |  | 8.1147 | [5 empty] | 86.3986
30.10.2007 16:00 | 3600 | 2 | 759.06 | GGB | 767.033 | 773.039 | 768.864 | 253.11 | GGB | 10548.3 | GGB | 9.85 | GGB | 1011.53 | GGB | 61.83 | GGB | 167712.38 | GGB | 136545.88 | GGB | 0 | 0 | 2306 | 3600 | 2290.86 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 48404.9 | GGB | 48405.47 | 2290.86 | 2290.86 |  |  |  | 1 | 1 |  |  |  |  | 136545.88 | 2290.86 | 136545.88 |  | 8.0372 | [5 empty] | 86.891
30.10.2007 17:00 | 3600 | 2 | 759.16 | GGB | 767.033 | 774.07 | 768.864 | 255.07 | GGB | 10541 | GGB | 9.85 | GGB | 1011.83 | GGB | 61.06 | GGB | 170398.3 | GGB | 139090.75 | GGB | 0 | 0 | 2286 | 3600 | 2270.61 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 48443.06 | GGB | 48443.63 | 2270.61 | 2270.61 |  |  |  | 1 | 1 |  |  |  |  | 139090.75 | 2270.61 | 139090.75 |  | 8.2762 | [5 empty] | 87.728
30.10.2007 18:00 | 3600 | 2 | 759.31 | GGB | 767.033 | 774.07 | 768.498 | 255.48 | GGB | 10562.1 | GGB | 9.85 | GGB | 1012.21 | GGB | 60.88 | GGB | 170733.91 | GGB | 139491.64 | GGB | 0 | 0 | 2290 | 3600 | 2274.61 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 48481.85 | GGB | 48482.42 | 2274.61 | 2274.61 |  |  |  | 1 | 1 |  |  |  |  | 139491.64 | 2274.61 | 139491.64 |  | 8.1797 | [5 empty] | 88.1359
30.10.2007 19:00 | 3600 | 2 | 758.8 | GGB | 765.934 | 771.82 | 768.132 | 254.85 | GGB | 10609.3 | GGB | 9.85 | GGB | 1012 | GGB | 61.04 | GGB | 169733.7 | GGB | 138582.01 | GGB | 0 | 0 | 2331 | 3600 | 2315.75 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 48520.12 | GGB | 48520.7 | 2315.75 | 2315.75 |  |  |  | 1 | 1 |  |  |  |  | 138582.01 | 2315.75 | 138582.01 | 2315.75 | 8.3835 | [5 empty] | 89.1448
30.10.2007 20:00 | 3600 | 2 | 758.65 | GGB | 767.033 | 773.133 | 768.132 | 254.92 | GGB | 10631.6 | GGB | 9.85 | GGB | 1012.39 | GGB | 61.08 | GGB | 170143.03 | GGB | 138951.12 | GGB | 0 | 0 | 2345 | 3600 | 2330.17 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 48559.3 | GGB | 48559.88 | 2330.17 | 2330.17 |  |  |  | 1 | 1 |  |  |  |  | 138951.12 | 2330.17 | 138951.12 | 2330.17 | 8.2639 | [5 empty] | 89.9388
30.10.2007 21:00 | 3600 | 2 | 758.66 | GGB | 765.934 | 772.008 | 768.132 | 255.4 | GGB | 10639.2 | GGB | 9.85 | GGB | 1012.36 | GGB | 60.79 | GGB | 171007.89 | GGB | 139775.26 | GGB | 0 | 0 | 2343 | 3600 | 2327.46 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 48597.72 | GGB | 48598.3 | 2327.46 | 2327.46 |  |  |  | 1 | 1 |  |  |  |  | 139775.26 | 2327.46 | 139775.26 | 2327.46 | 8.4675 | [5 empty] | 90.367
30.10.2007 22:00 | 3600 | 2 | 758.7 | GGB | 765.934 | 772.102 | 767.033 | 256.56 | GGB | 10652.4 | GGB | 9.85 | GGB | 1012.56 | GGB | 59.7 | GGB | 173732.33 | GGB | 142495.4 | GGB | 0 | 0 | 2329 | 3600 | 2314.36 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 48636.7 | GGB | 48637.28 | 2314.36 | 2314.36 |  |  |  | 1 | 1 |  |  |  |  | 142495.4 | 2314.36 | 142495.4 | 2314.36 | 8.4604 | [5 empty] | 91.6071
30.10.2007 23:00 | 3600 | 2 | 758.55 | GGB | 765.934 | 771.844 | 768.132 | 256.32 | GGB | 10670.8 | GGB | 9.85 | GGB | 1012.57 | GGB | 59.86 | GGB | 172435.03 | GGB | 141365.09 | GGB | 0 | 0 | 2351 | 3600 | 2336.24 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 48676.02 | GGB | 48676.6 | 2336.24 | 2336.24 |  |  |  | 1 | 1 |  |  |  |  | 141365.09 | 2336.24 | 141365.09 | 2336.24 | 8.3994 | [5 empty] | 91.7397
30.10.2007 24:00 | 3600 | 2 | 758.4 | GGB | 767.033 | 772.922 | 768.498 | 255.18 | GGB | 10676.5 | GGB | 9.86 | GGB | 1012.48 | GGB | 60.39 | GGB | 171207.05 | GGB | 140123.58 | GGB | 0 | 0 | 2360 | 3600 | 2344.77 | GGB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 48714.13 | GGB | 48714.72 | 2344.77 | 2344.77 |  |  |  | 1 | 1 |  |  |  |  | 140123.58 | 2344.77 | 140123.58 | 2344.77 | 8.619 | [5 empty] | 91.266
31.10.2007 01:00 | 3600 | 2 | 758.29 | GGB | 765.934 | 771.797 | 768.132 | 255.11 | GGB | 10664.7 | GGB | 9.85 | GGB | 1012.15 | GGB | 60.34 | GGB | 171044.2 | GGB | 139964.68 | GGB | 0 | 0 | 2362 | 3600 | 2347.13 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 48753.58 | GGB | 48754.17 | 2347.13 | 2347.13 |  |  |  | 1 | 1 |  |  |  |  | 139964.68 | 2347.13 | 139964.68 | 2347.13 | 8.3274 | [5 empty] | 91.2542
31.10.2007 02:00 | 3600 | 2 | 758.25 | GGB | 765.934 | 772.852 | 768.132 | 256.99 | GGB | 10649.9 | GGB | 9.85 | GGB | 1012.41 | GGB | 59.59 | GGB | 173785.14 | GGB | 142565.18 | GGB | 0 | 0 | 2354 | 3600 | 2338.61 | GGB | 100 | GGB | 38.87 | GGB | 38.87 | GGB | 48792.45 | GGB | 48793.04 | 2338.61 | 2338.61 |  |  |  | 1 | 1 |  |  |  |  | 142565.18 | 2338.61 | 142565.18 | 2338.61 | 8.5774 | [5 empty] | 92.6123
31.10.2007 03:00 | 3600 | 2 | 758.42 | GGB | 767.033 | 771.82 | 768.132 | 255.92 | GGB | 10687 | GGB | 9.86 | GGB | 1011.86 | GGB | 59.95 | GGB | 172336 | GGB | 141147.23 | GGB | 0 | 0 | 2368 | 3600 | 2353.37 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 48831.11 | GGB | 48831.71 | 2353.37 | 2353.37 |  |  |  | 1 | 1 |  |  |  |  | 141147.23 | 2353.37 | 141147.23 | 2353.37 | 8.5899 | [5 empty] | 92.2699
31.10.2007 04:00 | 3600 | 2 | 757.93 | GGB | 765.934 | 771.82 | 767.033 | 255.62 | GGB | 10695.1 | GGB | 9.85 | GGB | 1011.65 | GGB | 60.26 | GGB | 171361.1 | GGB | 140189.4 | GGB | 0 | 0 | 2400 | 3600 | 2385.12 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 48870.89 | GGB | 48871.49 | 2385.12 | 2385.12 |  |  |  | 1 | 1 |  |  |  |  | 140189.4 | 2385.12 | 140189.4 | 2385.12 | 8.4054 | [5 empty] | 92.8802
31.10.2007 05:00 | 3600 | 2 | 757.53 | GGB | 765.934 | 771.797 | 766.667 | 257.55 | GGB | 10700.9 | GGB | 9.84 | GGB | 1011.85 | GGB | 59.71 | GGB | 173188.76 | GGB | 141946.87 | GGB | 0 | 0 | 2431 | 3600 | 2415.38 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 48909.48 | GGB | 48910.08 | 2415.38 | 2415.38 |  |  |  | 1 | 1 |  |  |  |  | 141946.87 | 2415.38 | 141946.87 | 2415.38 | 8.8846 | [5 empty] | 95.2377
31.10.2007 06:00 | 3600 | 2 | 757.89 | GGB | 765.934 | 771.82 | 767.766 | 259.13 | GGB | 10728.4 | GGB | 9.85 | GGB | 1012.44 | GGB | 58.92 | GGB | 174706.13 | GGB | 143614.22 | GGB | 0 | 0 | 2431 | 3600 | 2415.51 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 48948.99 | GGB | 48949.58 | 2415.51 | 2415.51 |  |  |  | 1 | 1 |  |  |  |  | 143614.22 | 2415.51 | 143614.22 | 2415.51 | 8.7823 | [5 empty] | 96.3616
31.10.2007 07:00 | 3600 | 2 | 757.92 | GGB | 765.934 | 770.813 | 768.132 | 257.86 | GGB | 10749.4 | GGB | 9.86 | GGB | 1012.44 | GGB | 59.72 | GGB | 172731.02 | GGB | 141650.6 | GGB | 0 | 0 | 2449 | 3600 | 2433.65 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 48987.84 | GGB | 48988.44 | 2433.65 | 2433.65 |  |  |  | 1 | 1 |  |  |  |  | 141650.6 | 2433.65 | 141650.6 | 2433.65 | 8.871 | [5 empty] | 95.7578
31.10.2007 08:00 | 3600 | 2 | 757.95 | GGB | 765.934 | 771.773 | 768.132 | 257.55 | GGB | 10748.9 | GGB | 9.86 | GGB | 1012.57 | GGB | 59.87 | GGB | 172034.51 | GGB | 141032.24 | GGB | 0 | 0 | 2459 | 3600 | 2443.48 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 49027.6 | GGB | 49028.2 | 2443.48 | 2443.48 |  |  |  | 1 | 1 |  |  |  |  | 141032.24 | 2443.48 | 141032.24 | 2443.48 | 8.6672 | [5 empty] | 95.7248
31.10.2007 09:00 | 3600 | 2 | 758.22 | GGB | 765.934 | 771.75 | 767.033 | 256.74 | GGB | 10735.6 | GGB | 9.86 | GGB | 1013.38 | GGB | 59.67 | GGB | 171445.83 | GGB | 140746.92 | GGB | 0 | 0 | 2443 | 3600 | 2427.43 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 49066.7 | GGB | 49067.3 | 2427.43 | 2427.43 |  |  |  | 1 | 1 |  |  |  |  | 140746.92 | 2427.43 | 140746.92 | 2427.43 | 8.7379 | [5 empty] | 94.9037
31.10.2007 10:00 | 3600 | 2 | 757.71 | GGB | 765.934 | 771.68 | 767.033 | 257.74 | GGB | 10714.7 | GGB | 9.84 | GGB | 1014.85 | GGB | 59.95 | GGB | 172453.74 | GGB | 141659.83 | GGB | 0 | 0 | 2457 | 3600 | 2441.58 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 49106.34 | GGB | 49106.94 | 2441.58 | 2441.58 |  |  |  | 1 | 1 |  |  |  |  | 141659.83 | 2441.58 | 141659.83 | 2441.58 | 8.7254 | [5 empty] | 96.0761
31.10.2007 11:00 | 3600 | 2 | 758.54 | GGB | 765.934 | 771.984 | 768.132 | 258.3 | GGB | 10739.6 | GGB | 9.86 | GGB | 1015.65 | GGB | 59.87 | GGB | 172846.56 | GGB | 142126.9 | GGB | 0 | 0 | 2429 | 3600 | 2413.48 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 49145.43 | GGB | 49146.03 | 2413.48 | 2413.48 |  |  |  | 1 | 1 |  |  |  |  | 142126.9 | 2413.48 | 142126.9 | 2413.48 | 8.7751 | [5 empty] | 95.2835
31.10.2007 12:00 | 3600 | 2 | 758.51 | GGB | 765.934 | 771.984 | 768.132 | 256.95 | GGB | 10728.8 | GGB | 9.86 | GGB | 1015.84 | GGB | 60.58 | GGB | 171399.61 | GGB | 140666.27 | GGB | 0 | 0 | 2428 | 3600 | 2413.1 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 49184.42 | GGB | 49185.02 | 2413.1 | 2413.1 |  |  |  | 1 | 1 |  |  |  |  | 140666.27 | 2413.1 | 140666.27 | 2413.1 | 8.7059 | [5 empty] | 94.2894
31.10.2007 13:00 | 3600 | 2 | 758.08 | GGB | 765.934 | 771.938 | 768.132 | 257.1 | GGB | 10684.9 | GGB | 9.85 | GGB | 1015.62 | GGB | 60.5 | GGB | 171764.92 | GGB | 140967.04 | GGB | 0 | 0 | 2425 | 3600 | 2410.1 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 49224.85 | GGB | 49225.45 | 2410.1 | 2410.1 |  |  |  | 1 | 1 |  |  |  |  | 140967.04 | 2410.1 | 140967.04 | 2410.1 | 8.4033 | [5 empty] | 94.3735
31.10.2007 14:00 | 3600 | 2 | 758.91 | GGB | 767.033 | 772.219 | 768.498 | 258.3 | GGB | 10684.6 | GGB | 9.86 | GGB | 1015.88 | GGB | 59.91 | GGB | 173082.03 | GGB | 142338.96 | GGB | 0 | 0 | 2376 | 3600 | 2361.2 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 49263.64 | GGB | 49264.24 | 2361.2 | 2361.2 |  |  |  | 1 | 1 |  |  |  |  | 142338.96 | 2361.2 | 142338.96 | 2361.2 | 8.6644 | [5 empty] | 93.3585
31.10.2007 15:00 | 3600 | 2 | 758.68 | GGB | 767.033 | 772.195 | 768.132 | 258.08 | GGB | 10670.4 | GGB | 9.85 | GGB | 1016.54 | GGB | 59.93 | GGB | 172826.75 | GGB | 142212.9 | GGB | 0 | 0 | 2376 | 3600 | 2361.02 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 49302.84 | GGB | 49303.44 | 2361.02 | 2361.02 |  |  |  | 1 | 1 |  |  |  |  | 142212.9 | 2361.02 | 142212.9 | 2361.02 | 8.5655 | [5 empty] | 93.2688
31.10.2007 16:00 | 3600 | 2 | 758.77 | GGB | 767.033 | 772.219 | 768.132 | 258.38 | GGB | 10680.6 | GGB | 9.85 | GGB | 1016.91 | GGB | 59.89 | GGB | 173307.6 | GGB | 142677.21 | GGB | 0 | 0 | 2381 | 3600 | 2365.44 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 49342.53 | GGB | 49343.13 | 2365.44 | 2365.44 |  |  |  | 1 | 1 |  |  |  |  | 142677.21 | 2365.44 | 142677.21 | 2365.44 | 8.5033 | [5 empty] | 93.7484
31.10.2007 17:00 | 3600 | 2 | 758.49 | GGB | 767.033 | 772.242 | 768.132 | 257.43 | GGB | 10728.1 | GGB | 9.86 | GGB | 1017.42 | GGB | 60.41 | GGB | 172007 | GGB | 141455.16 | GGB | 0 | 0 | 2405 | 3600 | 2390.23 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 49381.18 | GGB | 49381.78 | 2390.23 | 2390.23 |  |  |  | 1 | 1 |  |  |  |  | 141455.16 | 2390.23 | 141455.16 | 2390.23 | 8.748 | [5 empty] | 93.9195
31.10.2007 18:00 | 3600 | 2 | 757.66 | GGB | 764.835 | 770.789 | 767.033 | 259.27 | GGB | 10743.4 | GGB | 9.84 | GGB | 1018.14 | GGB | 60.06 | GGB | 173963.4 | GGB | 143317.69 | GGB | 0 | 0 | 2459 | 3600 | 2443.98 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 49420.45 | GGB | 49421.06 | 2443.98 | 2443.98 |  |  |  | 1 | 1 |  |  |  |  | 143317.69 | 2443.98 | 143317.69 | 2443.98 | 8.9171 | [5 empty] | 97.296
31.10.2007 19:00 | 3600 | 2 | 758.14 | GGB | 765.934 | 770.766 | 767.033 | 259.54 | GGB | 10785.2 | GGB | 9.86 | GGB | 1018.81 | GGB | 59.64 | GGB | 174253.89 | GGB | 143829.57 | GGB | 0 | 0 | 2457 | 3600 | 2442.02 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 49461.13 | GGB | 49461.74 | 2442.02 | 2442.02 |  |  |  | 1 | 1 |  |  |  |  | 143829.57 | 2442.02 | 143829.57 | 2442.02 | 8.6341 | [5 empty] | 97.5652
31.10.2007 20:00 | 3600 | 2 | 758.04 | GGB | 765.934 | 771.891 | 768.132 | 260.99 | GGB | 10796.8 | GGB | 9.85 | GGB | 1019.74 | GGB | 59.18 | GGB | 176015.53 | GGB | 145621.34 | GGB | 0 | 0 | 2464 | 3600 | 2449.15 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 49500.23 | GGB | 49500.84 | 2449.15 | 2449.15 |  |  |  | 1 | 1 |  |  |  |  | 145621.34 | 2449.15 | 145621.34 | 2449.15 | 9.1214 | [5 empty] | 99.069
31.10.2007 21:00 | 3600 | 2 | 757.65 | GGB | 765.934 | 770.859 | 767.033 | 260.69 | GGB | 10851.4 | GGB | 9.85 | GGB | 1020.13 | GGB | 59.39 | GGB | 175106.65 | GGB | 144830.7 | GGB | 0 | 0 | 2516 | 3600 | 2501.09 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 49539.67 | GGB | 49540.28 | 2501.09 | 2501.09 |  |  |  | 1 | 1 |  |  |  |  | 144830.7 | 2501.09 | 144830.7 | 2501.09 | 9.1844 | [5 empty] | 100.6207
31.10.2007 22:00 | 3600 | 2 | 757.65 | GGB | 764.835 | 770.93 | 767.033 | 262.74 | GGB | 10847.5 | GGB | 9.85 | GGB | 1021 | GGB | 58.72 | GGB | 177924.61 | GGB | 147585.59 | GGB | 0 | 0 | 2518 | 3600 | 2502.4 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 49580.3 | GGB | 49580.91 | 2502.4 | 2502.4 |  |  |  | 1 | 1 |  |  |  |  | 147585.59 | 2502.4 | 147585.59 | 2502.4 | 9.0898 | [5 empty] | 102.5884
31.10.2007 23:00 | 3600 | 2 | 757.62 | GGB | 764.835 | 769.852 | 767.033 | 262.67 | GGB | 10881.1 | GGB | 9.85 | GGB | 1021.65 | GGB | 58.32 | GGB | 178706.95 | GGB | 148505.81 | GGB | 0 | 0 | 2528 | 3600 | 2512.3 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 49619.77 | GGB | 49620.38 | 2512.3 | 2512.3 |  |  |  | 1 | 1 |  |  |  |  | 148505.81 | 2512.3 | 148505.81 | 2512.3 | 9.4525 | [5 empty] | 103.6364
31.10.2007 24:00 | 3600 | 2 | 757.53 | GGB | 764.835 | 770.906 | 765.934 | 263.54 | GGB | 10907.6 | GGB | 9.85 | GGB | 1022.22 | GGB | 58.74 | GGB | 177739.76 | GGB | 147601.9 | GGB | 0 | 0 | 2551 | 3600 | 2536.08 | GGB | 100 | GGB | 37.66 | GGB | 37.66 | GGB | 49657.42 | GGB | 49658.04 | 2536.08 | 2536.08 |  |  |  | 1 | 1 |  |  |  |  | 147601.9 | 2536.08 | 147601.9 | 2536.08 | 9.9397 | [5 empty] | 103.9806
01.11.2007 01:00 | 3600 | 2 | 757.07 | GGB | 764.835 | 769.898 | 765.934 | 263.99 | GGB | 10929.5 | GGB | 9.85 | GGB | 1022.16 | GGB | 59.09 | GGB | 177604.42 | GGB | 147323.39 | GGB | 0 | 0 | 2596 | 3600 | 2580.67 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 49698.49 | GGB | 49699.1 | 2580.67 | 2580.67 |  |  |  | 1 | 1 |  |  |  |  | 147323.39 | 2580.67 | 147323.39 | 2580.67 | 9.2595 | [5 empty] | 105.6092 | 2565.2953
01.11.2007 02:00 | 3600 | 2 | 757.01 | GGB | 764.835 | 769.898 | 765.934 | 264.88 | GGB | 10956.6 | GGB | 9.85 | GGB | 1022.07 | GGB | 59.02 | GGB | 178251.41 | GGB | 147879.16 | GGB | 0 | 0 | 2613 | 3600 | 2597.36 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 49739.71 | GGB | 49740.32 | 2597.36 | 2597.36 |  |  |  | 1 | 1 |  |  |  |  | 147879.16 | 2597.36 | 147879.16 | 2597.36 | 9.3182 | [5 empty] | 106.6932 | 2555.6542
01.11.2007 03:00 | 3600 | 2 | 756.92 | GGB | 764.835 | 769.781 | 765.934 | 265.62 | GGB | 10972 | GGB | 9.85 | GGB | 1022.02 | GGB | 58.89 | GGB | 179099.78 | GGB | 148632.78 | GGB | 0 | 0 | 2623 | 3600 | 2607.47 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 49779.27 | GGB | 49779.88 | 2607.47 | 2607.47 |  |  |  | 1 | 1 |  |  |  |  | 148632.78 | 2607.47 | 148632.78 | 2607.47 | 9.7967 | [5 empty] | 107.6543 | 2542.6962
01.11.2007 04:00 | 3600 | 2 | 757 | GGB | 765.934 | 770.953 | 767.033 | 266.67 | GGB | 10960.8 | GGB | 9.85 | GGB | 1022.07 | GGB | 58.45 | GGB | 180581.93 | GGB | 150068.95 | GGB | 0 | 0 | 2610 | 3600 | 2594.8 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 49820.05 | GGB | 49820.66 | 2594.8 | 2594.8 |  |  |  | 1 | 1 |  |  |  |  | 150068.95 | 2594.8 | 150068.95 | 2594.8 | 9.5488 | [5 empty] | 108.1664 | 2518.3624
01.11.2007 05:00 | 3600 | 2 | 757.48 | GGB | 767.033 | 771.961 | 768.132 | 266.85 | GGB | 10980.1 | GGB | 9.86 | GGB | 1021.76 | GGB | 58.23 | GGB | 180962.65 | GGB | 150440.89 | GGB | 0 | 0 | 2592 | 3600 | 2576.39 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 49860.73 | GGB | 49861.34 | 2576.39 | 2576.39 |  |  |  | 1 | 1 |  |  |  |  | 150440.89 | 2576.39 | 150440.89 | 2576.39 | 9.5279 | [5 empty] | 107.6651 | 2512.1362
01.11.2007 06:00 | 3600 | 2 | 757.47 | GGB | 765.934 | 770.93 | 767.033 | 265.02 | GGB | 10989 | GGB | 9.86 | GGB | 1021.36 | GGB | 58.74 | GGB | 178971.04 | GGB | 148495.42 | GGB | 0 | 0 | 2592 | 3600 | 2576.69 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 49901.3 | GGB | 49901.91 | 2576.69 | 2576.69 |  |  |  | 1 | 1 |  |  |  |  | 148495.42 | 2576.69 | 148495.42 | 2576.69 | 9.4313 | [5 empty] | 106.2852 | 2545.0482
01.11.2007 07:00 | 3600 | 2 | 757.01 | GGB | 764.469 | 769.875 | 765.934 | 265.05 | GGB | 10940.1 | GGB | 9.85 | GGB | 1021.09 | GGB | 58.56 | GGB | 179358.35 | GGB | 148860.29 | GGB | 0 | 0 | 2593 | 3600 | 2577.62 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 49941.03 | GGB | 49941.65 | 2577.62 | 2577.62 |  |  |  | 1 | 1 |  |  |  |  | 148860.29 | 2577.62 | 148860.29 | 2577.62 | 9.6554 | [5 empty] | 106.5848 | 2538.81
01.11.2007 08:00 | 3600 | 2 | 757.76 | GGB | 765.934 | 770.953 | 767.033 | 265.4 | GGB | 10936 | GGB | 9.86 | GGB | 1020.79 | GGB | 58.3 | GGB | 180057.07 | GGB | 149513.71 | GGB | 0 | 0 | 2550 | 3600 | 2534.87 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 49982.04 | GGB | 49982.66 | 2534.87 | 2534.87 |  |  |  | 1 | 1 |  |  |  |  | 149513.71 | 2534.87 | 149513.71 | 2534.87 | 9.2416 | [5 empty] | 105.2772 | 2527.7147
01.11.2007 09:00 | 3600 | 2 | 757.68 | GGB | 764.835 | 770.109 | 767.033 | 263.17 | GGB | 10922.4 | GGB | 9.86 | GGB | 1020.45 | GGB | 59.14 | GGB | 177063.05 | GGB | 146606.03 | GGB | 0 | 0 | 2553 | 3600 | 2537.54 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 50021.97 | GGB | 50022.59 | 2537.54 | 2537.54 |  |  |  | 1 | 1 |  |  |  |  | 146606.03 | 2537.54 | 146606.03 | 2537.54 | 9.3168 | [5 empty] | 103.3385
01.11.2007 10:00 | 3600 | 2 | 757.7 | GGB | 764.835 | 770.156 | 765.934 | 262.51 | GGB | 10885 | GGB | 9.86 | GGB | 1019.61 | GGB | 59.13 | GGB | 176258.7 | GGB | 145822.58 | GGB | 0 | 0 | 2531 | 3600 | 2515.7 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 50061.46 | GGB | 50062.09 | 2515.7 | 2515.7 |  |  |  | 1 | 1 |  |  |  |  | 145822.58 | 2515.7 | 145822.58 | 2515.7 | 9.2872 | [5 empty] | 101.9016
01.11.2007 11:00 | 3600 | 2 | 757.56 | GGB | 766.3 | 771.258 | 767.033 | 263.48 | GGB | 10842.5 | GGB | 9.85 | GGB | 1019.27 | GGB | 58.57 | GGB | 177987.33 | GGB | 147452.78 | GGB | 0 | 0 | 2514 | 3600 | 2498.86 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 50101.5 | GGB | 50102.13 | 2498.86 | 2498.86 |  |  |  | 1 | 1 |  |  |  |  | 147452.78 | 2498.86 | 147452.78 | 2498.86 | 9.2024 | [5 empty] | 102.3511
01.11.2007 12:00 | 3600 | 2 | 757.89 | GGB | 766.3 | 771.234 | 767.033 | 261.66 | GGB | 10855.2 | GGB | 9.86 | GGB | 1018.51 | GGB | 59.13 | GGB | 175833.97 | GGB | 145315.18 | GGB | 0 | 0 | 2507 | 3600 | 2491.78 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 50141.59 | GGB | 50142.22 | 2491.78 | 2491.78 |  |  |  | 1 | 1 |  |  |  |  | 145315.18 | 2491.78 | 145315.18 | 2491.78 | 9.032 | [5 empty] | 100.5815
01.11.2007 13:00 | 3600 | 2 | 757.59 | GGB | 765.201 | 771.234 | 767.033 | 260.57 | GGB | 10823.4 | GGB | 9.86 | GGB | 1017.91 | GGB | 59.62 | GGB | 174274.79 | GGB | 143733 | GGB | 0 | 0 | 2508 | 3600 | 2493.23 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 50181.75 | GGB | 50182.38 | 2493.23 | 2493.23 |  |  |  | 1 | 1 |  |  |  |  | 143733 | 2493.23 | 143733 | 2493.23 | 8.9233 | [5 empty] | 99.5443
01.11.2007 14:00 | 3600 | 2 | 757.78 | GGB | 765.201 | 771.234 | 767.033 | 259.64 | GGB | 10793.8 | GGB | 9.86 | GGB | 1016.8 | GGB | 59.85 | GGB | 173323 | GGB | 142689.12 | GGB | 0 | 0 | 2491 | 3600 | 2475.88 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 50220.69 | GGB | 50221.32 | 2475.88 | 2475.88 |  |  |  | 1 | 1 |  |  |  |  | 142689.12 | 2475.88 | 142689.12 | 2475.88 | 9.0724 | [5 empty] | 98.1336
01.11.2007 15:00 | 3600 | 2 | 757.74 | GGB | 765.201 | 771.234 | 768.132 | 258.86 | GGB | 10756.7 | GGB | 9.86 | GGB | 1016.07 | GGB | 60.17 | GGB | 172260.08 | GGB | 141578.04 | GGB | 0 | 0 | 2477 | 3600 | 2461.87 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 50260.24 | GGB | 50260.87 | 2461.87 | 2461.87 |  |  |  | 1 | 1 |  |  |  |  | 141578.04 | 2461.87 | 141578.04 | 2461.87 | 8.8128 | [5 empty] | 96.8185
01.11.2007 16:00 | 3600 | 2 | 758.06 | GGB | 765.201 | 771.234 | 767.033 | 258.03 | GGB | 10724.9 | GGB | 9.86 | GGB | 1014.6 | GGB | 60.43 | GGB | 171249.97 | GGB | 140432.55 | GGB | 0 | 0 | 2454 | 3600 | 2438.49 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 50300.53 | GGB | 50301.17 | 2438.49 | 2438.49 |  |  |  | 1 | 1 |  |  |  |  | 140432.55 | 2438.49 | 140432.55 | 2438.49 | 8.4974 | [5 empty] | 95.1232
01.11.2007 17:00 | 3600 | 2 | 758.03 | GGB | 765.201 | 771.305 | 767.033 | 257.25 | GGB | 10694.4 | GGB | 9.86 | GGB | 1013.79 | GGB | 60.63 | GGB | 170564.46 | GGB | 139679.34 | GGB | 0 | 0 | 2443 | 3600 | 2427.66 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 50339.55 | GGB | 50340.18 | 2427.66 | 2427.66 |  |  |  | 1 | 1 |  |  |  |  | 139679.34 | 2427.66 | 139679.34 | 2427.66 | 8.6925 | [5 empty] | 94.1928
01.11.2007 18:00 | 3600 | 2 | 758.03 | GGB | 766.3 | 771.305 | 767.033 | 257.14 | GGB | 10666.4 | GGB | 9.86 | GGB | 1013.36 | GGB | 60.83 | GGB | 170066 | GGB | 139126.09 | GGB | 0 | 0 | 2440 | 3600 | 2424.64 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 50378.86 | GGB | 50379.49 | 2424.64 | 2424.64 |  |  |  | 1 | 1 |  |  |  |  | 139126.09 | 2424.64 | 139126.09 | 2424.64 | 8.5813 | [5 empty] | 93.703
01.11.2007 19:00 | 3600 | 2 | 758.04 | GGB | 766.3 | 771.258 | 767.766 | 256.62 | GGB | 10637 | GGB | 9.86 | GGB | 1012.45 | GGB | 61.06 | GGB | 169262.76 | GGB | 138250.14 | GGB | 0 | 0 | 2426 | 3600 | 2411.19 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 50417.49 | GGB | 50418.13 | 2411.19 | 2411.19 |  |  |  | 1 | 1 |  |  |  |  | 138250.14 | 2411.19 | 138250.14 | 2411.19 | 8.627 | [5 empty] | 92.5965
01.11.2007 20:00 | 3600 | 2 | 758.24 | GGB | 766.3 | 771.258 | 767.766 | 255.98 | GGB | 10605.7 | GGB | 9.86 | GGB | 1011.61 | GGB | 61.23 | GGB | 168583.85 | GGB | 137509.48 | GGB | 0 | 0 | 2408 | 3600 | 2392.78 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 50456.21 | GGB | 50456.85 | 2392.78 | 2392.78 |  |  |  | 1 | 1 |  |  |  |  | 137509.48 | 2392.78 | 137509.48 | 2392.78 | 8.4977 | [5 empty] | 91.3972
01.11.2007 21:00 | 3600 | 2 | 757.87 | GGB | 766.3 | 771.281 | 767.766 | 255.95 | GGB | 10588.4 | GGB | 9.85 | GGB | 1011.19 | GGB | 61.41 | GGB | 168303.26 | GGB | 137149.25 | GGB | 0 | 0 | 2418 | 3600 | 2402.63 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 50496.18 | GGB | 50496.82 | 2402.63 | 2402.63 |  |  |  | 1 | 1 |  |  |  |  | 137149.25 | 2402.63 | 137149.25 | 2402.63 | 8.2442 | [5 empty] | 91.533
01.11.2007 22:00 | 3600 | 2 | 758.35 | GGB | 766.3 | 772.313 | 768.132 | 255.19 | GGB | 10589.8 | GGB | 9.86 | GGB | 1010.76 | GGB | 61.54 | GGB | 168115.1 | GGB | 136888.6 | GGB | 0 | 0 | 2398 | 3600 | 2382.37 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 50534.36 | GGB | 50535 | 2382.37 | 2382.37 |  |  |  | 1 | 1 |  |  |  |  | 136888.6 | 2382.37 | 136888.6 | 2382.37 | 8.5416 | [5 empty] | 90.5887
01.11.2007 23:00 | 3600 | 2 | 758.45 | GGB | 765.201 | 771.305 | 768.132 | 254.82 | GGB | 10577.9 | GGB | 9.86 | GGB | 1010.16 | GGB | 61.43 | GGB | 167746.49 | GGB | 136547.75 | GGB | 0 | 0 | 2389 | 3600 | 2374.03 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 50573.43 | GGB | 50574.07 | 2374.03 | 2374.03 |  |  |  | 1 | 1 |  |  |  |  | 136547.75 | 2374.03 | 136547.75 | 2374.03 | 8.2971 | [5 empty] | 90.0468
01.11.2007 24:00 | 3600 | 2 | 758.16 | GGB | 765.201 | 771.328 | 767.033 | 254.76 | GGB | 10573.1 | GGB | 9.85 | GGB | 1009.66 | GGB | 61.26 | GGB | 167788.3 | GGB | 136586.08 | GGB | 0 | 0 | 2392 | 3600 | 2377.31 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 50612.09 | GGB | 50612.73 | 2377.31 | 2377.31 |  |  |  | 1 | 1 |  |  |  |  | 136586.08 | 2377.31 | 136586.08 | 2377.31 | 8.3991 | [5 empty] | 90.1965
02.11.2007 01:00 | 3600 | 2 | 758.26 | GGB | 765.201 | 771.422 | 767.033 | 254.23 | GGB | 10566.8 | GGB | 9.86 | GGB | 1009.77 | GGB | 61.37 | GGB | 167303.05 | GGB | 136161.18 | GGB | 0 | 0 | 2388 | 3600 | 2372.51 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 50651.55 | GGB | 50652.19 | 2372.51 | 2372.51 |  |  |  | 1 | 1 |  |  |  |  | 136161.18 | 2372.51 | 136161.18 | 2372.51 | 8.1866 | [5 empty] | 89.7344
02.11.2007 02:00 | 3600 | 2 | 758.24 | GGB | 764.102 | 770.344 | 765.934 | 254.94 | GGB | 10553.9 | GGB | 9.84 | GGB | 1010.9 | GGB | 61.98 | GGB | 167833.42 | GGB | 136496.5 | GGB | 0 | 0 | 2394 | 3600 | 2378.79 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 50690.62 | GGB | 50691.26 | 2378.79 | 2378.79 |  |  |  | 1 | 1 |  |  |  |  | 136496.5 | 2378.79 | 136496.5 | 2378.79 | 8.3106 | [5 empty] | 90.1935
02.11.2007 03:00 | 3600 | 2 | 758.35 | GGB | 766.3 | 772.313 | 768.132 | 257.08 | GGB | 10656.5 | GGB | 9.86 | GGB | 1011.6 | GGB | 61.13 | GGB | 170588.66 | GGB | 139186.58 | GGB | 0 | 0 | 2403 | 3600 | 2388.05 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 50728.93 | GGB | 50729.57 | 2388.05 | 2388.05 |  |  |  | 1 | 1 |  |  |  |  | 139186.58 | 2388.05 | 139186.58 | 2388.05 | 8.6762 | [5 empty] | 92.329
02.11.2007 04:00 | 3600 | 2 | 757.84 | GGB | 765.934 | 771.211 | 767.033 | 257.64 | GGB | 10701.4 | GGB | 9.85 | GGB | 1012.05 | GGB | 60.73 | GGB | 171913.47 | GGB | 140495.98 | GGB | 0 | 0 | 2442 | 3600 | 2426.5 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 50768.22 | GGB | 50768.86 | 2426.5 | 2426.5 |  |  |  | 1 | 1 |  |  |  |  | 140495.98 | 2426.5 | 140495.98 | 2426.5 | 8.6769 | [5 empty] | 94.6982
02.11.2007 05:00 | 3600 | 2 | 757.68 | GGB | 764.835 | 770.203 | 767.033 | 258.63 | GGB | 10747.7 | GGB | 9.85 | GGB | 1012.62 | GGB | 60 | GGB | 173378.02 | GGB | 142085.84 | GGB | 0 | 0 | 2470 | 3600 | 2455.05 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 50806.66 | GGB | 50807.29 | 2455.05 | 2455.05 |  |  |  | 1 | 1 |  |  |  |  | 142085.84 | 2455.05 | 142085.84 | 2455.05 | 9.077 | [5 empty] | 96.8966
02.11.2007 06:00 | 3600 | 2 | 757.86 | GGB | 765.934 | 771.305 | 767.033 | 258.58 | GGB | 10778.2 | GGB | 9.86 | GGB | 1013.09 | GGB | 59.56 | GGB | 173594.79 | GGB | 142517.14 | GGB | 0 | 0 | 2467 | 3600 | 2452.05 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 50847.41 | GGB | 50848.04 | 2452.05 | 2452.05 |  |  |  | 1 | 1 |  |  |  |  | 142517.14 | 2452.05 | 142517.14 | 2452.05 | 8.5757 | [5 empty] | 97.072
02.11.2007 07:00 | 3600 | 2 | 757.26 | GGB | 764.835 | 770.25 | 765.934 | 258.78 | GGB | 10777.1 | GGB | 9.85 | GGB | 1013.23 | GGB | 59.55 | GGB | 174007.41 | GGB | 142881.63 | GGB | 0 | 0 | 2499 | 3600 | 2483.32 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 50886.76 | GGB | 50887.39 | 2483.32 | 2483.32 |  |  |  | 1 | 1 |  |  |  |  | 142881.63 | 2483.32 | 142881.63 | 2483.32 | 9.017 | [5 empty] | 98.5613
02.11.2007 08:00 | 3600 | 2 | 757.11 | GGB | 765.934 | 770.414 | 767.033 | 259.69 | GGB | 10810.7 | GGB | 9.85 | GGB | 1013.92 | GGB | 59.1 | GGB | 174984.51 | GGB | 143974.29 | GGB | 0 | 0 | 2535 | 3208 | 2519.66 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 50926.26 | GGB | 50926.89 | 2519.66 | 2519.66 |  |  |  | 1 | 1 |  |  |  |  | 143974.29 | 2519.66 | 143974.29 | 2519.66 | 9.184 | [5 empty] | 100.7684
02.11.2007 09:00 | 3600 | 2 | 757.33 | GGB | 764.835 | 770.344 | 767.033 | 260.59 | GGB | 10855.1 | GGB | 9.85 | GGB | 1014.59 | GGB | 58.57 | GGB | 176100.25 | GGB | 145218.77 | GGB | 0 | 0 | 2543 | 3600 | 2527.56 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 50967.09 | GGB | 50967.72 | 2527.56 | 2527.56 |  |  |  | 1 | 1 |  |  |  |  | 145218.77 | 2527.56 | 145218.77 | 2527.56 | 8.9897 | [5 empty] | 101.9581
02.11.2007 10:00 | 3600 | 2 | 757.24 | GGB | 767.033 | 772.219 | 768.132 | 261.08 | GGB | 10839.5 | GGB | 9.85 | GGB | 1015.04 | GGB | 58.26 | GGB | 177072.95 | GGB | 146225.49 | GGB | 0 | 0 | 2531 | 3600 | 2515.79 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 51006.76 | GGB | 51007.4 | 2515.79 | 2515.79 |  |  |  | 1 | 1 |  |  |  |  | 146225.49 | 2515.79 | 146225.49 | 2515.79 | 9.271 | [5 empty] | 102.1868
02.11.2007 11:00 | 3600 | 2 | 758.09 | GGB | 764.835 | 770.18 | 765.934 | 259.17 | GGB | 10827.9 | GGB | 9.87 | GGB | 1014.91 | GGB | 58.53 | GGB | 175212.28 | GGB | 144550.58 | GGB | 0 | 0 | 2480 | 3600 | 2464.36 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 51045.97 | GGB | 51046.61 | 2464.36 | 2464.36 |  |  |  | 1 | 1 |  |  |  |  | 144550.58 | 2464.36 | 144550.58 | 2464.36 | 9.085 | [5 empty] | 98.9513
02.11.2007 12:00 | 3600 | 2 | 757.86 | GGB | 764.835 | 771.563 | 767.033 | 258.11 | GGB | 10802.1 | GGB | 9.86 | GGB | 1014.52 | GGB | 58.78 | GGB | 174350.72 | GGB | 143676 | GGB | 0 | 0 | 2487 | 3600 | 2471.35 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 51086.01 | GGB | 51086.64 | 2471.35 | 2471.35 |  |  |  | 1 | 1 |  |  |  |  | 143676 | 2471.35 | 143676 | 2471.35 | 8.8702 | [5 empty] | 98.6316
02.11.2007 13:00 | 3600 | 2 | 757.46 | GGB | 765.934 | 771.586 | 767.033 | 257.76 | GGB | 10787.5 | GGB | 9.85 | GGB | 1014.55 | GGB | 58.64 | GGB | 174296.8 | GGB | 143696.94 | GGB | 0 | 0 | 2494 | 3600 | 2479.1 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 51126.48 | GGB | 51127.12 | 2479.1 | 2479.1 |  |  |  | 1 | 1 |  |  |  |  | 143696.94 | 2479.1 | 143696.94 | 2479.1 | 8.8004 | [5 empty] | 98.9553
02.11.2007 14:00 | 3600 | 2 | 757.8 | GGB | 765.934 | 771.469 | 768.132 | 258.97 | GGB | 10774.8 | GGB | 9.86 | GGB | 1014.46 | GGB | 58.23 | GGB | 175937.4 | GGB | 145214.79 | GGB | 0 | 0 | 2455 | 3600 | 2439.67 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 51165.86 | GGB | 51166.5 | 2439.67 | 2439.67 |  |  |  | 1 | 1 |  |  |  |  | 145214.79 | 2439.67 | 145214.79 | 2439.67 | 8.9963 | [5 empty] | 98.41
02.11.2007 15:00 | 3600 | 2 | 757.76 | GGB | 765.934 | 770.344 | 767.033 | 258.6 | GGB | 10799.4 | GGB | 9.86 | GGB | 1014.79 | GGB | 58.23 | GGB | 175521.48 | GGB | 144919.91 | GGB | 0 | 0 | 2469 | 3600 | 2453.93 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 51205.15 | GGB | 51205.79 | 2453.93 | 2453.93 |  |  |  | 1 | 1 |  |  |  |  | 144919.91 | 2453.93 | 144919.91 | 2453.93 | 9.0512 | [5 empty] | 98.7843
02.11.2007 16:00 | 3600 | 2 | 757.44 | GGB | 765.934 | 771.375 | 767.033 | 259.1 | GGB | 10822 | GGB | 9.85 | GGB | 1015.58 | GGB | 58.39 | GGB | 175367.43 | GGB | 144836.97 | GGB | 0 | 0 | 2510 | 3600 | 2494.33 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 51245.95 | GGB | 51246.59 | 2494.33 | 2494.33 |  |  |  | 1 | 1 |  |  |  |  | 144836.97 | 2494.33 | 144836.97 | 2494.33 | 8.8547 | [5 empty] | 100.3531
02.11.2007 17:00 | 3600 | 2 | 757.22 | GGB | 765.934 | 770.32 | 767.033 | 260.24 | GGB | 10833.5 | GGB | 9.85 | GGB | 1016.47 | GGB | 58.18 | GGB | 176760.46 | GGB | 146208.85 | GGB | 0 | 0 | 2519 | 3600 | 2503.75 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 51285.81 | GGB | 51286.45 | 2503.75 | 2503.75 |  |  |  | 1 | 1 |  |  |  |  | 146208.85 | 2503.75 | 146208.85 | 2503.75 | 9.1839 | [5 empty] | 101.6862
02.11.2007 18:00 | 3600 | 2 | 757.37 | GGB | 764.835 | 770.18 | 765.934 | 260.39 | GGB | 10881.3 | GGB | 9.85 | GGB | 1017.56 | GGB | 58.2 | GGB | 176651.52 | GGB | 146263.47 | GGB | 0 | 0 | 2545 | 3600 | 2529.59 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 51324.82 | GGB | 51325.45 | 2529.59 | 2529.59 |  |  |  | 1 | 1 |  |  |  |  | 146263.47 | 2529.59 | 146263.47 | 2529.59 | 9.4868 | [5 empty] | 102.7741
02.11.2007 19:00 | 3600 | 2 | 757.17 | GGB | 765.934 | 770.18 | 767.033 | 261.17 | GGB | 10914.3 | GGB | 9.86 | GGB | 1018 | GGB | 58.08 | GGB | 177343.64 | GGB | 146956.65 | GGB | 0 | 0 | 2578 | 3600 | 2562.34 | GGB | 100 | GGB | 41.45 | GGB | 41.45 | GGB | 51366.27 | GGB | 51366.9 | 2562.34 | 2562.34 |  |  |  | 1 | 1 |  |  |  |  | 146956.65 | 2562.34 | 146956.65 | 2562.34 | 9.0845 | [5 empty] | 104.598
02.11.2007 20:00 | 3600 | 2 | 756.8 | GGB | 762.271 | 768 | 764.469 | 261.63 | GGB | 10928 | GGB | 9.85 | GGB | 1018.91 | GGB | 58.07 | GGB | 177894.91 | GGB | 147548.06 | GGB | 0 | 0 | 2604 | 3600 | 2588.3 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 51405.77 | GGB | 51406.41 | 2588.3 | 2588.3 |  |  |  | 0 | 1 | [14 empty] | 106.083 | 2561.3892
02.11.2007 21:00 | 3600 | 2 | 756.6 | GGB | 765.934 | 770.977 | 768.132 | 263.84 | GGB | 10921.1 | GGB | 9.84 | GGB | 1019.5 | GGB | 57.95 | GGB | 178990.84 | GGB | 148595.37 | GGB | 0 | 0 | 2624 | 3600 | 2608.94 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 51446.1 | GGB | 51446.74 | 2608.94 | 2608.94 |  |  |  | 1 | 1 |  |  |  |  | 148595.37 | 2608.94 | 148595.37 | 2608.94 | 9.6126 | [5 empty] | 107.6879 | 2543.3363
02.11.2007 22:00 | 3600 | 2 | 757.6 | GGB | 764.469 | 769.195 | 765.934 | 263.68 | GGB | 10958.9 | GGB | 9.86 | GGB | 1020.22 | GGB | 58.28 | GGB | 178254.72 | GGB | 147943.43 | GGB | 0 | 0 | 2595 | 3600 | 2579.83 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 51485.6 | GGB | 51486.24 | 2579.83 | 2579.83 |  |  |  | 1 | 1 |  |  |  |  | 147943.43 | 2579.83 | 147943.43 | 2579.83 | 9.6625 | [5 empty] | 106.0191 | 2554.544
02.11.2007 23:00 | 3600 | 2 | 756.41 | GGB | 764.835 | 770.297 | 765.934 | 265.82 | GGB | 10938.2 | GGB | 9.84 | GGB | 1020.51 | GGB | 57.92 | GGB | 180475.2 | GGB | 149991.07 | GGB | 0 | 0 | 2641 | 3600 | 2625.99 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 51526.43 | GGB | 51527.07 | 2625.99 | 2625.99 |  |  |  | 1 | 1 |  |  |  |  | 149991.07 | 2625.99 | 149991.07 | 2625.99 | 9.6467 | [5 empty] | 109.4097 | 2519.67
02.11.2007 24:00 | 3600 | 2 | 756.87 | GGB | 764.835 | 770.273 | 767.033 | 265.97 | GGB | 11006.8 | GGB | 9.86 | GGB | 1020.85 | GGB | 57.89 | GGB | 180504.91 | GGB | 150078.62 | GGB | 0 | 0 | 2645 | 3600 | 2630.13 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 51566.36 | GGB | 51566.99 | 2630.13 | 2630.13 |  |  |  | 1 | 1 |  |  |  |  | 150078.62 | 2630.13 | 150078.62 | 2630.13 | 9.8879 | [5 empty] | 109.6462 | 2518.2001
03.11.2007 01:00 | 3600 | 2 | 756.81 | GGB | 764.835 | 770.25 | 765.934 | 266.58 | GGB | 11039.3 | GGB | 9.85 | GGB | 1021.24 | GGB | 57.59 | GGB | 180835.01 | GGB | 150548.37 | GGB | 0 | 0 | 2669 | 3600 | 2653.72 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 51606.48 | GGB | 51607.11 | 2653.72 | 2653.72 |  |  |  | 1 | 1 |  |  |  |  | 150548.37 | 2653.72 | 150548.37 | 2653.72 | 9.958 | [5 empty] | 110.9759 | 2510.3427
03.11.2007 02:00 | 3600 | 2 | 756.29 | GGB | 764.469 | 769.313 | 765.934 | 267.06 | GGB | 11044.4 | GGB | 9.85 | GGB | 1020.98 | GGB | 57.55 | GGB | 181269.64 | GGB | 150890.26 | GGB | 0 | 0 | 2694 | 3600 | 2678.14 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 51646.91 | GGB | 51647.54 | 2678.14 | 2678.14 |  |  |  | 1 | 1 |  |  |  |  | 150890.26 | 2678.14 | 150890.26 | 2678.14 | 9.9952 | [5 empty] | 112.2515 | 2504.6547
03.11.2007 03:00 | 3600 | 2 | 756.49 | GGB | 765.934 | 770.344 | 767.033 | 268.93 | GGB | 11053.4 | GGB | 9.85 | GGB | 1021.04 | GGB | 56.94 | GGB | 183634.27 | GGB | 153149.14 | GNB | 0 | 0 | 2693 | 3600 | 2677.91 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 51688.18 | GGB | 51688.8 | 2677.91 | 2677.91 |  |  |  | 1 | 1 |  |  |  |  | 153149.14 | 2677.91 |  | 2677.91 | 9.9399 | [5 empty] | 113.9221 | 2467.7122
03.11.2007 04:00 | 3600 | 2 | 757.03 | GGB | 765.934 | 770.367 | 767.033 | 268.95 | GGB | 11063.7 | GGB | 9.86 | GGB | 1021 | GGB | 56.67 | GGB | 183923.66 | GGB | 153508.17 | GNB | 0 | 0 | 2662 | 3600 | 2646.8 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 51728.24 | GGB | 51728.86 | 2646.8 | 2646.8 |  |  |  | 1 | 1 |  |  |  |  | 153508.17 | 2646.8 |  | 2646.8 | 10.1424 | [5 empty] | 112.8626 | 2461.9406
03.11.2007 05:00 | 3600 | 2 | 756.89 | GGB | 764.835 | 770.273 | 767.033 | 267.45 | GGB | 11087.4 | GGB | 9.86 | GGB | 1019.99 | GGB | 57.52 | GGB | 182036.58 | GGB | 151395.76 | GGB | 0 | 0 | 2682 | 3600 | 2666.78 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 51768.92 | GGB | 51769.54 | 2666.78 | 2666.78 |  |  |  | 1 | 1 |  |  |  |  | 151395.76 | 2666.78 | 151395.76 | 2666.78 | 9.9248 | [5 empty] | 112.1498 | 2496.2918
03.11.2007 06:00 | 3600 | 2 | 756.55 | GGB | 764.469 | 769.289 | 765.934 | 266.89 | GGB | 11053.4 | GGB | 9.85 | GGB | 1019.37 | GGB | 57.63 | GGB | 181603.04 | GGB | 150893.63 | GGB | 0 | 0 | 2688 | 3600 | 2672.37 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 51808.55 | GGB | 51809.16 | 2672.37 | 2672.37 |  |  |  | 1 | 1 |  |  |  |  | 150893.63 | 2672.37 | 150893.63 | 2672.37 | 10.1778 | [5 empty] | 112.0121 | 2504.5988
03.11.2007 07:00 | 3600 | 2 | 757.03 | GGB | 764.835 | 769.594 | 765.934 | 266.2 | GGB | 11048.9 | GGB | 9.87 | GGB | 1018.27 | GGB | 57.77 | GGB | 181046.27 | GGB | 150203.98 | GGB | 0 | 0 | 2660 | 3600 | 2644.38 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 51849.37 | GGB | 51849.99 | 2644.38 | 2644.38 |  |  |  | 1 | 1 |  |  |  |  | 150203.98 | 2644.38 | 150203.98 | 2644.38 | 9.7281 | [5 empty] | 110.3323 | 2516.0984
03.11.2007 08:00 | 3600 | 2 | 756.88 | GGB | 764.835 | 770.789 | 765.934 | 265.27 | GGB | 11010.4 | GGB | 9.86 | GGB | 1016.96 | GGB | 57.79 | GGB | 180011.96 | GGB | 149145.62 | GGB | 0 | 0 | 2654 | 3600 | 2638.6 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 51890.43 | GGB | 51891.05 | 2638.6 | 2638.6 |  |  |  | 1 | 1 |  |  |  |  | 149145.62 | 2638.6 | 149145.62 | 2638.6 | 9.5844 | [5 empty] | 109.3155 | 2533.9531
03.11.2007 09:00 | 3600 | 2 | 756.79 | GGB | 764.835 | 769.57 | 765.934 | 264.88 | GGB | 10973 | GGB | 9.86 | GGB | 1016.29 | GGB | 57.91 | GGB | 179524.51 | GGB | 148586.7 | GGB | 0 | 0 | 2648 | 3600 | 2632.51 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 51930.54 | GGB | 51931.16 | 2632.51 | 2632.51 |  |  |  | 1 | 1 |  |  |  |  | 148586.7 | 2632.51 | 148586.7 | 2632.51 | 9.7521 | [5 empty] | 108.6544 | 2543.4847
03.11.2007 10:00 | 3600 | 2 | 757.26 | GGB | 764.469 | 769.805 | 767.033 | 263.91 | GGB | 10950.7 | GGB | 9.86 | GGB | 1015.14 | GGB | 58.1 | GGB | 178651.94 | GGB | 147615.62 | GGB | 0 | 0 | 2611 | 3600 | 2595.76 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 51970.6 | GGB | 51971.22 | 2595.76 | 2595.76 |  |  |  | 1 | 1 |  |  |  |  | 147615.62 | 2595.76 | 147615.62 | 2595.76 | 9.565 | [5 empty] | 106.4374 | 2560.2169
03.11.2007 11:00 | 3600 | 2 | 757.13 | GGB | 764.835 | 770.953 | 767.033 | 263.25 | GGB | 10921.3 | GGB | 9.86 | GGB | 1013.02 | GGB | 58.2 | GGB | 178100.67 | GGB | 146805.64 | GGB | 0 | 0 | 2594 | 3600 | 2578.49 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 52009.94 | GGB | 52010.56 | 2578.49 | 2578.49 |  |  |  | 1 | 1 |  |  |  |  | 146805.64 | 2578.49 | 146805.64 | 2578.49 | 9.6222 | [5 empty] | 105.1491 | 2574.3425
03.11.2007 12:00 | 3600 | 2 | 756.89 | GGB | 764.835 | 770.906 | 767.033 | 262.56 | GGB | 10899.4 | GGB | 9.86 | GGB | 1010.92 | GGB | 58.02 | GGB | 177582.41 | GGB | 146153.84 | GGB | 0 | 0 | 2596 | 3600 | 2580.95 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 52050.1 | GGB | 52050.73 | 2580.95 | 2580.95 |  |  |  | 1 | 1 |  |  |  |  | 146153.84 | 2580.95 | 146153.84 | 2580.95 | 9.3905 | [5 empty] | 104.7822
03.11.2007 13:00 | 3600 | 2 | 756.71 | GGB | 764.835 | 770.859 | 765.934 | 262.22 | GGB | 10883 | GGB | 9.86 | GGB | 1008.74 | GGB | 58.02 | GGB | 177362.34 | GGB | 145659.2 | GGB | 0 | 0 | 2585 | 3600 | 2569.68 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 52089.27 | GGB | 52089.9 | 2569.68 | 2569.68 |  |  |  | 1 | 1 |  |  |  |  | 145659.2 | 2569.68 | 145659.2 | 2569.68 | 9.5557 | [5 empty] | 103.9715
03.11.2007 14:00 | 3600 | 2 | 756.75 | GGB | 764.835 | 770.977 | 767.033 | 261.47 | GGB | 10859.8 | GGB | 9.86 | GGB | 1005.92 | GGB | 58.4 | GGB | 176900.2 | GGB | 144706.49 | GGB | 0 | 0 | 2567 | 3600 | 2551.57 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 52128.97 | GGB | 52129.6 | 2551.57 | 2551.57 |  |  |  | 1 | 1 |  |  |  |  | 144706.49 | 2551.57 | 144706.49 | 2551.57 | 9.3005 | [5 empty] | 102.5635
03.11.2007 15:00 | 3600 | 2 | 756.74 | GGB | 764.835 | 771.188 | 767.033 | 261.33 | GGB | 10813.1 | GGB | 9.86 | GGB | 1003.05 | GGB | 57.25 | GGB | 177487.78 | GGB | 145277.21 | GGB | 0 | 0 | 2542 | 3600 | 2526.4 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 52167.47 | GGB | 52168.1 | 2526.4 | 2526.4 |  |  |  | 1 | 1 |  |  |  |  | 145277.21 | 2526.4 | 145277.21 | 2526.4 | 9.5332 | [5 empty] | 101.9523
03.11.2007 16:00 | 3600 | 2 | 757.03 | GGB | 764.835 | 770.039 | 767.033 | 260.64 | GGB | 10781.6 | GGB | 9.86 | GGB | 1000.6 | GGB | 57.22 | GGB | 177308.43 | GGB | 144790.31 | GGB | 0 | 0 | 2512 | 3600 | 2496.37 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 52207.06 | GGB | 52207.69 | 2496.37 | 2496.37 |  |  |  | 1 | 1 |  |  |  |  | 144790.31 | 2496.37 | 144790.31 | 2496.37 | 9.1298 | [5 empty] | 100.4028
03.11.2007 17:00 | 3600 | 2 | 756.9 | GGB | 764.835 | 769.828 | 767.033 | 258.07 | GGB | 10771.8 | GGB | 9.86 | GGB | 999.1 | GGB | 57.69 | GGB | 174175.76 | GGB | 141817.72 | GGB | 0 | 0 | 2519 | 3600 | 2503.75 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 52246.74 | GGB | 52247.37 | 2503.75 | 2503.75 |  |  |  | 1 | 1 |  |  |  |  | 141817.72 | 2503.75 | 141817.72 | 2503.75 | 8.9485 | [5 empty] | 98.6323
03.11.2007 18:00 | 3600 | 2 | 757.28 | GGB | 764.835 | 770.836 | 767.033 | 257.14 | GGB | 10688.3 | GGB | 9.86 | GGB | 998.73 | GGB | 58.83 | GGB | 172915.88 | GGB | 140258.24 | GGB | 0 | 0 | 2472 | 3600 | 2456.49 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 52285.18 | GGB | 52285.81 | 2456.49 | 2456.49 |  |  |  | 1 | 1 |  |  |  |  | 140258.24 | 2456.49 | 140258.24 | 2456.49 | 8.9631 | [5 empty] | 95.7064
03.11.2007 19:00 | 3600 | 2 | 757.68 | GGB | 765.934 | 770.648 | 767.033 | 256.05 | GGB | 10625 | GGB | 9.86 | GGB | 998.15 | GGB | 59.18 | GGB | 171295.08 | GGB | 138712.91 | GGB | 0 | 0 | 2428 | 3600 | 2412.46 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 52324.6 | GGB | 52325.24 | 2412.46 | 2412.46 |  |  |  | 1 | 1 |  |  |  |  | 138712.91 | 2412.46 | 138712.91 | 2412.46 | 8.4869 | [5 empty] | 92.9554
03.11.2007 20:00 | 3600 | 2 | 757.36 | GGB | 765.934 | 770.742 | 767.033 | 255.27 | GGB | 10585.2 | GGB | 9.85 | GGB | 998.33 | GGB | 58.85 | GGB | 171302.78 | GGB | 138884.35 | GGB | 0 | 0 | 2416 | 3600 | 2400.75 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 52362.82 | GGB | 52363.46 | 2400.75 | 2400.75 |  |  |  | 1 | 1 |  |  |  |  | 138884.35 | 2400.75 | 138884.35 | 2400.75 | 8.7239 | [5 empty] | 92.6185
03.11.2007 21:00 | 3600 | 2 | 757.58 | GGB | 765.934 | 770.602 | 767.033 | 254.96 | GGB | 10603.9 | GGB | 9.86 | GGB | 998.75 | GGB | 59.22 | GGB | 169915.26 | GGB | 137662.38 | GGB | 0 | 0 | 2422 | 3600 | 2406.74 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 52402.24 | GGB | 52402.88 | 2406.74 | 2406.74 |  |  |  | 1 | 1 |  |  |  |  | 137662.38 | 2406.74 | 137662.38 | 2406.74 | 8.4048 | [5 empty] | 92.0327
03.11.2007 22:00 | 3600 | 2 | 757.6 | GGB | 765.934 | 771.609 | 768.132 | 256.62 | GGB | 10586.3 | GGB | 9.85 | GGB | 999.69 | GGB | 59.17 | GGB | 171968.49 | GGB | 139477.82 | GGB | 0 | 0 | 2415 | 3600 | 2400.16 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 52440.7 | GGB | 52441.35 | 2400.16 | 2400.16 |  |  |  | 1 | 1 |  |  |  |  | 139477.82 | 2400.16 | 139477.82 | 2400.16 | 8.7021 | [5 empty] | 92.9914
03.11.2007 23:00 | 3600 | 2 | 757.41 | GGB | 765.934 | 771.539 | 767.033 | 255.57 | GGB | 10622.8 | GGB | 9.85 | GGB | 1000.34 | GGB | 59.71 | GGB | 170616.17 | GGB | 138246.02 | GGB | 0 | 0 | 2440 | 3600 | 2424.85 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 52479.19 | GGB | 52479.84 | 2424.85 | 2424.85 |  |  |  | 1 | 1 |  |  |  |  | 138246.02 | 2424.85 | 138246.02 | 2424.85 | 8.7094 | [5 empty] | 93.1183
03.11.2007 24:00 | 3600 | 2 | 756.87 | GGB | 763.37 | 769.406 | 765.934 | 257.68 | GGB | 10657.4 | GGB | 9.84 | GGB | 1001.43 | GGB | 59.14 | GGB | 172682.61 | GGB | 140314.34 | GGB | 0 | 0 | 2484 | 3600 | 2468.78 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 52518.29 | GGB | 52518.94 | 2468.78 | 2468.78 |  |  |  | 0 | 1 | [14 empty] | 96.2237
04.11.2007 01:00 | 3600 | 2 | 757.24 | GGB | 765.934 | 770.531 | 767.033 | 260.83 | GGB | 10730.9 | GGB | 9.85 | GGB | 1002.54 | GGB | 58.13 | GGB | 176546.99 | GGB | 144051.4 | GGB | 0 | 0 | 2481 | 3600 | 2465.36 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 52556.35 | GGB | 52557 | 2465.36 | 2465.36 |  |  |  | 1 | 1 |  |  |  |  | 144051.4 | 2465.36 | 144051.4 | 2465.36 | 9.331 | [5 empty] | 98.6496
04.11.2007 02:00 | 3600 | 2 | 757.25 | GGB | 764.835 | 770.414 | 765.934 | 260.18 | GGB | 10783.9 | GGB | 9.86 | GGB | 1003.65 | GGB | 58.45 | GGB | 175703.03 | GGB | 143381.28 | GGB | 0 | 0 | 2498 | 3600 | 2482.56 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 52595.8 | GGB | 52596.45 | 2482.56 | 2482.56 |  |  |  | 1 | 1 |  |  |  |  | 143381.28 | 2482.56 | 143381.28 | 2482.56 | 9.0229 | [5 empty] | 98.8757
04.11.2007 03:00 | 3600 | 2 | 756.72 | GGB | 764.835 | 770.367 | 765.934 | 260.02 | GGB | 10798.5 | GGB | 9.85 | GGB | 1003.86 | GGB | 58.42 | GGB | 175595.2 | GGB | 143338.74 | GGB | 0 | 0 | 2541 | 3600 | 2525.5 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 52634.44 | GGB | 52635.09 | 2525.5 | 2525.5 |  |  |  | 1 | 1 |  |  |  |  | 143338.74 | 2525.5 | 143338.74 | 2525.5 | 9.3686 | [5 empty] | 100.5561
04.11.2007 04:00 | 3600 | 2 | 756.5 | GGB | 765.934 | 771.445 | 768.132 | 261.75 | GGB | 10829.8 | GGB | 9.85 | GGB | 1005.05 | GGB | 57.79 | GGB | 177738.66 | GGB | 145535.6 | GGB | 0 | 0 | 2553 | 3600 | 2538.18 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 52674.06 | GGB | 52674.7 | 2538.18 | 2538.18 |  |  |  | 1 | 1 |  |  |  |  | 145535.6 | 2538.18 | 145535.6 | 2538.18 | 9.3258 | [5 empty] | 102.6099
04.11.2007 05:00 | 3600 | 2 | 756.82 | GGB | 765.934 | 771.469 | 768.132 | 262.34 | GGB | 10836.4 | GGB | 9.85 | GGB | 1006.52 | GGB | 57.74 | GGB | 178449.48 | GGB | 146355.96 | GGB | 0 | 0 | 2550 | 3600 | 2535 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 52713.29 | GGB | 52713.94 | 2535 | 2535 |  |  |  | 1 | 1 |  |  |  |  | 146355.96 | 2535 | 146355.96 | 2535 | 9.455 | [5 empty] | 103.059
04.11.2007 06:00 | 3600 | 2 | 757.07 | GGB | 763.37 | 769.266 | 764.835 | 262.19 | GGB | 10878.7 | GGB | 9.86 | GGB | 1007.14 | GGB | 57.95 | GGB | 177958.72 | GGB | 145948.93 | GGB | 0 | 0 | 2562 | 3600 | 2546.62 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 52752.32 | GGB | 52752.97 | 2546.62 | 2546.62 |  |  |  | 0 | 1 | [14 empty] | 103.2435
04.11.2007 07:00 | 3600 | 2 | 756.02 | GGB | 764.469 | 769.289 | 765.934 | 265.1 | GGB | 10888 | GGB | 9.84 | GGB | 1007.79 | GGB | 56.74 | GGB | 181437.99 | GGB | 149444.63 | GGB | 0 | 0 | 2607 | 3600 | 2591.34 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 52792.43 | GGB | 52793.08 | 2591.34 | 2591.34 |  |  |  | 1 | 1 |  |  |  |  | 149444.63 | 2591.34 | 149444.63 | 2591.34 | 9.655 | [5 empty] | 107.5727 | 2528.8831
04.11.2007 08:00 | 3600 | 2 | 756.74 | GGB | 763.37 | 768.141 | 764.835 | 265.37 | GGB | 10958.7 | GGB | 9.86 | GGB | 1009.35 | GGB | 57.17 | GGB | 180967.05 | GGB | 149091.66 | GGB | 0 | 0 | 2609 | 3600 | 2593.67 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 52831.55 | GGB | 52832.19 | 2593.67 | 2593.67 |  |  |  | 0 | 1 | [14 empty] | 107.4152 | 2534.8702
04.11.2007 09:00 | 3600 | 2 | 756.31 | GGB | 764.469 | 769.148 | 765.934 | 265.47 | GGB | 10992.2 | GGB | 9.85 | GGB | 1010.59 | GGB | 57.49 | GGB | 180836.11 | GGB | 149025.03 | GGB | 0 | 0 | 2657 | 3600 | 2641.53 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 52871.61 | GGB | 52872.25 | 2641.53 | 2641.53 |  |  |  | 1 | 1 |  |  |  |  | 149025.03 | 2641.53 | 149025.03 | 2641.53 | 9.8266 | [5 empty] | 109.3484 | 2536.0035
04.11.2007 10:00 | 3600 | 2 | 756.67 | GGB | 765.934 | 771.141 | 767.033 | 267.05 | GGB | 10990.8 | GGB | 9.85 | GGB | 1011.63 | GGB | 56.84 | GGB | 183022.48 | GGB | 151279.74 | GGB | 0 | 0 | 2631 | 3600 | 2615.41 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 52911.28 | GGB | 52911.92 | 2615.41 | 2615.41 |  |  |  | 1 | 1 |  |  |  |  | 151279.74 | 2615.41 | 151279.74 | 2615.41 | 9.9737 | [5 empty] | 109.9052 | 2498.2063
04.11.2007 11:00 | 3600 | 2 | 756.87 | GGB | 764.835 | 769.945 | 765.934 | 265.75 | GGB | 11007.1 | GGB | 9.86 | GGB | 1012.02 | GGB | 57.32 | GGB | 181425.89 | GGB | 149796.49 | GGB | 0 | 0 | 2637 | 3600 | 2622.13 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 52951.03 | GGB | 52951.68 | 2622.13 | 2622.13 |  |  |  | 1 | 1 |  |  |  |  | 149796.49 | 2622.13 | 149796.49 | 2622.13 | 9.8789 | [5 empty] | 109.1072 | 2522.943
04.11.2007 12:00 | 3600 | 2 | 756.84 | GGB | 764.835 | 769.875 | 767.033 | 267.15 | GGB | 10979.1 | GGB | 9.85 | GGB | 1013.17 | GGB | 56.75 | GGB | 183208.44 | GGB | 151703.32 | GGB | 0 | 0 | 2618 | 3600 | 2602.75 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 52991.23 | GGB | 52991.87 | 2602.75 | 2602.75 |  |  |  | 1 | 1 |  |  |  |  | 151703.32 | 2602.75 | 151703.32 | 2602.75 | 9.8245 | [5 empty] | 109.6794 | 2491.2309
04.11.2007 13:00 | 3600 | 2 | 756.83 | GGB | 764.469 | 769.805 | 767.033 | 265.58 | GGB | 11017.1 | GGB | 9.86 | GGB | 1013.93 | GGB | 57.26 | GGB | 181081.48 | GGB | 149825.21 | GGB | 0 | 0 | 2644 | 3600 | 2628.26 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 53030.58 | GGB | 53031.23 | 2628.26 | 2628.26 |  |  |  | 1 | 1 |  |  |  |  | 149825.21 | 2628.26 | 149825.21 | 2628.26 | 10.0046 | [5 empty] | 109.3832 | 2522.4593
04.11.2007 14:00 | 3600 | 2 | 757.21 | GGB | 765.934 | 771.164 | 767.033 | 266.3 | GGB | 10972.8 | GGB | 9.86 | GGB | 1014.65 | GGB | 57.35 | GGB | 181826.41 | GGB | 150504.84 | GGB | 0 | 0 | 2603 | 3600 | 2587.62 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 53071.03 | GGB | 53071.68 | 2587.62 | 2587.62 |  |  |  | 1 | 1 |  |  |  |  | 150504.84 | 2587.62 | 150504.84 | 2587.62 | 9.6279 | [5 empty] | 108.1804 | 2511.0687
04.11.2007 15:00 | 3600 | 2 | 757.1 | GGB | 764.835 | 769.992 | 767.033 | 265.86 | GGB | 10992.1 | GGB | 9.86 | GGB | 1015.49 | GGB | 57.28 | GGB | 181272.94 | GGB | 150205.28 | GGB | 0 | 0 | 2610 | 3600 | 2594.47 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 53110.34 | GGB | 53110.99 | 2594.47 | 2594.47 |  |  |  | 1 | 1 |  |  |  |  | 150205.28 | 2594.47 | 150205.28 | 2594.47 | 9.9136 | [5 empty] | 108.2509 | 2516.0767
04.11.2007 16:00 | 3600 | 2 | 756.83 | GGB | 763.37 | 769.266 | 765.934 | 265.91 | GGB | 11005.7 | GGB | 9.85 | GGB | 1016.21 | GGB | 57.64 | GGB | 180901.03 | GGB | 149837.82 | GGB | 0 | 0 | 2638 | 3600 | 2622.55 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 53150.71 | GGB | 53151.37 | 2622.55 | 2622.55 |  |  |  | 0 | 1 | [14 empty] | 109.1548 | 2522.2471
04.11.2007 17:00 | 3600 | 2 | 756.55 | GGB | 764.835 | 770.438 | 765.934 | 268.36 | GGB | 10996.7 | GGB | 9.84 | GGB | 1017.25 | GGB | 56.56 | GGB | 183942.36 | GGB | 153013.04 | GNB | 0 | 0 | 2637 | 3600 | 2621.7 | GGB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 53192.04 | GGB | 53192.7 | 2621.7 | 2621.7 |  |  |  | 1 | 1 |  |  |  |  | 153013.04 | 2621.7 |  | 2621.7 | 9.7061 | [5 empty] | 111.4317 | 2469.9071
04.11.2007 18:00 | 3600 | 2 | 757.07 | GGB | 764.835 | 769.359 | 767.033 | 267.57 | GGB | 11062.7 | GGB | 9.86 | GGB | 1018.93 | GGB | 57.02 | GGB | 182529.53 | GGB | 151874.58 | GGB | 0 | 0 | 2654 | 3600 | 2638.28 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 53231.99 | GGB | 53232.65 | 2638.28 | 2638.28 |  |  |  | 1 | 1 |  |  |  |  | 151874.58 | 2638.28 | 151874.58 | 2638.28 | 10.0297 | [5 empty] | 111.3021 | 2488.4217
04.11.2007 19:00 | 3600 | 2 | 756.44 | GGB | 763.37 | 768.117 | 765.934 | 268.4 | GGB | 11047.9 | GGB | 9.84 | GGB | 1019.55 | GGB | 56.91 | GGB | 183345.98 | GGB | 152699.36 | GNB | 0 | 0 | 2681 | 3600 | 2665.43 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 53273.11 | GGB | 53273.77 | 2665.43 | 2665.43 |  |  |  | 0 | 1 | [14 empty] | 113.0582 | 2474.9809
04.11.2007 20:00 | 3600 | 2 | 758.08 | GGB | 767.033 | 772.359 | 768.132 | 267.24 | GGB | 11094.8 | GGB | 9.88 | GGB | 1020.52 | GGB | 56.6 | GGB | 183014.78 | GGB | 152711.53 | GNB | 0 | 0 | 2608 | 3600 | 2592.89 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 53312.73 | GGB | 53313.39 | 2592.89 | 2592.89 |  |  |  | 1 | 1 |  |  |  |  | 152711.53 | 2592.89 |  | 2592.89 | 9.994 | [5 empty] | 109.9901 | 2474.7837
04.11.2007 21:00 | 3600 | 2 | 757.17 | GGB | 764.469 | 769.031 | 765.934 | 266.02 | GGB | 10997.6 | GGB | 9.85 | GGB | 1021.6 | GGB | 57.51 | GGB | 181204.72 | GGB | 150946.82 | GGB | 0 | 0 | 2611 | 3600 | 2595.2 | GGB | 100 | GGB | 41.59 | GGB | 41.59 | GGB | 53354.32 | GGB | 53354.98 | 2595.2 | 2595.2 |  |  |  | 1 | 1 |  |  |  |  | 150946.82 | 2595.2 | 150946.82 | 2595.2 | 9.419 | [5 empty] | 108.8159 | 2503.7162
04.11.2007 22:00 | 3600 | 2 | 757.84 | GGB | 765.934 | 770.039 | 767.033 | 266.71 | GGB | 10998.9 | GGB | 9.86 | GGB | 1022.44 | GGB | 57.74 | GGB | 181524.92 | GGB | 151229.83 | GGB | 0 | 0 | 2583 | 3600 | 2567.72 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 53392.7 | GGB | 53393.36 | 2567.72 | 2567.72 |  |  |  | 1 | 1 |  |  |  |  | 151229.83 | 2567.72 | 151229.83 | 2567.72 | 10.1177 | [5 empty] | 107.8655 | 2499.0308
04.11.2007 23:00 | 3600 | 2 | 757.43 | GGB | 768.132 | 771.984 | 768.498 | 267.88 | GGB | 10989.4 | GGB | 9.85 | GGB | 1023.33 | GGB | 57.8 | GGB | 182180.72 | GGB | 151884.85 | GGB | 0 | 0 | 2599 | 3600 | 2583.75 | GGB | 100 | GGB | 41.75 | GGB | 41.75 | GGB | 53434.45 | GGB | 53435.11 | 2583.75 | 2583.75 |  |  |  | 1 | 1 |  |  |  |  | 151884.85 | 2583.75 | 151884.85 | 2583.75 | 9.3996 | [5 empty] | 109.009 | 2488.2534
04.11.2007 24:00 | 3600 | 2 | 758.13 | GGB | 768.132 | 772.898 | 769.597 | 268.52 | GGB | 11011.7 | GGB | 9.86 | GGB | 1023.87 | GGB | 57.65 | GGB | 182844.22 | GGB | 152583.92 | GGB | 0 | 0 | 2566 | 3600 | 2550.29 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 53473.19 | GGB | 53473.85 | 2550.29 | 2550.29 |  |  |  | 1 | 1 |  |  |  |  | 152583.92 | 2550.29 | 152583.92 | 2550.29 | 10.0447 | [5 empty] | 108.0926 | 2476.8534
05.11.2007 01:00 | 3600 | 2 | 757.38 | GGB | 764.835 | 769.875 | 767.033 | 267.59 | GGB | 11044.6 | GGB | 9.85 | GGB | 1024.57 | GGB | 57.84 | GGB | 181452.3 | GGB | 151438.4 | GGB | 0 | 0 | 2629 | 3600 | 2613.61 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 53514.01 | GGB | 53514.66 | 2613.61 | 2613.61 |  |  |  | 1 | 1 |  |  |  |  | 151438.4 | 2613.61 | 151438.4 | 2613.61 | 9.6986 | [5 empty] | 109.9447 | 2495.589
05.11.2007 02:00 | 3600 | 2 | 756.86 | GGB | 764.835 | 769.898 | 767.033 | 268.62 | GGB | 11092.9 | GGB | 9.85 | GGB | 1025.12 | GGB | 57.38 | GGB | 182704.48 | GGB | 152779.82 | GNB | 0 | 0 | 2679 | 3600 | 2663.55 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 53554.43 | GGB | 53555.08 | 2663.55 | 2663.55 |  |  |  | 1 | 1 |  |  |  |  | 152779.82 | 2663.55 |  | 2663.55 | 10.0677 | [5 empty] | 113.038 | 2473.6775
05.11.2007 03:00 | 3600 | 2 | 757.04 | GGB | 767.033 | 772.125 | 768.498 | 270.11 | GGB | 11081.3 | GGB | 9.85 | GGB | 1026.17 | GGB | 56.77 | GGB | 184698.29 | GGB | 154889.37 | GNB | 0 | 0 | 2663 | 3600 | 2648.08 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 53594.21 | GGB | 53594.86 | 2648.08 | 2648.08 |  |  |  | 1 | 1 |  |  |  |  | 154889.37 | 2648.08 |  | 2648.08 | 10.3107 | [5 empty] | 113.9332 | 2439.9867
05.11.2007 04:00 | 3600 | 2 | 756.72 | GGB | 765.934 | 769.758 | 767.033 | 270.49 | GGB | 11094.9 | GGB | 9.84 | GGB | 1025.84 | GGB | 56.72 | GGB | 185035 | GGB | 155147.99 | GNB | 0 | 0 | 2685 | 3600 | 2669.47 | GGB | 100 | GGB | 41.68 | GGB | 41.68 | GGB | 53635.89 | GGB | 53636.54 | 2669.47 | 2669.47 |  |  |  | 1 | 1 |  |  |  |  | 155147.99 | 2669.47 |  | 2669.47 | 9.9367 | [5 empty] | 115.0453 | 2435.9194
05.11.2007 05:00 | 3600 | 2 | 757.54 | GGB | 765.934 | 769.711 | 765.934 | 271.1 | GGB | 11103 | GGB | 9.86 | GGB | 1027.03 | GGB | 56.66 | GGB | 185766.72 | GGB | 155968.55 | GNB | 0 | 0 | 2650 | 3600 | 2634.5 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 53674.86 | GGB | 53675.5 | 2634.5 | 2634.5 |  |  |  | 1 | 1 |  |  |  |  | 155968.55 | 2634.5 |  | 2634.5 | 10.5467 | [5 empty] | 114.1387 | 2423.1039
05.11.2007 06:00 | 3600 | 2 | 757.26 | GGB | 764.469 | 768.492 | 765.934 | 270.77 | GGB | 11158 | GGB | 9.85 | GGB | 1027.71 | GGB | 56.72 | GGB | 185286.97 | GGB | 155640.26 | GNB | 0 | 0 | 2692 | 3600 | 2677.02 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 53716.4 | GGB | 53717.05 | 2677.02 | 2677.02 |  |  |  | 1 | 1 |  |  |  |  | 155640.26 | 2677.02 |  | 2677.02 | 10.0277 | [5 empty] | 115.7367 | 2428.2149
05.11.2007 07:00 | 3600 | 2 | 756.43 | GGB | 764.835 | 769.664 | 765.934 | 272.17 | GGB | 11149.9 | GGB | 9.84 | GGB | 1028.54 | GGB | 56.72 | GGB | 186857.16 | GGB | 157083.93 | GNB | 0 | 0 | 2737 | 3600 | 2722.04 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 53756.8 | GGB | 53757.44 | 2722.04 | 2722.04 |  |  |  | 1 | 1 |  |  |  |  | 157083.93 | 2722.04 |  | 2722.04 | 10.5865 | [5 empty] | 118.7747 | 2405.8986
05.11.2007 08:00 | 3600 | 2 | 757.33 | GGB | 765.934 | 770.742 | 767.033 | 273.13 | GGB | 11194.6 | GGB | 9.86 | GGB | 1029.52 | GGB | 56.26 | GGB | 187912.38 | GGB | 158342.4 | GNB | 0 | 0 | 2716 | 3600 | 2700.12 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 53796.76 | GGB | 53797.4 | 2700.12 | 2700.12 |  |  |  | 1 | 1 |  |  |  |  | 158342.4 | 2700.12 |  | 2700.12 | 10.6993 | [5 empty] | 118.7621 | 2386.777
05.11.2007 09:00 | 3600 | 2 | 757.5 | GGB | 764.835 | 770.297 | 765.934 | 271.95 | GGB | 11219.8 | GGB | 9.86 | GGB | 1029.93 | GGB | 56.91 | GGB | 186265.17 | GGB | 156708.35 | GNB | 0 | 0 | 2724 | 3600 | 2708.58 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 53837.97 | GGB | 53838.61 | 2708.58 | 2708.58 |  |  |  | 1 | 1 |  |  |  |  | 156708.35 | 2708.58 |  | 2708.58 | 10.2999 | [5 empty] | 117.9048 | 2411.6647
05.11.2007 10:00 | 3600 | 2 | 757.59 | GGB | 767.033 | 771.234 | 768.132 | 271.89 | GGB | 11157.5 | GGB | 9.86 | GGB | 1030.47 | GGB | 56.93 | GGB | 186349.9 | GGB | 156855.64 | GNB | 0 | 0 | 2696 | 3600 | 2681.04 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 53878.91 | GGB | 53879.56 | 2681.04 | 2681.04 |  |  |  | 1 | 1 |  |  |  |  | 156855.64 | 2681.04 |  | 2681.04 | 10.2695 | [5 empty] | 116.8156 | 2409.4001
05.11.2007 11:00 | 3600 | 2 | 758.49 | GGB | 764.835 | 770.25 | 767.033 | 270.18 | GGB | 11099.1 | GGB | 9.87 | GGB | 1028.48 | GGB | 58.89 | GGB | 167838.92 | GGB | 140167.26 | GGB | 0 | 0 | 2611 | 2811 | 2595.56 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 53918.77 | GGB | 53919.42 | 2595.56 | 2595.56 |  |  |  | 1 | 1 |  |  |  |  | 140167.26 | 2595.56 | 140167.26 | 2595.56 | 9.1273 | [5 empty] | 101.059
05.11.2007 12:00 | 3600 | 2 | 758.05 | GGB | 764.835 | 769.313 | 765.934 | 268.31 | GGB | 11070.5 | GGB | 9.86 | GGB | 1028.76 | GGB | 58.31 | GGB | 182298.46 | GGB | 152553.26 | GGB | 0 | 0 | 2623 | 3600 | 2607.46 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 53959.57 | GGB | 53960.22 | 2607.46 | 2607.46 |  |  |  | 1 | 1 |  |  |  |  | 152553.26 | 2607.46 | 152553.26 | 2607.46 | 9.7494 | [5 empty] | 110.4935 | 2477.3512
05.11.2007 13:00 | 3600 | 2 | 758.46 | GGB | 765.934 | 771.516 | 767.033 | 268.68 | GGB | 11001 | GGB | 9.86 | GGB | 1028.45 | GGB | 58.02 | GGB | 182865.13 | GGB | 153114.86 | GNB | 0 | 0 | 2566 | 3600 | 2550.81 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 53999.78 | GGB | 54000.43 | 2550.81 | 2550.81 |  |  |  | 1 | 1 |  |  |  |  | 153114.86 | 2550.81 |  | 2550.81 | 9.7132 | [5 empty] | 108.4908 | 2468.2647
05.11.2007 14:00 | 3600 | 2 | 758.96 | GGB | 767.033 | 773.602 | 768.498 | 267.92 | GGB | 10991.8 | GGB | 9.87 | GGB | 1028.1 | GGB | 58.35 | GGB | 182039.88 | GGB | 152216.92 | GGB | 0 | 0 | 2537 | 3600 | 2521.8 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 54039.63 | GGB | 54040.28 | 2521.8 | 2521.8 |  |  |  | 1 | 1 |  |  |  |  | 152216.92 | 2521.8 | 152216.92 | 2521.8 | 9.6326 | [5 empty] | 106.628 | 2482.8252
05.11.2007 15:00 | 3600 | 2 | 758.1 | GGB | 765.934 | 770.25 | 767.033 | 267.04 | GGB | 10960 | GGB | 9.85 | GGB | 1026.9 | GGB | 58.88 | GGB | 180829.51 | GGB | 150788.1 | GGB | 0 | 0 | 2568 | 3600 | 2553 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 54079.85 | GGB | 54080.49 | 2553 | 2553 |  |  |  | 1 | 1 |  |  |  |  | 150788.1 | 2553 | 150788.1 | 2553 | 9.5738 | [5 empty] | 106.9339 | 2506.3516
05.11.2007 16:00 | 3600 | 2 | 758.49 | GGB | 765.934 | 771.609 | 767.033 | 268.3 | GGB | 10948.5 | GGB | 9.86 | GGB | 1026.42 | GGB | 58.36 | GGB | 182406.29 | GGB | 152272.75 | GGB | 0 | 0 | 2533 | 3600 | 2517.72 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 54119.45 | GGB | 54120.1 | 2517.72 | 2517.72 |  |  |  | 1 | 1 |  |  |  |  | 152272.75 | 2517.72 | 152272.75 | 2517.72 | 9.6789 | [5 empty] | 106.4945 | 2481.9149
05.11.2007 17:00 | 3600 | 2 | 758.29 | GGB | 764.835 | 770.508 | 767.033 | 267.84 | GGB | 10989.7 | GGB | 9.85 | GGB | 1026.56 | GGB | 58.54 | GGB | 181073.78 | GGB | 151096.97 | GGB | 0 | 0 | 2571 | 3600 | 2555.63 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 54159.89 | GGB | 54160.54 | 2555.63 | 2555.63 |  |  |  | 1 | 1 |  |  |  |  | 151096.97 | 2555.63 | 151096.97 | 2555.63 | 9.5487 | [5 empty] | 107.2633 | 2501.2282
05.11.2007 18:00 | 3600 | 2 | 757.13 | GGB | 765.934 | 770.508 | 767.033 | 270.08 | GGB | 10992.5 | GGB | 9.84 | GGB | 1026.8 | GGB | 57.92 | GGB | 183199.63 | GGB | 153192.59 | GNB | 0 | 0 | 2627 | 3600 | 2611.18 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 54199.33 | GGB | 54199.98 | 2611.18 | 2611.18 |  |  |  | 1 | 1 |  |  |  |  | 153192.59 | 2611.18 |  | 2611.18 | 10.1423 | [5 empty] | 111.1148 | 2467.0123
05.11.2007 19:00 | 3600 | 2 | 757.76 | GGB | 765.934 | 771.773 | 767.033 | 270.65 | GGB | 11031.6 | GGB | 9.85 | GGB | 1026.64 | GGB | 57.68 | GGB | 184031.49 | GGB | 153979.71 | GNB | 0 | 0 | 2607 | 3600 | 2591.8 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 54240 | GGB | 54240.66 | 2591.8 | 2591.8 |  |  |  | 1 | 1 |  |  |  |  | 153979.71 | 2591.8 |  | 2591.8 | 9.8103 | [5 empty] | 110.8568 | 2454.4013
05.11.2007 20:00 | 3600 | 2 | 757.79 | GGB | 764.835 | 770.766 | 765.934 | 269.2 | GGB | 11075.8 | GGB | 9.86 | GGB | 1026.18 | GGB | 58.07 | GGB | 182208.23 | GGB | 152202.51 | GGB | 0 | 0 | 2636 | 3600 | 2621.11 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 54279.67 | GGB | 54280.33 | 2621.11 | 2621.11 |  |  |  | 1 | 1 |  |  |  |  | 152202.51 | 2621.11 | 152202.51 | 2621.11 | 10.0565 | [5 empty] | 110.8165 | 2483.0602
05.11.2007 21:00 | 3600 | 2 | 757.2 | GGB | 765.934 | 771.867 | 767.033 | 270.81 | GGB | 11070.1 | GGB | 9.85 | GGB | 1026.34 | GGB | 57.34 | GGB | 184854.54 | GGB | 154778.06 | GNB | 0 | 0 | 2656 | 3600 | 2640.76 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 54320.13 | GGB | 54320.79 | 2640.76 | 2640.76 |  |  |  | 1 | 1 |  |  |  |  | 154778.06 | 2640.76 |  | 2640.76 | 10.1021 | [5 empty] | 113.5366 | 2441.7414
05.11.2007 22:00 | 3600 | 2 | 757.1 | GGB | 765.934 | 771.586 | 768.132 | 271.24 | GGB | 11064.9 | GGB | 9.85 | GGB | 1025.68 | GGB | 57.04 | GGB | 184929.36 | GGB | 154884.07 | GNB | 0 | 0 | 2673 | 3600 | 2657.87 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 54360.4 | GGB | 54361.06 | 2657.87 | 2657.87 |  |  |  | 1 | 1 |  |  |  |  | 154884.07 | 2657.87 |  | 2657.87 | 10.2225 | [5 empty] | 114.3505 | 2440.0702
05.11.2007 23:00 | 3600 | 2 | 757.35 | GGB | 763.37 | 769.266 | 764.835 | 269.92 | GGB | 11103.2 | GGB | 9.86 | GGB | 1025 | GGB | 57.63 | GGB | 183361.38 | GGB | 153193.75 | GNB | 0 | 0 | 2679 | 3600 | 2663.69 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 54400.1 | GGB | 54400.76 | 2663.69 | 2663.69 |  |  |  | 0 | 1 | [14 empty] | 113.3502 | 2466.9936
05.11.2007 24:00 | 3600 | 2 | 756.81 | GGB | 764.469 | 769.266 | 766.3 | 271.35 | GGB | 11076.4 | GGB | 9.85 | GGB | 1024.9 | GGB | 56.62 | GGB | 185564.26 | GGB | 155494.72 | GNB | 0 | 0 | 2686 | 3600 | 2670.74 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 54440.78 | GGB | 54441.44 | 2670.74 | 2670.74 |  |  |  | 1 | 1 |  |  |  |  | 155494.72 | 2670.74 |  | 2670.74 | 10.2086 | [5 empty] | 115.3572 | 2430.4877
06.11.2007 01:00 | 3600 | 2 | 757.47 | GGB | 767.033 | 772.359 | 768.864 | 271.16 | GGB | 11132.7 | GGB | 9.87 | GGB | 1024.37 | GGB | 56.61 | GGB | 185402.51 | GGB | 155286.22 | GNB | 0 | 0 | 2680 | 3600 | 2664.7 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 54481.28 | GGB | 54481.94 | 2664.7 | 2664.7 |  |  |  | 1 | 1 |  |  |  |  | 155286.22 | 2664.7 |  | 2664.7 | 10.2171 | [5 empty] | 114.942 | 2433.751
06.11.2007 02:00 | 3600 | 2 | 756.19 | GGB | 763.37 | 768.703 | 765.201 | 270.66 | GGB | 11120.4 | GGB | 9.84 | GGB | 1023.85 | GGB | 56.71 | GGB | 185008.59 | GGB | 154828.05 | GNB | 0 | 0 | 2745 | 3600 | 2729.15 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 54521.61 | GGB | 54522.27 | 2729.15 | 2729.15 |  |  |  | 0 | 1 | [14 empty] | 117.3747 | 2440.953
06.11.2007 03:00 | 3600 | 2 | 757.29 | GGB | 764.835 | 769.852 | 766.3 | 271.55 | GGB | 11143.9 | GGB | 9.86 | GGB | 1023.08 | GGB | 55.94 | GGB | 187062.92 | GGB | 156793.27 | GNB | 0 | 0 | 2697 | 3600 | 2681.69 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 54562.55 | GGB | 54563.22 | 2681.69 | 2681.69 |  |  |  | 1 | 1 |  |  |  |  | 156793.27 | 2681.69 |  | 2681.69 | 10.2679 | [5 empty] | 116.7975 | 2410.3586
06.11.2007 04:00 | 3600 | 2 | 757.68 | GGB | 764.835 | 769.875 | 766.3 | 269.72 | GGB | 11166.1 | GGB | 9.88 | GGB | 1022.18 | GGB | 56.13 | GGB | 185037.2 | GGB | 154873.02 | GNB | 0 | 0 | 2677 | 3600 | 2661.77 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 54602.54 | GGB | 54603.2 | 2661.77 | 2661.77 |  |  |  | 1 | 1 |  |  |  |  | 154873.02 | 2661.77 |  | 2661.77 | 10.3111 | [5 empty] | 114.5101 | 2440.2443
06.11.2007 05:00 | 3600 | 2 | 756.79 | GGB | 763.37 | 769.711 | 765.201 | 269.5 | GGB | 11098.3 | GGB | 9.86 | GGB | 1021.6 | GGB | 56.31 | GGB | 184642.18 | GGB | 154369.19 | GNB | 0 | 0 | 2693 | 3600 | 2677.93 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 54643.77 | GGB | 54644.44 | 2677.93 | 2677.93 |  |  |  | 0 | 1 | [14 empty] | 114.8305 | 2448.2087
06.11.2007 06:00 | 3600 | 2 | 757.2 | GGB | 764.835 | 770.766 | 766.667 | 270.63 | GGB | 11028.8 | GGB | 9.85 | GGB | 1020.69 | GGB | 56.63 | GGB | 184491.43 | GGB | 153958.22 | GNB | 0 | 0 | 2654 | 3600 | 2638.72 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 54683.16 | GGB | 54683.82 | 2638.72 | 2638.72 |  |  |  | 1 | 1 |  |  |  |  | 153958.22 | 2638.72 |  | 2638.72 | 10.3162 | [5 empty] | 112.848 | 2454.7439
06.11.2007 07:00 | 3600 | 2 | 757.69 | GGB | 764.469 | 769.664 | 766.3 | 269.37 | GGB | 11038.1 | GGB | 9.86 | GGB | 1019.25 | GGB | 57.57 | GGB | 182236.84 | GGB | 151429.51 | GGB | 0 | 0 | 2639 | 3600 | 2623.4 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 54723.54 | GGB | 54724.2 | 2623.4 | 2623.4 |  |  |  | 1 | 1 |  |  |  |  | 151429.51 | 2623.4 | 151429.51 | 2623.4 | 9.838 | [5 empty] | 110.35 | 2495.7355
06.11.2007 08:00 | 3600 | 2 | 756.79 | GGB | 764.469 | 769.711 | 765.201 | 269.65 | GGB | 11010 | GGB | 9.85 | GGB | 1018.69 | GGB | 57.91 | GGB | 182297.36 | GGB | 151240.5 | GGB | 0 | 0 | 2672 | 3600 | 2656.44 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 54763.79 | GGB | 54764.45 | 2656.44 | 2656.44 |  |  |  | 1 | 1 |  |  |  |  | 151240.5 | 2656.44 | 151240.5 | 2656.44 | 9.9816 | [5 empty] | 111.6004 | 2498.8545
06.11.2007 09:00 | 3600 | 2 | 757.47 | GGB | 765.934 | 771.773 | 767.033 | 270.75 | GGB | 11001.9 | GGB | 9.86 | GGB | 1018.51 | GGB | 57.51 | GGB | 183970.97 | GGB | 152784.39 | GNB | 0 | 0 | 2625 | 3600 | 2609.96 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 54803.34 | GGB | 54804 | 2609.96 | 2609.96 |  |  |  | 1 | 1 |  |  |  |  | 152784.39 | 2609.96 |  | 2609.96 | 10.0825 | [5 empty] | 110.767 | 2473.6035
06.11.2007 10:00 | 3600 | 2 | 757.59 | GGB | 767.033 | 772.922 | 769.597 | 269.88 | GGB | 10993.1 | GGB | 9.87 | GGB | 1017.72 | GGB | 57.76 | GGB | 182842.02 | GGB | 151613.95 | GGB | 0 | 0 | 2613 | 3600 | 2597.98 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 54843.87 | GGB | 54844.53 | 2597.98 | 2597.98 |  |  |  | 1 | 1 |  |  |  |  | 151613.95 | 2597.98 | 151613.95 | 2597.98 | 9.7185 | [5 empty] | 109.4139 | 2492.6994
06.11.2007 11:00 | 3600 | 2 | 757.8 | GGB | 765.934 | 771.844 | 766.667 | 267.69 | GGB | 10982 | GGB | 9.87 | GGB | 1016.34 | GGB | 58.58 | GGB | 180227.62 | GGB | 148875.13 | GGB | 0 | 0 | 2600 | 3600 | 2584.56 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 54883.51 | GGB | 54884.17 | 2584.56 | 2584.56 |  |  |  | 1 | 1 |  |  |  |  | 148875.13 | 2584.56 | 148875.13 | 2584.56 | 9.7068 | [5 empty] | 106.8824 | 2538.557
06.11.2007 12:00 | 3600 | 2 | 757.52 | GGB | 767.033 | 771.797 | 767.766 | 268.65 | GGB | 10909.1 | GGB | 9.85 | GGB | 1015.5 | GGB | 58.16 | GGB | 181631.65 | GGB | 150103.31 | GGB | 0 | 0 | 2578 | 3600 | 2562.74 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 54923.04 | GGB | 54923.7 | 2562.74 | 2562.74 |  |  |  | 1 | 1 |  |  |  |  | 150103.31 | 2562.74 | 150103.31 | 2562.74 | 9.7312 | [5 empty] | 106.8544 | 2517.7859
06.11.2007 13:00 | 3600 | 2 | 757.87 | GGB | 765.934 | 771.867 | 767.766 | 266.54 | GGB | 10879 | GGB | 9.86 | GGB | 1014.68 | GGB | 58.74 | GGB | 179360.56 | GGB | 147845.46 | GGB | 0 | 0 | 2547 | 3600 | 2531.77 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 54963.35 | GGB | 54964.02 | 2531.77 | 2531.77 |  |  |  | 1 | 1 |  |  |  |  | 147845.46 | 2531.77 | 147845.46 | 2531.77 | 9.2835 | [5 empty] | 103.9752
06.11.2007 14:00 | 3600 | 2 | 757.84 | GGB | 768.132 | 774.07 | 769.963 | 266.46 | GGB | 10843.9 | GGB | 9.86 | GGB | 1013.66 | GGB | 58.43 | GGB | 180263.93 | GGB | 148580.99 | GGB | 0 | 0 | 2512 | 3600 | 2497.09 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 55001.95 | GGB | 55002.62 | 2497.09 | 2497.09 |  |  |  | 1 | 1 |  |  |  |  | 148580.99 | 2497.09 | 148580.99 | 2497.09 | 9.6119 | [5 empty] | 103.0611
06.11.2007 15:00 | 3600 | 2 | 758.36 | GGB | 765.934 | 771.844 | 767.766 | 264.84 | GGB | 10869.2 | GGB | 9.87 | GGB | 1012.66 | GGB | 57.92 | GGB | 180266.13 | GGB | 148666.83 | GGB | 0 | 0 | 2483 | 3600 | 2468.21 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 55042.63 | GGB | 55043.3 | 2468.21 | 2468.21 |  |  |  | 1 | 1 |  |  |  |  | 148666.83 | 2468.21 | 148666.83 | 2468.21 | 9.0202 | [5 empty] | 101.928
06.11.2007 16:00 | 3600 | 2 | 757.8 | GGB | 767.033 | 773.18 | 768.864 | 264.25 | GGB | 10880.2 | GGB | 9.86 | GGB | 1011.92 | GGB | 57.59 | GGB | 180324.45 | GGB | 148752.37 | GGB | 0 | 0 | 2511 | 3600 | 2496.25 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 55081.28 | GGB | 55081.95 | 2496.25 | 2496.25 |  |  |  | 1 | 1 |  |  |  |  | 148752.37 | 2496.25 | 148752.37 | 2496.25 | 9.6073 | [5 empty] | 103.1453
06.11.2007 17:00 | 3600 | 2 | 757.01 | GGB | 765.934 | 770.977 | 767.766 | 264.11 | GGB | 10878.5 | GGB | 9.85 | GGB | 1011.51 | GGB | 57.65 | GGB | 179936.03 | GGB | 148345.46 | GGB | 0 | 0 | 2548 | 3600 | 2532.67 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 55121.79 | GGB | 55122.46 | 2532.67 | 2532.67 |  |  |  | 1 | 1 |  |  |  |  | 148345.46 | 2532.67 | 148345.46 | 2532.67 | 9.2745 | [5 empty] | 104.3639
06.11.2007 18:00 | 3600 | 2 | 757.3 | GGB | 765.934 | 770.883 | 767.766 | 265.09 | GGB | 10885.9 | GGB | 9.85 | GGB | 1011.49 | GGB | 56.91 | GGB | 181263.04 | GGB | 149769.31 | GGB | 0 | 0 | 2539 | 3600 | 2524.01 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 55161.09 | GGB | 55161.76 | 2524.01 | 2524.01 |  |  |  | 1 | 1 |  |  |  |  | 149769.31 | 2524.01 | 149769.31 | 2524.01 | 9.6188 | [5 empty] | 105.0053 | 2523.4008
06.11.2007 19:00 | 3600 | 2 | 757.58 | GGB | 764.835 | 769.711 | 766.667 | 264.18 | GGB | 10916.8 | GGB | 9.86 | GGB | 1011.52 | GGB | 57.08 | GGB | 180251.83 | GGB | 148866.14 | GGB | 0 | 0 | 2542 | 3600 | 2527.1 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 55200.81 | GGB | 55201.48 | 2527.1 | 2527.1 |  |  |  | 1 | 1 |  |  |  |  | 148866.14 | 2527.1 | 148866.14 | 2527.1 | 9.4713 | [5 empty] | 104.4999
06.11.2007 20:00 | 3600 | 2 | 756.9 | GGB | 765.934 | 770.648 | 767.766 | 264.34 | GGB | 10909.6 | GGB | 9.85 | GGB | 1011.4 | GGB | 57.13 | GGB | 180353.06 | GGB | 148904.86 | GGB | 0 | 0 | 2578 | 3600 | 2562.76 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 55241.02 | GGB | 55241.7 | 2562.76 | 2562.76 |  |  |  | 1 | 1 |  |  |  |  | 148904.86 | 2562.76 | 148904.86 | 2562.76 | 9.488 | [5 empty] | 106.0021 | 2538.0501
06.11.2007 21:00 | 3600 | 2 | 757.31 | GGB | 765.934 | 770.602 | 766.667 | 264.96 | GGB | 10896 | GGB | 9.86 | GGB | 1010.97 | GGB | 56.71 | GGB | 181352.17 | GGB | 149859.69 | GGB | 0 | 0 | 2539 | 3600 | 2523.94 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 55279.69 | GGB | 55280.37 | 2523.94 | 2523.94 |  |  |  | 1 | 1 |  |  |  |  | 149859.69 | 2523.94 | 149859.69 | 2523.94 | 9.7811 | [5 empty] | 105.0658 | 2521.879
06.11.2007 22:00 | 3600 | 2 | 757.74 | GGB | 765.934 | 771.82 | 767.766 | 264.19 | GGB | 10914.6 | GGB | 9.87 | GGB | 1010.46 | GGB | 56.98 | GGB | 180252.93 | GGB | 148752.75 | GGB | 0 | 0 | 2531 | 3600 | 2515.63 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 55319.71 | GGB | 55320.38 | 2515.63 | 2515.63 |  |  |  | 1 | 1 |  |  |  |  | 148752.75 | 2515.63 | 148752.75 | 2515.63 | 9.3528 | [5 empty] | 103.9464
06.11.2007 23:00 | 3600 | 2 | 757.02 | GGB | 763.37 | 769.664 | 765.201 | 263.35 | GGB | 10896.1 | GGB | 9.85 | GGB | 1009.99 | GGB | 57.59 | GGB | 178963.33 | GGB | 147348.85 | GGB | 0 | 0 | 2562 | 3600 | 2546.82 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 55359.48 | GGB | 55360.16 | 2546.82 | 2546.82 |  |  |  | 0 | 1 | [14 empty] | 104.2419
06.11.2007 24:00 | 3600 | 2 | 757.26 | GGB | 765.934 | 771.047 | 767.766 | 264.13 | GGB | 10876.2 | GGB | 9.85 | GGB | 1009.84 | GGB | 56.7 | GGB | 180697.47 | GGB | 149156.58 | GGB | 0 | 0 | 2537 | 3600 | 2521.81 | GGB | 100 | GGB | 37.52 | GGB | 37.52 | GGB | 55397 | GGB | 55397.68 | 2521.81 | 2521.81 |  |  |  | 1 | 1 |  |  |  |  | 149156.58 | 2521.81 | 149156.58 | 2521.81 | 10.0252 | [5 empty] | 104.4846
07.11.2007 01:00 | 3600 | 2 | 757.39 | GGB | 764.835 | 771.047 | 766.667 | 264.79 | GGB | 10870.6 | GGB | 9.85 | GGB | 1009.1 | GGB | 57.01 | GGB | 180535.72 | GGB | 148773.73 | GGB | 0 | 0 | 2538 | 3600 | 2522.99 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 55438.28 | GGB | 55438.97 | 2522.99 | 2522.99 |  |  |  | 1 | 1 |  |  |  |  | 148773.73 | 2522.99 | 148773.73 | 2522.99 | 9.0907 | [5 empty] | 104.2652
07.11.2007 02:00 | 3600 | 2 | 757.16 | GGB | 764.469 | 769.734 | 766.3 | 264.34 | GGB | 10915.9 | GGB | 9.86 | GGB | 1008.57 | GGB | 57.32 | GGB | 179604.83 | GGB | 147788.76 | GGB | 0 | 0 | 2579 | 3600 | 2563.59 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 55476.19 | GGB | 55476.88 | 2563.59 | 2563.59 |  |  |  | 1 | 1 |  |  |  |  | 147788.76 | 2563.59 | 147788.76 | 2563.59 | 9.9939 | [5 empty] | 105.2416 | 2557.2175
07.11.2007 03:00 | 3600 | 2 | 756.39 | GGB | 764.469 | 770.625 | 766.3 | 265.32 | GGB | 10916.7 | GGB | 9.84 | GGB | 1008.22 | GGB | 57.07 | GGB | 180434.48 | GGB | 148531.43 | GGB | 0 | 0 | 2619 | 3600 | 2603.32 | GGB | 100 | GGB | 42.48 | GGB | 42.48 | GGB | 55518.68 | GGB | 55519.36 | 2603.32 | 2603.32 |  |  |  | 1 | 1 |  |  |  |  | 148531.43 | 2603.32 | 148531.43 | 2603.32 | 9.1025 | [5 empty] | 107.4097 | 2544.4312
07.11.2007 04:00 | 3600 | 2 | 757.13 | GGB | 764.835 | 770.625 | 766.3 | 266.19 | GGB | 10936.2 | GGB | 9.86 | GGB | 1007.56 | GGB | 56.37 | GGB | 181926.54 | GGB | 149979.85 | GGB | 0 | 0 | 2596 | 3600 | 2580.76 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 55557.81 | GGB | 55558.49 | 2580.76 | 2580.76 |  |  |  | 1 | 1 |  |  |  |  | 149979.85 | 2580.76 | 149979.85 | 2580.76 | 9.8917 | [5 empty] | 107.5172 | 2519.8585
07.11.2007 05:00 | 3600 | 2 | 757.28 | GGB | 764.835 | 770.602 | 766.667 | 265.22 | GGB | 10959.4 | GGB | 9.87 | GGB | 1007.09 | GGB | 56.59 | GGB | 180630.34 | GGB | 148745.15 | GGB | 0 | 0 | 2600 | 3600 | 2585.11 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 55597.57 | GGB | 55598.25 | 2585.11 | 2585.11 |  |  |  | 1 | 1 |  |  |  |  | 148745.15 | 2585.11 | 148745.15 | 2585.11 | 9.6711 | [5 empty] | 106.8118 | 2540.7753
07.11.2007 06:00 | 3600 | 2 | 756.65 | GGB | 763.37 | 769.453 | 766.3 | 264.48 | GGB | 10935.5 | GGB | 9.85 | GGB | 1006.65 | GGB | 56.81 | GGB | 179856.81 | GGB | 147941.38 | GGB | 0 | 0 | 2626 | 3600 | 2611.13 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 55638.58 | GGB | 55639.26 | 2611.13 | 2611.13 |  |  |  | 0 | 1 | [14 empty] | 107.3039 | 2554.5794
07.11.2007 07:00 | 3600 | 2 | 757.21 | GGB | 764.835 | 770.508 | 766.667 | 265.64 | GGB | 10911.2 | GGB | 9.86 | GGB | 1006.19 | GGB | 56.43 | GGB | 181447.9 | GGB | 149357.01 | GGB | 0 | 0 | 2586 | 3600 | 2570.61 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 55676.99 | GGB | 55677.66 | 2570.61 | 2570.61 |  |  |  | 1 | 1 |  |  |  |  | 149357.01 | 2570.61 | 149357.01 | 2570.61 | 9.9984 | [5 empty] | 106.6496 | 2530.3667
07.11.2007 08:00 | 3600 | 2 | 757.47 | GGB | 764.835 | 771.586 | 766.667 | 264.89 | GGB | 10915.4 | GGB | 9.86 | GGB | 1006.07 | GGB | 57 | GGB | 180043.86 | GGB | 147925.32 | GGB | 0 | 0 | 2576 | 3600 | 2561.09 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 55717.26 | GGB | 55717.93 | 2561.09 | 2561.09 |  |  |  | 1 | 1 |  |  |  |  | 147925.32 | 2561.09 | 147925.32 | 2561.09 | 9.4077 | [5 empty] | 105.2361 | 2554.8567
07.11.2007 09:00 | 3600 | 2 | 756.65 | GGB | 765.934 | 770.906 | 766.667 | 264.48 | GGB | 10885.8 | GGB | 9.85 | GGB | 1006.19 | GGB | 57.45 | GGB | 179373.76 | GGB | 147192.29 | GGB | 0 | 0 | 2602 | 3600 | 2586.35 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 55757.13 | GGB | 55757.8 | 2586.35 | 2586.35 |  |  |  | 1 | 1 |  |  |  |  | 147192.29 | 2586.35 | 147192.29 | 2586.35 | 9.5483 | [5 empty] | 105.7474 | 2567.5801
07.11.2007 10:00 | 3600 | 2 | 757.61 | GGB | 764.835 | 770.883 | 766.667 | 264.83 | GGB | 10872.1 | GGB | 9.86 | GGB | 1005.77 | GGB | 57.26 | GGB | 179960.24 | GGB | 147695.94 | GGB | 0 | 0 | 2546 | 3600 | 2530.91 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 55796.4 | GGB | 55797.08 | 2530.91 | 2530.91 |  |  |  | 1 | 1 |  |  |  |  | 147695.94 | 2530.91 | 147695.94 | 2530.91 | 9.5164 | [5 empty] | 103.8348
07.11.2007 11:00 | 3600 | 2 | 757.56 | GGB | 765.934 | 770.695 | 767.766 | 264.37 | GGB | 10841.6 | GGB | 9.86 | GGB | 1005.14 | GGB | 57.54 | GGB | 179142.69 | GGB | 146811.36 | GGB | 0 | 0 | 2533 | 3600 | 2517.76 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 55836.27 | GGB | 55836.94 | 2517.76 | 2517.76 |  |  |  | 1 | 1 |  |  |  |  | 146811.36 | 2517.76 | 146811.36 | 2517.76 | 9.2734 | [5 empty] | 102.6766
07.11.2007 12:00 | 3600 | 2 | 757.82 | GGB | 765.934 | 771.75 | 767.766 | 263.59 | GGB | 10802.8 | GGB | 9.86 | GGB | 1004.37 | GGB | 57.8 | GGB | 178265.72 | GGB | 145863.35 | GGB | 0 | 0 | 2510 | 3600 | 2494.45 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 55875.41 | GGB | 55876.08 | 2494.45 | 2494.45 |  |  |  | 1 | 1 |  |  |  |  | 145863.35 | 2494.45 | 145863.35 | 2494.45 | 9.2961 | [5 empty] | 101.0691
07.11.2007 13:00 | 3600 | 2 | 757.91 | GGB | 765.934 | 771.75 | 767.766 | 262.77 | GGB | 10762.8 | GGB | 9.86 | GGB | 1003.75 | GGB | 58.18 | GGB | 177126.87 | GGB | 144678.45 | GGB | 0 | 0 | 2482 | 3600 | 2466.58 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 55914.68 | GGB | 55915.35 | 2466.58 | 2466.58 |  |  |  | 1 | 1 |  |  |  |  | 144678.45 | 2466.58 | 144678.45 | 2466.58 | 9.0874 | [5 empty] | 99.128
07.11.2007 14:00 | 3600 | 2 | 758.05 | GGB | 765.934 | 771.75 | 767.766 | 261.51 | GGB | 10717 | GGB | 9.86 | GGB | 1002.78 | GGB | 58.57 | GGB | 175627.11 | GGB | 143146.38 | GGB | 0 | 0 | 2456 | 3600 | 2440.67 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 55954.03 | GGB | 55954.7 | 2440.67 | 2440.67 |  |  |  | 1 | 1 |  |  |  |  | 143146.38 | 2440.67 | 143146.38 | 2440.67 | 8.8786 | [5 empty] | 97.0481
07.11.2007 15:00 | 3600 | 2 | 757.96 | GGB | 765.934 | 771.867 | 768.132 | 259.64 | GGB | 10721.5 | GGB | 9.86 | GGB | 1001.99 | GGB | 59.41 | GGB | 173238.28 | GGB | 140731.43 | GGB | 0 | 0 | 2469 | 3600 | 2453.31 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 55992.76 | GGB | 55993.42 | 2453.31 | 2453.31 |  |  |  | 1 | 1 |  |  |  |  | 140731.43 | 2453.31 | 140731.43 | 2453.31 | 8.9168 | [5 empty] | 95.905
07.11.2007 16:00 | 3600 | 2 | 757.82 | GGB | 765.934 | 771.867 | 767.033 | 261.12 | GGB | 10691.9 | GGB | 9.85 | GGB | 1001.25 | GGB | 58.75 | GGB | 175370.73 | GGB | 142638.61 | GGB | 0 | 0 | 2455 | 3600 | 2440.24 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 56032.41 | GGB | 56033.08 | 2440.24 | 2440.24 |  |  |  | 1 | 1 |  |  |  |  | 142638.61 | 2440.24 | 142638.61 | 2440.24 | 8.7764 | [5 empty] | 96.6868
07.11.2007 17:00 | 3600 | 2 | 757.43 | GGB | 765.934 | 771 | 767.766 | 261.93 | GGB | 10703.9 | GGB | 9.85 | GGB | 1000.94 | GGB | 58.44 | GGB | 176173.98 | GGB | 143383.43 | GGB | 0 | 0 | 2466 | 3600 | 2450.41 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 56070.68 | GGB | 56071.35 | 2450.41 | 2450.41 |  |  |  | 1 | 1 |  |  |  |  | 143383.43 | 2450.41 | 143383.43 | 2450.41 | 9.1808 | [5 empty] | 97.5967
07.11.2007 18:00 | 3600 | 2 | 757.62 | GGB | 765.934 | 771.984 | 767.766 | 260.33 | GGB | 10754.6 | GGB | 9.86 | GGB | 1000.2 | GGB | 58.89 | GGB | 174336.41 | GGB | 141588.86 | GGB | 0 | 0 | 2487 | 3600 | 2471.29 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 56109.44 | GGB | 56110.11 | 2471.29 | 2471.29 |  |  |  | 1 | 1 |  |  |  |  | 141588.86 | 2471.29 | 141588.86 | 2471.29 | 9.0275 | [5 empty] | 97.1964
07.11.2007 19:00 | 3600 | 2 | 757.42 | GGB | 765.934 | 771.82 | 767.766 | 261.29 | GGB | 10719.1 | GGB | 9.85 | GGB | 999.6 | GGB | 58.21 | GGB | 176539.29 | GGB | 143586.73 | GGB | 0 | 0 | 2470 | 3600 | 2455.24 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 56149.27 | GGB | 56149.94 | 2455.24 | 2455.24 |  |  |  | 1 | 1 |  |  |  |  | 143586.73 | 2455.24 | 143586.73 | 2455.24 | 8.8511 | [5 empty] | 97.9277
07.11.2007 20:00 | 3600 | 2 | 757.56 | GGB | 764.835 | 770.742 | 767.766 | 260.77 | GGB | 10716.7 | GGB | 9.86 | GGB | 998.94 | GGB | 57.99 | GGB | 176400.65 | GGB | 143476.3 | GGB | 0 | 0 | 2458 | 3600 | 2442.65 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 56188.05 | GGB | 56188.72 | 2442.65 | 2442.65 |  |  |  | 1 | 1 |  |  |  |  | 143476.3 | 2442.65 | 143476.3 | 2442.65 | 9.0372 | [5 empty] | 97.3507
07.11.2007 21:00 | 3600 | 2 | 757.46 | GGB | 765.201 | 770.672 | 766.667 | 258.54 | GGB | 10731.3 | GGB | 9.86 | GGB | 998.14 | GGB | 58.5 | GGB | 173552.97 | GGB | 140830.02 | GGB | 0 | 0 | 2471 | 3600 | 2456.18 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 56226.8 | GGB | 56227.47 | 2456.18 | 2456.18 |  |  |  | 1 | 1 |  |  |  |  | 140830.02 | 2456.18 | 140830.02 | 2456.18 | 8.9266 | [5 empty] | 96.0844
07.11.2007 22:00 | 3600 | 2 | 756.94 | GGB | 764.102 | 769.758 | 766.3 | 257.87 | GGB | 10729.1 | GGB | 9.85 | GGB | 997.81 | GGB | 58.31 | GGB | 174154.86 | GGB | 141354.31 | GGB | 0 | 0 | 2498 | 3600 | 2483.05 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 56266.06 | GGB | 56266.73 | 2483.05 | 2483.05 |  |  |  | 1 | 1 |  |  |  |  | 141354.31 | 2483.05 | 141354.31 | 2483.05 | 8.9401 | [5 empty] | 97.4972
07.11.2007 23:00 | 3600 | 2 | 757.19 | GGB | 765.201 | 770.953 | 766.667 | 258.69 | GGB | 10728.6 | GGB | 9.86 | GGB | 997.3 | GGB | 58.46 | GGB | 174081.13 | GGB | 141156.31 | GGB | 0 | 0 | 2496 | 3600 | 2480.75 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 56305.58 | GGB | 56306.25 | 2480.75 | 2480.75 |  |  |  | 1 | 1 |  |  |  |  | 141156.31 | 2480.75 | 141156.31 | 2480.75 | 8.8607 | [5 empty] | 97.2704
07.11.2007 24:00 | 3600 | 2 | 757.35 | GGB | 765.201 | 771.023 | 766.667 | 258.6 | GGB | 10723.1 | GGB | 9.86 | GGB | 996.87 | GGB | 58.49 | GGB | 173930.39 | GGB | 140961.57 | GGB | 0 | 0 | 2490 | 3600 | 2475.04 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 56343.98 | GGB | 56344.65 | 2475.04 | 2475.04 |  |  |  | 1 | 1 |  |  |  |  | 140961.57 | 2475.04 | 140961.57 | 2475.04 | 9.0856 | [5 empty] | 96.9126
08.11.2007 01:00 | 3600 | 2 | 757.24 | GGB | 765.201 | 771.023 | 766.667 | 258.54 | GGB | 10712.1 | GGB | 9.86 | GGB | 996.76 | GGB | 58.49 | GGB | 173774.14 | GGB | 140820.36 | GGB | 0 | 0 | 2486 | 3600 | 2470.46 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 56383.52 | GGB | 56384.19 | 2470.46 | 2470.46 |  |  |  | 1 | 1 |  |  |  |  | 140820.36 | 2470.46 | 140820.36 | 2470.46 | 8.7985 | [5 empty] | 96.6364
08.11.2007 02:00 | 3600 | 2 | 757.26 | GGB | 766.3 | 771.094 | 767.766 | 260.25 | GGB | 10687.6 | GGB | 9.85 | GGB | 996.84 | GGB | 57.91 | GGB | 175967.11 | GGB | 142855.21 | GGB | 0 | 0 | 2469 | 3600 | 2453.91 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 56422.23 | GGB | 56422.91 | 2453.91 | 2453.91 |  |  |  | 1 | 1 |  |  |  |  | 142855.21 | 2453.91 | 142855.21 | 2453.91 | 9.0536 | [5 empty] | 97.3761
08.11.2007 03:00 | 3600 | 2 | 757.55 | GGB | 765.201 | 771.141 | 766.667 | 259.44 | GGB | 10716 | GGB | 9.86 | GGB | 996.74 | GGB | 58.24 | GGB | 174676.42 | GGB | 141652.17 | GGB | 0 | 0 | 2473 | 3600 | 2457.47 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 56461.12 | GGB | 56461.8 | 2457.47 | 2457.47 |  |  |  | 1 | 1 |  |  |  |  | 141652.17 | 2457.47 | 141652.17 | 2457.47 | 8.951 | [5 empty] | 96.6961
08.11.2007 04:00 | 3600 | 2 | 757.16 | GGB | 765.201 | 769.992 | 767.766 | 259.64 | GGB | 10708 | GGB | 9.85 | GGB | 996.85 | GGB | 58.4 | GGB | 174625.8 | GGB | 141561.93 | GGB | 0 | 0 | 2493 | 3600 | 2478.25 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 56500.51 | GGB | 56501.19 | 2478.25 | 2478.25 |  |  |  | 1 | 1 |  |  |  |  | 141561.93 | 2478.25 | 141561.93 | 2478.25 | 8.9065 | [5 empty] | 97.4516
08.11.2007 05:00 | 3600 | 2 | 757.51 | GGB | 765.201 | 771.188 | 767.766 | 260.58 | GGB | 10706 | GGB | 9.86 | GGB | 997.34 | GGB | 57.99 | GGB | 176142.07 | GGB | 143036.69 | GGB | 0 | 0 | 2467 | 3600 | 2452.03 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 56538.83 | GGB | 56539.51 | 2452.03 | 2452.03 |  |  |  | 1 | 1 |  |  |  |  | 143036.69 | 2452.03 | 143036.69 | 2452.03 | 9.1527 | [5 empty] | 97.4251
08.11.2007 06:00 | 3600 | 2 | 757.38 | GGB | 765.201 | 771.234 | 766.667 | 259.3 | GGB | 10732.8 | GGB | 9.86 | GGB | 997.31 | GGB | 58.5 | GGB | 174504.76 | GGB | 141481.75 | GGB | 0 | 0 | 2494 | 3600 | 2478.29 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 56578.22 | GGB | 56578.91 | 2478.29 | 2478.29 |  |  |  | 1 | 1 |  |  |  |  | 141481.75 | 2478.29 | 141481.75 | 2478.29 | 8.8993 | [5 empty] | 97.398
08.11.2007 07:00 | 3600 | 2 | 757.25 | GGB | 765.201 | 771.516 | 767.033 | 260.82 | GGB | 10713.6 | GGB | 9.85 | GGB | 998.01 | GGB | 58.11 | GGB | 176226.79 | GGB | 143149.87 | GGB | 0 | 0 | 2491 | 3600 | 2475.36 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 56616.78 | GGB | 56617.47 | 2475.36 | 2475.36 |  |  |  | 1 | 1 |  |  |  |  | 143149.87 | 2475.36 | 143149.87 | 2475.36 | 9.1895 | [5 empty] | 98.4299
08.11.2007 08:00 | 3600 | 2 | 757.64 | GGB | 766.3 | 772.523 | 768.132 | 260.77 | GGB | 10735.8 | GGB | 9.86 | GGB | 998.47 | GGB | 58.09 | GGB | 176212.49 | GGB | 143209.47 | GGB | 0 | 0 | 2474 | 3600 | 2458.75 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 56655.85 | GGB | 56656.54 | 2458.75 | 2458.75 |  |  |  | 1 | 1 |  |  |  |  | 143209.47 | 2458.75 | 143209.47 | 2458.75 | 9.0124 | [5 empty] | 97.8101
08.11.2007 09:00 | 3600 | 2 | 756.33 | GGB | 765.201 | 771.141 | 767.033 | 260.87 | GGB | 10801.1 | GGB | 9.83 | GGB | 999.34 | GGB | 58.55 | GGB | 175325.62 | GGB | 142416.7 | GGB | 0 | 0 | 2582 | 3600 | 2566.36 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 56694.91 | GGB | 56695.6 | 2566.36 | 2566.36 |  |  |  | 1 | 1 |  |  |  |  | 142416.7 | 2566.36 | 142416.7 | 2566.36 | 9.3572 | [5 empty] | 101.5257
08.11.2007 10:00 | 3600 | 2 | 757.74 | GGB | 766.3 | 772.148 | 768.132 | 263.33 | GGB | 10988.8 | GGB | 9.85 | GGB | 1000.17 | GGB | 59.13 | GGB | 176519.48 | GGB | 143255.52 | GGB | 0 | 0 | 2617 | 3600 | 2601.2 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 56734.51 | GGB | 56735.21 | 2601.2 | 2601.2 |  |  |  | 1 | 1 |  |  |  |  | 143255.52 | 2601.2 | 143255.52 | 2601.2 | 9.4076 | [5 empty] | 103.5101
08.11.2007 11:00 | 3600 | 2 | 757.99 | GGB | 765.201 | 770.203 | 767.033 | 261.82 | GGB | 11053.5 | GGB | 9.86 | GGB | 1000.33 | GGB | 60.19 | GGB | 174073.43 | GGB | 140842.93 | GGB | 0 | 0 | 2640 | 3600 | 2624.88 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 56774.42 | GGB | 56775.12 | 2624.88 | 2624.88 |  |  |  | 1 | 1 |  |  |  |  | 140842.93 | 2624.88 | 140842.93 | 2624.88 | 9.2632 | [5 empty] | 102.6933
08.11.2007 12:00 | 3600 | 2 | 757.49 | GGB | 765.201 | 771.094 | 767.033 | 261.83 | GGB | 11045.2 | GGB | 9.86 | GGB | 1000.44 | GGB | 60.49 | GGB | 173956.8 | GGB | 140638.66 | GGB | 0 | 0 | 2632 | 3600 | 2616.88 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 56814.27 | GGB | 56814.97 | 2616.88 | 2616.88 |  |  |  | 1 | 1 |  |  |  |  | 140638.66 | 2616.88 | 140638.66 | 2616.88 | 9.2355 | [5 empty] | 102.2318
08.11.2007 13:00 | 3600 | 2 | 758.05 | GGB | 766.3 | 771.281 | 768.498 | 262.29 | GGB | 11019.1 | GGB | 9.86 | GGB | 1000.24 | GGB | 60.27 | GGB | 174863.47 | GGB | 141435.62 | GGB | 0 | 0 | 2600 | 3600 | 2584.37 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 56854.34 | GGB | 56855.04 | 2584.37 | 2584.37 |  |  |  | 1 | 1 |  |  |  |  | 141435.62 | 2584.37 | 141435.62 | 2584.37 | 9.1221 | [5 empty] | 101.5339
08.11.2007 14:00 | 3600 | 2 | 757.73 | GGB | 766.3 | 771.141 | 768.132 | 261.9 | GGB | 11003.8 | GGB | 9.85 | GGB | 1000.72 | GGB | 60.68 | GGB | 174077.83 | GGB | 140692.95 | GGB | 0 | 0 | 2614 | 3600 | 2598.47 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 56894.3 | GGB | 56895 | 2598.47 | 2598.47 |  |  |  | 1 | 1 |  |  |  |  | 140692.95 | 2598.47 | 140692.95 | 2598.47 | 9.1488 | [5 empty] | 101.5518
08.11.2007 15:00 | 3600 | 2 | 758.33 | GGB | 766.3 | 772.172 | 767.033 | 261.31 | GGB | 11004.1 | GGB | 9.86 | GGB | 1000.85 | GGB | 60.92 | GGB | 173220.67 | GGB | 139919.7 | GGB | 0 | 0 | 2595 | 3600 | 2580.03 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 56933.89 | GGB | 56934.59 | 2580.03 | 2580.03 |  |  |  | 1 | 1 |  |  |  |  | 139919.7 | 2580.03 | 139919.7 | 2580.03 | 9.1184 | [5 empty] | 100.277
08.11.2007 16:00 | 3600 | 2 | 758.32 | GGB | 765.201 | 772.43 | 768.132 | 261.75 | GGB | 10992.5 | GGB | 9.86 | GGB | 1001.19 | GGB | 60.93 | GGB | 173612.39 | GGB | 140278.75 | GGB | 0 | 0 | 2588 | 3600 | 2572.45 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 56974.38 | GGB | 56975.08 | 2572.45 | 2572.45 |  |  |  | 1 | 1 |  |  |  |  | 140278.75 | 2572.45 | 140278.75 | 2572.45 | 8.9123 | [5 empty] | 100.2389
08.11.2007 17:00 | 3600 | 2 | 758.23 | GGB | 766.667 | 773.531 | 769.597 | 261.88 | GGB | 10992 | GGB | 9.86 | GGB | 1001.23 | GGB | 61 | GGB | 173535.37 | GGB | 140193.65 | GGB | 0 | 0 | 2594 | 3600 | 2579.06 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 57014.11 | GGB | 57014.82 | 2579.06 | 2579.06 |  |  |  | 1 | 1 |  |  |  |  | 140193.65 | 2579.06 | 140193.65 | 2579.06 | 9.0983 | [5 empty] | 100.4355
08.11.2007 18:00 | 3600 | 2 | 757.94 | GGB | 766.667 | 772.453 | 769.597 | 262.35 | GGB | 10977.1 | GGB | 9.85 | GGB | 1002.01 | GGB | 61.02 | GGB | 174098.74 | GGB | 140749.6 | GGB | 0 | 0 | 2603 | 3600 | 2587.5 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 57054.25 | GGB | 57054.96 | 2587.5 | 2587.5 |  |  |  | 1 | 1 |  |  |  |  | 140749.6 | 2587.5 | 140749.6 | 2587.5 | 9.073 | [5 empty] | 101.1638
08.11.2007 19:00 | 3600 | 2 | 758.27 | GGB | 765.201 | 772.453 | 768.132 | 261.4 | GGB | 11010.1 | GGB | 9.86 | GGB | 1001.68 | GGB | 61.13 | GGB | 173005 | GGB | 139775.05 | GGB | 0 | 0 | 2595 | 3600 | 2579.47 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 57094.11 | GGB | 57094.83 | 2579.47 | 2579.47 |  |  |  | 1 | 1 |  |  |  |  | 139775.05 | 2579.47 | 139775.05 | 2579.47 | 9.043 | [5 empty] | 100.1515
08.11.2007 20:00 | 3600 | 2 | 758.2 | GGB | 766.3 | 772.453 | 768.498 | 262.91 | GGB | 10978.4 | GGB | 9.85 | GGB | 1002.37 | GGB | 60.54 | GGB | 175046.13 | GGB | 141769.75 | GGB | 0 | 0 | 2591 | 3600 | 2576.18 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 57134.2 | GGB | 57134.92 | 2576.18 | 2576.18 |  |  |  | 1 | 1 |  |  |  |  | 141769.75 | 2576.18 | 141769.75 | 2576.18 | 9.1101 | [5 empty] | 101.4512
08.11.2007 21:00 | 3600 | 2 | 758.32 | GGB | 766.667 | 772.266 | 768.498 | 261.56 | GGB | 11025.7 | GGB | 9.86 | GGB | 1002.19 | GGB | 60.98 | GGB | 173090.83 | GGB | 139977.43 | GGB | 0 | 0 | 2607 | 3600 | 2591.81 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 57174.23 | GGB | 57174.95 | 2591.81 | 2591.81 |  |  |  | 1 | 1 |  |  |  |  | 139977.43 | 2591.81 | 139977.43 | 2591.81 | 9.0631 | [5 empty] | 100.7764
08.11.2007 22:00 | 3600 | 2 | 757.77 | GGB | 767.766 | 773.719 | 769.597 | 262.62 | GGB | 11007.3 | GGB | 9.85 | GGB | 1002.34 | GGB | 60.67 | GGB | 174473.96 | GGB | 141246.55 | GGB | 0 | 0 | 2624 | 3600 | 2608.89 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 57214.2 | GGB | 57214.93 | 2608.89 | 2608.89 |  |  |  | 1 | 1 |  |  |  |  | 141246.55 | 2608.89 | 141246.55 | 2608.89 | 9.217 | [5 empty] | 102.3602
08.11.2007 23:00 | 3600 | 2 | 757.97 | GGB | 766.3 | 772.383 | 768.498 | 262.41 | GGB | 11018 | GGB | 9.85 | GGB | 1001.97 | GGB | 60.3 | GGB | 175074.74 | GGB | 141840.54 | GGB | 0 | 0 | 2619 | 3600 | 2603.99 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 57254.36 | GGB | 57255.08 | 2603.99 | 2603.99 |  |  |  | 1 | 1 |  |  |  |  | 141840.54 | 2603.99 | 141840.54 | 2603.99 | 9.1993 | [5 empty] | 102.5976
08.11.2007 24:00 | 3600 | 2 | 758.39 | GGB | 766.667 | 773.391 | 769.597 | 262.87 | GGB | 11025 | GGB | 9.86 | GGB | 1001.57 | GGB | 60.01 | GGB | 174959.2 | GGB | 141813.35 | GGB | 0 | 0 | 2596 | 3600 | 2580.91 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 57293.89 | GGB | 57294.62 | 2580.91 | 2580.91 |  |  |  | 1 | 1 |  |  |  |  | 141813.35 | 2580.91 | 141813.35 | 2580.91 | 9.2566 | [5 empty] | 101.6687
09.11.2007 01:00 | 3600 | 2 | 757.68 | GGB | 765.201 | 771.164 | 768.132 | 261.86 | GGB | 11025.8 | GGB | 9.85 | GGB | 1001.05 | GGB | 60.54 | GGB | 173527.66 | GGB | 140357.54 | GGB | 0 | 0 | 2638 | 3600 | 2622.45 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 57335 | GGB | 57335.73 | 2622.45 | 2622.45 |  |  |  | 1 | 1 |  |  |  |  | 140357.54 | 2622.45 | 140357.54 | 2622.45 | 8.9536 | [5 empty] | 102.2446
09.11.2007 02:00 | 3600 | 2 | 757.95 | GGB | 766.667 | 773.203 | 769.597 | 262.45 | GGB | 11020.6 | GGB | 9.86 | GGB | 1000.89 | GGB | 60.2 | GGB | 174439.84 | GGB | 141215.12 | GGB | 0 | 0 | 2619 | 3600 | 2603.8 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 57374.36 | GGB | 57375.09 | 2603.8 | 2603.8 |  |  |  | 1 | 1 |  |  |  |  | 141215.12 | 2603.8 | 141215.12 | 2603.8 | 9.3419 | [5 empty] | 102.1378
09.11.2007 03:00 | 3600 | 2 | 757.95 | GGB | 766.3 | 772.172 | 768.132 | 262.63 | GGB | 11009.7 | GGB | 9.85 | GGB | 1000.4 | GGB | 60.04 | GGB | 174888.78 | GGB | 141575.58 | GGB | 0 | 0 | 2615 | 3600 | 2599.68 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 57414.89 | GGB | 57415.63 | 2599.68 | 2599.68 |  |  |  | 1 | 1 |  |  |  |  | 141575.58 | 2599.68 | 141575.58 | 2599.68 | 9.0787 | [5 empty] | 102.2364
09.11.2007 04:00 | 3600 | 2 | 758.35 | GGB | 766.3 | 772.125 | 768.498 | 261.62 | GGB | 11030.4 | GGB | 9.87 | GGB | 999.54 | GGB | 60.27 | GGB | 173782.94 | GGB | 140463.31 | GGB | 0 | 0 | 2603 | 3600 | 2587.86 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 57454.28 | GGB | 57455.02 | 2587.86 | 2587.86 |  |  |  | 1 | 1 |  |  |  |  | 140463.31 | 2587.86 | 140463.31 | 2587.86 | 9.2282 | [5 empty] | 100.9721
09.11.2007 05:00 | 3600 | 2 | 757.73 | GGB | 766.3 | 772.242 | 768.498 | 262.15 | GGB | 10987.8 | GGB | 9.85 | GGB | 998.84 | GGB | 60.03 | GGB | 174692.92 | GGB | 141203.81 | GGB | 0 | 0 | 2607 | 3600 | 2591.91 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 57495.14 | GGB | 57495.88 | 2591.91 | 2591.91 |  |  |  | 1 | 1 |  |  |  |  | 141203.81 | 2591.91 | 141203.81 | 2591.91 | 8.9571 | [5 empty] | 101.6632
09.11.2007 06:00 | 3600 | 2 | 758.34 | GGB | 766.667 | 773.273 | 768.498 | 261.73 | GGB | 10992.8 | GGB | 9.86 | GGB | 998.2 | GGB | 59.95 | GGB | 174245.08 | GGB | 140781.98 | GGB | 0 | 0 | 2583 | 3600 | 2567.63 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 57534.51 | GGB | 57535.24 | 2567.63 | 2567.63 |  |  |  | 1 | 1 |  |  |  |  | 140781.98 | 2567.63 | 140781.98 | 2567.63 | 9.1838 | [5 empty] | 100.41
09.11.2007 07:00 | 3600 | 2 | 757.88 | GGB | 766.3 | 772.359 | 768.864 | 260.55 | GGB | 10993.2 | GGB | 9.86 | GGB | 997.89 | GGB | 60.59 | GGB | 172854.26 | GGB | 139351.1 | GGB | 0 | 0 | 2612 | 3600 | 2596.59 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 57574.8 | GGB | 57575.54 | 2596.59 | 2596.59 |  |  |  | 1 | 1 |  |  |  |  | 139351.1 | 2596.59 | 139351.1 | 2596.59 | 8.9786 | [5 empty] | 100.5105
09.11.2007 08:00 | 3600 | 2 | 758.08 | GGB | 766.3 | 772.523 | 768.864 | 261.17 | GGB | 10958 | GGB | 9.85 | GGB | 997.58 | GGB | 60.32 | GGB | 173770.84 | GGB | 140157.94 | GGB | 0 | 0 | 2574 | 3207 | 2559.08 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 57614.77 | GGB | 57615.5 | 2559.08 | 2559.08 |  |  |  | 1 | 1 |  |  |  |  | 140157.94 | 2559.08 | 140157.94 | 2559.08 | 8.9759 | [5 empty] | 99.6321
09.11.2007 09:00 | 3600 | 2 | 758.38 | GGB | 765.201 | 772.523 | 767.766 | 259.77 | GGB | 10966.2 | GGB | 9.86 | GGB | 997.08 | GGB | 60.71 | GGB | 172000.4 | GGB | 138496.55 | GGB | 0 | 0 | 2564 | 3600 | 2548.78 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 57654.89 | GGB | 57655.63 | 2548.78 | 2548.78 |  |  |  | 1 | 1 |  |  |  |  | 138496.55 | 2548.78 | 138496.55 | 2548.78 | 8.7963 | [5 empty] | 98.0548
09.11.2007 10:00 | 3600 | 2 | 758.53 | GGB | 766.667 | 773.414 | 768.864 | 260.11 | GGB | 10948.2 | GGB | 9.86 | GGB | 996.85 | GGB | 60.5 | GGB | 172893.87 | GGB | 139272.15 | GGB | 0 | 0 | 2544 | 3600 | 2528.71 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 57694.86 | GGB | 57695.6 | 2528.71 | 2528.71 |  |  |  | 1 | 1 |  |  |  |  | 139272.15 | 2528.71 | 139272.15 | 2528.71 | 8.8111 | [5 empty] | 97.8275
09.11.2007 11:00 | 3600 | 2 | 757.9 | GGB | 766.3 | 772.242 | 768.864 | 259.63 | GGB | 10909.3 | GGB | 9.85 | GGB | 996.39 | GGB | 60.73 | GGB | 172134.64 | GGB | 138502.7 | GGB | 0 | 0 | 2540 | 3600 | 2525.07 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 57734.84 | GGB | 57735.58 | 2525.07 | 2525.07 |  |  |  | 1 | 1 |  |  |  |  | 138502.7 | 2525.07 | 138502.7 | 2525.07 | 8.7476 | [5 empty] | 97.1469
09.11.2007 12:00 | 3600 | 2 | 758.43 | GGB | 766.667 | 773.25 | 768.864 | 259.58 | GGB | 10884.7 | GGB | 9.86 | GGB | 995.82 | GGB | 60.5 | GGB | 172315.09 | GGB | 138662.29 | GGB | 0 | 0 | 2498 | 3600 | 2482.42 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 57774.13 | GGB | 57774.87 | 2482.42 | 2482.42 |  |  |  | 1 | 1 |  |  |  |  | 138662.29 | 2482.42 | 138662.29 | 2482.42 | 8.761 | [5 empty] | 95.6161
09.11.2007 13:00 | 3600 | 2 | 758.29 | GGB | 766.3 | 772.125 | 767.766 | 257.91 | GGB | 10891.6 | GGB | 9.86 | GGB | 994.78 | GGB | 61.07 | GGB | 170122.12 | GGB | 136522.82 | GGB | 0 | 0 | 2516 | 3600 | 2500.3 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 57814.31 | GGB | 57815.05 | 2500.3 | 2500.3 |  |  |  | 1 | 1 |  |  |  |  | 136522.82 | 2500.3 | 136522.82 | 2500.3 | 8.4955 | [5 empty] | 94.8189
09.11.2007 14:00 | 3600 | 2 | 758.21 | GGB | 766.667 | 772.125 | 768.864 | 257.4 | GGB | 10884.7 | GGB | 9.86 | GGB | 994.39 | GGB | 61.53 | GGB | 169537.84 | GGB | 135812.99 | GGB | 0 | 0 | 2518 | 3600 | 2502.85 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 57853.54 | GGB | 57854.28 | 2502.85 | 2502.85 |  |  |  | 1 | 1 |  |  |  |  | 135812.99 | 2502.85 | 135812.99 | 2502.85 | 8.6648 | [5 empty] | 94.4221
09.11.2007 15:00 | 3600 | 2 | 758.08 | GGB | 766.3 | 772.125 | 767.766 | 257.04 | GGB | 10873.5 | GGB | 9.85 | GGB | 994.08 | GGB | 61.67 | GGB | 169187.93 | GGB | 135434.51 | GGB | 0 | 0 | 2519 | 3600 | 2503.28 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 57893.59 | GGB | 57894.33 | 2503.28 | 2503.28 |  |  |  | 1 | 1 |  |  |  |  | 135434.51 | 2503.28 | 135434.51 | 2503.28 | 8.4652 | [5 empty] | 94.1751
09.11.2007 16:00 | 3600 | 2 | 758.12 | GGB | 766.3 | 772.125 | 768.864 | 257.38 | GGB | 10875.9 | GGB | 9.85 | GGB | 993.78 | GGB | 61.57 | GGB | 169564.25 | GGB | 135736.28 | GGB | 0 | 0 | 2526 | 3600 | 2510.31 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 57932.87 | GGB | 57933.62 | 2510.31 | 2510.31 |  |  |  | 1 | 1 |  |  |  |  | 135736.28 | 2510.31 | 135736.28 | 2510.31 | 8.6724 | [5 empty] | 94.65
09.11.2007 17:00 | 3600 | 2 | 758.25 | GGB | 768.864 | 774 | 771.429 | 257.9 | GGB | 10888.5 | GGB | 9.86 | GGB | 993.72 | GGB | 61.41 | GGB | 169850.34 | GGB | 136019.47 | GGB | 0 | 0 | 2535 | 3600 | 2520.2 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 57972.65 | GGB | 57973.4 | 2520.2 | 2520.2 |  |  |  | 1 | 1 |  |  |  |  | 136019.47 | 2520.2 | 136019.47 | 2520.2 | 8.6173 | [5 empty] | 95.2212
09.11.2007 18:00 | 3600 | 2 | 758.12 | GGB | 766.667 | 772.992 | 768.864 | 258.59 | GGB | 10863.2 | GGB | 9.85 | GGB | 993.68 | GGB | 61.75 | GGB | 169581.85 | GGB | 135662.52 | GGB | 0 | 0 | 2533 | 3600 | 2517.54 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 58012.15 | GGB | 58012.9 | 2517.54 | 2517.54 |  |  |  | 1 | 1 |  |  |  |  | 135662.52 | 2517.54 | 135662.52 | 2517.54 | 8.6465 | [5 empty] | 94.8711
09.11.2007 19:00 | 3600 | 2 | 757.44 | GGB | 763.004 | 768.773 | 765.201 | 258.91 | GGB | 10836.8 | GGB | 9.84 | GGB | 993.5 | GGB | 61.91 | GGB | 169515.83 | GGB | 135520.37 | GGB | 0 | 0 | 2561 | 3600 | 2546.07 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 58051.22 | GGB | 58051.97 | 2546.07 | 2546.07 |  |  |  | 0 | 1 | [14 empty] | 95.8457
09.11.2007 20:00 | 3600 | 2 | 758.51 | GGB | 765.201 | 771.984 | 767.766 | 258.54 | GGB | 10890.4 | GGB | 9.87 | GGB | 992.91 | GGB | 61.94 | GGB | 169731.5 | GGB | 135601.52 | GGB | 0 | 0 | 2529 | 3600 | 2514.07 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 58091.2 | GGB | 58091.95 | 2514.07 | 2514.07 |  |  |  | 1 | 1 |  |  |  |  | 135601.52 | 2514.07 | 135601.52 | 2514.07 | 8.5271 | [5 empty] | 94.6977
09.11.2007 21:00 | 3600 | 2 | 758.11 | GGB | 767.766 | 772.992 | 768.864 | 259.36 | GGB | 10865 | GGB | 9.86 | GGB | 992.65 | GGB | 61.13 | GGB | 171824.34 | GGB | 137567.91 | GGB | 0 | 0 | 2525 | 3600 | 2510.19 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 58130.68 | GGB | 58131.43 | 2510.19 | 2510.19 |  |  |  | 1 | 1 |  |  |  |  | 137567.91 | 2510.19 | 137567.91 | 2510.19 | 8.7467 | [5 empty] | 95.9227
09.11.2007 22:00 | 3600 | 2 | 758.05 | GGB | 766.3 | 771.867 | 767.766 | 257.88 | GGB | 10886.8 | GGB | 9.86 | GGB | 992.07 | GGB | 61.42 | GGB | 170013.19 | GGB | 135920.45 | GGB | 0 | 0 | 2536 | 3600 | 2520.86 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 58170.62 | GGB | 58171.37 | 2520.86 | 2520.86 |  |  |  | 1 | 1 |  |  |  |  | 135920.45 | 2520.86 | 135920.45 | 2520.86 | 8.5788 | [5 empty] | 95.1768
09.11.2007 23:00 | 3600 | 2 | 757.95 | GGB | 767.766 | 774.281 | 769.963 | 258.15 | GGB | 10879.4 | GGB | 9.86 | GGB | 991.6 | GGB | 61.1 | GGB | 170765.82 | GGB | 136590.09 | GGB | 0 | 0 | 2535 | 3600 | 2519.99 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 58209.07 | GGB | 58209.82 | 2519.99 | 2519.99 |  |  |  | 1 | 1 |  |  |  |  | 136590.09 | 2519.99 | 136590.09 | 2519.99 | 8.952 | [5 empty] | 95.6127
09.11.2007 24:00 | 3600 | 2 | 758.01 | GGB | 765.201 | 771.516 | 766.667 | 257.6 | GGB | 10866.8 | GGB | 9.85 | GGB | 991.14 | GGB | 61.15 | GGB | 169861.34 | GGB | 135780.54 | GGB | 0 | 0 | 2523 | 3600 | 2508.12 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 58250.06 | GGB | 58250.81 | 2508.12 | 2508.12 |  |  |  | 1 | 1 |  |  |  |  | 135780.54 | 2508.12 | 135780.54 | 2508.12 | 8.3082 | [5 empty] | 94.5983
10.11.2007 01:00 | 3600 | 2 | 757.67 | GGB | 765.201 | 770.531 | 766.667 | 258.38 | GGB | 10882.7 | GGB | 9.85 | GGB | 991.25 | GGB | 60.81 | GGB | 170468.73 | GGB | 136418.7 | GGB | 0 | 0 | 2552 | 3600 | 2537.09 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 58288.5 | GGB | 58289.26 | 2537.09 | 2537.09 |  |  |  | 1 | 1 |  |  |  |  | 136418.7 | 2537.09 | 136418.7 | 2537.09 | 9.0015 | [5 empty] | 96.1407
10.11.2007 02:00 | 3600 | 2 | 757.47 | GGB | 766.3 | 771.539 | 768.864 | 259.99 | GGB | 10894 | GGB | 9.85 | GGB | 991.27 | GGB | 61.03 | GGB | 171817.74 | GGB | 137412.43 | GGB | 0 | 0 | 2566 | 3600 | 2550.27 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 58329 | GGB | 58329.75 | 2550.27 | 2550.27 |  |  |  | 1 | 1 |  |  |  |  | 137412.43 | 2550.27 | 137412.43 | 2550.27 | 8.6549 | [5 empty] | 97.3441
10.11.2007 03:00 | 3600 | 2 | 758.03 | GGB | 766.3 | 772.875 | 768.864 | 259.33 | GGB | 10931.3 | GGB | 9.86 | GGB | 991 | GGB | 61.23 | GGB | 171153.14 | GGB | 136760.56 | GGB | 0 | 0 | 2550 | 3600 | 2535.14 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 58368.15 | GGB | 58368.9 | 2535.14 | 2535.14 |  |  |  | 1 | 1 |  |  |  |  | 136760.56 | 2535.14 | 136760.56 | 2535.14 | 8.8559 | [5 empty] | 96.3075
10.11.2007 04:00 | 3600 | 2 | 757.67 | GGB | 765.201 | 772.031 | 767.766 | 259.16 | GGB | 10922.9 | GGB | 9.85 | GGB | 990.67 | GGB | 61.18 | GGB | 171586.67 | GGB | 137081.99 | GGB | 0 | 0 | 2564 | 3600 | 2548.79 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 58407.84 | GGB | 58408.59 | 2548.79 | 2548.79 |  |  |  | 1 | 1 |  |  |  |  | 137081.99 | 2548.79 | 137081.99 | 2548.79 | 8.8031 | [5 empty] | 97.0537
10.11.2007 05:00 | 3600 | 2 | 757.65 | GGB | 766.3 | 771.984 | 767.766 | 259.12 | GGB | 10940.8 | GGB | 9.86 | GGB | 990.45 | GGB | 60.91 | GGB | 171911.27 | GGB | 137422.08 | GGB | 0 | 0 | 2569 | 3600 | 2553.57 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 58448.04 | GGB | 58448.8 | 2553.57 | 2553.57 |  |  |  | 1 | 1 |  |  |  |  | 137422.08 | 2553.57 | 137422.08 | 2553.57 | 8.7271 | [5 empty] | 97.4769
10.11.2007 06:00 | 3600 | 2 | 757.54 | GGB | 766.3 | 771.891 | 768.864 | 260.16 | GGB | 10913 | GGB | 9.85 | GGB | 990.07 | GGB | 60.38 | GGB | 173681.71 | GGB | 139003.9 | GGB | 0 | 0 | 2556 | 3600 | 2540.85 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 58487.13 | GGB | 58487.89 | 2540.85 | 2540.85 |  |  |  | 1 | 1 |  |  |  |  | 139003.9 | 2540.85 | 139003.9 | 2540.85 | 9.0353 | [5 empty] | 98.1078
10.11.2007 07:00 | 3600 | 2 | 757.98 | GGB | 766.3 | 771.75 | 767.766 | 260.26 | GGB | 10907.8 | GGB | 9.86 | GGB | 990.08 | GGB | 60.14 | GGB | 174117.45 | GGB | 139456.71 | GGB | 0 | 0 | 2531 | 3600 | 2515.68 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 58527.35 | GGB | 58528.11 | 2515.68 | 2515.68 |  |  |  | 1 | 1 |  |  |  |  | 139456.71 | 2515.68 | 139456.71 | 2515.68 | 8.7227 | [5 empty] | 97.4523
10.11.2007 08:00 | 3600 | 2 | 758 | GGB | 766.3 | 771.844 | 767.766 | 259.2 | GGB | 10928.9 | GGB | 9.86 | GGB | 990.56 | GGB | 60.39 | GGB | 172364.61 | GGB | 138014.55 | GGB | 0 | 0 | 2541 | 3600 | 2525.28 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 58566.4 | GGB | 58567.16 | 2525.28 | 2525.28 |  |  |  | 1 | 1 |  |  |  |  | 138014.55 | 2525.28 | 138014.55 | 2525.28 | 8.9251 | [5 empty] | 96.8126
10.11.2007 09:00 | 3600 | 2 | 757.9 | GGB | 765.201 | 771.984 | 767.766 | 258.8 | GGB | 10930.1 | GGB | 9.85 | GGB | 991.07 | GGB | 60.78 | GGB | 171431.52 | GGB | 137179.8 | GGB | 0 | 0 | 2548 | 3600 | 2532.9 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 58606.65 | GGB | 58607.41 | 2532.9 | 2532.9 |  |  |  | 1 | 1 |  |  |  |  | 137179.8 | 2532.9 | 137179.8 | 2532.9 | 8.6326 | [5 empty] | 96.5174
10.11.2007 10:00 | 3600 | 2 | 757.64 | GGB | 766.3 | 771.984 | 767.766 | 258.89 | GGB | 10938.5 | GGB | 9.85 | GGB | 991.17 | GGB | 60.62 | GGB | 171839.75 | GGB | 137585.34 | GGB | 0 | 0 | 2559 | 3600 | 2543.97 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 58646.23 | GGB | 58646.99 | 2543.97 | 2543.97 |  |  |  | 1 | 1 |  |  |  |  | 137585.34 | 2543.97 | 137585.34 | 2543.97 | 8.8432 | [5 empty] | 97.2258
10.11.2007 11:00 | 3600 | 2 | 757.39 | GGB | 765.201 | 771 | 767.766 | 260.16 | GGB | 10919.4 | GGB | 9.85 | GGB | 991.15 | GGB | 59.95 | GGB | 173726.83 | GGB | 139373.49 | GGB | 0 | 0 | 2539 | 3600 | 2523.45 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 58685.98 | GGB | 58686.74 | 2523.45 | 2523.45 |  |  |  | 1 | 1 |  |  |  |  | 139373.49 | 2523.45 | 139373.49 | 2523.45 | 8.8478 | [5 empty] | 97.695
10.11.2007 12:00 | 3600 | 2 | 757.59 | GGB | 765.201 | 771.07 | 767.766 | 259.84 | GGB | 10904.8 | GGB | 9.86 | GGB | 990.63 | GGB | 59.61 | GGB | 173790.65 | GGB | 139495.09 | GGB | 0 | 0 | 2513 | 3600 | 2498.23 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 58725.77 | GGB | 58726.53 | 2498.23 | 2498.23 |  |  |  | 1 | 1 |  |  |  |  | 139495.09 | 2498.23 | 139495.09 | 2498.23 | 8.7583 | [5 empty] | 96.803
10.11.2007 13:00 | 3600 | 2 | 757.54 | GGB | 765.201 | 771.07 | 767.766 | 259.95 | GGB | 10904.2 | GGB | 9.85 | GGB | 990.65 | GGB | 59.59 | GGB | 173922.69 | GGB | 139609.77 | GGB | 0 | 0 | 2515 | 3600 | 2499.61 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 58765.22 | GGB | 58765.98 | 2499.61 | 2499.61 |  |  |  | 1 | 1 |  |  |  |  | 139609.77 | 2499.61 | 139609.77 | 2499.61 | 8.8459 | [5 empty] | 96.9361
10.11.2007 14:00 | 3600 | 2 | 757.55 | GGB | 765.201 | 771.07 | 767.766 | 258.87 | GGB | 10944 | GGB | 9.86 | GGB | 991.02 | GGB | 60.36 | GGB | 171821.04 | GGB | 137655.97 | GGB | 0 | 0 | 2546 | 3600 | 2530.73 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 58804.84 | GGB | 58805.6 | 2530.73 | 2530.73 |  |  |  | 1 | 1 |  |  |  |  | 137655.97 | 2530.73 | 137655.97 | 2530.73 | 8.7928 | [5 empty] | 96.7695
10.11.2007 15:00 | 3600 | 2 | 757.46 | GGB | 765.201 | 771.07 | 767.766 | 258.95 | GGB | 10944.3 | GGB | 9.86 | GGB | 991.17 | GGB | 60.47 | GGB | 171992.69 | GGB | 137768.62 | GGB | 0 | 0 | 2553 | 3600 | 2537.99 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 58844.6 | GGB | 58845.37 | 2537.99 | 2537.99 |  |  |  | 1 | 1 |  |  |  |  | 137768.62 | 2537.99 | 137768.62 | 2537.99 | 8.7919 | [5 empty] | 97.1265
10.11.2007 16:00 | 3600 | 2 | 757.38 | GGB | 765.201 | 771.07 | 767.766 | 259.13 | GGB | 10950.3 | GGB | 9.85 | GGB | 991.17 | GGB | 60.48 | GGB | 172008.1 | GGB | 137775.82 | GGB | 0 | 0 | 2562 | 3600 | 2546.36 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 58884.54 | GGB | 58885.31 | 2546.36 | 2546.36 |  |  |  | 1 | 1 |  |  |  |  | 137775.82 | 2546.36 | 137775.82 | 2546.36 | 8.7838 | [5 empty] | 97.4519
10.11.2007 17:00 | 3600 | 2 | 757.39 | GGB | 765.201 | 771.07 | 767.766 | 259.03 | GGB | 10950.2 | GGB | 9.85 | GGB | 991.14 | GGB | 60.21 | GGB | 172155.54 | GGB | 138003.36 | GGB | 0 | 0 | 2562 | 3600 | 2546.39 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 58924.26 | GGB | 58925.03 | 2546.39 | 2546.39 |  |  |  | 1 | 1 |  |  |  |  | 138003.36 | 2546.39 | 138003.36 | 2546.39 | 8.8472 | [5 empty] | 97.614
10.11.2007 18:00 | 3600 | 2 | 757.49 | GGB | 766.667 | 772.102 | 768.864 | 259.73 | GGB | 10950.9 | GGB | 9.86 | GGB | 991.12 | GGB | 59.74 | GGB | 173276.79 | GGB | 139094.95 | GGB | 0 | 0 | 2555 | 3600 | 2540.07 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 58964.38 | GGB | 58965.15 | 2540.07 | 2540.07 |  |  |  | 1 | 1 |  |  |  |  | 139094.95 | 2540.07 | 139094.95 | 2540.07 | 8.8064 | [5 empty] | 98.1419
10.11.2007 19:00 | 3600 | 2 | 757.4 | GGB | 765.201 | 770.086 | 767.766 | 259.32 | GGB | 10969.4 | GGB | 9.85 | GGB | 991.21 | GGB | 59.81 | GGB | 172792.64 | GGB | 138691.26 | GGB | 0 | 0 | 2572 | 3600 | 2556.47 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 59003.08 | GGB | 59003.85 | 2556.47 | 2556.47 |  |  |  | 1 | 1 |  |  |  |  | 138691.26 | 2556.47 | 138691.26 | 2556.47 | 9.1618 | [5 empty] | 98.4889
10.11.2007 20:00 | 3600 | 2 | 757.14 | GGB | 766.3 | 772.125 | 767.766 | 261.18 | GGB | 10967.8 | GGB | 9.85 | GGB | 991.47 | GGB | 59.35 | GGB | 174881.08 | GGB | 140600.72 | GGB | 0 | 0 | 2581 | 3600 | 2565.49 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 59044.18 | GGB | 59044.96 | 2565.49 | 2565.49 |  |  |  | 1 | 1 |  |  |  |  | 140600.72 | 2565.49 | 140600.72 | 2565.49 | 8.7743 | [5 empty] | 100.1972
10.11.2007 21:00 | 3600 | 2 | 757.48 | GGB | 765.201 | 771.094 | 766.667 | 261.65 | GGB | 10980.6 | GGB | 9.85 | GGB | 991.29 | GGB | 58.77 | GGB | 175973.72 | GGB | 141699.41 | GGB | 0 | 0 | 2567 | 3600 | 2551.4 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 59083.24 | GGB | 59084.02 | 2551.4 | 2551.4 |  |  |  | 1 | 1 |  |  |  |  | 141699.41 | 2551.4 | 141699.41 | 2551.4 | 9.2558 | [5 empty] | 100.4255
10.11.2007 22:00 | 3600 | 2 | 757.15 | GGB | 765.201 | 771.094 | 767.766 | 260.75 | GGB | 11027.2 | GGB | 9.86 | GGB | 990.78 | GGB | 59.28 | GGB | 174591.69 | GGB | 140295.5 | GGB | 0 | 0 | 2607 | 3600 | 2591.51 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 59123.54 | GGB | 59124.32 | 2591.51 | 2591.51 |  |  |  | 1 | 1 |  |  |  |  | 140295.5 | 2591.51 | 140295.5 | 2591.51 | 9.0218 | [5 empty] | 100.9937
10.11.2007 23:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 771.094 | 766.667 | 260.47 | GGB | 11033.3 | GGB | 9.86 | GGB | 990.55 | GGB | 59.43 | GGB | 174403.53 | GGB | 140051.72 | GGB | 0 | 0 | 2621 | 3600 | 2605.62 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 59163.82 | GGB | 59164.59 | 2605.62 | 2605.62 |  |  |  | 1 | 1 |  |  |  |  | 140051.72 | 2605.62 | 140051.72 | 2605.62 | 9.0619 | [5 empty] | 101.3671
10.11.2007 24:00 | 3600 | 2 | 756.64 | GGB | 765.201 | 771.047 | 767.766 | 260.9 | GGB | 11059.5 | GGB | 9.85 | GGB | 989.66 | GGB | 58.81 | GGB | 175080.24 | GGB | 140729.07 | GGB | 0 | 0 | 2659 | 3600 | 2643.67 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 59203.17 | GGB | 59203.94 | 2643.67 | 2643.67 |  |  |  | 1 | 1 |  |  |  |  | 140729.07 | 2643.67 | 140729.07 | 2643.67 | 9.4547 | [5 empty] | 103.3448
11.11.2007 01:00 | 3600 | 2 | 756.54 | GGB | 764.102 | 769.969 | 765.934 | 260.11 | GGB | 11071.8 | GGB | 9.85 | GGB | 988.73 | GGB | 58.37 | GGB | 175380.63 | GGB | 141025.83 | GGB | 0 | 0 | 2664 | 3600 | 2648.32 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 59244.21 | GGB | 59244.99 | 2648.32 | 2648.32 |  |  |  | 1 | 1 |  |  |  |  | 141025.83 | 2648.32 | 141025.83 | 2648.32 | 9.0982 | [5 empty] | 103.7449
11.11.2007 02:00 | 3600 | 2 | 756.57 | GGB | 764.102 | 769.969 | 765.934 | 260.88 | GGB | 11073.3 | GGB | 9.85 | GGB | 989 | GGB | 58.27 | GGB | 175419.15 | GGB | 141139.53 | GGB | 0 | 0 | 2675 | 3600 | 2660.02 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 59284.58 | GGB | 59285.36 | 2660.02 | 2660.02 |  |  |  | 1 | 1 |  |  |  |  | 141139.53 | 2660.02 | 141139.53 | 2660.02 | 9.2998 | [5 empty] | 104.2872
11.11.2007 03:00 | 3600 | 2 | 756.51 | GGB | 764.102 | 769.969 | 765.934 | 261.14 | GGB | 11077.7 | GGB | 9.85 | GGB | 989.77 | GGB | 58.36 | GGB | 175405.94 | GGB | 141200.55 | GGB | 0 | 0 | 2681 | 3600 | 2665.95 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 59325.16 | GGB | 59325.93 | 2665.95 | 2665.95 |  |  |  | 1 | 1 |  |  |  |  | 141200.55 | 2665.95 | 141200.55 | 2665.95 | 9.2786 | [5 empty] | 104.5649
11.11.2007 04:00 | 3600 | 2 | 756.56 | GGB | 765.201 | 769.969 | 767.033 | 261.53 | GGB | 11090.3 | GGB | 9.85 | GGB | 990.52 | GGB | 58.26 | GGB | 175622.71 | GGB | 141523.36 | GGB | 0 | 0 | 2689 | 3600 | 2673.49 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 59364.92 | GGB | 59365.69 | 2673.49 | 2673.49 |  |  |  | 1 | 1 |  |  |  |  | 141523.36 | 2673.49 | 141523.36 | 2673.49 | 9.5161 | [5 empty] | 105.1004 | 2670.4284
11.11.2007 05:00 | 3600 | 2 | 756.79 | GGB | 764.102 | 769.922 | 765.934 | 261.4 | GGB | 11090 | GGB | 9.86 | GGB | 991.15 | GGB | 58.56 | GGB | 175548.99 | GGB | 141427.24 | GGB | 0 | 0 | 2675 | 3600 | 2659.47 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 59405.94 | GGB | 59406.72 | 2659.47 | 2659.47 |  |  |  | 1 | 1 |  |  |  |  | 141427.24 | 2659.47 | 141427.24 | 2659.47 | 9.167 | [5 empty] | 104.4782
11.11.2007 06:00 | 3600 | 2 | 756.71 | GGB | 764.102 | 768.938 | 765.934 | 261.71 | GGB | 11075.6 | GGB | 9.85 | GGB | 991.53 | GGB | 58.57 | GGB | 175923.1 | GGB | 141778.05 | GGB | 0 | 0 | 2676 | 3600 | 2660.41 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 59445.67 | GGB | 59446.45 | 2660.41 | 2660.41 |  |  |  | 1 | 1 |  |  |  |  | 141778.05 | 2660.41 | 141778.05 | 2660.41 | 9.4938 | [5 empty] | 104.7744
11.11.2007 07:00 | 3600 | 2 | 756.55 | GGB | 765.201 | 769.945 | 767.033 | 263.5 | GGB | 11049.4 | GGB | 9.85 | GGB | 992.83 | GGB | 58.11 | GGB | 177846.49 | GGB | 143715.85 | GGB | 0 | 0 | 2661 | 3600 | 2646 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 59486.06 | GGB | 59486.84 | 2646 | 2646 |  |  |  | 1 | 1 |  |  |  |  | 143715.85 | 2646 | 143715.85 | 2646 | 9.415 | [5 empty] | 105.6311 | 2629.6891
11.11.2007 08:00 | 3600 | 2 | 757.13 | GGB | 765.201 | 769.969 | 767.033 | 262.32 | GGB | 11084.6 | GGB | 9.86 | GGB | 993.41 | GGB | 58.72 | GGB | 175979.22 | GGB | 142028.68 | GGB | 0 | 0 | 2651 | 3600 | 2635.79 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 59526.26 | GGB | 59527.04 | 2635.79 | 2635.79 |  |  |  | 1 | 1 |  |  |  |  | 142028.68 | 2635.79 | 142028.68 | 2635.79 | 9.3124 | [5 empty] | 103.9883
11.11.2007 09:00 | 3600 | 2 | 756.82 | GGB | 765.201 | 769.969 | 767.033 | 262.28 | GGB | 11099.3 | GGB | 9.85 | GGB | 994.06 | GGB | 58.95 | GGB | 175833.97 | GGB | 141904.61 | GGB | 0 | 0 | 2678 | 3600 | 2663.07 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 59566.24 | GGB | 59567.02 | 2663.07 | 2663.07 |  |  |  | 1 | 1 |  |  |  |  | 141904.61 | 2663.07 | 141904.61 | 2663.07 | 9.4523 | [5 empty] | 104.9728
11.11.2007 10:00 | 3600 | 2 | 756.79 | GGB | 765.201 | 769.969 | 767.033 | 262.74 | GGB | 11106.1 | GGB | 9.85 | GGB | 994.69 | GGB | 58.93 | GGB | 176259.8 | GGB | 142348.72 | GGB | 0 | 0 | 2693 | 3600 | 2677.28 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 59607.23 | GGB | 59608.01 | 2677.28 | 2677.28 |  |  |  | 1 | 1 |  |  |  |  | 142348.72 | 2677.28 | 142348.72 | 2677.28 | 9.2976 | [5 empty] | 105.8632 | 2654.9448
11.11.2007 11:00 | 3600 | 2 | 757.06 | GGB | 765.201 | 771.164 | 768.132 | 262.71 | GGB | 11106 | GGB | 9.86 | GGB | 995.56 | GGB | 59.04 | GGB | 175968.21 | GGB | 142190.9 | GGB | 0 | 0 | 2676 | 3600 | 2661.01 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 59646.54 | GGB | 59647.32 | 2661.01 | 2661.01 |  |  |  | 1 | 1 |  |  |  |  | 142190.9 | 2661.01 | 142190.9 | 2661.01 | 9.6253 | [5 empty] | 105.1032 | 2657.8916
11.11.2007 12:00 | 3600 | 2 | 756.85 | GGB | 765.201 | 770.367 | 767.033 | 262.52 | GGB | 11100.4 | GGB | 9.86 | GGB | 995.44 | GGB | 59.3 | GGB | 175705.23 | GGB | 141847.93 | GGB | 0 | 0 | 2665 | 3600 | 2649.45 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 59688.05 | GGB | 59688.83 | 2649.45 | 2649.45 |  |  |  | 1 | 1 |  |  |  |  | 141847.93 | 2649.45 | 141847.93 | 2649.45 | 9.0537 | [5 empty] | 104.3942
11.11.2007 13:00 | 3600 | 2 | 756.52 | GGB | 766.3 | 771.492 | 768.132 | 263.4 | GGB | 11064.4 | GGB | 9.85 | GGB | 995.74 | GGB | 58.96 | GGB | 177023.44 | GGB | 143104.2 | GGB | 0 | 0 | 2658 | 3600 | 2642.3 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 59727.5 | GGB | 59728.28 | 2642.3 | 2642.3 |  |  |  | 1 | 1 |  |  |  |  | 143104.2 | 2642.3 | 143104.2 | 2642.3 | 9.5849 | [5 empty] | 105.0345 | 2640.9288
11.11.2007 14:00 | 3600 | 2 | 757.63 | GGB | 767.766 | 772.172 | 769.597 | 263.38 | GGB | 11068.4 | GGB | 9.87 | GGB | 995.75 | GGB | 58.76 | GGB | 177097.16 | GGB | 143250.92 | GGB | 0 | 0 | 2607 | 3600 | 2591.63 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 59768.01 | GGB | 59768.79 | 2591.63 | 2591.63 |  |  |  | 1 | 1 |  |  |  |  | 143250.92 | 2591.63 | 143250.92 | 2591.63 | 9.1645 | [5 empty] | 103.1259
11.11.2007 15:00 | 3600 | 2 | 756.99 | GGB | 766.3 | 771.07 | 768.132 | 262.31 | GGB | 11081.6 | GGB | 9.85 | GGB | 996.25 | GGB | 59.21 | GGB | 175360.83 | GGB | 141722.09 | GGB | 0 | 0 | 2652 | 3600 | 2636.67 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 59808.4 | GGB | 59809.19 | 2636.67 | 2636.67 |  |  |  | 1 | 1 |  |  |  |  | 141722.09 | 2636.67 | 141722.09 | 2636.67 | 9.2494 | [5 empty] | 103.7984
11.11.2007 16:00 | 3600 | 2 | 756.61 | GGB | 764.102 | 770.039 | 765.201 | 263.86 | GGB | 11049.2 | GGB | 9.84 | GGB | 996.53 | GGB | 58.89 | GGB | 177558.2 | GGB | 143677.08 | GGB | 0 | 0 | 2647 | 3600 | 2631.53 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 59848.71 | GGB | 59849.5 | 2631.53 | 2631.53 |  |  |  | 1 | 1 |  |  |  |  | 143677.08 | 2631.53 | 143677.08 | 2631.53 | 9.3796 | [5 empty] | 105.0252 | 2630.3987
11.11.2007 17:00 | 3600 | 2 | 757.14 | GGB | 766.3 | 771.164 | 768.864 | 263.25 | GGB | 11107 | GGB | 9.86 | GGB | 996.59 | GGB | 59.08 | GGB | 176356.63 | GGB | 142635.6 | GGB | 0 | 0 | 2651 | 3600 | 2635.7 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 59889.31 | GGB | 59890.1 | 2635.7 | 2635.7 |  |  |  | 1 | 1 |  |  |  |  | 142635.6 | 2635.7 | 142635.6 | 2635.7 | 9.2597 | [5 empty] | 104.4291
11.11.2007 18:00 | 3600 | 2 | 756.57 | GGB | 766.3 | 771.234 | 767.766 | 264.73 | GGB | 11086.5 | GGB | 9.84 | GGB | 996.97 | GGB | 58.74 | GGB | 178329.54 | GGB | 144430.94 | GGB | 0 | 0 | 2672 | 3600 | 2656.34 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 59929.14 | GGB | 59929.93 | 2656.34 | 2656.34 |  |  |  | 1 | 1 |  |  |  |  | 144430.94 | 2656.34 | 144430.94 | 2656.34 | 9.6324 | [5 empty] | 106.5716 | 2616.6693
11.11.2007 19:00 | 3600 | 2 | 756.94 | GGB | 765.201 | 771.305 | 767.766 | 263.75 | GGB | 11115.2 | GGB | 9.86 | GGB | 997.15 | GGB | 59.2 | GGB | 177033.34 | GGB | 143207.04 | GGB | 0 | 0 | 2665 | 3600 | 2649.24 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 59970.06 | GGB | 59970.86 | 2649.24 | 2649.24 |  |  |  | 1 | 1 |  |  |  |  | 143207.04 | 2649.24 | 143207.04 | 2649.24 | 9.2692 | [5 empty] | 105.3861 | 2639.0323
11.11.2007 20:00 | 3600 | 2 | 757.04 | GGB | 766.667 | 771.656 | 767.766 | 264.66 | GGB | 11143.2 | GGB | 9.86 | GGB | 996.97 | GGB | 58.52 | GGB | 179444.18 | GGB | 145431.8 | GGB | 0 | 0 | 2668 | 3600 | 2652.61 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 60009.83 | GGB | 60010.63 | 2652.61 | 2652.61 |  |  |  | 1 | 1 |  |  |  |  | 145431.8 | 2652.61 | 145431.8 | 2652.61 | 9.7001 | [5 empty] | 107.1594 | 2598.6614
11.11.2007 21:00 | 3600 | 2 | 756.63 | GGB | 765.201 | 770.813 | 766.667 | 264.11 | GGB | 11151.5 | GGB | 9.85 | GGB | 996.85 | GGB | 58.55 | GGB | 178229.41 | GGB | 144417.01 | GGB | 0 | 0 | 2697 | 3600 | 2681.64 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 60051.07 | GGB | 60051.87 | 2681.64 | 2681.64 |  |  |  | 1 | 1 |  |  |  |  | 144417.01 | 2681.64 | 144417.01 | 2681.64 | 9.3907 | [5 empty] | 107.5762 | 2616.9216
11.11.2007 22:00 | 3600 | 2 | 756.52 | GGB | 766.3 | 772.125 | 768.864 | 264.35 | GGB | 11147 | GGB | 9.85 | GGB | 996.72 | GGB | 58.56 | GGB | 178689.35 | GGB | 144767.19 | GGB | 0 | 0 | 2712 | 3600 | 2696.51 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 60090.99 | GGB | 60091.79 | 2696.51 | 2696.51 |  |  |  | 1 | 1 |  |  |  |  | 144767.19 | 2696.51 | 144767.19 | 2696.51 | 9.7787 | [5 empty] | 108.435 | 2610.5915
11.11.2007 23:00 | 3600 | 2 | 756.73 | GGB | 766.3 | 771.047 | 768.132 | 264.83 | GGB | 11144.5 | GGB | 9.85 | GGB | 996.94 | GGB | 58.35 | GGB | 179143.79 | GGB | 145257.59 | GGB | 0 | 0 | 2691 | 3600 | 2675.62 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 60132.17 | GGB | 60132.97 | 2675.62 | 2675.62 |  |  |  | 1 | 1 |  |  |  |  | 145257.59 | 2675.62 | 145257.59 | 2675.62 | 9.4379 | [5 empty] | 107.9595 | 2601.778
11.11.2007 24:00 | 3600 | 2 | 757 | GGB | 766.3 | 771.328 | 768.132 | 265.21 | GGB | 11134.1 | GGB | 9.86 | GGB | 996.93 | GGB | 57.98 | GGB | 179500.3 | GGB | 145708.75 | GGB | 0 | 0 | 2675 | 3600 | 2659.91 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 60171.86 | GGB | 60172.66 | 2659.91 | 2659.91 |  |  |  | 1 | 1 |  |  |  |  | 145708.75 | 2659.91 | 145708.75 | 2659.91 | 9.765 | [5 empty] | 107.6589 | 2593.7221
12.11.2007 01:00 | 3600 | 2 | 757.37 | GGB | 765.201 | 771.281 | 768.132 | 263.25 | GGB | 11155.3 | GGB | 9.87 | GGB | 996.63 | GGB | 58.49 | GGB | 176838.58 | GGB | 143283.94 | GGB | 0 | 0 | 2672 | 3600 | 2656.59 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 60212.88 | GGB | 60213.68 | 2656.59 | 2656.59 |  |  |  | 1 | 1 |  |  |  |  | 143283.94 | 2656.59 | 143283.94 | 2656.59 | 9.2795 | [5 empty] | 105.7352 | 2637.6159
12.11.2007 02:00 | 3600 | 2 | 756.53 | GGB | 764.102 | 769.102 | 765.934 | 263.7 | GGB | 11105.7 | GGB | 9.84 | GGB | 996.82 | GGB | 58.24 | GGB | 177590.11 | GGB | 144028.74 | GGB | 0 | 0 | 2697 | 3600 | 2681.44 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 60253.22 | GGB | 60254.02 | 2681.44 | 2681.44 |  |  |  | 1 | 1 |  |  |  |  | 144028.74 | 2681.44 | 144028.74 | 2681.44 | 9.5737 | [5 empty] | 107.279 | 2623.9763
12.11.2007 03:00 | 3600 | 2 | 757.45 | GGB | 765.201 | 771.281 | 767.033 | 264.04 | GGB | 11132.6 | GGB | 9.87 | GGB | 996.98 | GGB | 57.97 | GGB | 177791.47 | GGB | 144330.02 | GGB | 0 | 0 | 2659 | 3600 | 2643.46 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 60293.64 | GGB | 60294.44 | 2643.46 | 2643.46 |  |  |  | 1 | 1 |  |  |  |  | 144330.02 | 2643.46 | 144330.02 | 2643.46 | 9.4392 | [5 empty] | 105.9807 | 2618.4989
12.11.2007 04:00 | 3600 | 2 | 756.72 | GGB | 764.102 | 770.344 | 767.033 | 263.46 | GGB | 11133.5 | GGB | 9.85 | GGB | 996.83 | GGB | 58.52 | GGB | 176839.68 | GGB | 143299.01 | GGB | 0 | 0 | 2704 | 3600 | 2688.95 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 60334.25 | GGB | 60335.05 | 2688.95 | 2688.95 |  |  |  | 1 | 1 |  |  |  |  | 143299.01 | 2688.95 | 143299.01 | 2688.95 | 9.4884 | [5 empty] | 107.0344 | 2637.3385
12.11.2007 05:00 | 3600 | 2 | 756.94 | GGB | 765.201 | 770.156 | 767.033 | 264.23 | GGB | 11133.5 | GGB | 9.86 | GGB | 997.27 | GGB | 58.23 | GGB | 178002.74 | GGB | 144430.42 | GGB | 0 | 0 | 2682 | 3600 | 2666.29 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 60374.17 | GGB | 60374.98 | 2666.29 | 2666.29 |  |  |  | 1 | 1 |  |  |  |  | 144430.42 | 2666.29 | 144430.42 | 2666.29 | 9.6442 | [5 empty] | 106.9704 | 2616.6787
12.11.2007 06:00 | 3600 | 2 | 757.06 | GGB | 766.667 | 772.547 | 768.498 | 263.97 | GGB | 11137.1 | GGB | 9.86 | GGB | 997.02 | GGB | 58.34 | GGB | 177713.35 | GGB | 144112.18 | GGB | 0 | 0 | 2680 | 3600 | 2664.44 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 60415.39 | GGB | 60416.2 | 2664.44 | 2664.44 |  |  |  | 1 | 1 |  |  |  |  | 144112.18 | 2664.44 | 144112.18 | 2664.44 | 9.3153 | [5 empty] | 106.6606 | 2622.457
12.11.2007 07:00 | 3600 | 2 | 756.68 | GGB | 765.201 | 771.305 | 768.132 | 264.18 | GGB | 11112.6 | GGB | 9.84 | GGB | 997.2 | GGB | 58.18 | GGB | 178258.02 | GGB | 144649.63 | GGB | 0 | 0 | 2689 | 3600 | 2673.59 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 60455.25 | GGB | 60456.06 | 2673.59 | 2673.59 |  |  |  | 1 | 1 |  |  |  |  | 144649.63 | 2673.59 | 144649.63 | 2673.59 | 9.7023 | [5 empty] | 107.4261 | 2612.7132
12.11.2007 08:00 | 3600 | 2 | 757.37 | GGB | 765.201 | 770.203 | 767.033 | 264.9 | GGB | 11131.1 | GGB | 9.85 | GGB | 997.42 | GGB | 57.96 | GGB | 179559.72 | GGB | 145836.02 | GGB | 0 | 0 | 2656 | 3600 | 2640.56 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 60495.87 | GGB | 60496.68 | 2640.56 | 2640.56 |  |  |  | 1 | 1 |  |  |  |  | 145836.02 | 2640.56 | 145836.02 | 2640.56 | 9.4803 | [5 empty] | 106.9691 | 2591.4585
12.11.2007 09:00 | 3600 | 2 | 757.68 | GGB | 765.201 | 771.305 | 767.033 | 263.4 | GGB | 11166 | GGB | 9.86 | GGB | 997.28 | GGB | 58.5 | GGB | 177295.22 | GGB | 143742.8 | GGB | 0 | 0 | 2669 | 3600 | 2653.72 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 60536.38 | GGB | 60537.19 | 2653.72 | 2653.72 |  |  |  | 1 | 1 |  |  |  |  | 143742.8 | 2653.72 | 143742.8 | 2653.72 | 9.4163 | [5 empty] | 105.9592 | 2629.196
12.11.2007 10:00 | 3600 | 2 | 757.11 | GGB | 764.102 | 770.133 | 765.934 | 263.93 | GGB | 11155.8 | GGB | 9.85 | GGB | 997.58 | GGB | 58.46 | GGB | 177838.79 | GGB | 144241 | GGB | 0 | 0 | 2688 | 3600 | 2672.25 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 60576.74 | GGB | 60577.55 | 2672.25 | 2672.25 |  |  |  | 1 | 1 |  |  |  |  | 144241 | 2672.25 | 144241 | 2672.25 | 9.5502 | [5 empty] | 107.0689 | 2620.1149
12.11.2007 11:00 | 3600 | 2 | 757.23 | GGB | 765.201 | 770.063 | 767.033 | 265.3 | GGB | 11143 | GGB | 9.85 | GGB | 998.33 | GGB | 57.69 | GGB | 179856.81 | GGB | 146328.52 | GGB | 0 | 0 | 2673 | 3600 | 2657.29 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 60617.8 | GGB | 60618.61 | 2657.29 | 2657.29 |  |  |  | 1 | 1 |  |  |  |  | 146328.52 | 2657.29 | 146328.52 | 2657.29 | 9.47 | [5 empty] | 108.0104 | 2582.7364
12.11.2007 12:00 | 3600 | 2 | 757.34 | GGB | 765.201 | 770.063 | 767.033 | 264.12 | GGB | 11187.5 | GGB | 9.86 | GGB | 998.28 | GGB | 58.21 | GGB | 178123.78 | GGB | 144686.35 | GGB | 0 | 0 | 2682 | 3600 | 2666.9 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 60657.58 | GGB | 60658.4 | 2666.9 | 2666.9 |  |  |  | 1 | 1 |  |  |  |  | 144686.35 | 2666.9 | 144686.35 | 2666.9 | 9.6975 | [5 empty] | 107.1845 | 2612.0501
12.11.2007 13:00 | 3600 | 2 | 757.32 | GGB | 765.201 | 771.211 | 767.033 | 263.59 | GGB | 11180.4 | GGB | 9.86 | GGB | 997.7 | GGB | 58.48 | GGB | 177389.85 | GGB | 143890.18 | GGB | 0 | 0 | 2689 | 3600 | 2673.61 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 60698.76 | GGB | 60699.58 | 2673.61 | 2673.61 |  |  |  | 1 | 1 |  |  |  |  | 143890.18 | 2673.61 | 143890.18 | 2673.61 | 9.3421 | [5 empty] | 106.8628 | 2626.5031
12.11.2007 14:00 | 3600 | 2 | 757.16 | GGB | 765.201 | 770.156 | 767.033 | 263.29 | GGB | 11159.2 | GGB | 9.85 | GGB | 997.34 | GGB | 58.8 | GGB | 176851.79 | GGB | 143262.38 | GGB | 0 | 0 | 2690 | 3600 | 2674.34 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 60739.12 | GGB | 60739.95 | 2674.34 | 2674.34 |  |  |  | 1 | 1 |  |  |  |  | 143262.38 | 2674.34 | 143262.38 | 2674.34 | 9.4905 | [5 empty] | 106.4256 | 2638.0129
12.11.2007 15:00 | 3600 | 2 | 757.16 | GGB | 765.201 | 771.047 | 767.033 | 263.49 | GGB | 11166.1 | GGB | 9.85 | GGB | 997.19 | GGB | 58.84 | GGB | 177178.59 | GGB | 143485.3 | GGB | 0 | 0 | 2694 | 3600 | 2678.69 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 60779.76 | GGB | 60780.59 | 2678.69 | 2678.69 |  |  |  | 1 | 1 |  |  |  |  | 143485.3 | 2678.69 | 143485.3 | 2678.69 | 9.4575 | [5 empty] | 106.7646 | 2633.9144
12.11.2007 16:00 | 3600 | 2 | 756.87 | GGB | 765.201 | 769.969 | 767.033 | 263.78 | GGB | 11171.8 | GGB | 9.85 | GGB | 997.06 | GGB | 58.78 | GGB | 177528.49 | GGB | 143778.45 | GGB | 0 | 0 | 2709 | 3600 | 2693.61 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 60820.42 | GGB | 60821.25 | 2693.61 | 2693.61 |  |  |  | 1 | 1 |  |  |  |  | 143778.45 | 2693.61 | 143778.45 | 2693.61 | 9.5249 | [5 empty] | 107.5786 | 2628.5441
12.11.2007 17:00 | 3600 | 2 | 757.21 | GGB | 765.201 | 771.211 | 767.033 | 263.72 | GGB | 11184 | GGB | 9.86 | GGB | 996.98 | GGB | 58.8 | GGB | 177500.98 | GGB | 143734.76 | GGB | 0 | 0 | 2695 | 3600 | 2679.22 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 60860.71 | GGB | 60861.53 | 2679.22 | 2679.22 |  |  |  | 1 | 1 |  |  |  |  | 143734.76 | 2679.22 | 143734.76 | 2679.22 | 9.5605 | [5 empty] | 106.9714 | 2629.3431
12.11.2007 18:00 | 3600 | 2 | 757.07 | GGB | 764.102 | 769.969 | 767.033 | 263.69 | GGB | 11178.7 | GGB | 9.85 | GGB | 996.77 | GGB | 58.71 | GGB | 177605.52 | GGB | 143831.18 | GGB | 0 | 0 | 2705 | 3600 | 2689.11 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 60901.59 | GGB | 60902.41 | 2689.11 | 2689.11 |  |  |  | 1 | 1 |  |  |  |  | 143831.18 | 2689.11 | 143831.18 | 2689.11 | 9.4613 | [5 empty] | 107.4383 | 2627.5805
12.11.2007 19:00 | 3600 | 2 | 757.12 | GGB | 765.201 | 769.922 | 767.033 | 263.81 | GGB | 11184.1 | GGB | 9.86 | GGB | 997.15 | GGB | 58.78 | GGB | 177711.15 | GGB | 143938.99 | GGB | 0 | 0 | 2710 | 3600 | 2694.19 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 60941.93 | GGB | 60942.76 | 2694.19 | 2694.19 |  |  |  | 1 | 1 |  |  |  |  | 143938.99 | 2694.19 | 143938.99 | 2694.19 | 9.6109 | [5 empty] | 107.7219 | 2625.6124
12.11.2007 20:00 | 3600 | 2 | 757.05 | GGB | 764.102 | 769.969 | 767.033 | 264.33 | GGB | 11165.3 | GGB | 9.85 | GGB | 996.95 | GGB | 58.33 | GGB | 178527.6 | GGB | 144768.02 | GGB | 0 | 0 | 2704 | 3600 | 2688.45 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 60983.2 | GGB | 60984.03 | 2688.45 | 2688.45 |  |  |  | 1 | 1 |  |  |  |  | 144768.02 | 2688.45 | 144768.02 | 2688.45 | 9.4306 | [5 empty] | 108.1116 | 2610.5766
12.11.2007 21:00 | 3600 | 2 | 757.49 | GGB | 765.201 | 769.875 | 767.033 | 264.23 | GGB | 11191.3 | GGB | 9.86 | GGB | 996.87 | GGB | 57.9 | GGB | 178521 | GGB | 144939.67 | GGB | 0 | 0 | 2680 | 3600 | 2664.59 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 61023.37 | GGB | 61024.2 | 2664.59 | 2664.59 |  |  |  | 1 | 1 |  |  |  |  | 144939.67 | 2664.59 | 144939.67 | 2664.59 | 9.6143 | [5 empty] | 107.2791 | 2607.4849
12.11.2007 22:00 | 3600 | 2 | 757.29 | GGB | 766.667 | 773.039 | 768.498 | 264.94 | GGB | 11178.6 | GGB | 9.86 | GGB | 997.16 | GGB | 58.05 | GGB | 178760.87 | GGB | 145110.06 | GGB | 0 | 0 | 2695 | 3600 | 2679.19 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 61064.3 | GGB | 61065.13 | 2679.19 | 2679.19 |  |  |  | 1 | 1 |  |  |  |  | 145110.06 | 2679.19 | 145110.06 | 2679.19 | 9.4986 | [5 empty] | 107.9937 | 2604.4232
12.11.2007 23:00 | 3600 | 2 | 756.88 | GGB | 765.201 | 770.977 | 767.033 | 264.74 | GGB | 11161.5 | GGB | 9.84 | GGB | 997.07 | GGB | 58.07 | GGB | 178494.59 | GGB | 144873.96 | GGB | 0 | 0 | 2707 | 3600 | 2691.22 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 61104.93 | GGB | 61105.77 | 2691.22 | 2691.22 |  |  |  | 1 | 1 |  |  |  |  | 144873.96 | 2691.22 | 144873.96 | 2691.22 | 9.5937 | [5 empty] | 108.3021 | 2608.6676
12.11.2007 24:00 | 3600 | 2 | 757.55 | GGB | 766.3 | 772.125 | 768.132 | 265.51 | GGB | 11164.7 | GGB | 9.86 | GGB | 997.05 | GGB | 57.91 | GGB | 179892.02 | GGB | 146073.34 | GGB | 0 | 0 | 2668 | 3600 | 2652.39 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 61144.91 | GGB | 61145.74 | 2652.39 | 2652.39 |  |  |  | 1 | 1 |  |  |  |  | 146073.34 | 2652.39 | 146073.34 | 2652.39 | 9.6934 | [5 empty] | 107.6232 | 2587.2483
13.11.2007 01:00 | 3600 | 2 | 757.67 | GGB | 764.102 | 769.828 | 765.934 | 263.13 | GGB | 11191.4 | GGB | 9.86 | GGB | 996.54 | GGB | 58.41 | GGB | 177558.2 | GGB | 143888.28 | GGB | 0 | 0 | 2678 | 3600 | 2662.78 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 61185.68 | GGB | 61186.51 | 2662.78 | 2662.78 |  |  |  | 1 | 1 |  |  |  |  | 143888.28 | 2662.78 | 143888.28 | 2662.78 | 9.3977 | [5 empty] | 106.4286 | 2626.5378
13.11.2007 02:00 | 3600 | 2 | 757.3 | GGB | 765.201 | 770.906 | 767.033 | 263.3 | GGB | 11182.2 | GGB | 9.86 | GGB | 996.47 | GGB | 58.59 | GGB | 177451.47 | GGB | 143713.12 | GGB | 0 | 0 | 2695 | 3600 | 2679.69 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 61226.5 | GGB | 61227.34 | 2679.69 | 2679.69 |  |  |  | 1 | 1 |  |  |  |  | 143713.12 | 2679.69 | 143713.12 | 2679.69 | 9.432 | [5 empty] | 106.9741 | 2629.739
13.11.2007 03:00 | 3600 | 2 | 757.27 | GGB | 765.201 | 770.813 | 767.033 | 262.9 | GGB | 11180.3 | GGB | 9.85 | GGB | 996.27 | GGB | 58.52 | GGB | 177381.05 | GGB | 143659.26 | GGB | 0 | 0 | 2694 | 3600 | 2678.43 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 61267.23 | GGB | 61268.07 | 2678.43 | 2678.43 |  |  |  | 1 | 1 |  |  |  |  | 143659.26 | 2678.43 | 143659.26 | 2678.43 | 9.4471 | [5 empty] | 106.8837 | 2630.725
13.11.2007 04:00 | 3600 | 2 | 757.33 | GGB | 765.201 | 770.648 | 767.033 | 262.78 | GGB | 11185.4 | GGB | 9.86 | GGB | 996.41 | GGB | 58.44 | GGB | 177462.47 | GGB | 143777.19 | GGB | 0 | 0 | 2686 | 3600 | 2670.61 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 61307.88 | GGB | 61308.72 | 2670.61 | 2670.61 |  |  |  | 1 | 1 |  |  |  |  | 143777.19 | 2670.61 | 143777.19 | 2670.61 | 9.4458 | [5 empty] | 106.6591 | 2628.5672
13.11.2007 05:00 | 3600 | 2 | 757.37 | GGB | 765.201 | 771.727 | 767.033 | 262.78 | GGB | 11180 | GGB | 9.86 | GGB | 996.31 | GGB | 58.44 | GGB | 177470.17 | GGB | 143770.15 | GGB | 0 | 0 | 2688 | 3600 | 2672.69 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 61348.52 | GGB | 61349.36 | 2672.69 | 2672.69 |  |  |  | 1 | 1 |  |  |  |  | 143770.15 | 2672.69 | 143770.15 | 2672.69 | 9.455 | [5 empty] | 106.737 | 2628.6959
13.11.2007 06:00 | 3600 | 2 | 757.24 | GGB | 765.201 | 770.625 | 767.033 | 262.77 | GGB | 11171.6 | GGB | 9.85 | GGB | 996.28 | GGB | 58.38 | GGB | 177355.74 | GGB | 143700.13 | GGB | 0 | 0 | 2692 | 3600 | 2676.83 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 61389.37 | GGB | 61390.21 | 2676.83 | 2676.83 |  |  |  | 1 | 1 |  |  |  |  | 143700.13 | 2676.83 | 143700.13 | 2676.83 | 9.4164 | [5 empty] | 106.8502 | 2629.9767
13.11.2007 07:00 | 3600 | 2 | 756.91 | GGB | 764.102 | 770.578 | 765.934 | 263.12 | GGB | 11154.5 | GGB | 9.85 | GGB | 996.17 | GGB | 58.21 | GGB | 177825.58 | GGB | 144135.68 | GGB | 0 | 0 | 2695 | 3600 | 2679.86 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 61429.87 | GGB | 61430.72 | 2679.86 | 2679.86 |  |  |  | 1 | 1 |  |  |  |  | 144135.68 | 2679.86 | 144135.68 | 2679.86 | 9.535 | [5 empty] | 107.2954 | 2622.0295
13.11.2007 08:00 | 3600 | 2 | 757.17 | GGB | 765.201 | 770.813 | 768.132 | 265.68 | GGB | 11104.3 | GGB | 9.85 | GGB | 996.4 | GGB | 57.65 | GGB | 178891.81 | GGB | 145282.09 | GGB | 0 | 0 | 2678 | 3600 | 2662.87 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 61470.29 | GGB | 61471.14 | 2662.87 | 2662.87 |  |  |  | 1 | 1 |  |  |  |  | 145282.09 | 2662.87 | 145282.09 | 2662.87 | 9.5712 | [5 empty] | 107.4631 | 2601.3392
13.11.2007 09:00 | 3600 | 2 | 757.63 | GGB | 766.3 | 771.891 | 768.132 | 266.6 | GGB | 11096.4 | GGB | 9.86 | GGB | 996.5 | GGB | 57.83 | GGB | 178009.34 | GGB | 144499.24 | GGB | 0 | 0 | 2657 | 3600 | 2641.96 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 61510.85 | GGB | 61511.69 | 2641.96 | 2641.96 |  |  |  | 1 | 1 |  |  |  |  | 144499.24 | 2641.96 | 144499.24 | 2641.96 | 9.4146 | [5 empty] | 106.0448 | 2615.4324
13.11.2007 10:00 | 3600 | 2 | 757.64 | GGB | 766.3 | 771.891 | 768.132 | 265.87 | GGB | 11107.5 | GGB | 9.86 | GGB | 997.06 | GGB | 57.72 | GGB | 178304.23 | GGB | 144867.9 | GGB | 0 | 0 | 2653 | 3600 | 2637.47 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 61550.87 | GGB | 61551.71 | 2637.47 | 2637.47 |  |  |  | 1 | 1 |  |  |  |  | 144867.9 | 2637.47 | 144867.9 | 2637.47 | 9.5473 | [5 empty] | 106.1347 | 2608.7767
13.11.2007 11:00 | 3600 | 2 | 757.62 | GGB | 766.3 | 771.656 | 768.498 | 265.32 | GGB | 11099.1 | GGB | 9.86 | GGB | 997.11 | GGB | 57.76 | GGB | 177835.49 | GGB | 144480 | GGB | 0 | 0 | 2649 | 3600 | 2633.9 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 61591.96 | GGB | 61592.81 | 2633.9 | 2633.9 |  |  |  | 1 | 1 |  |  |  |  | 144480 | 2633.9 | 144480 | 2633.9 | 9.259 | [5 empty] | 105.7072 | 2615.7807
13.11.2007 12:00 | 3600 | 2 | 757.53 | GGB | 765.201 | 770.672 | 767.033 | 265.37 | GGB | 11086.3 | GGB | 9.85 | GGB | 997.41 | GGB | 57.65 | GGB | 177567 | GGB | 144352.96 | GGB | 0 | 0 | 2648 | 3600 | 2632.95 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 61631.77 | GGB | 61632.61 | 2632.95 | 2632.95 |  |  |  | 1 | 1 |  |  |  |  | 144352.96 | 2632.95 | 144352.96 | 2632.95 | 9.5496 | [5 empty] | 105.5761 | 2618.0828
13.11.2007 13:00 | 3600 | 2 | 757.54 | GGB | 766.3 | 771.773 | 768.132 | 265.33 | GGB | 11092.8 | GGB | 9.86 | GGB | 997.44 | GGB | 57.65 | GGB | 177624.22 | GGB | 144402.14 | GGB | 0 | 0 | 2652 | 3600 | 2636.18 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 61672.23 | GGB | 61673.08 | 2636.18 | 2636.18 |  |  |  | 1 | 1 |  |  |  |  | 144402.14 | 2636.18 | 144402.14 | 2636.18 | 9.4062 | [5 empty] | 105.7417 | 2617.1911
13.11.2007 14:00 | 3600 | 2 | 757.52 | GGB | 764.102 | 770.883 | 767.033 | 265.23 | GGB | 11093.5 | GGB | 9.85 | GGB | 997.41 | GGB | 57.61 | GGB | 177788.17 | GGB | 144547.97 | GGB | 0 | 0 | 2649 | 3600 | 2633.3 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 61712.07 | GGB | 61712.92 | 2633.3 | 2633.3 |  |  |  | 1 | 1 |  |  |  |  | 144547.97 | 2633.3 | 144547.97 | 2633.3 | 9.5542 | [5 empty] | 105.7328 | 2614.5507
13.11.2007 15:00 | 3600 | 2 | 757.41 | GGB | 765.201 | 770.883 | 767.033 | 265.38 | GGB | 11100.9 | GGB | 9.85 | GGB | 997.65 | GGB | 57.7 | GGB | 177870.7 | GGB | 144608.43 | GGB | 0 | 0 | 2661 | 3600 | 2645.61 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 61751.64 | GGB | 61752.49 | 2645.61 | 2645.61 |  |  |  | 1 | 1 |  |  |  |  | 144608.43 | 2645.61 | 144608.43 | 2645.61 | 9.6684 | [5 empty] | 106.2715 | 2613.4576
13.11.2007 16:00 | 3600 | 2 | 757.65 | GGB | 765.201 | 771.961 | 767.033 | 265.6 | GGB | 11107.3 | GGB | 9.86 | GGB | 998.26 | GGB | 57.91 | GGB | 177891.6 | GGB | 144625.55 | GGB | 0 | 0 | 2654 | 3600 | 2638.17 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 61792.19 | GGB | 61793.04 | 2638.17 | 2638.17 |  |  |  | 1 | 1 |  |  |  |  | 144625.55 | 2638.17 | 144625.55 | 2638.17 | 9.4093 | [5 empty] | 105.9852 | 2613.1482
13.11.2007 17:00 | 3600 | 2 | 757.35 | GGB | 766.3 | 771.891 | 768.132 | 266.54 | GGB | 11110.2 | GGB | 9.85 | GGB | 999.08 | GGB | 57.86 | GGB | 178113.87 | GGB | 144946.18 | GGB | 0 | 0 | 2678 | 3600 | 2662.29 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 61832.55 | GGB | 61833.4 | 2662.29 | 2662.29 |  |  |  | 1 | 1 |  |  |  |  | 144946.18 | 2662.29 | 144946.18 | 2662.29 | 9.5612 | [5 empty] | 107.1913 | 2607.3678
13.11.2007 18:00 | 3600 | 2 | 757.72 | GGB | 766.3 | 771.891 | 768.132 | 265.77 | GGB | 11112.7 | GGB | 9.86 | GGB | 999.18 | GGB | 58.09 | GGB | 177833.29 | GGB | 144632.48 | GGB | 0 | 0 | 2648 | 3600 | 2632.64 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 61872.75 | GGB | 61873.6 | 2632.64 | 2632.64 |  |  |  | 1 | 1 |  |  |  |  | 144632.48 | 2632.64 | 144632.48 | 2632.64 | 9.4718 | [5 empty] | 105.7681 | 2613.023
13.11.2007 19:00 | 3600 | 2 | 757.43 | GGB | 766.3 | 771.75 | 768.132 | 266.13 | GGB | 11095.6 | GGB | 9.85 | GGB | 999.37 | GGB | 58.05 | GGB | 177666.04 | GGB | 144541.69 | GGB | 0 | 0 | 2662 | 3600 | 2646.43 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 61913.39 | GGB | 61914.23 | 2646.43 | 2646.43 |  |  |  | 1 | 1 |  |  |  |  | 144541.69 | 2646.43 | 144541.69 | 2646.43 | 9.4147 | [5 empty] | 106.2554 | 2614.6643
13.11.2007 20:00 | 3600 | 2 | 757.67 | GGB | 766.3 | 771.891 | 768.132 | 266.18 | GGB | 11118.1 | GGB | 9.86 | GGB | 999.67 | GGB | 57.99 | GGB | 178207.4 | GGB | 145051.97 | GGB | 0 | 0 | 2661 | 3600 | 2645.79 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 61953.68 | GGB | 61954.52 | 2645.79 | 2645.79 |  |  |  | 1 | 1 |  |  |  |  | 145051.97 | 2645.79 | 145051.97 | 2645.79 | 9.5254 | [5 empty] | 106.6047 | 2605.4662
13.11.2007 21:00 | 3600 | 2 | 757.67 | GGB | 765.201 | 770.883 | 767.033 | 265.79 | GGB | 11110 | GGB | 9.86 | GGB | 999.66 | GGB | 58.05 | GGB | 178113.87 | GGB | 144947.21 | GGB | 0 | 0 | 2661 | 3600 | 2645.6 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 61994.02 | GGB | 61994.87 | 2645.6 | 2645.6 |  |  |  | 1 | 1 |  |  |  |  | 144947.21 | 2645.6 | 144947.21 | 2645.6 | 9.5037 | [5 empty] | 106.5201 | 2607.3493
13.11.2007 22:00 | 3600 | 2 | 757.63 | GGB | 766.3 | 770.977 | 768.132 | 265.08 | GGB | 11130.8 | GGB | 9.85 | GGB | 999.6 | GGB | 57.92 | GGB | 178678.35 | GGB | 145454.95 | GGB | 0 | 0 | 2666 | 3600 | 2650.31 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 62034.48 | GGB | 62035.33 | 2650.31 | 2650.31 |  |  |  | 1 | 1 |  |  |  |  | 145454.95 | 2650.31 | 145454.95 | 2650.31 | 9.5279 | [5 empty] | 107.0835 | 2598.2478
13.11.2007 23:00 | 3600 | 2 | 757.62 | GGB | 765.201 | 770.977 | 767.033 | 265.77 | GGB | 11127.8 | GGB | 9.86 | GGB | 999.27 | GGB | 58.13 | GGB | 178840.1 | GGB | 145448.48 | GGB | 0 | 0 | 2670 | 3600 | 2654.6 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 62074.81 | GGB | 62075.66 | 2654.6 | 2654.6 |  |  |  | 1 | 1 |  |  |  |  | 145448.48 | 2654.6 | 145448.48 | 2654.6 | 9.5737 | [5 empty] | 107.2521 | 2598.3634
13.11.2007 24:00 | 3600 | 2 | 757.58 | GGB | 765.201 | 770.18 | 767.033 | 264.84 | GGB | 11164.6 | GGB | 9.86 | GGB | 999 | GGB | 58.38 | GGB | 177364.54 | GGB | 144098.92 | GGB | 0 | 0 | 2692 | 3600 | 2676.12 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 62115.81 | GGB | 62116.66 | 2676.12 | 2676.12 |  |  |  | 1 | 1 |  |  |  |  | 144098.92 | 2676.12 | 144098.92 | 2676.12 | 9.4055 | [5 empty] | 107.1183 | 2622.6984
14.11.2007 01:00 | 3600 | 2 | 757.21 | GGB | 764.102 | 770.156 | 767.033 | 265.07 | GGB | 11168.5 | GGB | 9.85 | GGB | 999.47 | GGB | 58.36 | GGB | 177656.13 | GGB | 144413.24 | GGB | 0 | 0 | 2714 | 3600 | 2699.06 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 62155.78 | GGB | 62156.63 | 2699.06 | 2699.06 |  |  |  | 1 | 1 |  |  |  |  | 144413.24 | 2699.06 | 144413.24 | 2699.06 | 9.7518 | [5 empty] | 108.2722 | 2616.99
14.11.2007 02:00 | 3600 | 2 | 757.51 | GGB | 765.201 | 771.258 | 767.033 | 265.74 | GGB | 11131.9 | GGB | 9.86 | GGB | 999.68 | GGB | 57.94 | GGB | 178767.47 | GGB | 145529.48 | GGB | 0 | 0 | 2678 | 3600 | 2662.48 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 62197.05 | GGB | 62197.9 | 2662.48 | 2662.48 |  |  |  | 1 | 1 |  |  |  |  | 145529.48 | 2662.48 | 145529.48 | 2662.48 | 9.3886 | [5 empty] | 107.6304 | 2596.9171
14.11.2007 03:00 | 3600 | 2 | 757.54 | GGB | 766.3 | 772.242 | 768.132 | 265.38 | GGB | 11136.3 | GGB | 9.86 | GGB | 999.8 | GGB | 57.88 | GGB | 178543 | GGB | 145394.09 | GGB | 0 | 0 | 2674 | 3600 | 2658.37 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 62236.45 | GGB | 62237.3 | 2658.37 | 2658.37 |  |  |  | 1 | 1 |  |  |  |  | 145394.09 | 2658.37 | 145394.09 | 2658.37 | 9.8099 | [5 empty] | 107.3642 | 2599.3354
14.11.2007 04:00 | 3600 | 2 | 757.56 | GGB | 766.3 | 771.164 | 767.033 | 264.34 | GGB | 11166 | GGB | 9.86 | GGB | 999.93 | GGB | 58.55 | GGB | 176706.54 | GGB | 143626.39 | GGB | 0 | 0 | 2700 | 3600 | 2684.49 | GGB | 100 | GGB | 41.63 | GGB | 41.63 | GGB | 62278.08 | GGB | 62278.93 | 2684.49 | 2684.49 |  |  |  | 1 | 1 |  |  |  |  | 143626.39 | 2684.49 | 143626.39 | 2684.49 | 9.2617 | [5 empty] | 107.101 | 2631.327
14.11.2007 05:00 | 3600 | 2 | 757.26 | GGB | 766.3 | 772.195 | 767.033 | 266.54 | GGB | 11111.9 | GGB | 9.85 | GGB | 1000.63 | GGB | 58.06 | GGB | 178711.36 | GGB | 145568.1 | GGB | 0 | 0 | 2694 | 3600 | 2678.52 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 62317.24 | GGB | 62318.09 | 2678.52 | 2678.52 |  |  |  | 1 | 1 |  |  |  |  | 145568.1 | 2678.52 | 145568.1 | 2678.52 | 9.9568 | [5 empty] | 108.3075 | 2596.2282
14.11.2007 06:00 | 3600 | 2 | 757.55 | GGB | 765.201 | 771.188 | 768.132 | 267.01 | GGB | 11123.6 | GGB | 9.85 | GGB | 1001.16 | GGB | 58.01 | GGB | 178775.18 | GGB | 145722.02 | GGB | 0 | 0 | 2682 | 3600 | 2667.09 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 62357.61 | GGB | 62358.46 | 2667.09 | 2667.09 |  |  |  | 1 | 1 |  |  |  |  | 145722.02 | 2667.09 | 145722.02 | 2667.09 | 9.6273 | [5 empty] | 107.9594 | 2593.4859
14.11.2007 07:00 | 3600 | 2 | 757.86 | GGB | 765.201 | 771.047 | 767.033 | 265.45 | GGB | 11168.9 | GGB | 9.86 | GGB | 1001.59 | GGB | 58.48 | GGB | 177263.31 | GGB | 144343.97 | GGB | 0 | 0 | 2686 | 3600 | 2670.13 | GGB | 100 | GGB | 35.41 | GGB | 35.41 | GGB | 62393.02 | GGB | 62393.87 | 2670.13 | 2670.13 |  |  |  | 1 | 1 |  |  |  |  | 144343.97 | 2670.13 | 144343.97 | 2670.13 | 10.8844 | [5 empty] | 107.0603 | 2618.2458
14.11.2007 08:00 | 3600 | 2 | 757.36 | GGB | 766.3 | 771.961 | 768.132 | 266.19 | GGB | 11160.1 | GGB | 9.85 | GGB | 1002.46 | GGB | 58.53 | GGB | 177954.32 | GGB | 145012.69 | GGB | 0 | 0 | 2711 | 3600 | 2696.02 | GGB | 100 | GGB | 37.11 | GGB | 37.11 | GGB | 62430.13 | GGB | 62430.98 | 2696.02 | 2696.02 |  |  |  | 1 | 1 |  |  |  |  | 145012.69 | 2696.02 | 145012.69 | 2696.02 | 10.5351 | [5 empty] | 108.5992 | 2606.1719
14.11.2007 09:00 | 3600 | 2 | 757.33 | GGB | 766.3 | 770.953 | 767.033 | 265.66 | GGB | 11191.1 | GGB | 9.85 | GGB | 1003.06 | GGB | 58.94 | GGB | 177327.13 | GGB | 144411.49 | GGB | 0 | 0 | 2733 | 3600 | 2717.95 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 62468.59 | GGB | 62469.45 | 2717.95 | 2717.95 |  |  |  | 1 | 1 |  |  |  |  | 144411.49 | 2717.95 | 144411.49 | 2717.95 | 10.2028 | [5 empty] | 109.0287 | 2617.0217
14.11.2007 10:00 | 3600 | 2 | 757.34 | GGB | 765.201 | 770.953 | 768.132 | 266.3 | GGB | 11208.4 | GGB | 9.85 | GGB | 1003.93 | GGB | 58.99 | GGB | 178026.95 | GGB | 145081.48 | GGB | 0 | 0 | 2743 | 3600 | 2727.1 | GGB | 100 | GGB | 37.76 | GGB | 37.76 | GGB | 62506.36 | GGB | 62507.21 | 2727.1 | 2727.1 |  |  |  | 1 | 1 |  |  |  |  | 145081.48 | 2727.1 | 145081.48 | 2727.1 | 10.4781 | [5 empty] | 109.9033 | 2604.9362
14.11.2007 11:00 | 3600 | 2 | 757.49 | GGB | 765.201 | 771 | 767.033 | 266.32 | GGB | 11206.5 | GGB | 9.85 | GGB | 1004.6 | GGB | 58.98 | GGB | 178026.95 | GGB | 145184.59 | GGB | 0 | 0 | 2740 | 3600 | 2724.69 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 62545.27 | GGB | 62546.12 | 2724.69 | 2724.69 |  |  |  | 1 | 1 |  |  |  |  | 145184.59 | 2724.69 | 145184.59 | 2724.69 | 10.1666 | [5 empty] | 109.8842 | 2603.0862
14.11.2007 12:00 | 3600 | 2 | 757.63 | GGB | 766.3 | 771 | 768.132 | 266.37 | GGB | 11213.9 | GGB | 9.86 | GGB | 1004.98 | GGB | 59.06 | GGB | 177927.92 | GGB | 145123.8 | GGB | 0 | 0 | 2738 | 3600 | 2722.62 | GGB | 100 | GGB | 41.61 | GGB | 41.61 | GGB | 62586.88 | GGB | 62587.73 | 2722.62 | 2722.62 |  |  |  | 1 | 1 |  |  |  |  | 145123.8 | 2722.62 | 145123.8 | 2722.62 | 9.4957 | [5 empty] | 109.7547 | 2604.1766
14.11.2007 13:00 | 3600 | 2 | 757.48 | GGB | 766.3 | 771 | 767.033 | 266.7 | GGB | 11213.6 | GGB | 9.85 | GGB | 1005.65 | GGB | 58.88 | GGB | 178041.25 | GGB | 145390.26 | GGB | 0 | 0 | 2747 | 3600 | 2731.14 | GGB | 100 | GGB | 42.24 | GGB | 42.24 | GGB | 62629.12 | GGB | 62629.97 | 2731.14 | 2731.14 |  |  |  | 1 | 1 |  |  |  |  | 145390.26 | 2731.14 | 145390.26 | 2731.14 | 9.4006 | [5 empty] | 110.3003 | 2599.4038
14.11.2007 14:00 | 3600 | 2 | 757.81 | GGB | 765.201 | 771.07 | 767.033 | 266.31 | GGB | 11213 | GGB | 9.86 | GGB | 1006.91 | GGB | 58.99 | GGB | 177553.8 | GGB | 145128.53 | GGB | 0 | 0 | 2729 | 3600 | 2713.75 | GGB | 100 | GGB | 42.26 | GGB | 42.26 | GGB | 62671.37 | GGB | 62672.23 | 2713.75 | 2713.75 |  |  |  | 1 | 1 |  |  |  |  | 145128.53 | 2713.75 | 145128.53 | 2713.75 | 9.3195 | [5 empty] | 109.4007 | 2604.0917
14.11.2007 15:00 | 3600 | 2 | 757.12 | GGB | 765.201 | 771 | 768.132 | 267.35 | GGB | 11224.6 | GGB | 9.84 | GGB | 1007.76 | GGB | 58.42 | GGB | 178308.63 | GGB | 146116.83 | GGB | 0 | 0 | 2774 | 3600 | 2758.33 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 62711.57 | GGB | 62712.43 | 2758.33 | 2758.33 |  |  |  | 1 | 1 |  |  |  |  | 146116.83 | 2758.33 | 146116.83 | 2758.33 | 10.0258 | [5 empty] | 111.9551 | 2586.4782
14.11.2007 16:00 | 3600 | 2 | 757.42 | GGB | 766.3 | 770.695 | 768.132 | 267.77 | GGB | 11252.8 | GGB | 9.85 | GGB | 1007.67 | GGB | 58.46 | GGB | 178998.54 | GGB | 146654.21 | GGB | 0 | 0 | 2771 | 3600 | 2755.92 | GGB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 62753.15 | GGB | 62754 | 2755.92 | 2755.92 |  |  |  | 1 | 1 |  |  |  |  | 146654.21 | 2755.92 | 146654.21 | 2755.92 | 9.7226 | [5 empty] | 112.2687 | 2577.0007
14.11.2007 17:00 | 3600 | 2 | 757.41 | GGB | 764.102 | 769.617 | 765.934 | 268.43 | GGB | 11268.1 | GGB | 9.85 | GGB | 1007.84 | GGB | 58.4 | GGB | 179552.01 | GGB | 147157.63 | GGB | 0 | 0 | 2775 | 3600 | 2759.94 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 62793.62 | GGB | 62794.47 | 2759.94 | 2759.94 |  |  |  | 1 | 1 |  |  |  |  | 147157.63 | 2759.94 | 147157.63 | 2759.94 | 10.0357 | [5 empty] | 112.8184 | 2568.1849
14.11.2007 18:00 | 3600 | 2 | 757.66 | GGB | 765.201 | 770.672 | 768.132 | 268.73 | GGB | 11292.7 | GGB | 9.86 | GGB | 1008.8 | GGB | 58.37 | GGB | 179921.73 | GGB | 147613.95 | GGB | 0 | 0 | 2777 | 3600 | 2761.88 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 62834.46 | GGB | 62835.32 | 2761.88 | 2761.88 |  |  |  | 1 | 1 |  |  |  |  | 147613.95 | 2761.88 | 147613.95 | 2761.88 | 9.9802 | [5 empty] | 113.2478 | 2560.2458
14.11.2007 19:00 | 3600 | 2 | 757.76 | GGB | 766.667 | 772.055 | 768.132 | 268.5 | GGB | 11289.7 | GGB | 9.86 | GGB | 1009.69 | GGB | 58.33 | GGB | 179662.05 | GGB | 147548.93 | GGB | 0 | 0 | 2775 | 3600 | 2759.82 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 62875.79 | GGB | 62876.64 | 2759.82 | 2759.82 |  |  |  | 1 | 1 |  |  |  |  | 147548.93 | 2759.82 | 147548.93 | 2759.82 | 9.855 | [5 empty] | 113.1135 | 2561.374
14.11.2007 20:00 | 3600 | 2 | 757.49 | GGB | 764.102 | 770.906 | 765.934 | 267.83 | GGB | 11267.7 | GGB | 9.85 | GGB | 1010.49 | GGB | 58.03 | GGB | 179577.32 | GGB | 147730.93 | GGB | 0 | 0 | 2760 | 3600 | 2744.84 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 62916.94 | GGB | 62917.79 | 2744.84 | 2744.84 |  |  |  | 1 | 1 |  |  |  |  | 147730.93 | 2744.84 | 147730.93 | 2744.84 | 9.8541 | [5 empty] | 112.6383 | 2558.2185
14.11.2007 21:00 | 3600 | 2 | 757.37 | GGB | 766.3 | 771.938 | 768.498 | 269.89 | GGB | 11265.3 | GGB | 9.85 | GGB | 1011.6 | GGB | 56.88 | GGB | 182461.31 | GGB | 150790.47 | GGB | 0 | 0 | 2767 | 3600 | 2751.73 | GGB | 100 | GGB | 41.62 | GGB | 41.62 | GGB | 62958.55 | GGB | 62959.41 | 2751.73 | 2751.73 |  |  |  | 1 | 1 |  |  |  |  | 150790.47 | 2751.73 | 150790.47 | 2751.73 | 9.9696 | [5 empty] | 115.2596 | 2506.3122
14.11.2007 22:00 | 3600 | 2 | 757.6 | GGB | 768.864 | 773.25 | 770.696 | 269.72 | GGB | 11312.5 | GGB | 9.86 | GGB | 1012.35 | GGB | 56.87 | GGB | 182431.6 | GGB | 150881.84 | GGB | 0 | 0 | 2772 | 3600 | 2756.87 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 62999.08 | GGB | 62999.94 | 2756.87 | 2756.87 |  |  |  | 1 | 1 |  |  |  |  | 150881.84 | 2756.87 | 150881.84 | 2756.87 | 10.2631 | [5 empty] | 115.5449 | 2504.7945
14.11.2007 23:00 | 3600 | 2 | 757.09 | GGB | 766.3 | 772.148 | 768.132 | 269.65 | GGB | 11312.5 | GGB | 9.84 | GGB | 1012.89 | GGB | 56.78 | GGB | 182278.65 | GGB | 150876.92 | GGB | 0 | 0 | 2807 | 3600 | 2791.08 | GGB | 100 | GGB | 42.35 | GGB | 42.35 | GGB | 63041.43 | GGB | 63042.29 | 2791.08 | 2791.08 |  |  |  | 1 | 1 |  |  |  |  | 150876.92 | 2791.08 | 150876.92 | 2791.08 | 9.9436 | [5 empty] | 116.9749 | 2504.8762
14.11.2007 24:00 | 3600 | 2 | 757.79 | GGB | 766.3 | 770.93 | 768.132 | 270.84 | GGB | 11331.9 | GGB | 9.86 | GGB | 1013.6 | GGB | 56.59 | GGB | 183753.1 | GGB | 152291 | GGB | 0 | 0 | 2778 | 3600 | 2762.99 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 63081.88 | GGB | 63082.74 | 2762.99 | 2762.99 |  |  |  | 1 | 1 |  |  |  |  | 152291 | 2762.99 | 152291 | 2762.99 | 10.4024 | [5 empty] | 116.8829 | 2481.6174
15.11.2007 01:00 | 3600 | 2 | 758.41 | GGB | 765.201 | 770.109 | 767.033 | 269.51 | GGB | 11366.2 | GGB | 9.87 | GGB | 1014.49 | GGB | 57.1 | GGB | 182035.48 | GGB | 150766.96 | GGB | 0 | 0 | 2766 | 3600 | 2750.84 | GGB | 100 | GGB | 42.13 | GGB | 42.13 | GGB | 63124.01 | GGB | 63124.87 | 2750.84 | 2750.84 |  |  |  | 1 | 1 |  |  |  |  | 150766.96 | 2750.84 | 150766.96 | 2750.84 | 9.8442 | [5 empty] | 115.2044 | 2506.7031
15.11.2007 02:00 | 3600 | 2 | 756.95 | GGB | 764.102 | 769.125 | 765.934 | 270.15 | GGB | 11308.3 | GGB | 9.84 | GGB | 1015.08 | GGB | 56.89 | GGB | 182932.25 | GGB | 151697.06 | GGB | 0 | 0 | 2814 | 3600 | 2798.7 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 63165.42 | GGB | 63166.28 | 2798.7 | 2798.7 |  |  |  | 1 | 1 |  |  |  |  | 151697.06 | 2798.7 | 151697.06 | 2798.7 | 10.2525 | [5 empty] | 117.9318 | 2491.3337
15.11.2007 03:00 | 3600 | 2 | 757.15 | GGB | 765.201 | 770.461 | 765.934 | 270.9 | GGB | 11326.7 | GGB | 9.84 | GGB | 1015.45 | GGB | 56.43 | GGB | 183750.9 | GGB | 152641.92 | GGB | 0 | 0 | 2802 | 3600 | 2786.02 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 63206.98 | GGB | 63207.84 | 2786.02 | 2786.02 |  |  |  | 1 | 1 |  |  |  |  | 152641.92 | 2786.02 | 152641.92 | 2786.02 | 10.2325 | [5 empty] | 118.1287 | 2475.9123
15.11.2007 04:00 | 3600 | 2 | 757.82 | GGB | 766.667 | 772.664 | 768.498 | 272.22 | GGB | 11402.2 | GGB | 9.86 | GGB | 1016.12 | GGB | 56.15 | GGB | 185233.06 | GGB | 154106.41 | GNB | 0 | 0 | 2806 | 3600 | 2790.66 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 63247.95 | GGB | 63248.81 | 2790.66 | 2790.66 |  |  |  | 1 | 1 |  |  |  |  | 154106.41 | 2790.66 |  | 2790.66 | 10.4969 | [5 empty] | 119.4607 | 2452.3834
15.11.2007 05:00 | 3600 | 2 | 757.38 | GGB | 765.201 | 769.5 | 767.033 | 271.14 | GGB | 11430.4 | GGB | 9.85 | GGB | 1016.69 | GGB | 56.64 | GGB | 183895.05 | GGB | 152852.35 | GNB | 0 | 0 | 2839 | 3600 | 2823.73 | GGB | 100 | GGB | 42.02 | GGB | 42.02 | GGB | 63289.97 | GGB | 63290.83 | 2823.73 | 2823.73 |  |  |  | 1 | 1 |  |  |  |  | 152852.35 | 2823.73 |  | 2823.73 | 10.2716 | [5 empty] | 119.8927 | 2472.5037
15.11.2007 06:00 | 3600 | 2 | 756.71 | GGB | 765.201 | 770.508 | 767.033 | 272.7 | GGB | 11435.9 | GGB | 9.84 | GGB | 1017.63 | GGB | 56.25 | GGB | 185744.71 | GGB | 154713.55 | GNB | 0 | 0 | 2886 | 3600 | 2870.2 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 63331.1 | GGB | 63331.96 | 2870.2 | 2870.2 |  |  |  | 1 | 1 |  |  |  |  | 154713.55 | 2870.2 |  | 2870.2 | 10.7965 | [5 empty] | 123.3497 | 2442.7595
15.11.2007 07:00 | 3600 | 2 | 757.28 | GGB | 766.3 | 771.609 | 767.033 | 273.91 | GGB | 11471.2 | GGB | 9.85 | GGB | 1018.22 | GGB | 55.62 | GGB | 187289.59 | GGB | 156393.21 | GNB | 0 | 0 | 2866 | 3600 | 2850.8 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 63372.46 | GGB | 63373.33 | 2850.8 | 2850.8 |  |  |  | 1 | 1 |  |  |  |  | 156393.21 | 2850.8 |  | 2850.8 | 10.777 | [5 empty] | 123.846 | 2416.5243
15.11.2007 08:00 | 3600 | 2 | 757.38 | GGB | 767.766 | 772.617 | 768.498 | 274.54 | GGB | 11505.5 | GNB | 9.86 | GGB | 1019.01 | GGB | 55.7 | GGB | 187260.98 | GGB | 156451.78 | GGB | 0 | 0 | 2887 | 3600 | 2871.36 | GGB | 100 | GGB | 41.61 | GGB | 41.61 | GGB | 63414.07 | GGB | 63414.94 | 2871.36 | 2871.36 |  |  |  | 0 | 1 | [14 empty] | 124.7859 | 2415.6197
15.11.2007 09:00 | 3600 | 2 | 756.99 | GGB | 765.201 | 771.164 | 767.033 | 274.58 | GGB | 11504.8 | GNB | 9.85 | GGB | 1019.92 | GGB | 56.23 | GGB | 186616.18 | GGB | 155800.57 | GGB | 0 | 0 | 2921 | 3600 | 2905.24 | GGB | 100 | GGB | 41.65 | GGB | 41.65 | GGB | 63455.72 | GGB | 63456.59 | 2905.24 | 2905.24 |  |  |  | 0 | 1 | [14 empty] | 125.7328 | 2425.7164
15.11.2007 10:00 | 3600 | 2 | 757.85 | GGB | 766.3 | 771.164 | 769.597 | 275.32 | GGB | 11492.2 | GGB | 9.86 | GGB | 1020.65 | GGB | 55.98 | GGB | 187611.99 | GGB | 156863.15 | GNB | 0 | 0 | 2862 | 3600 | 2846.59 | GGB | 100 | GGB | 42.54 | GGB | 42.54 | GGB | 63498.27 | GGB | 63499.13 | 2846.59 | 2846.59 |  |  |  | 1 | 1 |  |  |  |  | 156863.15 | 2846.59 |  | 2846.59 | 10.4966 | [5 empty] | 124.0347 | 2409.2848
15.11.2007 11:00 | 3600 | 2 | 758.49 | GGB | 766.3 | 771.375 | 768.132 | 273.29 | GGB | 11443.4 | GGB | 9.87 | GGB | 1020.83 | GGB | 56.49 | GGB | 185364 | GGB | 154770.76 | GNB | 0 | 0 | 2803 | 3600 | 2787.54 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 63539.81 | GGB | 63540.68 | 2787.54 | 2787.54 |  |  |  | 1 | 1 |  |  |  |  | 154770.76 | 2787.54 |  | 2787.54 | 10.3834 | [5 empty] | 119.8416 | 2441.8566
15.11.2007 12:00 | 3600 | 2 | 758.92 | GGB | 766.3 | 771.797 | 768.132 | 270.35 | GGB | 11423.8 | GGB | 9.88 | GGB | 1020.96 | GGB | 57.81 | GGB | 181648.16 | GGB | 151084.41 | GGB | 0 | 0 | 2779 | 3600 | 2763.7 | GGB | 100 | GGB | 43.88 | GGB | 43.88 | GGB | 63583.69 | GGB | 63584.56 | 2763.7 | 2763.7 |  |  |  | 1 | 1 |  |  |  |  | 151084.41 | 2763.7 | 151084.41 | 2763.7 | 9.5158 | [5 empty] | 115.9867 | 2501.4361
15.11.2007 13:00 | 3600 | 2 | 758.19 | GGB | 767.033 | 772.945 | 769.597 | 271.79 | GGB | 11334.3 | GGB | 9.85 | GGB | 1019.57 | GGB | 58.72 | GGB | 183174.33 | GGB | 151728.72 | GGB | 0 | 0 | 2762 | 2974 | 2746.67 | GGB | 100 | GGB | 41.35 | GGB | 41.35 | GGB | 63625.03 | GGB | 63625.91 | 2746.67 | 2746.67 |  |  |  | 1 | 1 |  |  |  |  | 151728.72 | 2746.67 | 151728.72 | 2746.67 | 10.0786 | [5 empty] | 115.7635 | 2490.8139
15.11.2007 14:00 | 3600 | 2 | 757.78 | GGB | 765.934 | 770.859 | 767.033 | 272.54 | GGB | 11331.8 | GGB | 9.84 | GGB | 1020.65 | GGB | 57.06 | GGB | 183917.05 | GGB | 153271.62 | GNB | 0 | 0 | 2796 | 3600 | 2780.71 | GGB | 100 | GGB | 42.33 | GGB | 42.33 | GGB | 63667.36 | GGB | 63668.24 | 2780.71 | 2780.71 |  |  |  | 1 | 1 |  |  |  |  | 153271.62 | 2780.71 |  | 2780.71 | 10.0686 | [5 empty] | 118.39 | 2465.7402
15.11.2007 15:00 | 3600 | 2 | 758.81 | GGB | 765.934 | 771.75 | 768.498 | 272.12 | GGB | 11390.2 | GGB | 9.87 | GGB | 1020.75 | GGB | 57.55 | GGB | 182953.16 | GGB | 152258.02 | GGB | 0 | 0 | 2774 | 3600 | 2758.33 | GGB | 100 | GGB | 41.44 | GGB | 41.44 | GGB | 63708.8 | GGB | 63709.68 | 2758.33 | 2758.33 |  |  |  | 1 | 1 |  |  |  |  | 152258.02 | 2758.33 | 152258.02 | 2758.33 | 10.1346 | [5 empty] | 116.6605 | 2482.155
15.11.2007 16:00 | 3600 | 2 | 756.74 | GGB | 765.934 | 769.945 | 767.033 | 273.11 | GGB | 11360 | GGB | 9.83 | GGB | 1020.59 | GGB | 57.52 | GGB | 183847.73 | GGB | 152991.15 | GNB | 0 | 0 | 2874 | 3600 | 2858.36 | GGB | 100 | GGB | 41.92 | GGB | 41.92 | GGB | 63750.71 | GGB | 63751.6 | 2858.36 | 2858.36 |  |  |  | 1 | 1 |  |  |  |  | 152991.15 | 2858.36 |  | 2858.36 | 10.4319 | [5 empty] | 121.4733 | 2470.2605
15.11.2007 17:00 | 3600 | 2 | 758.12 | GGB | 765.934 | 771.352 | 768.132 | 274.31 | GGB | 11403.5 | GGB | 9.86 | GGB | 1021.02 | GGB | 56.77 | GGB | 185237.46 | GGB | 154561 | GNB | 0 | 0 | 2816 | 3600 | 2800.36 | GGB | 100 | GGB | 42.18 | GGB | 42.18 | GGB | 63792.9 | GGB | 63793.78 | 2800.36 | 2800.36 |  |  |  | 1 | 1 |  |  |  |  | 154561 | 2800.36 |  | 2800.36 | 10.2614 | [5 empty] | 120.2296 | 2445.1705
15.11.2007 18:00 | 3600 | 2 | 758.12 | GGB | 765.934 | 771.258 | 768.498 | 273.85 | GGB | 11445.3 | GGB | 9.86 | GGB | 1021.73 | GGB | 56.86 | GGB | 184544.25 | GGB | 154051.31 | GNB | 0 | 0 | 2832 | 3600 | 2816.54 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 63833.98 | GGB | 63834.87 | 2816.54 | 2816.54 |  |  |  | 1 | 1 |  |  |  |  | 154051.31 | 2816.54 |  | 2816.54 | 10.5595 | [5 empty] | 120.5255 | 2453.2605
15.11.2007 19:00 | 3600 | 2 | 756.96 | GGB | 764.469 | 770.32 | 767.033 | 274.23 | GGB | 11427.8 | GGB | 9.84 | GGB | 1021.59 | GGB | 56.85 | GGB | 184586.06 | GGB | 154070.17 | GNB | 0 | 0 | 2892 | 3600 | 2876.34 | GGB | 100 | GGB | 42.3 | GGB | 42.3 | GGB | 63876.28 | GGB | 63877.17 | 2876.34 | 2876.34 |  |  |  | 1 | 1 |  |  |  |  | 154070.17 | 2876.34 |  | 2876.34 | 10.4766 | [5 empty] | 123.0995 | 2452.9602
15.11.2007 20:00 | 3600 | 2 | 757.4 | GGB | 765.934 | 770.977 | 768.132 | 275.83 | GGB | 11431.3 | GGB | 9.85 | GGB | 1022.07 | GGB | 56.28 | GGB | 186283.88 | GGB | 155828.94 | GNB | 0 | 0 | 2871 | 3600 | 2855.03 | GGB | 100 | GGB | 42.07 | GGB | 42.07 | GGB | 63918.35 | GGB | 63919.24 | 2855.03 | 2855.03 |  |  |  | 1 | 1 |  |  |  |  | 155828.94 | 2855.03 |  | 2855.03 | 10.5751 | [5 empty] | 123.5823 | 2425.2748
15.11.2007 21:00 | 3600 | 2 | 758.22 | GGB | 765.934 | 772.125 | 768.498 | 275.55 | GGB | 11450.8 | GGB | 9.87 | GGB | 1021.99 | GGB | 56.5 | GGB | 185375 | GGB | 154952.37 | GNB | 0 | 0 | 2837 | 3600 | 2821.61 | GGB | 100 | GGB | 41.69 | GGB | 41.69 | GGB | 63960.05 | GGB | 63960.93 | 2821.61 | 2821.61 |  |  |  | 1 | 1 |  |  |  |  | 154952.37 | 2821.61 |  | 2821.61 | 10.4873 | [5 empty] | 121.4487 | 2438.9946
15.11.2007 22:00 | 3600 | 2 | 758.1 | GGB | 763.37 | 767.953 | 764.835 | 273.23 | GGB | 11463.9 | GGB | 9.86 | GGB | 1022.01 | GGB | 57.09 | GGB | 183490.12 | GGB | 153103.55 | GNB | 0 | 0 | 2849 | 3600 | 2833.4 | GGB | 100 | GGB | 41.54 | GGB | 41.54 | GGB | 64001.58 | GGB | 64002.47 | 2833.4 | 2833.4 |  |  |  | 0 | 1 | [14 empty] | 120.501 | 2468.447
15.11.2007 23:00 | 3600 | 2 | 757.16 | GGB | 765.934 | 771.164 | 768.132 | 272.65 | GGB | 11384.6 | GGB | 9.85 | GGB | 1021.81 | GGB | 57.42 | GGB | 182219.23 | GGB | 151863.88 | GGB | 0 | 0 | 2867 | 3600 | 2851.09 | GGB | 100 | GGB | 43.1 | GGB | 43.1 | GGB | 64044.68 | GGB | 64045.57 | 2851.09 | 2851.09 |  |  |  | 1 | 1 |  |  |  |  | 151863.88 | 2851.09 | 151863.88 | 2851.09 | 10.0459 | [5 empty] | 120.2716 | 2488.597
15.11.2007 24:00 | 3600 | 2 | 758.05 | GGB | 763.37 | 769.008 | 765.934 | 272.47 | GGB | 11357.5 | GGB | 9.86 | GGB | 1021.66 | GGB | 57.93 | GGB | 182005.77 | GGB | 151427.15 | GGB | 0 | 0 | 2796 | 3600 | 2780.58 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 64085.8 | GGB | 64086.7 | 2780.58 | 2780.58 |  |  |  | 0 | 1 | [14 empty] | 116.9598 | 2495.7744
16.11.2007 01:00 | 3600 | 2 | 758.3 | GGB | 767.033 | 772.453 | 768.498 | 273.28 | GGB | 11328 | GGB | 9.86 | GGB | 1021.32 | GGB | 57.45 | GGB | 183018.08 | GGB | 152443.04 | GGB | 0 | 0 | 2767 | 3600 | 2751.51 | GGB | 100 | GGB | 41.25 | GGB | 41.25 | GGB | 64127.06 | GGB | 64127.95 | 2751.51 | 2751.51 |  |  |  | 1 | 1 |  |  |  |  | 152443.04 | 2751.51 | 152443.04 | 2751.51 | 10.1684 | [5 empty] | 116.5135 | 2479.1424
16.11.2007 02:00 | 3600 | 2 | 758.65 | GGB | 767.033 | 772.266 | 768.498 | 271.83 | GGB | 11332 | GGB | 9.86 | GGB | 1020.54 | GGB | 58.07 | GGB | 181243.23 | GGB | 150565.23 | GGB | 0 | 0 | 2761 | 3600 | 2745.16 | GGB | 100 | GGB | 42.49 | GGB | 42.49 | GGB | 64169.54 | GGB | 64170.44 | 2745.16 | 2745.16 |  |  |  | 1 | 1 |  |  |  |  | 150565.23 | 2745.16 | 150565.23 | 2745.16 | 9.7276 | [5 empty] | 114.8127 | 2510.0616
16.11.2007 03:00 | 3600 | 2 | 758.48 | GGB | 765.934 | 771.398 | 767.033 | 270.68 | GGB | 11311.4 | GGB | 9.86 | GGB | 1019.97 | GGB | 58.59 | GGB | 179923.93 | GGB | 149152.6 | GGB | 0 | 0 | 2768 | 3600 | 2752.45 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 64210.27 | GGB | 64211.17 | 2752.45 | 2752.45 |  |  |  | 1 | 1 |  |  |  |  | 149152.6 | 2752.45 | 149152.6 | 2752.45 | 10.0794 | [5 empty] | 114.0375 | 2533.8345
16.11.2007 04:00 | 3600 | 2 | 758.53 | GGB | 768.132 | 772.734 | 769.963 | 271.47 | GGB | 11276.7 | GGB | 9.86 | GGB | 1019.72 | GGB | 58.33 | GGB | 180759.08 | GGB | 149922.79 | GGB | 0 | 0 | 2742 | 3600 | 2726.77 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 64251.45 | GGB | 64252.35 | 2726.77 | 2726.77 |  |  |  | 1 | 1 |  |  |  |  | 149922.79 | 2726.77 | 149922.79 | 2726.77 | 9.9273 | [5 empty] | 113.5569 | 2520.8175
16.11.2007 05:00 | 3600 | 2 | 758.04 | GGB | 765.934 | 771.656 | 767.766 | 271.2 | GGB | 11242.7 | GGB | 9.84 | GGB | 1019.15 | GGB | 58.5 | GGB | 180628.14 | GGB | 149655.1 | GGB | 0 | 0 | 2744 | 3600 | 2728.17 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 64292.68 | GGB | 64293.58 | 2728.17 | 2728.17 |  |  |  | 1 | 1 |  |  |  |  | 149655.1 | 2728.17 | 149655.1 | 2728.17 | 9.9026 | [5 empty] | 113.4124 | 2525.3266
16.11.2007 06:00 | 3600 | 2 | 758.58 | GGB | 765.934 | 770.508 | 766.667 | 270.32 | GGB | 11261.3 | GGB | 9.86 | GGB | 1018.85 | GGB | 58.88 | GGB | 179432.08 | GGB | 148451.04 | GGB | 0 | 0 | 2730 | 3600 | 2714.63 | GGB | 100 | GGB | 41.54 | GGB | 41.54 | GGB | 64334.22 | GGB | 64335.12 | 2714.63 | 2714.63 |  |  |  | 1 | 1 |  |  |  |  | 148451.04 | 2714.63 | 148451.04 | 2714.63 | 9.7012 | [5 empty] | 111.9416 | 2545.809
16.11.2007 07:00 | 3600 | 2 | 758.82 | GGB | 768.498 | 773.813 | 770.33 | 270.93 | GGB | 11258.3 | GGB | 9.86 | GGB | 1018.53 | GGB | 58.59 | GGB | 180541.22 | GGB | 149450.89 | GGB | 0 | 0 | 2707 | 3600 | 2691.66 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 64375.34 | GGB | 64376.24 | 2691.66 | 2691.66 |  |  |  | 1 | 1 |  |  |  |  | 149450.89 | 2691.66 | 149450.89 | 2691.66 | 9.7829 | [5 empty] | 111.7419 | 2528.7772
16.11.2007 08:00 | 3600 | 2 | 758.31 | GGB | 765.934 | 770.273 | 767.766 | 270.56 | GGB | 11230.9 | GGB | 9.84 | GGB | 1018.14 | GGB | 59.05 | GGB | 179938.23 | GGB | 148690.29 | GGB | 0 | 0 | 2750 | 3209 | 2734.95 | GGB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 64416.91 | GGB | 64417.81 | 2734.95 | 2734.95 |  |  |  | 1 | 1 |  |  |  |  | 148690.29 | 2734.95 | 148690.29 | 2734.95 | 9.7825 | [5 empty] | 112.9613 | 2541.7127
16.11.2007 09:00 | 3600 | 2 | 759.18 | GGB | 764.835 | 770.273 | 766.667 | 270.15 | GGB | 11246.7 | GGB | 9.86 | GGB | 1018.13 | GGB | 59.16 | GGB | 179424.37 | GGB | 148216.45 | GGB | 0 | 0 | 2727 | 3600 | 2711.24 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 64456.89 | GGB | 64457.79 | 2711.24 | 2711.24 |  |  |  | 1 | 1 |  |  |  |  | 148216.45 | 2711.24 | 148216.45 | 2711.24 | 10.0513 | [5 empty] | 111.6251 | 2549.8384
16.11.2007 10:00 | 3600 | 2 | 759.1 | GGB | 767.033 | 772.406 | 768.864 | 270.5 | GGB | 11215.4 | GGB | 9.86 | GGB | 1018.54 | GGB | 58.6 | GGB | 180195.71 | GGB | 149163.37 | GGB | 0 | 0 | 2713 | 3600 | 2697.4 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 64498.44 | GGB | 64499.34 | 2697.4 | 2697.4 |  |  |  | 1 | 1 |  |  |  |  | 149163.37 | 2697.4 | 149163.37 | 2697.4 | 9.6836 | [5 empty] | 111.7648 | 2533.6515
16.11.2007 11:00 | 3600 | 2 | 759.52 | GGB | 768.498 | 773.531 | 770.33 | 268.98 | GGB | 11226.2 | GGB | 9.87 | GGB | 1018.1 | GGB | 59.06 | GGB | 178327.34 | GGB | 147346.72 | GGB | 0 | 0 | 2697 | 3600 | 2681.29 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 64539.14 | GGB | 64540.03 | 2681.29 | 2681.29 |  |  |  | 1 | 1 |  |  |  |  | 147346.72 | 2681.29 | 147346.72 | 2681.29 | 9.7095 | [5 empty] | 109.7442 | 2564.8891
16.11.2007 12:00 | 3600 | 2 | 758.58 | GGB | 767.033 | 773.461 | 768.864 | 268.81 | GGB | 11170.4 | GGB | 9.85 | GGB | 1017.35 | GGB | 59.22 | GGB | 178485.79 | GGB | 147300.28 | GGB | 0 | 0 | 2721 | 3600 | 2705.83 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 64580 | GGB | 64580.9 | 2705.83 | 2705.83 |  |  |  | 1 | 1 |  |  |  |  | 147300.28 | 2705.83 | 147300.28 | 2705.83 | 9.7521 | [5 empty] | 110.7138 | 2565.6978
16.11.2007 13:00 | 3600 | 2 | 759.38 | GGB | 767.033 | 771.328 | 767.766 | 267.37 | GGB | 11174.6 | GGB | 9.87 | GGB | 1016.69 | GGB | 60.01 | GGB | 176588.8 | GGB | 145292.63 | GGB | 0 | 0 | 2682 | 3600 | 2666.32 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 64620.46 | GGB | 64621.35 | 2666.32 | 2666.32 |  |  |  | 1 | 1 |  |  |  |  | 145292.63 | 2666.32 | 145292.63 | 2666.32 | 9.5772 | [5 empty] | 107.6102 | 2601.1505
16.11.2007 14:00 | 3600 | 2 | 759.25 | GGB | 769.597 | 774.563 | 771.429 | 267.6 | GGB | 11140.2 | GGB | 9.87 | GGB | 1016 | GGB | 59.3 | GGB | 177395.35 | GGB | 146172.07 | GGB | 0 | 0 | 2668 | 3600 | 2652.61 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 64661.09 | GGB | 64661.99 | 2652.61 | 2652.61 |  |  |  | 1 | 1 |  |  |  |  | 146172.07 | 2652.61 | 146172.07 | 2652.61 | 9.5408 | [5 empty] | 107.7049 | 2585.5008
16.11.2007 15:00 | 3600 | 2 | 759.1 | GGB | 767.033 | 772.383 | 768.864 | 265.62 | GGB | 11142.7 | GGB | 9.86 | GGB | 1015.21 | GGB | 59.61 | GGB | 175344.32 | GGB | 144233.53 | GGB | 0 | 0 | 2673 | 3600 | 2658.05 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 64701.96 | GGB | 64702.85 | 2658.05 | 2658.05 |  |  |  | 1 | 1 |  |  |  |  | 144233.53 | 2658.05 | 144233.53 | 2658.05 | 9.3828 | [5 empty] | 106.4944 | 2620.2506
16.11.2007 16:00 | 3600 | 2 | 759.07 | GGB | 767.033 | 772.641 | 768.498 | 265.95 | GGB | 11122.4 | GGB | 9.86 | GGB | 1014.93 | GGB | 59.24 | GGB | 175896.69 | GGB | 144809.33 | GGB | 0 | 0 | 2659 | 3600 | 2643.88 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 64742.3 | GGB | 64743.19 | 2643.88 | 2643.88 |  |  |  | 1 | 1 |  |  |  |  | 144809.33 | 2643.88 | 144809.33 | 2643.88 | 9.4908 | [5 empty] | 106.3496 | 2609.8318
16.11.2007 17:00 | 3600 | 2 | 758.43 | GGB | 767.033 | 773.602 | 769.597 | 266.59 | GGB | 11096.8 | GGB | 9.85 | GGB | 1014.7 | GGB | 58.94 | GGB | 176829.78 | GGB | 145673.9 | GGB | 0 | 0 | 2675 | 3600 | 2659.97 | GGB | 100 | GGB | 41.9 | GGB | 41.9 | GGB | 64784.2 | GGB | 64785.09 | 2659.97 | 2659.97 |  |  |  | 1 | 1 |  |  |  |  | 145673.9 | 2659.97 | 145673.9 | 2659.97 | 9.2479 | [5 empty] | 107.6356 | 2594.3426
16.11.2007 18:00 | 3600 | 2 | 759.07 | GGB | 767.033 | 772.664 | 768.498 | 264.79 | GGB | 11128.9 | GGB | 9.86 | GGB | 1014.46 | GGB | 59.41 | GGB | 174799.66 | GGB | 143764.25 | GGB | 0 | 0 | 2660 | 3600 | 2644.85 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 64824.64 | GGB | 64825.53 | 2644.85 | 2644.85 |  |  |  | 1 | 1 |  |  |  |  | 143764.25 | 2644.85 | 143764.25 | 2644.85 | 9.4024 | [5 empty] | 105.6208 | 2628.8038
16.11.2007 19:00 | 3600 | 2 | 758.7 | GGB | 768.132 | 773.039 | 769.597 | 265.93 | GGB | 11096.4 | GGB | 9.85 | GGB | 1014.59 | GGB | 58.84 | GGB | 176309.32 | GGB | 145273.32 | GGB | 0 | 0 | 2670 | 3600 | 2654.9 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 64865.88 | GGB | 64866.77 | 2654.9 | 2654.9 |  |  |  | 1 | 1 |  |  |  |  | 145273.32 | 2654.9 | 145273.32 | 2654.9 | 9.3522 | [5 empty] | 107.135 | 2601.4963
16.11.2007 20:00 | 3600 | 2 | 759.26 | GGB | 767.033 | 772.852 | 768.498 | 266.25 | GGB | 11108.2 | GGB | 9.86 | GGB | 1014.15 | GGB | 58.44 | GGB | 176889.2 | GGB | 145864.05 | GGB | 0 | 0 | 2643 | 3600 | 2627.42 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 64906.71 | GGB | 64907.6 | 2627.42 | 2627.42 |  |  |  | 1 | 1 |  |  |  |  | 145864.05 | 2627.42 | 145864.05 | 2627.42 | 9.3864 | [5 empty] | 106.4573 | 2590.9606
16.11.2007 21:00 | 3600 | 2 | 758.81 | GGB | 768.132 | 772.477 | 769.597 | 264.38 | GGB | 11126.5 | GGB | 9.86 | GGB | 1013.65 | GGB | 58.92 | GGB | 174393.63 | GGB | 143529.05 | GGB | 0 | 0 | 2673 | 3600 | 2657.62 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 64947.85 | GGB | 64948.74 | 2657.62 | 2657.62 |  |  |  | 1 | 1 |  |  |  |  | 143529.05 | 2657.62 | 143529.05 | 2657.62 | 9.2719 | [5 empty] | 105.9571 | 2633.1116
16.11.2007 22:00 | 3600 | 2 | 758.83 | GGB | 767.033 | 772.406 | 768.498 | 263.91 | GGB | 11119.5 | GGB | 9.86 | GGB | 1013.14 | GGB | 59 | GGB | 174235.18 | GGB | 143291.71 | GGB | 0 | 0 | 2674 | 3600 | 2658.54 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 64988.78 | GGB | 64989.67 | 2658.54 | 2658.54 |  |  |  | 1 | 1 |  |  |  |  | 143291.71 | 2658.54 | 143291.71 | 2658.54 | 9.3073 | [5 empty] | 105.8185 | 2637.4729
16.11.2007 23:00 | 3600 | 2 | 758.38 | GGB | 765.934 | 771.258 | 768.132 | 263.22 | GGB | 11105.9 | GGB | 9.85 | GGB | 1013.28 | GGB | 59.01 | GGB | 174377.13 | GGB | 143422.52 | GGB | 0 | 0 | 2687 | 3600 | 2671.19 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 65030.2 | GGB | 65031.08 | 2671.19 | 2671.19 |  |  |  | 1 | 1 |  |  |  |  | 143422.52 | 2671.19 | 143422.52 | 2671.19 | 9.2516 | [5 empty] | 106.4191 | 2635.0674
16.11.2007 24:00 | 3600 | 2 | 759.06 | GGB | 767.033 | 772.266 | 768.498 | 263.74 | GGB | 11108.5 | GGB | 9.86 | GGB | 1013.44 | GGB | 59.3 | GGB | 173914.98 | GGB | 142939.54 | GGB | 0 | 0 | 2664 | 3600 | 2648.47 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 65070.51 | GGB | 65071.39 | 2648.47 | 2648.47 |  |  |  | 1 | 1 |  |  |  |  | 142939.54 | 2648.47 | 142939.54 | 2648.47 | 9.3915 | [5 empty] | 105.1586 | 2643.971
17.11.2007 01:00 | 3600 | 2 | 758.48 | GGB | 767.033 | 772.266 | 769.597 | 264.06 | GGB | 11106.1 | GGB | 9.85 | GGB | 1013.31 | GGB | 59.27 | GGB | 174117.45 | GGB | 143103.57 | GGB | 0 | 0 | 2682 | 3600 | 2666.24 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 65111.63 | GGB | 65112.52 | 2666.24 | 2666.24 |  |  |  | 1 | 1 |  |  |  |  | 143103.57 | 2666.24 | 143103.57 | 2666.24 | 9.2766 | [5 empty] | 105.9857 | 2640.9404
17.11.2007 02:00 | 3600 | 2 | 758.87 | GGB | 767.033 | 772.266 | 768.498 | 263.86 | GGB | 11105.6 | GGB | 9.86 | GGB | 1013.27 | GGB | 59.3 | GGB | 174019.52 | GGB | 143003.91 | GGB | 0 | 0 | 2671 | 3600 | 2655.29 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 65151.77 | GGB | 65152.66 | 2655.29 | 2655.29 |  |  |  | 1 | 1 |  |  |  |  | 143003.91 | 2655.29 | 143003.91 | 2655.29 | 9.4598 | [5 empty] | 105.4769 | 2642.7809
17.11.2007 03:00 | 3600 | 2 | 758.82 | GGB | 768.132 | 773.438 | 769.597 | 264.94 | GGB | 11065.8 | GGB | 9.85 | GGB | 1013.79 | GGB | 58.91 | GGB | 175578.69 | GGB | 144527.06 | GGB | 0 | 0 | 2652 | 3600 | 2636.64 | GGB | 100 | GGB | 41.96 | GGB | 41.96 | GGB | 65193.73 | GGB | 65194.62 | 2636.64 | 2636.64 |  |  |  | 1 | 1 |  |  |  |  | 144527.06 | 2636.64 | 144527.06 | 2636.64 | 9.0816 | [5 empty] | 105.8516 | 2614.929
17.11.2007 04:00 | 3600 | 2 | 758.86 | GGB | 765.934 | 771.164 | 767.033 | 264.76 | GGB | 11074.5 | GGB | 9.85 | GGB | 1014.31 | GGB | 59.44 | GGB | 174718.23 | GGB | 143663.08 | GGB | 0 | 0 | 2653 | 3600 | 2637.64 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 65233.88 | GGB | 65234.77 | 2637.64 | 2637.64 |  |  |  | 1 | 1 |  |  |  |  | 143663.08 | 2637.64 | 143663.08 | 2637.64 | 9.4379 | [5 empty] | 105.2587 | 2630.655
17.11.2007 05:00 | 3600 | 2 | 759.16 | GGB | 767.033 | 772.102 | 768.498 | 264.31 | GGB | 11096.4 | GGB | 9.86 | GGB | 1014.97 | GGB | 59.81 | GGB | 174214.28 | GGB | 143185.2 | GGB | 0 | 0 | 2652 | 3600 | 2636.44 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 65273.86 | GGB | 65274.76 | 2636.44 | 2636.44 |  |  |  | 1 | 1 |  |  |  |  | 143185.2 | 2636.44 | 143185.2 | 2636.44 | 9.4398 | [5 empty] | 104.8609
17.11.2007 06:00 | 3600 | 2 | 758.72 | GGB | 767.033 | 773.156 | 769.597 | 265.73 | GGB | 11057.2 | GGB | 9.85 | GGB | 1015.36 | GGB | 59.44 | GGB | 175975.92 | GGB | 144847.55 | GGB | 0 | 0 | 2657 | 3600 | 2641.91 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 65315.1 | GGB | 65316 | 2641.91 | 2641.91 |  |  |  | 1 | 1 |  |  |  |  | 144847.55 | 2641.91 | 144847.55 | 2641.91 | 9.2792 | [5 empty] | 106.2984 | 2609.1432
17.11.2007 07:00 | 3600 | 2 | 759.21 | GGB | 767.033 | 773.156 | 768.498 | 265.59 | GGB | 11063.5 | GGB | 9.86 | GGB | 1016.15 | GGB | 59.26 | GGB | 175775.65 | GGB | 144873.55 | GGB | 0 | 0 | 2635 | 3600 | 2619.85 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 65355.01 | GGB | 65355.91 | 2619.85 | 2619.85 |  |  |  | 1 | 1 |  |  |  |  | 144873.55 | 2619.85 | 144873.55 | 2619.85 | 9.5101 | [5 empty] | 105.4297 | 2608.6749
17.11.2007 08:00 | 3600 | 2 | 759.15 | GGB | 767.033 | 771.961 | 768.498 | 263.89 | GGB | 11113.1 | GGB | 9.86 | GGB | 1016.96 | GGB | 59.79 | GGB | 173930.39 | GGB | 143239.17 | GGB | 0 | 0 | 2663 | 3600 | 2648.1 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 65396.24 | GGB | 65397.13 | 2648.1 | 2648.1 |  |  |  | 1 | 1 |  |  |  |  | 143239.17 | 2648.1 | 143239.17 | 2648.1 | 9.2021 | [5 empty] | 105.3643 | 2638.4403
17.11.2007 09:00 | 3600 | 2 | 758.37 | GGB | 767.033 | 772.242 | 768.498 | 265.77 | GGB | 11112.8 | GGB | 9.84 | GGB | 1018.13 | GGB | 59.07 | GGB | 176911.2 | GGB | 146177.89 | GGB | 0 | 0 | 2692 | 3600 | 2676.4 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 65437.61 | GGB | 65438.51 | 2676.4 | 2676.4 |  |  |  | 1 | 1 |  |  |  |  | 146177.89 | 2676.4 | 146177.89 | 2676.4 | 9.4546 | [5 empty] | 108.6751 | 2585.3978
17.11.2007 10:00 | 3600 | 2 | 759.51 | GGB | 767.033 | 772.875 | 769.597 | 265.25 | GGB | 11163.7 | GGB | 9.87 | GGB | 1018.13 | GGB | 59.15 | GGB | 176507.38 | GGB | 145810.29 | GGB | 0 | 0 | 2656 | 3600 | 2640.89 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 65477.25 | GGB | 65478.15 | 2640.89 | 2640.89 |  |  |  | 1 | 1 |  |  |  |  | 145810.29 | 2640.89 | 145810.29 | 2640.89 | 9.7142 | [5 empty] | 106.9636 | 2591.9158
17.11.2007 11:00 | 3600 | 2 | 758.34 | GGB | 764.469 | 770.742 | 767.033 | 264.67 | GGB | 11132 | GGB | 9.84 | GGB | 1018.19 | GGB | 59.44 | GGB | 176061.74 | GGB | 145324.63 | GGB | 0 | 0 | 2709 | 3600 | 2693.13 | GGB | 100 | GGB | 42.44 | GGB | 42.44 | GGB | 65519.7 | GGB | 65520.59 | 2693.13 | 2693.13 |  |  |  | 1 | 1 |  |  |  |  | 145324.63 | 2693.13 | 145324.63 | 2693.13 | 9.2219 | [5 empty] | 108.7161 | 2600.5778
17.11.2007 12:00 | 3600 | 2 | 759.42 | GGB | 765.934 | 771.867 | 768.132 | 264.44 | GGB | 11162.7 | GGB | 9.87 | GGB | 1018.48 | GGB | 59.31 | GGB | 175764.65 | GGB | 145175.39 | GGB | 0 | 0 | 2663 | 3600 | 2647.9 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 65559.87 | GGB | 65560.76 | 2647.9 | 2647.9 |  |  |  | 1 | 1 |  |  |  |  | 145175.39 | 2647.9 | 145175.39 | 2647.9 | 9.5696 | [5 empty] | 106.7805 | 2603.2511
17.11.2007 13:00 | 3600 | 2 | 759.28 | GGB | 765.934 | 771.844 | 768.498 | 264.21 | GGB | 11140.3 | GGB | 9.86 | GGB | 1018.53 | GGB | 59.29 | GGB | 175555.59 | GGB | 145019.83 | GGB | 0 | 0 | 2662 | 3600 | 2646.69 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 65600.97 | GGB | 65601.86 | 2646.69 | 2646.69 |  |  |  | 1 | 1 |  |  |  |  | 145019.83 | 2646.69 | 145019.83 | 2646.69 | 9.3387 | [5 empty] | 106.6174 | 2606.0436
17.11.2007 14:00 | 3600 | 2 | 758.76 | GGB | 767.033 | 773.039 | 768.498 | 264.55 | GGB | 11113 | GGB | 9.85 | GGB | 1018.65 | GGB | 59.46 | GGB | 176034.23 | GGB | 145358.29 | GGB | 0 | 0 | 2677 | 3600 | 2661.53 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 65641.84 | GGB | 65642.74 | 2661.53 | 2661.53 |  |  |  | 1 | 1 |  |  |  |  | 145358.29 | 2661.53 | 145358.29 | 2661.53 | 9.4637 | [5 empty] | 107.4654 | 2599.9756
17.11.2007 15:00 | 3600 | 2 | 759.12 | GGB | 765.934 | 771.867 | 768.498 | 264.09 | GGB | 11139.2 | GGB | 9.86 | GGB | 1018.78 | GGB | 59.66 | GGB | 175207.88 | GGB | 144607.33 | GGB | 0 | 0 | 2670 | 3600 | 2654.86 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 65682.96 | GGB | 65683.86 | 2654.86 | 2654.86 |  |  |  | 1 | 1 |  |  |  |  | 144607.33 | 2654.86 | 144607.33 | 2654.86 | 9.3364 | [5 empty] | 106.6423 | 2613.4775
17.11.2007 16:00 | 3600 | 2 | 759.25 | GGB | 767.033 | 772.758 | 768.864 | 264.79 | GGB | 11143.7 | GGB | 9.86 | GGB | 1019.17 | GGB | 59.53 | GGB | 175766.85 | GGB | 145178.48 | GGB | 0 | 0 | 2667 | 3600 | 2651.56 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 65723.96 | GGB | 65724.86 | 2651.56 | 2651.56 |  |  |  | 1 | 1 |  |  |  |  | 145178.48 | 2651.56 | 145178.48 | 2651.56 | 9.389 | [5 empty] | 106.9304 | 2603.1957
17.11.2007 17:00 | 3600 | 2 | 758.57 | GGB | 768.132 | 773.695 | 769.963 | 265.3 | GGB | 11120.3 | GGB | 9.85 | GGB | 1019.29 | GGB | 59.41 | GGB | 176501.88 | GGB | 145857.66 | GGB | 0 | 0 | 2688 | 3600 | 2672.22 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 65764.88 | GGB | 65765.78 | 2672.22 | 2672.22 |  |  |  | 1 | 1 |  |  |  |  | 145857.66 | 2672.22 | 145857.66 | 2672.22 | 9.525 | [5 empty] | 108.2677 | 2591.0741
17.11.2007 18:00 | 3600 | 2 | 759.53 | GGB | 767.033 | 772.641 | 768.864 | 264.44 | GGB | 11142.7 | GGB | 9.87 | GGB | 1019.79 | GGB | 59.64 | GGB | 175260.7 | GGB | 144800.21 | GGB | 0 | 0 | 2651 | 3600 | 2636.09 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 65804.65 | GGB | 65805.55 | 2636.09 | 2636.09 |  |  |  | 1 | 1 |  |  |  |  | 144800.21 | 2636.09 | 144800.21 | 2636.09 | 9.5978 | [5 empty] | 106.0296 | 2609.9962
17.11.2007 19:00 | 3600 | 2 | 758.96 | GGB | 767.033 | 772.383 | 768.864 | 264.12 | GGB | 11146.7 | GGB | 9.85 | GGB | 1019.62 | GGB | 59.88 | GGB | 174681.92 | GGB | 144194.92 | GGB | 0 | 0 | 2689 | 3600 | 2673.35 | GGB | 100 | GGB | 42.41 | GGB | 42.41 | GGB | 65847.06 | GGB | 65847.96 | 2673.35 | 2673.35 |  |  |  | 1 | 1 |  |  |  |  | 144194.92 | 2673.35 | 144194.92 | 2673.35 | 9.0894 | [5 empty] | 107.0787 | 2620.9522
17.11.2007 20:00 | 3600 | 2 | 759.1 | GGB | 768.498 | 774.563 | 770.33 | 264.57 | GGB | 11142.6 | GGB | 9.86 | GGB | 1019.74 | GGB | 59.83 | GGB | 175416.94 | GGB | 144841.79 | GGB | 0 | 0 | 2677 | 3600 | 2661.49 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 65887.6 | GGB | 65888.5 | 2661.49 | 2661.49 |  |  |  | 1 | 1 |  |  |  |  | 144841.79 | 2661.49 | 144841.79 | 2661.49 | 9.509 | [5 empty] | 107.0819 | 2609.247
17.11.2007 21:00 | 3600 | 2 | 758.69 | GGB | 767.033 | 772.43 | 768.864 | 265.43 | GGB | 11110.2 | GGB | 9.85 | GGB | 1019.87 | GGB | 59.45 | GGB | 176524.98 | GGB | 145939.63 | GGB | 0 | 0 | 2677 | 3600 | 2661.83 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 65928.3 | GGB | 65929.2 | 2661.83 | 2661.83 |  |  |  | 1 | 1 |  |  |  |  | 145939.63 | 2661.83 | 145939.63 | 2661.83 | 9.5446 | [5 empty] | 107.9074 | 2589.6187
17.11.2007 22:00 | 3600 | 2 | 759.48 | GGB | 767.033 | 772.313 | 768.864 | 264.29 | GGB | 11144.3 | GGB | 9.86 | GGB | 1019.98 | GGB | 59.7 | GGB | 175038.43 | GGB | 144617.54 | GGB | 0 | 0 | 2661 | 3600 | 2646.04 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 65968.34 | GGB | 65969.23 | 2646.04 | 2646.04 |  |  |  | 1 | 1 |  |  |  |  | 144617.54 | 2646.04 | 144617.54 | 2646.04 | 9.5594 | [5 empty] | 106.2955 | 2613.293
17.11.2007 23:00 | 3600 | 2 | 759.06 | GGB | 767.033 | 773.344 | 768.864 | 263.79 | GGB | 11136.2 | GGB | 9.86 | GGB | 1020.15 | GGB | 59.95 | GGB | 174128.45 | GGB | 143784.54 | GGB | 0 | 0 | 2682 | 3600 | 2666.72 | GGB | 100 | GGB | 42.21 | GGB | 42.21 | GGB | 66010.55 | GGB | 66011.44 | 2666.72 | 2666.72 |  |  |  | 1 | 1 |  |  |  |  | 143784.54 | 2666.72 | 143784.54 | 2666.72 | 9.0839 | [5 empty] | 106.5092 | 2628.4328
17.11.2007 24:00 | 3600 | 2 | 758.88 | GGB | 765.934 | 771.188 | 767.766 | 263.52 | GGB | 11128.4 | GGB | 9.85 | GGB | 1020.39 | GGB | 59.74 | GGB | 174217.58 | GGB | 143980.21 | GGB | 0 | 0 | 2688 | 3600 | 2672.37 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 66051.21 | GGB | 66052.1 | 2672.37 | 2672.37 |  |  |  | 1 | 1 |  |  |  |  | 143980.21 | 2672.37 | 143980.21 | 2672.37 | 9.4631 | [5 empty] | 106.8801 | 2624.8607
18.11.2007 01:00 | 3600 | 2 | 758.95 | GGB | 767.033 | 772.195 | 768.864 | 263.77 | GGB | 11145.6 | GGB | 9.86 | GGB | 1020.56 | GGB | 59.7 | GGB | 174534.47 | GGB | 144286.26 | GGB | 0 | 0 | 2696 | 3600 | 2680.74 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 66091.68 | GGB | 66092.57 | 2680.74 | 2680.74 |  |  |  | 1 | 1 |  |  |  |  | 144286.26 | 2680.74 | 144286.26 | 2680.74 | 9.5575 | [5 empty] | 107.4428 | 2619.2931
18.11.2007 02:00 | 3600 | 2 | 758.88 | GGB | 767.033 | 772.266 | 768.864 | 263.78 | GGB | 11149 | GGB | 9.86 | GGB | 1020.65 | GGB | 59.63 | GGB | 174676.42 | GGB | 144446.84 | GGB | 0 | 0 | 2691 | 3600 | 2676.07 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 66132.39 | GGB | 66133.28 | 2676.07 | 2676.07 |  |  |  | 1 | 1 |  |  |  |  | 144446.84 | 2676.07 | 144446.84 | 2676.07 | 9.4952 | [5 empty] | 107.375 | 2616.3812
18.11.2007 03:00 | 3600 | 2 | 758.86 | GGB | 767.033 | 772.266 | 768.864 | 263.79 | GGB | 11145.5 | GGB | 9.85 | GGB | 1021.11 | GGB | 59.76 | GGB | 174629.1 | GGB | 144416.58 | GGB | 0 | 0 | 2698 | 3600 | 2682.73 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 66172.81 | GGB | 66173.7 | 2682.73 | 2682.73 |  |  |  | 1 | 1 |  |  |  |  | 144416.58 | 2682.73 | 144416.58 | 2682.73 | 9.5851 | [5 empty] | 107.6196 | 2616.9294
18.11.2007 04:00 | 3600 | 2 | 758.96 | GGB | 765.934 | 771.492 | 767.766 | 263.84 | GGB | 11157.1 | GGB | 9.86 | GGB | 1020.84 | GGB | 59.47 | GGB | 174852.47 | GGB | 144687.47 | GGB | 0 | 0 | 2697 | 3600 | 2681.17 | GGB | 100 | GGB | 42.17 | GGB | 42.17 | GGB | 66214.97 | GGB | 66215.87 | 2681.17 | 2681.17 |  |  |  | 1 | 1 |  |  |  |  | 144687.47 | 2681.17 | 144687.47 | 2681.17 | 9.1992 | [5 empty] | 107.7588 | 2612.0299
18.11.2007 05:00 | 3600 | 2 | 758.91 | GGB | 765.934 | 772.547 | 768.864 | 263.83 | GGB | 11156.3 | GGB | 9.86 | GGB | 1020.44 | GGB | 59.28 | GGB | 174996.62 | GGB | 144834.13 | GGB | 0 | 0 | 2700 | 3600 | 2684.46 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 66255.43 | GGB | 66256.33 | 2684.46 | 2684.46 |  |  |  | 1 | 1 |  |  |  |  | 144834.13 | 2684.46 | 144834.13 | 2684.46 | 9.6095 | [5 empty] | 108.0004 | 2609.385
18.11.2007 06:00 | 3600 | 2 | 758.86 | GGB | 768.132 | 773.625 | 769.963 | 264.12 | GGB | 11171.1 | GGB | 9.86 | GGB | 1020.68 | GGB | 59.17 | GGB | 175319.01 | GGB | 145179.99 | GGB | 0 | 0 | 2706 | 3600 | 2690.92 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 66296.23 | GGB | 66297.13 | 2690.92 | 2690.92 |  |  |  | 1 | 1 |  |  |  |  | 145179.99 | 2690.92 | 145179.99 | 2690.92 | 9.5752 | [5 empty] | 108.5188 | 2603.1687
18.11.2007 07:00 | 3600 | 2 | 758.18 | GGB | 767.033 | 771.586 | 767.766 | 265.53 | GGB | 11141 | GGB | 9.84 | GGB | 1021.2 | GGB | 58.85 | GGB | 176852.89 | GGB | 146670.45 | GGB | 0 | 0 | 2718 | 3600 | 2703.08 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 66337.23 | GGB | 66338.12 | 2703.08 | 2703.08 |  |  |  | 1 | 1 |  |  |  |  | 146670.45 | 2703.08 | 146670.45 | 2703.08 | 9.6722 | [5 empty] | 110.1283 | 2576.7154
18.11.2007 08:00 | 3600 | 2 | 759.49 | GGB | 765.934 | 771.469 | 767.766 | 264.63 | GGB | 11186.4 | GGB | 9.87 | GGB | 1021.92 | GGB | 59.24 | GGB | 175899.99 | GGB | 145806.96 | GGB | 0 | 0 | 2677 | 3600 | 2661.51 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 66378.54 | GGB | 66379.43 | 2661.51 | 2661.51 |  |  |  | 1 | 1 |  |  |  |  | 145806.96 | 2661.51 | 145806.96 | 2661.51 | 9.394 | [5 empty] | 107.7963 | 2591.975
18.11.2007 09:00 | 3600 | 2 | 758.57 | GGB | 767.033 | 772.641 | 768.864 | 265.42 | GGB | 11165.3 | GGB | 9.85 | GGB | 1022.67 | GGB | 59.41 | GGB | 176291.71 | GGB | 146168.03 | GGB | 0 | 0 | 2715 | 3600 | 2699.65 | GGB | 100 | GGB | 41.25 | GGB | 41.25 | GGB | 66419.79 | GGB | 66420.68 | 2699.65 | 2699.65 |  |  |  | 1 | 1 |  |  |  |  | 146168.03 | 2699.65 | 146168.03 | 2699.65 | 9.5661 | [5 empty] | 109.6118 | 2585.5722
18.11.2007 10:00 | 3600 | 2 | 758.98 | GGB | 764.835 | 770.484 | 767.766 | 264.9 | GGB | 11188 | GGB | 9.86 | GGB | 1022.38 | GGB | 59.45 | GGB | 175754.75 | GGB | 145661.8 | GGB | 0 | 0 | 2707 | 3600 | 2691.35 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 66460.24 | GGB | 66461.13 | 2691.35 | 2691.35 |  |  |  | 1 | 1 |  |  |  |  | 145661.8 | 2691.35 | 145661.8 | 2691.35 | 9.6916 | [5 empty] | 108.8964 | 2594.5581
18.11.2007 11:00 | 3600 | 2 | 759.13 | GGB | 765.934 | 771.75 | 768.864 | 264.65 | GGB | 11184.1 | GGB | 9.86 | GGB | 1022.6 | GGB | 59.65 | GGB | 175645.81 | GGB | 145515.99 | GGB | 0 | 0 | 2703 | 3600 | 2687.49 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 66500.97 | GGB | 66501.86 | 2687.49 | 2687.49 |  |  |  | 1 | 1 |  |  |  |  | 145515.99 | 2687.49 | 145515.99 | 2687.49 | 9.6016 | [5 empty] | 108.6313 | 2597.1579
18.11.2007 12:00 | 3600 | 2 | 759.22 | GGB | 767.033 | 772.922 | 768.864 | 264.34 | GGB | 11170.7 | GGB | 9.86 | GGB | 1022.45 | GGB | 59.72 | GGB | 175051.63 | GGB | 144970.74 | GGB | 0 | 0 | 2697 | 3600 | 2681.65 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 66542.24 | GGB | 66543.12 | 2681.65 | 2681.65 |  |  |  | 1 | 1 |  |  |  |  | 144970.74 | 2681.65 | 144970.74 | 2681.65 | 9.4222 | [5 empty] | 107.9891 | 2606.9261
18.11.2007 13:00 | 3600 | 2 | 759.15 | GGB | 767.033 | 772.828 | 768.864 | 264.31 | GGB | 11152.7 | GGB | 9.86 | GGB | 1022.15 | GGB | 59.83 | GGB | 175116.55 | GGB | 144935.29 | GGB | 0 | 0 | 2693 | 3600 | 2677.23 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 66583.55 | GGB | 66584.43 | 2677.23 | 2677.23 |  |  |  | 1 | 1 |  |  |  |  | 144935.29 | 2677.23 | 144935.29 | 2677.23 | 9.393 | [5 empty] | 107.7848 | 2607.5637
18.11.2007 14:00 | 3600 | 2 | 759.27 | GGB | 768.132 | 773.789 | 769.963 | 264.85 | GGB | 11133.5 | GGB | 9.86 | GGB | 1022.4 | GGB | 59.46 | GGB | 176047.44 | GGB | 145903.52 | GGB | 0 | 0 | 2665 | 3600 | 2649.86 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 66624.39 | GGB | 66625.28 | 2649.86 | 2649.86 |  |  |  | 1 | 1 |  |  |  |  | 145903.52 | 2649.86 | 145903.52 | 2649.86 | 9.4645 | [5 empty] | 107.3955 | 2590.2596
18.11.2007 15:00 | 3600 | 2 | 758.9 | GGB | 765.934 | 771.797 | 768.864 | 264 | GGB | 11137.1 | GGB | 9.85 | GGB | 1022.21 | GGB | 60.03 | GGB | 174722.63 | GGB | 144530.69 | GGB | 0 | 0 | 2690 | 3600 | 2674.94 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 66665.19 | GGB | 66666.07 | 2674.94 | 2674.94 |  |  |  | 1 | 1 |  |  |  |  | 144530.69 | 2674.94 | 144530.69 | 2674.94 | 9.4781 | [5 empty] | 107.3919 | 2614.8633
18.11.2007 16:00 | 3600 | 2 | 758.95 | GGB | 767.033 | 772.734 | 768.864 | 264.43 | GGB | 11144.7 | GGB | 9.86 | GGB | 1022.34 | GGB | 60.09 | GGB | 174630.2 | GGB | 144445.67 | GGB | 0 | 0 | 2690 | 3600 | 2675.08 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 66705.42 | GGB | 66706.3 | 2675.08 | 2675.08 |  |  |  | 1 | 1 |  |  |  |  | 144445.67 | 2675.08 | 144445.67 | 2675.08 | 9.6049 | [5 empty] | 107.3344 | 2616.4024
18.11.2007 17:00 | 3600 | 2 | 759.11 | GGB | 767.033 | 772.734 | 768.864 | 264.38 | GGB | 11144.8 | GGB | 9.86 | GGB | 1022.27 | GGB | 60.13 | GGB | 174710.53 | GGB | 144487.82 | GGB | 0 | 0 | 2691 | 3600 | 2675.52 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 66746.68 | GGB | 66747.56 | 2675.52 | 2675.52 |  |  |  | 1 | 1 |  |  |  |  | 144487.82 | 2675.52 | 144487.82 | 2675.52 | 9.3694 | [5 empty] | 107.3833 | 2615.6392
18.11.2007 18:00 | 3600 | 2 | 759.07 | GGB | 767.033 | 772.805 | 768.864 | 264.53 | GGB | 11150.2 | GGB | 9.86 | GGB | 1021.95 | GGB | 60.13 | GGB | 175024.12 | GGB | 144700.62 | GGB | 0 | 0 | 2689 | 3600 | 2673.82 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 66787.85 | GGB | 66788.73 | 2673.82 | 2673.82 |  |  |  | 1 | 1 |  |  |  |  | 144700.62 | 2673.82 | 144700.62 | 2673.82 | 9.3977 | [5 empty] | 107.4732 | 2611.7925
18.11.2007 19:00 | 3600 | 2 | 758.81 | GGB | 767.033 | 772.852 | 769.963 | 264.49 | GGB | 11148.5 | GGB | 9.85 | GGB | 1021.82 | GGB | 60.04 | GGB | 175043.93 | GGB | 144735.1 | GGB | 0 | 0 | 2701 | 3600 | 2685.47 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 66829.06 | GGB | 66829.94 | 2685.47 | 2685.47 |  |  |  | 1 | 1 |  |  |  |  | 144735.1 | 2685.47 | 144735.1 | 2685.47 | 9.4317 | [5 empty] | 107.9672 | 2611.1703
18.11.2007 20:00 | 3600 | 2 | 758.94 | GGB | 764.835 | 770.906 | 767.766 | 265.09 | GGB | 11144.6 | GGB | 9.85 | GGB | 1022.12 | GGB | 59.82 | GGB | 175624.91 | GGB | 145352.95 | GGB | 0 | 0 | 2689 | 3600 | 2673.35 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 66869.32 | GGB | 66870.2 | 2673.35 | 2673.35 |  |  |  | 1 | 1 |  |  |  |  | 145352.95 | 2673.35 | 145352.95 | 2673.35 | 9.6517 | [5 empty] | 107.9387 | 2600.0711
18.11.2007 21:00 | 3600 | 2 | 758.64 | GGB | 768.132 | 772.828 | 769.963 | 266.07 | GGB | 11139.2 | GGB | 9.85 | GGB | 1022.56 | GGB | 59.4 | GGB | 176922.21 | GGB | 146675.87 | GGB | 0 | 0 | 2711 | 3600 | 2695.29 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 66909.69 | GGB | 66910.58 | 2695.29 | 2695.29 |  |  |  | 1 | 1 |  |  |  |  | 146675.87 | 2695.29 | 146675.87 | 2695.29 | 9.7903 | [5 empty] | 109.815 | 2576.6201
18.11.2007 22:00 | 3600 | 2 | 759.66 | GGB | 767.033 | 772.617 | 769.963 | 265.82 | GGB | 11166.2 | GGB | 9.87 | GGB | 1023.03 | GGB | 59.19 | GGB | 176695.54 | GGB | 146649.86 | GGB | 0 | 0 | 2670 | 3600 | 2654.86 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 66950.57 | GGB | 66951.45 | 2654.86 | 2654.86 |  |  |  | 1 | 1 |  |  |  |  | 146649.86 | 2654.86 | 146649.86 | 2654.86 | 9.5262 | [5 empty] | 108.1486 | 2577.0771
18.11.2007 23:00 | 3600 | 2 | 759.36 | GGB | 767.033 | 772.617 | 768.864 | 264.47 | GGB | 11174.7 | GGB | 9.86 | GGB | 1023.27 | GGB | 59.4 | GGB | 175150.66 | GGB | 145311.4 | GGB | 0 | 0 | 2695 | 3600 | 2679.22 | GGB | 100 | GGB | 41.91 | GGB | 41.91 | GGB | 66992.48 | GGB | 66993.36 | 2679.22 | 2679.22 |  |  |  | 1 | 1 |  |  |  |  | 145311.4 | 2679.22 | 145311.4 | 2679.22 | 9.2895 | [5 empty] | 108.1448 | 2600.8145
18.11.2007 24:00 | 3600 | 2 | 759.07 | GGB | 767.033 | 772.852 | 768.864 | 264.58 | GGB | 11179 | GGB | 9.86 | GGB | 1023.49 | GGB | 59.19 | GGB | 176269.71 | GGB | 146363.15 | GGB | 0 | 0 | 2698 | 3600 | 2682.39 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 67033.24 | GGB | 67034.12 | 2682.39 | 2682.39 |  |  |  | 1 | 1 |  |  |  |  | 146363.15 | 2682.39 | 146363.15 | 2682.39 | 9.6321 | [5 empty] | 109.0564 | 2582.1254
19.11.2007 01:00 | 3600 | 2 | 758.56 | GGB | 768.132 | 772.594 | 769.963 | 266.39 | GGB | 11153 | GGB | 9.84 | GGB | 1023.74 | GGB | 58.82 | GGB | 177699.05 | GGB | 147747.76 | GGB | 0 | 0 | 2719 | 3600 | 2703.99 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 67074.41 | GGB | 67075.29 | 2703.99 | 2703.99 |  |  |  | 1 | 1 |  |  |  |  | 147747.76 | 2703.99 | 147747.76 | 2703.99 | 9.7039 | [5 empty] | 110.9746 | 2557.9271
19.11.2007 02:00 | 3600 | 2 | 758.73 | GGB | 767.033 | 771.727 | 769.963 | 265.68 | GGB | 11214.2 | GGB | 9.86 | GGB | 1023.65 | GGB | 59.27 | GGB | 176546.99 | GGB | 146580.61 | GGB | 0 | 0 | 2737 | 3600 | 2721.29 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 67115.2 | GGB | 67116.08 | 2721.29 | 2721.29 |  |  |  | 1 | 1 |  |  |  |  | 146580.61 | 2721.29 | 146580.61 | 2721.29 | 9.7791 | [5 empty] | 110.8023 | 2578.2946
19.11.2007 03:00 | 3600 | 2 | 758.76 | GGB | 767.033 | 772.828 | 768.864 | 266.68 | GGB | 11216 | GGB | 9.85 | GGB | 1023.63 | GGB | 58.99 | GGB | 177958.72 | GGB | 147874.88 | GGB | 0 | 0 | 2738 | 3600 | 2722.51 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 67155.85 | GGB | 67156.73 | 2722.51 | 2722.51 |  |  |  | 1 | 1 |  |  |  |  | 147874.88 | 2722.51 | 147874.88 | 2722.51 | 9.9038 | [5 empty] | 111.8308 | 2555.7282
19.11.2007 04:00 | 3600 | 2 | 759.12 | GGB | 767.033 | 772.781 | 768.864 | 266.06 | GGB | 11230.4 | GGB | 9.86 | GGB | 1023.61 | GGB | 59.33 | GGB | 177171.98 | GGB | 147067.94 | GGB | 0 | 0 | 2728 | 3600 | 2712.77 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 67197.33 | GGB | 67198.2 | 2712.77 | 2712.77 |  |  |  | 1 | 1 |  |  |  |  | 147067.94 | 2712.77 | 147067.94 | 2712.77 | 9.6205 | [5 empty] | 110.8226 | 2569.7511
19.11.2007 05:00 | 3600 | 2 | 758.74 | GGB | 767.033 | 772.828 | 768.864 | 266.42 | GGB | 11203.4 | GGB | 9.85 | GGB | 1023.71 | GGB | 59.03 | GGB | 177796.98 | GGB | 147731.35 | GGB | 0 | 0 | 2718 | 3600 | 2702.68 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 67238.63 | GGB | 67239.5 | 2702.68 | 2702.68 |  |  |  | 1 | 1 |  |  |  |  | 147731.35 | 2702.68 | 147731.35 | 2702.68 | 9.6676 | [5 empty] | 110.9085 | 2558.2112
19.11.2007 06:00 | 3600 | 2 | 758.38 | GGB | 768.132 | 772.922 | 769.963 | 266.77 | GGB | 11189.9 | GGB | 9.85 | GGB | 1023.69 | GGB | 59.07 | GGB | 178044.55 | GGB | 147916.03 | GGB | 0 | 0 | 2731 | 3171 | 2715.37 | GGB | 100 | GGB | 41.77 | GGB | 41.77 | GGB | 67280.4 | GGB | 67281.27 | 2715.37 | 2715.37 |  |  |  | 1 | 1 |  |  |  |  | 147916.03 | 2715.37 | 147916.03 | 2715.37 | 9.6157 | [5 empty] | 111.5685 | 2555.0172
19.11.2007 07:00 | 3600 | 2 | 759.09 | GGB | 765.934 | 770.695 | 767.766 | 266.29 | GGB | 11213.3 | GGB | 9.86 | GGB | 1023.4 | GGB | 59.12 | GGB | 177372.24 | GGB | 147295.59 | GGB | 0 | 0 | 2713 | 3600 | 2697.71 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 67320.44 | GGB | 67321.31 | 2697.71 | 2697.71 |  |  |  | 1 | 1 |  |  |  |  | 147295.59 | 2697.71 | 147295.59 | 2697.71 | 9.9241 | [5 empty] | 110.378 | 2565.7795
19.11.2007 08:00 | 3600 | 2 | 758.48 | GGB | 767.033 | 773.039 | 769.597 | 267.53 | GGB | 11206.4 | GGB | 9.85 | GGB | 1023.6 | GGB | 59.05 | GGB | 178711.36 | GGB | 148467.7 | GGB | 0 | 0 | 2747 | 3600 | 2732.05 | GGB | 100 | GGB | 41.44 | GGB | 41.44 | GGB | 67361.88 | GGB | 67362.75 | 2732.05 | 2732.05 |  |  |  | 1 | 1 |  |  |  |  | 148467.7 | 2732.05 | 148467.7 | 2732.05 | 9.7882 | [5 empty] | 112.6725 | 2545.5234
19.11.2007 09:00 | 3600 | 2 | 759.09 | GGB | 768.132 | 773.227 | 769.597 | 267.15 | GGB | 11260.7 | GGB | 9.86 | GGB | 1024.08 | GGB | 59.24 | GGB | 178109.47 | GGB | 147950.05 | GGB | 0 | 0 | 2748 | 3600 | 2732.4 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 67402.66 | GGB | 67403.53 | 2732.4 | 2732.4 |  |  |  | 1 | 1 |  |  |  |  | 147950.05 | 2732.4 | 147950.05 | 2732.4 | 9.9132 | [5 empty] | 112.2941 | 2554.4297
19.11.2007 10:00 | 3600 | 2 | 758.76 | GGB | 767.033 | 772.383 | 769.597 | 268.54 | GGB | 11244.5 | GGB | 9.85 | GGB | 1024.74 | GGB | 58.4 | GGB | 180295.84 | GGB | 150246.13 | GGB | 0 | 0 | 2749 | 3600 | 2733.52 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 67443.79 | GGB | 67444.65 | 2733.52 | 2733.52 |  |  |  | 1 | 1 |  |  |  |  | 150246.13 | 2733.52 | 150246.13 | 2733.52 | 9.9879 | [5 empty] | 114.0836 | 2515.3926
19.11.2007 11:00 | 3600 | 2 | 758.86 | GGB | 767.033 | 772.078 | 768.132 | 266.92 | GGB | 11293.9 | GGB | 9.86 | GGB | 1024.7 | GGB | 58.81 | GGB | 178337.24 | GGB | 148425.08 | GGB | 0 | 0 | 2761 | 3600 | 2745.74 | GGB | 100 | GGB | 42.29 | GGB | 42.29 | GGB | 67486.08 | GGB | 67486.94 | 2745.74 | 2745.74 |  |  |  | 1 | 1 |  |  |  |  | 148425.08 | 2745.74 | 148425.08 | 2745.74 | 9.6367 | [5 empty] | 113.2046 | 2546.2543
19.11.2007 12:00 | 3600 | 2 | 758.52 | GGB | 765.934 | 771.914 | 768.132 | 267.18 | GGB | 11258.7 | GGB | 9.85 | GGB | 1024.63 | GGB | 58.6 | GGB | 179433.18 | GGB | 149420.94 | GGB | 0 | 0 | 2761 | 3600 | 2745.9 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 67526.91 | GGB | 67527.78 | 2745.9 | 2745.9 |  |  |  | 1 | 1 |  |  |  |  | 149420.94 | 2745.9 | 149420.94 | 2745.9 | 10.0464 | [5 empty] | 113.9708 | 2529.284
19.11.2007 13:00 | 3600 | 2 | 759.25 | GGB | 765.934 | 771.867 | 768.498 | 266.84 | GGB | 11271 | GGB | 9.87 | GGB | 1024.4 | GGB | 58.7 | GGB | 178925.92 | GGB | 148918.6 | GGB | 0 | 0 | 2731 | 3600 | 2715.72 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 67567.88 | GGB | 67568.74 | 2715.72 | 2715.72 |  |  |  | 1 | 1 |  |  |  |  | 148918.6 | 2715.72 | 148918.6 | 2715.72 | 9.8736 | [5 empty] | 112.3392 | 2537.816
19.11.2007 14:00 | 3600 | 2 | 758.32 | GGB | 767.033 | 772.875 | 769.963 | 267.09 | GGB | 11238.9 | GGB | 9.85 | GGB | 1024.23 | GGB | 58.55 | GGB | 179498.1 | GGB | 149439.86 | GGB | 0 | 0 | 2754 | 3600 | 2738.13 | GGB | 100 | GGB | 41.7 | GGB | 41.7 | GGB | 67609.58 | GGB | 67610.44 | 2738.13 | 2738.13 |  |  |  | 1 | 1 |  |  |  |  | 149439.86 | 2738.13 | 149439.86 | 2738.13 | 9.8126 | [5 empty] | 113.6627 | 2528.9638
19.11.2007 15:00 | 3600 | 2 | 759.26 | GGB | 768.132 | 774.164 | 769.963 | 266.66 | GGB | 11245 | GGB | 9.87 | GGB | 1023.63 | GGB | 58.26 | GGB | 179408.97 | GGB | 149409.03 | GGB | 0 | 0 | 2707 | 3600 | 2691.17 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 67649.95 | GGB | 67650.81 | 2691.17 | 2691.17 |  |  |  | 1 | 1 |  |  |  |  | 149409.03 | 2691.17 | 149409.03 | 2691.17 | 9.96 | [5 empty] | 111.6903 | 2529.4857
19.11.2007 16:00 | 3600 | 2 | 758.43 | GGB | 767.033 | 772.055 | 768.864 | 265.24 | GGB | 11240.1 | GGB | 9.85 | GGB | 1023.25 | GGB | 58.88 | GGB | 177447.07 | GGB | 147443.52 | GGB | 0 | 0 | 2748 | 3600 | 2732.93 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 67691.35 | GGB | 67692.21 | 2732.93 | 2732.93 |  |  |  | 1 | 1 |  |  |  |  | 147443.52 | 2732.93 | 147443.52 | 2732.93 | 9.7332 | [5 empty] | 111.9313 | 2563.2052
19.11.2007 17:00 | 3600 | 2 | 758.59 | GGB | 765.934 | 772.055 | 767.766 | 265.16 | GGB | 11245.2 | GGB | 9.85 | GGB | 1022.7 | GGB | 58.74 | GGB | 177444.87 | GGB | 147423.09 | GGB | 0 | 0 | 2750 | 3600 | 2734.05 | GGB | 100 | GGB | 42.19 | GGB | 42.19 | GGB | 67733.55 | GGB | 67734.4 | 2734.05 | 2734.05 |  |  |  | 1 | 1 |  |  |  |  | 147423.09 | 2734.05 | 147423.09 | 2734.05 | 9.5535 | [5 empty] | 111.9617 | 2563.5604
19.11.2007 18:00 | 3600 | 2 | 758.54 | GGB | 767.033 | 772.055 | 768.864 | 265.44 | GGB | 11249.4 | GGB | 9.85 | GGB | 1022.78 | GGB | 58.65 | GGB | 177760.66 | GGB | 147736.55 | GGB | 0 | 0 | 2755 | 3600 | 2740.01 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 67774.52 | GGB | 67775.37 | 2740.01 | 2740.01 |  |  |  | 1 | 1 |  |  |  |  | 147736.55 | 2740.01 | 147736.55 | 2740.01 | 9.8804 | [5 empty] | 112.4443 | 2558.1212
19.11.2007 19:00 | 3600 | 2 | 758.61 | GGB | 765.934 | 771.961 | 767.766 | 265.58 | GGB | 11252.2 | GGB | 9.85 | GGB | 1022.39 | GGB | 58.64 | GGB | 177795.87 | GGB | 147717.42 | GGB | 0 | 0 | 2756 | 3600 | 2740.77 | GGB | 100 | GGB | 41.45 | GGB | 41.45 | GGB | 67815.96 | GGB | 67816.82 | 2740.77 | 2740.77 |  |  |  | 1 | 1 |  |  |  |  | 147717.42 | 2740.77 | 147717.42 | 2740.77 | 9.7674 | [5 empty] | 112.461 | 2558.4525
19.11.2007 20:00 | 3600 | 2 | 758.42 | GGB | 767.033 | 771.844 | 768.864 | 265.99 | GGB | 11260.3 | GGB | 9.85 | GGB | 1022.85 | GGB | 58.56 | GGB | 178158.99 | GGB | 148117.57 | GGB | 0 | 0 | 2766 | 3600 | 2750.11 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 67856.46 | GGB | 67857.32 | 2750.11 | 2750.11 |  |  |  | 1 | 1 |  |  |  |  | 148117.57 | 2750.11 | 148117.57 | 2750.11 | 10.0578 | [5 empty] | 113.1499 | 2551.5406
19.11.2007 21:00 | 3600 | 2 | 758.41 | GGB | 763.37 | 769.828 | 765.201 | 265.94 | GGB | 11275.1 | GGB | 9.85 | GGB | 1023.04 | GGB | 58.51 | GGB | 178669.54 | GGB | 148591.99 | GGB | 0 | 0 | 2766 | 3600 | 2750.99 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 67897.59 | GGB | 67898.45 | 2750.99 | 2750.99 |  |  |  | 0 | 1 | [14 empty] | 113.5486 | 2543.3942
19.11.2007 22:00 | 3600 | 2 | 758.1 | GGB | 765.934 | 772.148 | 767.766 | 267.09 | GGB | 11278.7 | GGB | 9.85 | GGB | 1022.81 | GGB | 58.51 | GGB | 178955.63 | GGB | 148797.45 | GGB | 0 | 0 | 2794 | 3600 | 2779.02 | GGB | 100 | GGB | 41.9 | GGB | 41.9 | GGB | 67939.49 | GGB | 67940.35 | 2779.02 | 2779.02 |  |  |  | 1 | 1 |  |  |  |  | 148797.45 | 2779.02 | 148797.45 | 2779.02 | 9.869 | [5 empty] | 114.8642 | 2539.8822
19.11.2007 23:00 | 3600 | 2 | 758.17 | GGB | 767.033 | 772.195 | 768.864 | 268.12 | GGB | 11268 | GGB | 9.85 | GGB | 1022.9 | GGB | 58.16 | GGB | 180188.01 | GGB | 149992.8 | GGB | 0 | 0 | 2779 | 3600 | 2763.55 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 67979.76 | GGB | 67980.63 | 2763.55 | 2763.55 |  |  |  | 1 | 1 |  |  |  |  | 149992.8 | 2763.55 | 149992.8 | 2763.55 | 10.2908 | [5 empty] | 115.1424 | 2519.6409
19.11.2007 24:00 | 3600 | 2 | 758.68 | GGB | 765.934 | 771.094 | 767.766 | 267.84 | GGB | 11294.9 | GGB | 9.86 | GGB | 1022.69 | GGB | 57.93 | GGB | 179726.97 | GGB | 149683.47 | GGB | 0 | 0 | 2766 | 3600 | 2750.79 | GGB | 100 | GGB | 42.55 | GGB | 42.55 | GGB | 68022.32 | GGB | 68023.18 | 2750.79 | 2750.79 |  |  |  | 1 | 1 |  |  |  |  | 149683.47 | 2750.79 | 149683.47 | 2750.79 | 9.6768 | [5 empty] | 114.3744 | 2524.8479
20.11.2007 01:00 | 3600 | 2 | 758.58 | GGB | 767.033 | 772.148 | 768.864 | 267.19 | GGB | 11311.7 | GGB | 9.86 | GGB | 1022.47 | GGB | 57.84 | GGB | 179061.26 | GGB | 149140.31 | GGB | 0 | 0 | 2782 | 3600 | 2766.82 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 68063.11 | GGB | 68063.98 | 2766.82 | 2766.82 |  |  |  | 1 | 1 |  |  |  |  | 149140.31 | 2766.82 | 149140.31 | 2766.82 | 10.1138 | [5 empty] | 114.6234 | 2534.0433
20.11.2007 02:00 | 3600 | 2 | 758.42 | GGB | 765.934 | 772.172 | 768.864 | 267.28 | GGB | 11311.7 | GGB | 9.85 | GGB | 1022.63 | GGB | 57.88 | GGB | 179267.03 | GGB | 149313.24 | GGB | 0 | 0 | 2787 | 3600 | 2771.76 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 68104.51 | GGB | 68105.38 | 2771.76 | 2771.76 |  |  |  | 1 | 1 |  |  |  |  | 149313.24 | 2771.76 | 149313.24 | 2771.76 | 9.9966 | [5 empty] | 114.9612 | 2531.1084
20.11.2007 03:00 | 3600 | 2 | 758.11 | GGB | 767.033 | 772.594 | 768.864 | 267.4 | GGB | 11305.8 | GGB | 9.85 | GGB | 1022.63 | GGB | 57.85 | GGB | 179346.25 | GGB | 149392.93 | GGB | 0 | 0 | 2807 | 3600 | 2791.37 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 68145.82 | GGB | 68146.69 | 2791.37 | 2791.37 |  |  |  | 1 | 1 |  |  |  |  | 149392.93 | 2791.37 | 149392.93 | 2791.37 | 10.0947 | [5 empty] | 115.8364 | 2529.7583
20.11.2007 04:00 | 3600 | 2 | 758.78 | GGB | 767.033 | 772.664 | 768.864 | 267.19 | GGB | 11318.9 | GGB | 9.86 | GGB | 1022.52 | GGB | 57.98 | GGB | 179202.11 | GGB | 149201.48 | GGB | 0 | 0 | 2771 | 3600 | 2755.38 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 68187.05 | GGB | 68187.92 | 2755.38 | 2755.38 |  |  |  | 1 | 1 |  |  |  |  | 149201.48 | 2755.38 | 149201.48 | 2755.38 | 9.9711 | [5 empty] | 114.1963 | 2533.0044
20.11.2007 05:00 | 3600 | 2 | 758.4 | GGB | 764.835 | 769.992 | 767.766 | 266.97 | GGB | 11295.4 | GGB | 9.85 | GGB | 1022.02 | GGB | 58.13 | GGB | 178975.44 | GGB | 148871.14 | GGB | 0 | 0 | 2781 | 3600 | 2765.26 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 68228.32 | GGB | 68229.19 | 2765.26 | 2765.26 |  |  |  | 1 | 1 |  |  |  |  | 148871.14 | 2765.26 | 148871.14 | 2765.26 | 9.975 | [5 empty] | 114.3521 | 2538.625
20.11.2007 06:00 | 3600 | 2 | 758.43 | GGB | 765.934 | 771.281 | 767.766 | 267.05 | GGB | 11299.9 | GGB | 9.86 | GGB | 1022.12 | GGB | 58.19 | GGB | 178920.42 | GGB | 148812.48 | GGB | 0 | 0 | 2781 | 3600 | 2766.02 | GGB | 100 | GGB | 41.44 | GGB | 41.44 | GGB | 68269.76 | GGB | 68270.63 | 2766.02 | 2766.02 |  |  |  | 1 | 1 |  |  |  |  | 148812.48 | 2766.02 | 148812.48 | 2766.02 | 9.9329 | [5 empty] | 114.3384 | 2539.6257
20.11.2007 07:00 | 3600 | 2 | 758.45 | GGB | 765.934 | 771.328 | 767.033 | 266.87 | GGB | 11291.3 | GGB | 9.86 | GGB | 1021.84 | GGB | 58.19 | GGB | 178833.49 | GGB | 148700.77 | GGB | 0 | 0 | 2776 | 3600 | 2760.59 | GGB | 100 | GGB | 42.16 | GGB | 42.16 | GGB | 68311.92 | GGB | 68312.79 | 2760.59 | 2760.59 |  |  |  | 1 | 1 |  |  |  |  | 148700.77 | 2760.59 | 148700.77 | 2760.59 | 9.7368 | [5 empty] | 114.0283 | 2541.5336
20.11.2007 08:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 772.313 | 768.498 | 267.81 | GGB | 11282.9 | GGB | 9.85 | GGB | 1021.82 | GGB | 57.86 | GGB | 180112.09 | GGB | 149908.05 | GGB | 0 | 0 | 2780 | 3600 | 2764.87 | GGB | 100 | GGB | 41.58 | GGB | 41.58 | GGB | 68353.5 | GGB | 68354.37 | 2764.87 | 2764.87 |  |  |  | 1 | 1 |  |  |  |  | 149908.05 | 2764.87 | 149908.05 | 2764.87 | 9.9682 | [5 empty] | 115.1323 | 2521.0654
20.11.2007 09:00 | 3600 | 2 | 758.13 | GGB | 765.934 | 772.195 | 768.132 | 267.14 | GGB | 11303.5 | GGB | 9.86 | GGB | 1021.88 | GGB | 58.16 | GGB | 179174.6 | GGB | 149003.29 | GGB | 0 | 0 | 2792 | 3600 | 2776.88 | GGB | 100 | GGB | 41.46 | GGB | 41.46 | GGB | 68394.96 | GGB | 68395.83 | 2776.88 | 2776.88 |  |  |  | 1 | 1 |  |  |  |  | 149003.29 | 2776.88 | 149003.29 | 2776.88 | 9.9798 | [5 empty] | 114.9345 | 2536.3735
20.11.2007 10:00 | 3600 | 2 | 758.11 | GGB | 765.934 | 772.266 | 768.132 | 267.09 | GGB | 11307.2 | GGB | 9.85 | GGB | 1022.28 | GGB | 58.17 | GGB | 178950.13 | GGB | 148870.18 | GGB | 0 | 0 | 2798 | 3600 | 2782.27 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 68435.87 | GGB | 68436.74 | 2782.27 | 2782.27 |  |  |  | 1 | 1 |  |  |  |  | 148870.18 | 2782.27 | 148870.18 | 2782.27 | 10.1246 | [5 empty] | 115.0547 | 2538.6414
20.11.2007 11:00 | 3600 | 2 | 758.22 | GGB | 764.469 | 770.203 | 767.033 | 267.02 | GGB | 11299.9 | GGB | 9.85 | GGB | 1023.36 | GGB | 58.15 | GGB | 178965.53 | GGB | 149047.54 | GGB | 0 | 0 | 2796 | 3600 | 2780.11 | GGB | 100 | GGB | 41.92 | GGB | 41.92 | GGB | 68477.79 | GGB | 68478.66 | 2780.11 | 2780.11 |  |  |  | 1 | 1 |  |  |  |  | 149047.54 | 2780.11 | 149047.54 | 2780.11 | 9.8847 | [5 empty] | 115.1024 | 2535.6205
20.11.2007 12:00 | 3600 | 2 | 758.32 | GGB | 765.934 | 771.281 | 767.033 | 267.19 | GGB | 11305.9 | GGB | 9.86 | GGB | 1023.52 | GGB | 58.3 | GGB | 179169.1 | GGB | 149173.84 | GGB | 0 | 0 | 2792 | 3600 | 2776.77 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 68518.43 | GGB | 68519.29 | 2776.77 | 2776.77 |  |  |  | 1 | 1 |  |  |  |  | 149173.84 | 2776.77 | 149173.84 | 2776.77 | 10.195 | [5 empty] | 115.0615 | 2533.4737
20.11.2007 13:00 | 3600 | 2 | 758.01 | GGB | 765.934 | 771.305 | 768.498 | 267.43 | GGB | 11311 | GGB | 9.86 | GGB | 1023.58 | GGB | 58.28 | GGB | 179144.89 | GGB | 149173.42 | GGB | 0 | 0 | 2806 | 3600 | 2790.99 | GGB | 100 | GGB | 41.68 | GGB | 41.68 | GGB | 68560.11 | GGB | 68560.97 | 2790.99 | 2790.99 |  |  |  | 1 | 1 |  |  |  |  | 149173.42 | 2790.99 | 149173.42 | 2790.99 | 9.989 | [5 empty] | 115.6504 | 2533.4808
20.11.2007 14:00 | 3600 | 2 | 758.03 | GGB | 765.934 | 770.484 | 768.132 | 267.35 | GGB | 11311.6 | GGB | 9.85 | GGB | 1023.23 | GGB | 58.28 | GGB | 179166.9 | GGB | 149138.83 | GGB | 0 | 0 | 2815 | 3600 | 2799.21 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 68601.41 | GGB | 68602.27 | 2799.21 | 2799.21 |  |  |  | 1 | 1 |  |  |  |  | 149138.83 | 2799.21 | 149138.83 | 2799.21 | 10.1083 | [5 empty] | 115.9641 | 2534.0684
20.11.2007 15:00 | 3600 | 2 | 758.75 | GGB | 765.934 | 772.688 | 768.498 | 267.11 | GGB | 11308.5 | GGB | 9.87 | GGB | 1023.08 | GGB | 58.16 | GGB | 178977.64 | GGB | 149011.27 | GGB | 0 | 0 | 2780 | 3600 | 2764.62 | GGB | 100 | GGB | 42.07 | GGB | 42.07 | GGB | 68643.48 | GGB | 68644.34 | 2764.62 | 2764.62 |  |  |  | 1 | 1 |  |  |  |  | 149011.27 | 2764.62 | 149011.27 | 2764.62 | 9.7922 | [5 empty] | 114.4332 | 2536.2377
20.11.2007 16:00 | 3600 | 2 | 758.31 | GGB | 765.934 | 771.398 | 767.766 | 266.97 | GGB | 11257.1 | GGB | 9.85 | GGB | 1023.07 | GGB | 58.11 | GGB | 179401.27 | GGB | 149385.02 | GGB | 0 | 0 | 2770 | 3600 | 2754.51 | GGB | 100 | GGB | 41.77 | GGB | 41.77 | GGB | 68685.25 | GGB | 68686.11 | 2754.51 | 2754.51 |  |  |  | 1 | 1 |  |  |  |  | 149385.02 | 2754.51 | 149385.02 | 2754.51 | 9.8511 | [5 empty] | 114.3007 | 2529.8922
20.11.2007 17:00 | 3600 | 2 | 759.13 | GGB | 767.033 | 773.578 | 768.864 | 266.66 | GGB | 11283.7 | GGB | 9.87 | GGB | 1023.07 | GGB | 57.94 | GGB | 178979.84 | GGB | 149113.83 | GGB | 0 | 0 | 2743 | 3600 | 2727.75 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 68725.42 | GGB | 68726.28 | 2727.75 | 2727.75 |  |  |  | 1 | 1 |  |  |  |  | 149113.83 | 2727.75 | 149113.83 | 2727.75 | 10.1256 | [5 empty] | 112.9848 | 2534.4933
20.11.2007 18:00 | 3600 | 2 | 758.24 | GGB | 765.934 | 771.609 | 767.766 | 266.64 | GGB | 11275.6 | GGB | 9.85 | GGB | 1023.22 | GGB | 58.23 | GGB | 178354.85 | GGB | 148483.71 | GGB | 0 | 0 | 2785 | 3600 | 2769.85 | GGB | 100 | GGB | 41.91 | GGB | 41.91 | GGB | 68767.33 | GGB | 68768.19 | 2769.85 | 2769.85 |  |  |  | 1 | 1 |  |  |  |  | 148483.71 | 2769.85 | 148483.71 | 2769.85 | 9.8134 | [5 empty] | 114.2438 | 2545.2489
20.11.2007 19:00 | 3600 | 2 | 758.08 | GGB | 765.934 | 771.586 | 767.766 | 266.93 | GGB | 11284.2 | GGB | 9.85 | GGB | 1023.15 | GGB | 58.19 | GGB | 178554.01 | GGB | 148657.66 | GGB | 0 | 0 | 2800 | 3600 | 2784.77 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 68808.26 | GGB | 68809.12 | 2784.77 | 2784.77 |  |  |  | 1 | 1 |  |  |  |  | 148657.66 | 2784.77 | 148657.66 | 2784.77 | 10.1143 | [5 empty] | 114.9937 | 2542.2706
20.11.2007 20:00 | 3600 | 2 | 758.44 | GGB | 767.033 | 772.664 | 768.864 | 266.95 | GGB | 11285.7 | GGB | 9.86 | GGB | 1023.22 | GGB | 58.25 | GGB | 178112.77 | GGB | 148274.07 | GGB | 0 | 0 | 2794 | 3600 | 2778.16 | GGB | 100 | GGB | 42 | GGB | 42 | GGB | 68850.26 | GGB | 68851.12 | 2778.16 | 2778.16 |  |  |  | 1 | 1 |  |  |  |  | 148274.07 | 2778.16 | 148274.07 | 2778.16 | 9.8078 | [5 empty] | 114.4247 | 2548.8475
20.11.2007 21:00 | 3600 | 2 | 758.21 | GGB | 767.033 | 771.539 | 768.864 | 267.34 | GGB | 11260.6 | GGB | 9.85 | GGB | 1023.58 | GGB | 58.52 | GGB | 177834.39 | GGB | 147971.69 | GGB | 0 | 0 | 2803 | 3600 | 2787.05 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 68891.66 | GGB | 68892.52 | 2787.05 | 2787.05 |  |  |  | 1 | 1 |  |  |  |  | 147971.69 | 2787.05 | 147971.69 | 2787.05 | 9.9615 | [5 empty] | 114.5568 | 2554.0561
20.11.2007 22:00 | 3600 | 2 | 758.46 | GGB | 765.934 | 772.734 | 768.864 | 267.31 | GGB | 11251.8 | GGB | 9.86 | GGB | 1023.64 | GGB | 58.85 | GGB | 177328.23 | GGB | 147414.43 | GGB | 0 | 0 | 2780 | 3600 | 2764.66 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 68932.17 | GGB | 68933.03 | 2764.66 | 2764.66 |  |  |  | 1 | 1 |  |  |  |  | 147414.43 | 2764.66 | 147414.43 | 2764.66 | 10.0605 | [5 empty] | 113.2085 | 2563.711
20.11.2007 23:00 | 3600 | 2 | 758.34 | GGB | 764.469 | 770.695 | 766.3 | 266.71 | GGB | 11243.8 | GGB | 9.85 | GGB | 1023.39 | GGB | 58.72 | GGB | 177639.63 | GGB | 147694.25 | GGB | 0 | 0 | 2778 | 3600 | 2762.45 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 68973.15 | GGB | 68974 | 2762.45 | 2762.45 |  |  |  | 1 | 1 |  |  |  |  | 147694.25 | 2762.45 | 147694.25 | 2762.45 | 9.9585 | [5 empty] | 113.3328 | 2558.8538
20.11.2007 24:00 | 3600 | 2 | 758.37 | GGB | 767.033 | 772.641 | 768.864 | 267.66 | GGB | 11239.6 | GGB | 9.85 | GGB | 1023.4 | GGB | 58.98 | GGB | 177735.36 | GGB | 147660.27 | GGB | 0 | 0 | 2778 | 3600 | 2762.29 | GGB | 100 | GGB | 41.67 | GGB | 41.67 | GGB | 69014.82 | GGB | 69015.67 | 2762.29 | 2762.29 |  |  |  | 1 | 1 |  |  |  |  | 147660.27 | 2762.29 | 147660.27 | 2762.29 | 9.7883 | [5 empty] | 113.3001 | 2559.4427
21.11.2007 01:00 | 3600 | 2 | 758.55 | GGB | 763.37 | 769.57 | 765.201 | 268.03 | GGB | 11250.8 | GGB | 9.85 | GGB | 1023.42 | GGB | 58.79 | GGB | 178339.44 | GGB | 148248.26 | GGB | 0 | 0 | 2779 | 3600 | 2763.79 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 69054.95 | GGB | 69055.8 | 2763.79 | 2763.79 |  |  |  | 0 | 1 | [14 empty] | 113.8131 | 2549.2913
21.11.2007 02:00 | 3600 | 2 | 758.8 | GGB | 765.934 | 771.586 | 767.766 | 268.33 | GGB | 11276.6 | GGB | 9.86 | GGB | 1023.31 | GGB | 58.86 | GGB | 178458.28 | GGB | 148301.54 | GGB | 0 | 0 | 2778 | 3600 | 2762.16 | GGB | 100 | GGB | 41.74 | GGB | 41.74 | GGB | 69096.68 | GGB | 69097.54 | 2762.16 | 2762.16 |  |  |  | 1 | 1 |  |  |  |  | 148301.54 | 2762.16 | 148301.54 | 2762.16 | 9.8139 | [5 empty] | 113.7868 | 2548.3754
21.11.2007 03:00 | 3600 | 2 | 758.9 | GGB | 765.934 | 771.539 | 767.766 | 268.5 | GGB | 11283.4 | GGB | 9.86 | GGB | 1023.01 | GGB | 58.81 | GGB | 178842.3 | GGB | 148596.86 | GGB | 0 | 0 | 2777 | 3600 | 2761.91 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 69137.56 | GGB | 69138.42 | 2761.91 | 2761.91 |  |  |  | 1 | 1 |  |  |  |  | 148596.86 | 2761.91 | 148596.86 | 2761.91 | 10.0394 | [5 empty] | 114.0031 | 2543.3108
21.11.2007 04:00 | 3600 | 2 | 758.24 | GGB | 765.934 | 771.586 | 767.766 | 269.42 | GGB | 11273.4 | GGB | 9.84 | GGB | 1022.95 | GGB | 58.42 | GGB | 179907.42 | GGB | 149651.88 | GGB | 0 | 0 | 2803 | 3600 | 2787.56 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 69178.68 | GGB | 69179.54 | 2787.56 | 2787.56 |  |  |  | 1 | 1 |  |  |  |  | 149651.88 | 2787.56 | 149651.88 | 2787.56 | 10.145 | [5 empty] | 115.8788 | 2525.3809
21.11.2007 05:00 | 3600 | 2 | 759 | GGB | 765.934 | 771.75 | 767.766 | 270.26 | GGB | 11311.1 | GGB | 9.86 | GGB | 1023.03 | GGB | 58.08 | GGB | 180877.92 | GGB | 150624.79 | GGB | 0 | 0 | 2770 | 3600 | 2754.7 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 69219.82 | GGB | 69220.67 | 2754.7 | 2754.7 |  |  |  | 1 | 1 |  |  |  |  | 150624.79 | 2754.7 | 150624.79 | 2754.7 | 10.0882 | [5 empty] | 115.2573 | 2509.0691
21.11.2007 06:00 | 3600 | 2 | 758.34 | GGB | 765.934 | 771.797 | 767.766 | 269.99 | GGB | 11324.5 | GGB | 9.85 | GGB | 1023.03 | GGB | 58.26 | GGB | 180473 | GGB | 150206.22 | GGB | 0 | 0 | 2816 | 3600 | 2800.03 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 69261.22 | GGB | 69262.07 | 2800.03 | 2800.03 |  |  |  | 1 | 1 |  |  |  |  | 150206.22 | 2800.03 | 150206.22 | 2800.03 | 10.159 | [5 empty] | 116.8283 | 2516.0609
21.11.2007 07:00 | 3600 | 2 | 758.65 | GGB | 768.132 | 772.805 | 769.963 | 271.09 | GGB | 11318.9 | GGB | 9.86 | GGB | 1023.17 | GGB | 57.47 | GGB | 182346.87 | GGB | 152149.43 | GGB | 0 | 0 | 2789 | 3600 | 2773.97 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 69302.35 | GGB | 69303.2 | 2773.97 | 2773.97 |  |  |  | 1 | 1 |  |  |  |  | 152149.43 | 2773.97 | 152149.43 | 2773.97 | 10.2616 | [5 empty] | 117.2383 | 2483.9265
21.11.2007 08:00 | 3600 | 2 | 758.81 | GGB | 765.934 | 771.633 | 767.766 | 269.36 | GGB | 11351.1 | GGB | 9.86 | GGB | 1022.78 | GGB | 58.09 | GGB | 180094.48 | GGB | 149929.25 | GGB | 0 | 0 | 2801 | 3600 | 2785.59 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 69343.82 | GGB | 69344.67 | 2785.59 | 2785.59 |  |  |  | 1 | 1 |  |  |  |  | 149929.25 | 2785.59 | 149929.25 | 2785.59 | 10.0709 | [5 empty] | 116.0115 | 2520.7089
21.11.2007 09:00 | 3600 | 2 | 758.57 | GGB | 765.934 | 771.609 | 767.766 | 269.15 | GGB | 11340 | GGB | 9.86 | GGB | 1022.77 | GGB | 58.07 | GGB | 180117.59 | GGB | 149957.07 | GGB | 0 | 0 | 2815 | 3600 | 2799.48 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 69384.73 | GGB | 69385.58 | 2799.48 | 2799.48 |  |  |  | 1 | 1 |  |  |  |  | 149957.07 | 2799.48 | 149957.07 | 2799.48 | 10.2616 | [5 empty] | 116.6116 | 2520.2413
21.11.2007 10:00 | 3600 | 2 | 758.58 | GGB | 765.934 | 771.797 | 768.864 | 268.82 | GGB | 11334.7 | GGB | 9.86 | GGB | 1022.75 | GGB | 58.15 | GGB | 179510.2 | GGB | 149411.06 | GGB | 0 | 0 | 2808 | 3600 | 2792.55 | GGB | 100 | GGB | 41.92 | GGB | 41.92 | GGB | 69426.64 | GGB | 69427.5 | 2792.55 | 2792.55 |  |  |  | 1 | 1 |  |  |  |  | 149411.06 | 2792.55 | 149411.06 | 2792.55 | 9.9532 | [5 empty] | 115.8994 | 2529.4513
21.11.2007 11:00 | 3600 | 2 | 757.79 | GGB | 764.835 | 771.727 | 767.766 | 268.61 | GGB | 11313.5 | GGB | 9.86 | GGB | 1022.99 | GGB | 58.3 | GGB | 179381.46 | GGB | 149271.54 | GGB | 0 | 0 | 2808 | 3600 | 2792.54 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 69467.64 | GGB | 69468.5 | 2792.54 | 2792.54 |  |  |  | 1 | 1 |  |  |  |  | 149271.54 | 2792.54 | 149271.54 | 2792.54 | 10.167 | [5 empty] | 115.7908 | 2531.8155
21.11.2007 12:00 | 3600 | 2 | 757.89 | GGB | 765.934 | 770.672 | 768.864 | 268.07 | GGB | 11295.6 | GGB | 9.86 | GGB | 1022.7 | GGB | 58.42 | GGB | 178947.93 | GGB | 148814.89 | GGB | 0 | 0 | 2787 | 3600 | 2771.61 | GGB | 100 | GGB | 42.33 | GGB | 42.33 | GGB | 69509.97 | GGB | 69510.83 | 2771.61 | 2771.61 |  |  |  | 1 | 1 |  |  |  |  | 148814.89 | 2771.61 | 148814.89 | 2771.61 | 9.7438 | [5 empty] | 114.5713 | 2539.5846
21.11.2007 13:00 | 3600 | 2 | 757.41 | GGB | 767.033 | 773.063 | 768.864 | 269.3 | GGB | 11245.6 | GGB | 9.85 | GGB | 1022.32 | GGB | 58.07 | GGB | 180273.84 | GGB | 150022.33 | GGB | 0 | 0 | 2793 | 3600 | 2777.76 | GGB | 100 | GGB | 41.43 | GGB | 41.43 | GGB | 69551.4 | GGB | 69552.26 | 2777.76 | 2777.76 |  |  |  | 1 | 1 |  |  |  |  | 150022.33 | 2777.76 | 150022.33 | 2777.76 | 10.0586 | [5 empty] | 115.7572 | 2519.145
21.11.2007 14:00 | 3600 | 2 | 758.24 | GGB | 765.934 | 771.492 | 768.864 | 268.38 | GGB | 11284.3 | GGB | 9.87 | GGB | 1021.69 | GGB | 58.2 | GGB | 179053.56 | GGB | 148855.06 | GGB | 0 | 0 | 2771 | 3600 | 2755.88 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 69591.88 | GGB | 69592.74 | 2755.88 | 2755.88 |  |  |  | 1 | 1 |  |  |  |  | 148855.06 | 2755.88 | 148855.06 | 2755.88 | 10.1341 | [5 empty] | 113.9519 | 2538.8992
21.11.2007 15:00 | 3600 | 2 | 757.62 | GGB | 764.835 | 770.297 | 767.033 | 268.14 | GGB | 11245.4 | GGB | 9.86 | GGB | 1021.48 | GGB | 58.39 | GGB | 178594.72 | GGB | 148358.86 | GGB | 0 | 0 | 2785 | 3600 | 2769.76 | GGB | 100 | GGB | 41.53 | GGB | 41.53 | GGB | 69633.41 | GGB | 69634.27 | 2769.76 | 2769.76 |  |  |  | 1 | 1 |  |  |  |  | 148358.86 | 2769.76 | 148358.86 | 2769.76 | 9.8945 | [5 empty] | 114.144 | 2547.3908
21.11.2007 16:00 | 3600 | 2 | 757.74 | GGB | 765.934 | 772.359 | 768.498 | 269.15 | GGB | 11211.2 | GGB | 9.86 | GGB | 1020.98 | GGB | 57.98 | GGB | 179973.44 | GGB | 149614.27 | GGB | 0 | 0 | 2759 | 3600 | 2743.29 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 69674.21 | GGB | 69675.08 | 2743.29 | 2743.29 |  |  |  | 1 | 1 |  |  |  |  | 149614.27 | 2743.29 | 149614.27 | 2743.29 | 10.0572 | [5 empty] | 114.0098 | 2526.0157
21.11.2007 17:00 | 3600 | 2 | 758 | GGB | 765.934 | 771.164 | 768.132 | 268.14 | GGB | 11225.8 | GGB | 9.86 | GGB | 1020.62 | GGB | 58.38 | GGB | 178654.14 | GGB | 148287.3 | GGB | 0 | 0 | 2758 | 3600 | 2742.35 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 69714.62 | GGB | 69715.49 | 2742.35 | 2742.35 |  |  |  | 1 | 1 |  |  |  |  | 148287.3 | 2742.35 | 148287.3 | 2742.35 | 10.0632 | [5 empty] | 112.9599 | 2548.6201
21.11.2007 18:00 | 3600 | 2 | 757.68 | GGB | 765.934 | 772.336 | 768.498 | 267.63 | GGB | 11242.3 | GGB | 9.85 | GGB | 1020.62 | GGB | 58.62 | GGB | 178002.74 | GGB | 147640.57 | GGB | 0 | 0 | 2782 | 3600 | 2766.07 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 69756.27 | GGB | 69757.13 | 2766.07 | 2766.07 |  |  |  | 1 | 1 |  |  |  |  | 147640.57 | 2766.07 | 147640.57 | 2766.07 | 9.8075 | [5 empty] | 113.44 | 2559.7842
21.11.2007 19:00 | 3600 | 2 | 758.06 | GGB | 767.033 | 773.25 | 768.498 | 269.25 | GGB | 11207 | GGB | 9.85 | GGB | 1020.41 | GGB | 58.12 | GGB | 180025.16 | GGB | 149512.02 | GGB | 0 | 0 | 2743 | 3600 | 2727.91 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 69796.5 | GGB | 69797.37 | 2727.91 | 2727.91 |  |  |  | 1 | 1 |  |  |  |  | 149512.02 | 2727.91 | 149512.02 | 2727.91 | 10.1356 | [5 empty] | 113.2931 | 2527.7433
21.11.2007 20:00 | 3600 | 2 | 758.56 | GGB | 765.934 | 772.008 | 768.498 | 267.91 | GGB | 11229.1 | GGB | 9.86 | GGB | 1019.97 | GGB | 58.5 | GGB | 178281.12 | GGB | 147828.5 | GGB | 0 | 0 | 2729 | 3600 | 2713.58 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 69837.46 | GGB | 69838.33 | 2713.58 | 2713.58 |  |  |  | 1 | 1 |  |  |  |  | 147828.5 | 2713.58 | 147828.5 | 2713.58 | 9.7936 | [5 empty] | 111.429 | 2556.53
21.11.2007 21:00 | 3600 | 2 | 758.15 | GGB | 765.934 | 771.164 | 767.033 | 267.38 | GGB | 11213.3 | GGB | 9.86 | GGB | 1019.47 | GGB | 58.72 | GGB | 177474.58 | GGB | 146992.98 | GGB | 0 | 0 | 2745 | 3600 | 2729.61 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 69878.54 | GGB | 69879.4 | 2729.61 | 2729.61 |  |  |  | 1 | 1 |  |  |  |  | 146992.98 | 2729.61 | 146992.98 | 2729.61 | 9.7695 | [5 empty] | 111.4538 | 2571.0616
21.11.2007 22:00 | 3600 | 2 | 757.99 | GGB | 765.934 | 771.047 | 767.033 | 268.78 | GGB | 11168.9 | GGB | 9.85 | GGB | 1019.52 | GGB | 58.35 | GGB | 179357.25 | GGB | 148725.52 | GGB | 0 | 0 | 2737 | 3600 | 2721.49 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 69918.94 | GGB | 69919.81 | 2721.49 | 2721.49 |  |  |  | 1 | 1 |  |  |  |  | 148725.52 | 2721.49 | 148725.52 | 2721.49 | 10.0162 | [5 empty] | 112.4319 | 2541.1106
21.11.2007 23:00 | 3600 | 2 | 758.72 | GGB | 763.37 | 770.227 | 765.934 | 266.41 | GGB | 11226.5 | GGB | 9.87 | GGB | 1018.95 | GGB | 58.68 | GGB | 177135.67 | GGB | 146652.55 | GGB | 0 | 0 | 2723 | 3600 | 2707.81 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 69959.88 | GGB | 69960.75 | 2707.81 | 2707.81 |  |  |  | 0 | 1 | [14 empty] | 110.3076 | 2577.0299
21.11.2007 24:00 | 3600 | 2 | 757.48 | GGB | 765.934 | 771.258 | 768.132 | 267.98 | GGB | 11182 | GGB | 9.84 | GGB | 1018.96 | GGB | 58.38 | GGB | 178734.46 | GGB | 148111.77 | GGB | 0 | 0 | 2766 | 3600 | 2750.52 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 70000.98 | GGB | 70001.85 | 2750.52 | 2750.52 |  |  |  | 1 | 1 |  |  |  |  | 148111.77 | 2750.52 | 148111.77 | 2750.52 | 9.912 | [5 empty] | 113.1623 | 2551.6406
22.11.2007 01:00 | 3600 | 2 | 758.61 | GGB | 768.498 | 774.305 | 770.696 | 268.43 | GGB | 11211.5 | GGB | 9.87 | GGB | 1018.42 | GGB | 58.24 | GGB | 179506.9 | GGB | 148735.24 | GGB | 0 | 0 | 2719 | 3600 | 2703.22 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 70041.12 | GGB | 70042 | 2703.22 | 2703.22 |  |  |  | 1 | 1 |  |  |  |  | 148735.24 | 2703.22 | 148735.24 | 2703.22 | 10.014 | [5 empty] | 111.6845 | 2540.9446
22.11.2007 02:00 | 3600 | 2 | 758.29 | GGB | 767.033 | 772.383 | 768.498 | 267.03 | GGB | 11219.5 | GGB | 9.86 | GGB | 1017.65 | GGB | 58.79 | GGB | 177500.98 | GGB | 146717.57 | GGB | 0 | 0 | 2744 | 3600 | 2728.81 | GGB | 100 | GGB | 41.73 | GGB | 41.73 | GGB | 70082.85 | GGB | 70083.73 | 2728.81 | 2728.81 |  |  |  | 1 | 1 |  |  |  |  | 146717.57 | 2728.81 | 146717.57 | 2728.81 | 9.5942 | [5 empty] | 111.2123 | 2575.8878
22.11.2007 03:00 | 3600 | 2 | 758.08 | GGB | 767.033 | 772.688 | 769.597 | 266.98 | GGB | 11216.7 | GGB | 9.86 | GGB | 1017.78 | GGB | 58.9 | GGB | 177605.52 | GGB | 146776.1 | GGB | 0 | 0 | 2766 | 3600 | 2750.25 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 70122.99 | GGB | 70123.87 | 2750.25 | 2750.25 |  |  |  | 1 | 1 |  |  |  |  | 146776.1 | 2750.25 | 146776.1 | 2750.25 | 10.0566 | [5 empty] | 112.1308 | 2574.8606
22.11.2007 04:00 | 3600 | 2 | 757.91 | GGB | 765.934 | 771.586 | 768.132 | 266.78 | GGB | 11217.8 | GGB | 9.85 | GGB | 1017.31 | GGB | 58.74 | GGB | 177576.91 | GGB | 146755.24 | GGB | 0 | 0 | 2763 | 3600 | 2747.75 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 70164.31 | GGB | 70165.19 | 2747.75 | 2747.75 |  |  |  | 1 | 1 |  |  |  |  | 146755.24 | 2747.75 | 146755.24 | 2747.75 | 9.7591 | [5 empty] | 112.013 | 2575.2266
22.11.2007 05:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 771.727 | 768.132 | 266.7 | GGB | 11212.1 | GGB | 9.86 | GGB | 1016.75 | GGB | 58.65 | GGB | 177417.36 | GGB | 146581.24 | GGB | 0 | 0 | 2747 | 3600 | 2731.95 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 70205.18 | GGB | 70206.07 | 2731.95 | 2731.95 |  |  |  | 1 | 1 |  |  |  |  | 146581.24 | 2731.95 | 146581.24 | 2731.95 | 9.7958 | [5 empty] | 111.2368 | 2578.2836
22.11.2007 06:00 | 3600 | 2 | 758.17 | GGB | 765.934 | 771.633 | 768.132 | 266.58 | GGB | 11204.1 | GGB | 9.86 | GGB | 1016.41 | GGB | 58.69 | GGB | 177368.94 | GGB | 146475.75 | GGB | 0 | 0 | 2749 | 3600 | 2733.07 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 70245.84 | GGB | 70246.73 | 2733.07 | 2733.07 |  |  |  | 1 | 1 |  |  |  |  | 146475.75 | 2733.07 | 146475.75 | 2733.07 | 9.8458 | [5 empty] | 111.2024 | 2580.1404
22.11.2007 07:00 | 3600 | 2 | 757.99 | GGB | 767.033 | 772.875 | 769.597 | 266.34 | GGB | 11203 | GGB | 9.86 | GGB | 1016 | GGB | 58.52 | GGB | 177243.51 | GGB | 146388.54 | GGB | 0 | 0 | 2744 | 3600 | 2729.06 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 70286.95 | GGB | 70287.84 | 2729.06 | 2729.06 |  |  |  | 1 | 1 |  |  |  |  | 146388.54 | 2729.06 | 146388.54 | 2729.06 | 9.7179 | [5 empty] | 110.9731 | 2581.6775
22.11.2007 08:00 | 3600 | 2 | 757.91 | GGB | 765.934 | 771.891 | 768.132 | 266.37 | GGB | 11200.1 | GGB | 9.85 | GGB | 1016.26 | GGB | 58.65 | GGB | 177108.16 | GGB | 146258.37 | GGB | 0 | 0 | 2748 | 3600 | 2732.85 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 70327.38 | GGB | 70328.27 | 2732.85 | 2732.85 |  |  |  | 1 | 1 |  |  |  |  | 146258.37 | 2732.85 | 146258.37 | 2732.85 | 9.8863 | [5 empty] | 111.0284 | 2583.9752
22.11.2007 09:00 | 3600 | 2 | 758.19 | GGB | 764.835 | 771.703 | 768.132 | 266.16 | GGB | 11210.7 | GGB | 9.86 | GGB | 1016.12 | GGB | 58.61 | GGB | 177383.25 | GGB | 146480.78 | GGB | 0 | 0 | 2738 | 3600 | 2722.18 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 70368.56 | GGB | 70369.45 | 2722.18 | 2722.18 |  |  |  | 1 | 1 |  |  |  |  | 146480.78 | 2722.18 | 146480.78 | 2722.18 | 9.683 | [5 empty] | 110.7631 | 2580.0518
22.11.2007 10:00 | 3600 | 2 | 758.09 | GGB | 767.033 | 772.688 | 769.597 | 267.06 | GGB | 11177.2 | GGB | 9.85 | GGB | 1016.11 | GGB | 58.18 | GGB | 178827.99 | GGB | 147866.08 | GGB | 0 | 0 | 2724 | 3600 | 2709.03 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 70409.41 | GGB | 70410.3 | 2709.03 | 2709.03 |  |  |  | 1 | 1 |  |  |  |  | 147866.08 | 2709.03 | 147866.08 | 2709.03 | 9.806 | [5 empty] | 111.2705 | 2555.8803
22.11.2007 11:00 | 3600 | 2 | 758.94 | GGB | 768.498 | 775.313 | 772.161 | 267.21 | GGB | 11182.9 | GGB | 9.87 | GGB | 1016.06 | GGB | 58.01 | GGB | 179019.45 | GGB | 148092.68 | GGB | 0 | 0 | 2674 | 3600 | 2658.51 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 70450.09 | GGB | 70450.98 | 2658.51 | 2658.51 |  |  |  | 1 | 1 |  |  |  |  | 148092.68 | 2658.51 | 148092.68 | 2658.51 | 9.6781 | [5 empty] | 109.3627 | 2551.9695
22.11.2007 12:00 | 3600 | 2 | 758 | GGB | 765.934 | 772.289 | 768.498 | 266.1 | GGB | 11156.7 | GGB | 9.86 | GGB | 1015.35 | GGB | 58.4 | GGB | 177865.2 | GGB | 146861.02 | GGB | 0 | 0 | 2694 | 3600 | 2678.21 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 70490.7 | GGB | 70491.59 | 2678.21 | 2678.21 |  |  |  | 1 | 1 |  |  |  |  | 146861.02 | 2678.21 | 146861.02 | 2678.21 | 9.6854 | [5 empty] | 109.2568 | 2573.3717
22.11.2007 13:00 | 3600 | 2 | 757.51 | GGB | 765.934 | 771.375 | 767.033 | 265.39 | GGB | 11131.9 | GGB | 9.85 | GGB | 1014.98 | GGB | 58.92 | GGB | 176594.31 | GGB | 145532.28 | GGB | 0 | 0 | 2709 | 3600 | 2693.27 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 70531.7 | GGB | 70532.59 | 2693.27 | 2693.27 |  |  |  | 1 | 1 |  |  |  |  | 145532.28 | 2693.27 | 145532.28 | 2693.27 | 9.5599 | [5 empty] | 108.8771 | 2596.8672
22.11.2007 14:00 | 3600 | 2 | 758.34 | GGB | 767.033 | 772.43 | 768.498 | 265.94 | GGB | 11108.5 | GGB | 9.86 | GGB | 1015.08 | GGB | 58.62 | GGB | 177403.05 | GGB | 146342.52 | GGB | 0 | 0 | 2659 | 3600 | 2643.44 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 70571.82 | GGB | 70572.72 | 2643.44 | 2643.44 |  |  |  | 1 | 1 |  |  |  |  | 146342.52 | 2643.44 | 146342.52 | 2643.44 | 9.6399 | [5 empty] | 107.4577 | 2582.4894
22.11.2007 15:00 | 3600 | 2 | 758.47 | GGB | 764.835 | 771.586 | 767.766 | 264.96 | GGB | 11113.6 | GGB | 9.86 | GGB | 1014.58 | GGB | 58.93 | GGB | 175967.11 | GGB | 144951.28 | GGB | 0 | 0 | 2659 | 3600 | 2643.29 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 70612.73 | GGB | 70613.63 | 2643.29 | 2643.29 |  |  |  | 1 | 1 |  |  |  |  | 144951.28 | 2643.29 | 144951.28 | 2643.29 | 9.3656 | [5 empty] | 106.4301 | 2607.276
22.11.2007 16:00 | 3600 | 2 | 757.88 | GGB | 767.033 | 773.766 | 769.963 | 265.24 | GGB | 11100.4 | GGB | 9.85 | GGB | 1014.17 | GGB | 59 | GGB | 176226.79 | GGB | 145076.56 | GGB | 0 | 0 | 2695 | 3600 | 2679.45 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 70653.24 | GGB | 70654.13 | 2679.45 | 2679.45 |  |  |  | 1 | 1 |  |  |  |  | 145076.56 | 2679.45 | 145076.56 | 2679.45 | 9.5982 | [5 empty] | 107.9793 | 2605.0245
22.11.2007 17:00 | 3600 | 2 | 758.15 | GGB | 765.934 | 771.398 | 768.498 | 265.18 | GGB | 11102.6 | GGB | 9.85 | GGB | 1014.29 | GGB | 59.14 | GGB | 176127.76 | GGB | 144949.36 | GGB | 0 | 0 | 2679 | 3600 | 2663.78 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 70693.4 | GGB | 70694.29 | 2663.78 | 2663.78 |  |  |  | 1 | 1 |  |  |  |  | 144949.36 | 2663.78 | 144949.36 | 2663.78 | 9.6144 | [5 empty] | 107.2537 | 2607.3106
22.11.2007 18:00 | 3600 | 2 | 758.44 | GGB | 767.033 | 773.531 | 769.597 | 265.92 | GGB | 11102.8 | GGB | 9.86 | GGB | 1014.3 | GGB | 58.77 | GGB | 177212.7 | GGB | 146007.8 | GGB | 0 | 0 | 2660 | 3600 | 2645 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 70734.12 | GGB | 70735.01 | 2645 | 2645 |  |  |  | 1 | 1 |  |  |  |  | 146007.8 | 2645 | 146007.8 | 2645 | 9.4841 | [5 empty] | 107.2752 | 2588.4097
22.11.2007 19:00 | 3600 | 2 | 758.49 | GGB | 764.835 | 771.328 | 767.033 | 264.49 | GGB | 11118.9 | GGB | 9.86 | GGB | 1014.22 | GGB | 59.27 | GGB | 175228.79 | GGB | 144144.13 | GGB | 0 | 0 | 2670 | 3600 | 2655.05 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 70774.59 | GGB | 70775.48 | 2655.05 | 2655.05 |  |  |  | 1 | 1 |  |  |  |  | 144144.13 | 2655.05 | 144144.13 | 2655.05 | 9.4566 | [5 empty] | 106.3083 | 2621.8758
22.11.2007 20:00 | 3600 | 2 | 758.14 | GGB | 765.934 | 770.719 | 768.132 | 265.24 | GGB | 11110.2 | GGB | 9.85 | GGB | 1014.66 | GGB | 58.97 | GGB | 176112.36 | GGB | 145065.85 | GGB | 0 | 0 | 2689 | 3600 | 2673.94 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 70814.78 | GGB | 70815.67 | 2673.94 | 2673.94 |  |  |  | 1 | 1 |  |  |  |  | 145065.85 | 2673.94 | 145065.85 | 2673.94 | 9.6516 | [5 empty] | 107.7493 | 2605.2169
22.11.2007 21:00 | 3600 | 2 | 758.4 | GGB | 767.033 | 772.898 | 769.597 | 265.77 | GGB | 11116.7 | GGB | 9.86 | GGB | 1014.47 | GGB | 58.59 | GGB | 177047.65 | GGB | 145977.62 | GGB | 0 | 0 | 2679 | 3600 | 2663.17 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 70855.88 | GGB | 70856.76 | 2663.17 | 2663.17 |  |  |  | 1 | 1 |  |  |  |  | 145977.62 | 2663.17 | 145977.62 | 2663.17 | 9.4613 | [5 empty] | 107.9898 | 2588.9448
22.11.2007 22:00 | 3600 | 2 | 758.14 | GGB | 764.835 | 770.742 | 767.033 | 264.18 | GGB | 11144.7 | GGB | 9.86 | GGB | 1014.51 | GGB | 58.92 | GGB | 175530.28 | GGB | 144587.77 | GGB | 0 | 0 | 2701 | 3600 | 2685.74 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 70896.02 | GGB | 70896.91 | 2685.74 | 2685.74 |  |  |  | 1 | 1 |  |  |  |  | 144587.77 | 2685.74 | 144587.77 | 2685.74 | 9.6719 | [5 empty] | 107.8681 | 2613.831
22.11.2007 23:00 | 3600 | 2 | 758.11 | GGB | 765.934 | 772.102 | 768.498 | 266.25 | GGB | 11097.2 | GGB | 9.85 | GGB | 1014.43 | GGB | 58.68 | GGB | 177357.94 | GGB | 146187.56 | GGB | 0 | 0 | 2685 | 3600 | 2669.74 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 70937.04 | GGB | 70937.93 | 2669.74 | 2669.74 |  |  |  | 1 | 1 |  |  |  |  | 146187.56 | 2669.74 | 146187.56 | 2669.74 | 9.5145 | [5 empty] | 108.4119 | 2585.2268
22.11.2007 24:00 | 3600 | 2 | 758.89 | GGB | 767.033 | 773.109 | 768.864 | 264.64 | GGB | 11119.2 | GGB | 9.87 | GGB | 1013.82 | GGB | 59.21 | GGB | 175497.27 | GGB | 144334.37 | GGB | 0 | 0 | 2660 | 3600 | 2644.92 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 70976.49 | GGB | 70977.37 | 2644.92 | 2644.92 |  |  |  | 1 | 1 |  |  |  |  | 144334.37 | 2644.92 | 144334.37 | 2644.92 | 9.6793 | [5 empty] | 106.0425 | 2618.42
23.11.2007 01:00 | 3600 | 2 | 758.27 | GGB | 767.033 | 772.031 | 768.864 | 263.62 | GGB | 11105.7 | GGB | 9.86 | GGB | 1013.6 | GGB | 59.57 | GGB | 174186.77 | GGB | 143070.28 | GGB | 0 | 0 | 2687 | 3600 | 2671.2 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 71017.75 | GGB | 71018.63 | 2671.2 | 2671.2 |  |  |  | 1 | 1 |  |  |  |  | 143070.28 | 2671.2 | 143070.28 | 2671.2 | 9.2625 | [5 empty] | 106.1581 | 2641.5549
23.11.2007 02:00 | 3600 | 2 | 758.29 | GGB | 765.934 | 772.008 | 768.864 | 263.51 | GGB | 11097.5 | GGB | 9.86 | GGB | 1013.38 | GGB | 59.53 | GGB | 174142.75 | GGB | 143022.95 | GGB | 0 | 0 | 2682 | 3600 | 2666.39 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 71057.56 | GGB | 71058.44 | 2666.39 | 2666.39 |  |  |  | 1 | 1 |  |  |  |  | 143022.95 | 2666.39 | 143022.95 | 2666.39 | 9.5794 | [5 empty] | 105.9319 | 2642.4291
23.11.2007 03:00 | 3600 | 2 | 758.24 | GGB | 765.934 | 772.078 | 768.864 | 263.58 | GGB | 11094.9 | GGB | 9.86 | GGB | 1013.3 | GGB | 59.6 | GGB | 174196.67 | GGB | 143022.5 | GGB | 0 | 0 | 2683 | 3600 | 2667.91 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 71098.76 | GGB | 71099.65 | 2667.91 | 2667.91 |  |  |  | 1 | 1 |  |  |  |  | 143022.5 | 2667.91 | 143022.5 | 2667.91 | 9.2592 | [5 empty] | 105.992 | 2642.4374
23.11.2007 04:00 | 3600 | 2 | 758.2 | GGB | 765.934 | 773.32 | 768.864 | 263.67 | GGB | 11088.3 | GGB | 9.85 | GGB | 1013.04 | GGB | 59.66 | GGB | 174197.77 | GGB | 142961.44 | GGB | 0 | 0 | 2685 | 3600 | 2669.64 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 71138.6 | GGB | 71139.48 | 2669.64 | 2669.64 |  |  |  | 1 | 1 |  |  |  |  | 142961.44 | 2669.64 | 142961.44 | 2669.64 | 9.5821 | [5 empty] | 106.0154 | 2643.566
23.11.2007 05:00 | 3600 | 2 | 758.18 | GGB | 765.934 | 772.102 | 768.864 | 263.62 | GGB | 11079.8 | GGB | 9.85 | GGB | 1012.72 | GGB | 59.77 | GGB | 173906.18 | GGB | 142629.5 | GGB | 0 | 0 | 2684 | 3600 | 2668.7 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 71179.88 | GGB | 71180.77 | 2668.7 | 2668.7 |  |  |  | 1 | 1 |  |  |  |  | 142629.5 | 2668.7 | 142629.5 | 2668.7 | 9.2186 | [5 empty] | 105.732 | 2649.7183
23.11.2007 06:00 | 3600 | 2 | 758.25 | GGB | 767.033 | 773.133 | 769.597 | 263.71 | GGB | 11083.1 | GGB | 9.86 | GGB | 1012.53 | GGB | 59.74 | GGB | 174061.33 | GGB | 142742.09 | GGB | 0 | 0 | 2681 | 3600 | 2665.57 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 71219.55 | GGB | 71220.44 | 2665.57 | 2665.57 |  |  |  | 1 | 1 |  |  |  |  | 142742.09 | 2665.57 | 142742.09 | 2665.57 | 9.5914 | [5 empty] | 105.6914 | 2647.6283
23.11.2007 07:00 | 3600 | 2 | 758.57 | GGB | 765.934 | 772.031 | 768.498 | 263.53 | GGB | 11081.4 | GGB | 9.86 | GGB | 1011.61 | GGB | 59.71 | GGB | 173910.58 | GGB | 142506.38 | GGB | 0 | 0 | 2668 | 3600 | 2652.15 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 71260.57 | GGB | 71261.46 | 2652.15 | 2652.15 |  |  |  | 1 | 1 |  |  |  |  | 142506.38 | 2652.15 | 142506.38 | 2652.15 | 9.2138 | [5 empty] | 104.9856 | 2652.0076
23.11.2007 08:00 | 3600 | 2 | 758.25 | GGB | 765.934 | 772.055 | 768.864 | 264.3 | GGB | 11056.2 | GGB | 9.85 | GGB | 1011.23 | GGB | 59.16 | GGB | 175098.95 | GGB | 143661.36 | GGB | 0 | 0 | 2682 | 3208 | 2666.12 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 71300.33 | GGB | 71301.23 | 2666.12 | 2666.12 |  |  |  | 1 | 1 |  |  |  |  | 143661.36 | 2666.12 | 143661.36 | 2666.12 | 9.6308 | [5 empty] | 106.394 | 2630.6865
23.11.2007 09:00 | 3600 | 2 | 758.49 | GGB | 767.033 | 772.641 | 768.864 | 263.24 | GGB | 11090.8 | GGB | 9.86 | GGB | 1012.03 | GGB | 59.5 | GGB | 174161.46 | GGB | 142860.83 | GGB | 0 | 0 | 2694 | 3600 | 2678.1 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 71340.88 | GGB | 71341.77 | 2678.1 | 2678.1 |  |  |  | 1 | 1 |  |  |  |  | 142860.83 | 2678.1 | 142860.83 | 2678.1 | 9.4375 | [5 empty] | 106.2766 | 2645.4277
23.11.2007 10:00 | 3600 | 2 | 758.28 | GGB | 767.033 | 772.523 | 769.597 | 263.88 | GGB | 11074.1 | GGB | 9.85 | GGB | 1011.95 | GGB | 59 | GGB | 175760.25 | GGB | 144377.41 | GGB | 0 | 0 | 2685 | 3600 | 2669.71 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 71381.79 | GGB | 71382.69 | 2669.71 | 2669.71 |  |  |  | 1 | 1 |  |  |  |  | 144377.41 | 2669.71 | 144377.41 | 2669.71 | 9.4195 | [5 empty] | 107.0683 | 2617.6394
23.11.2007 11:00 | 3600 | 2 | 758.7 | GGB | 765.934 | 771.281 | 768.132 | 263.66 | GGB | 11069.4 | GGB | 9.86 | GGB | 1012.41 | GGB | 58.56 | GGB | 176144.27 | GGB | 144949.88 | GGB | 0 | 0 | 2651 | 3600 | 2636.06 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 71422.16 | GGB | 71423.06 | 2636.06 | 2636.06 |  |  |  | 1 | 1 |  |  |  |  | 144949.88 | 2636.06 | 144949.88 | 2636.06 | 9.4649 | [5 empty] | 106.1379 | 2607.3012
23.11.2007 12:00 | 3600 | 2 | 758.1 | GGB | 765.934 | 772.266 | 767.766 | 263.38 | GGB | 11061.2 | GGB | 9.86 | GGB | 1011.82 | GGB | 58.53 | GGB | 176077.15 | GGB | 144825.05 | GGB | 0 | 0 | 2641 | 3600 | 2625.72 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 71462.55 | GGB | 71463.45 | 2625.72 | 2625.72 |  |  |  | 1 | 1 |  |  |  |  | 144825.05 | 2625.72 | 144825.05 | 2625.72 | 9.415 | [5 empty] | 105.6306 | 2609.5486
23.11.2007 13:00 | 3600 | 2 | 758.17 | GGB | 767.033 | 773.414 | 768.498 | 262.61 | GGB | 11034.6 | GGB | 9.86 | GGB | 1010.23 | GGB | 58.4 | GGB | 175420.25 | GGB | 144111.6 | GGB | 0 | 0 | 2634 | 3600 | 2618.33 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 71502.88 | GGB | 71503.77 | 2618.33 | 2618.33 |  |  |  | 1 | 1 |  |  |  |  | 144111.6 | 2618.33 | 144111.6 | 2618.33 | 9.3584 | [5 empty] | 104.8144
23.11.2007 14:00 | 3600 | 2 | 758.09 | GGB | 765.934 | 772.523 | 768.132 | 262.35 | GGB | 11015.9 | GGB | 9.86 | GGB | 1009.41 | GGB | 58.48 | GGB | 175144.06 | GGB | 143736.71 | GGB | 0 | 0 | 2628 | 3600 | 2612.27 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 71543.12 | GGB | 71544.02 | 2612.27 | 2612.27 |  |  |  | 1 | 1 |  |  |  |  | 143736.71 | 2612.27 | 143736.71 | 2612.27 | 9.3287 | [5 empty] | 104.2997
23.11.2007 15:00 | 3600 | 2 | 757.95 | GGB | 767.033 | 772.5 | 768.498 | 262.38 | GGB | 11012.9 | GGB | 9.86 | GGB | 1009.68 | GGB | 58.57 | GGB | 174961.4 | GGB | 143585.42 | GGB | 0 | 0 | 2627 | 3600 | 2612.02 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 71583.33 | GGB | 71584.23 | 2612.02 | 2612.02 |  |  |  | 1 | 1 |  |  |  |  | 143585.42 | 2612.02 | 143585.42 | 2612.02 | 9.3272 | [5 empty] | 104.18
23.11.2007 16:00 | 3600 | 2 | 758.19 | GGB | 767.033 | 772.523 | 769.597 | 262.72 | GGB | 11018.9 | GGB | 9.86 | GGB | 1010.25 | GGB | 58.62 | GGB | 175210.08 | GGB | 143844.6 | GGB | 0 | 0 | 2637 | 3600 | 2621.42 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 71623.59 | GGB | 71624.49 | 2621.42 | 2621.42 |  |  |  | 1 | 1 |  |  |  |  | 143844.6 | 2621.42 | 143844.6 | 2621.42 | 9.366 | [5 empty] | 104.7436
23.11.2007 17:00 | 3600 | 2 | 757.74 | GGB | 765.934 | 771.164 | 768.132 | 263.18 | GGB | 11025 | GGB | 9.85 | GGB | 1010.84 | GGB | 58.6 | GGB | 175555.59 | GGB | 144222.16 | GGB | 0 | 0 | 2656 | 3600 | 2640.35 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 71663.7 | GGB | 71664.6 | 2640.35 | 2640.35 |  |  |  | 1 | 1 |  |  |  |  | 144222.16 | 2640.35 | 144222.16 | 2640.35 | 9.4938 | [5 empty] | 105.7769 | 2620.4572
23.11.2007 18:00 | 3600 | 2 | 758.11 | GGB | 765.934 | 772.453 | 768.132 | 263.4 | GGB | 11040 | GGB | 9.86 | GGB | 1010.98 | GGB | 58.67 | GGB | 175666.72 | GGB | 144302.97 | GGB | 0 | 0 | 2650 | 3600 | 2634.44 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 71704.12 | GGB | 71705.01 | 2634.44 | 2634.44 |  |  |  | 1 | 1 |  |  |  |  | 144302.97 | 2634.44 | 144302.97 | 2634.44 | 9.4075 | [5 empty] | 105.5993 | 2618.9898
23.11.2007 19:00 | 3600 | 2 | 758.35 | GGB | 765.934 | 771.328 | 768.132 | 261.7 | GGB | 11061.6 | GGB | 9.86 | GGB | 1010.43 | GGB | 59.28 | GGB | 173591.48 | GGB | 142259.4 | GGB | 0 | 0 | 2657 | 3600 | 2642.09 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 71743.96 | GGB | 71744.86 | 2642.09 | 2642.09 |  |  |  | 1 | 1 |  |  |  |  | 142259.4 | 2642.09 | 142259.4 | 2642.09 | 9.4319 | [5 empty] | 104.4061
23.11.2007 20:00 | 3600 | 2 | 757.99 | GGB | 765.934 | 772.406 | 768.132 | 261.36 | GGB | 11055.2 | GGB | 9.86 | GGB | 1010.52 | GGB | 59.68 | GGB | 172986.3 | GGB | 141608.7 | GGB | 0 | 0 | 2668 | 3600 | 2653.07 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 71784.44 | GGB | 71785.34 | 2653.07 | 2653.07 |  |  |  | 1 | 1 |  |  |  |  | 141608.7 | 2653.07 | 141608.7 | 2653.07 | 9.2811 | [5 empty] | 104.3605
23.11.2007 21:00 | 3600 | 2 | 758.05 | GGB | 765.934 | 771.375 | 768.132 | 261.28 | GGB | 11042.5 | GGB | 9.86 | GGB | 1010.81 | GGB | 59.83 | GGB | 172620.99 | GGB | 141283.62 | GGB | 0 | 0 | 2670 | 3600 | 2654.87 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 71824.59 | GGB | 71825.49 | 2654.87 | 2654.87 |  |  |  | 1 | 1 |  |  |  |  | 141283.62 | 2654.87 | 141283.62 | 2654.87 | 9.3422 | [5 empty] | 104.1916
23.11.2007 22:00 | 3600 | 2 | 758.17 | GGB | 765.934 | 772.406 | 768.132 | 261.26 | GGB | 11039.7 | GGB | 9.86 | GGB | 1010.89 | GGB | 59.94 | GGB | 172466.94 | GGB | 141123.66 | GGB | 0 | 0 | 2663 | 3600 | 2647.21 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 71864.4 | GGB | 71865.3 | 2647.21 | 2647.21 |  |  |  | 1 | 1 |  |  |  |  | 141123.66 | 2647.21 | 141123.66 | 2647.21 | 9.3842 | [5 empty] | 103.7733
23.11.2007 23:00 | 3600 | 2 | 757.98 | GGB | 768.132 | 773.25 | 770.696 | 262.12 | GGB | 11015.7 | GGB | 9.85 | GGB | 1011.21 | GGB | 59.45 | GGB | 174492.66 | GGB | 143034.79 | GGB | 0 | 0 | 2655 | 3600 | 2639.87 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 71904.66 | GGB | 71905.57 | 2639.87 | 2639.87 |  |  |  | 1 | 1 |  |  |  |  | 143034.79 | 2639.87 | 143034.79 | 2639.87 | 9.3765 | [5 empty] | 104.887
23.11.2007 24:00 | 3600 | 2 | 758.3 | GGB | 767.033 | 773.227 | 769.597 | 262.46 | GGB | 11020.4 | GGB | 9.86 | GGB | 1011.39 | GGB | 58.99 | GGB | 174335.31 | GGB | 143131.22 | GGB | 0 | 0 | 2642 | 3600 | 2626.61 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 71944.74 | GGB | 71945.65 | 2626.61 | 2626.61 |  |  |  | 1 | 1 |  |  |  |  | 143131.22 | 2626.61 | 143131.22 | 2626.61 | 9.38 | [5 empty] | 104.4305
24.11.2007 01:00 | 3600 | 2 | 758.29 | GGB | 765.934 | 771.234 | 768.132 | 261.13 | GGB | 11046.8 | GGB | 9.86 | GGB | 1011.24 | GGB | 59.72 | GGB | 172721.12 | GGB | 141471.98 | GGB | 0 | 0 | 2670 | 3600 | 2654.15 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 71984.43 | GGB | 71985.34 | 2654.15 | 2654.15 |  |  |  | 1 | 1 |  |  |  |  | 141471.98 | 2654.15 | 141471.98 | 2654.15 | 9.4605 | [5 empty] | 104.3022
24.11.2007 02:00 | 3600 | 2 | 757.76 | GGB | 764.835 | 771.117 | 767.033 | 261.92 | GGB | 11027.1 | GGB | 9.85 | GGB | 1011.59 | GGB | 59.21 | GGB | 173736.73 | GGB | 142571.72 | GGB | 0 | 0 | 2681 | 3600 | 2665.35 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 72025.35 | GGB | 72026.26 | 2665.35 | 2665.35 |  |  |  | 1 | 1 |  |  |  |  | 142571.72 | 2665.35 | 142571.72 | 2665.35 | 9.2865 | [5 empty] | 105.5565 | 2650.7922
24.11.2007 03:00 | 3600 | 2 | 758.62 | GGB | 765.934 | 771.492 | 768.498 | 261.35 | GGB | 11065.3 | GGB | 9.87 | GGB | 1011.94 | GGB | 59.29 | GGB | 172974.19 | GGB | 141961.38 | GGB | 0 | 0 | 2660 | 3600 | 2644.55 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 72065.08 | GGB | 72065.99 | 2644.55 | 2644.55 |  |  |  | 1 | 1 |  |  |  |  | 141961.38 | 2644.55 | 141961.38 | 2644.55 | 9.4494 | [5 empty] | 104.2844
24.11.2007 04:00 | 3600 | 2 | 757.95 | GGB | 767.033 | 772.617 | 769.597 | 262.24 | GGB | 11022.2 | GGB | 9.85 | GGB | 1012.28 | GGB | 59.14 | GGB | 174188.97 | GGB | 143072.41 | GGB | 0 | 0 | 2670 | 3600 | 2654.9 | GGB | 100 | GGB | 42.51 | GGB | 42.51 | GGB | 72107.59 | GGB | 72108.5 | 2654.9 | 2654.9 |  |  |  | 1 | 1 |  |  |  |  | 143072.41 | 2654.9 | 143072.41 | 2654.9 | 8.9354 | [5 empty] | 105.5119 | 2641.5156
24.11.2007 05:00 | 3600 | 2 | 758.44 | GGB | 767.033 | 772.57 | 768.498 | 262.05 | GGB | 11043.5 | GGB | 9.86 | GGB | 1012.52 | GGB | 58.9 | GGB | 173655.3 | GGB | 142769.03 | GGB | 0 | 0 | 2650 | 3600 | 2635.08 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 72146.87 | GGB | 72147.78 | 2635.08 | 2635.08 |  |  |  | 1 | 1 |  |  |  |  | 142769.03 | 2635.08 | 142769.03 | 2635.08 | 9.5776 | [5 empty] | 104.5022
24.11.2007 06:00 | 3600 | 2 | 757.92 | GGB | 764.835 | 770.227 | 767.033 | 261.16 | GGB | 11047.6 | GGB | 9.85 | GGB | 1012.59 | GGB | 59.69 | GGB | 172540.66 | GGB | 141525.56 | GGB | 0 | 0 | 2678 | 3600 | 2662.14 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 72187.72 | GGB | 72188.64 | 2662.14 | 2662.14 |  |  |  | 1 | 1 |  |  |  |  | 141525.56 | 2662.14 | 141525.56 | 2662.14 | 9.2208 | [5 empty] | 104.6558
24.11.2007 07:00 | 3600 | 2 | 758.14 | GGB | 765.934 | 771.352 | 768.132 | 261.33 | GGB | 11050.8 | GGB | 9.86 | GGB | 1012.85 | GGB | 59.88 | GGB | 172768.43 | GGB | 141670.29 | GGB | 0 | 0 | 2683 | 3600 | 2667.54 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 72227.93 | GGB | 72228.84 | 2667.54 | 2667.54 |  |  |  | 1 | 1 |  |  |  |  | 141670.29 | 2667.54 | 141670.29 | 2667.54 | 9.4008 | [5 empty] | 104.9753
24.11.2007 08:00 | 3600 | 2 | 758.17 | GGB | 765.934 | 771.492 | 768.498 | 261.51 | GGB | 11053.4 | GGB | 9.86 | GGB | 1013.16 | GGB | 59.96 | GGB | 172711.21 | GGB | 141631.71 | GGB | 0 | 0 | 2683 | 3600 | 2667.51 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 72268.23 | GGB | 72269.14 | 2667.51 | 2667.51 |  |  |  | 1 | 1 |  |  |  |  | 141631.71 | 2667.51 | 141631.71 | 2667.51 | 9.3748 | [5 empty] | 104.9456
24.11.2007 09:00 | 3600 | 2 | 758.21 | GGB | 765.934 | 771.492 | 768.498 | 261.4 | GGB | 11044.6 | GGB | 9.86 | GGB | 1013.18 | GGB | 60.18 | GGB | 172667.2 | GGB | 141505.78 | GGB | 0 | 0 | 2678 | 3600 | 2662.91 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 72308.73 | GGB | 72309.64 | 2662.91 | 2662.91 |  |  |  | 1 | 1 |  |  |  |  | 141505.78 | 2662.91 | 141505.78 | 2662.91 | 9.3041 | [5 empty] | 104.6714
24.11.2007 10:00 | 3600 | 2 | 758.53 | GGB | 767.033 | 772.664 | 768.498 | 261.13 | GGB | 11040.8 | GGB | 9.86 | GGB | 1013.65 | GGB | 60.26 | GGB | 172306.29 | GGB | 141240.94 | GGB | 0 | 0 | 2668 | 3600 | 2653.08 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 72348.67 | GGB | 72349.58 | 2653.08 | 2653.08 |  |  |  | 1 | 1 |  |  |  |  | 141240.94 | 2653.08 | 141240.94 | 2653.08 | 9.3822 | [5 empty] | 104.0899
24.11.2007 11:00 | 3600 | 2 | 758.53 | GGB | 767.033 | 773.461 | 769.597 | 260.7 | GGB | 11037 | GGB | 9.86 | GGB | 1014.07 | GGB | 60.38 | GGB | 171935.48 | GGB | 140945.29 | GGB | 0 | 0 | 2659 | 3600 | 2644.04 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 72389.06 | GGB | 72389.97 | 2644.04 | 2644.04 |  |  |  | 1 | 1 |  |  |  |  | 140945.29 | 2644.04 | 140945.29 | 2644.04 | 9.2267 | [5 empty] | 103.5181
24.11.2007 12:00 | 3600 | 2 | 758.2 | GGB | 765.934 | 772.055 | 768.498 | 260.54 | GGB | 11010.4 | GGB | 9.85 | GGB | 1014.01 | GGB | 60.55 | GGB | 171586.67 | GGB | 140578.13 | GGB | 0 | 0 | 2660 | 3600 | 2644.71 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 72429.42 | GGB | 72430.33 | 2644.71 | 2644.71 |  |  |  | 1 | 1 |  |  |  |  | 140578.13 | 2644.71 | 140578.13 | 2644.71 | 9.2118 | [5 empty] | 103.2746
24.11.2007 13:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 770.977 | 768.498 | 260.22 | GGB | 10994.8 | GGB | 9.86 | GGB | 1013.92 | GGB | 60.57 | GGB | 171080.51 | GGB | 140141.77 | GGB | 0 | 0 | 2650 | 3600 | 2634.26 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 72469.48 | GGB | 72470.39 | 2634.26 | 2634.26 |  |  |  | 1 | 1 |  |  |  |  | 140141.77 | 2634.26 | 140141.77 | 2634.26 | 9.2154 | [5 empty] | 102.5472
24.11.2007 14:00 | 3600 | 2 | 758.62 | GGB | 765.934 | 772.102 | 768.498 | 260.02 | GGB | 10987.5 | GGB | 9.86 | GGB | 1013.55 | GGB | 60.5 | GGB | 170702 | GGB | 139809.67 | GGB | 0 | 0 | 2639 | 3600 | 2623.54 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 72509.83 | GGB | 72510.75 | 2623.54 | 2623.54 |  |  |  | 1 | 1 |  |  |  |  | 139809.67 | 2623.54 | 139809.67 | 2623.54 | 9.0881 | [5 empty] | 101.8879
24.11.2007 15:00 | 3600 | 2 | 758.19 | GGB | 767.033 | 772.102 | 768.498 | 260.03 | GGB | 10977.6 | GGB | 9.85 | GGB | 1013.3 | GGB | 60.52 | GGB | 170653.58 | GGB | 139727.26 | GGB | 0 | 0 | 2640 | 3600 | 2625.13 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 72549.98 | GGB | 72550.9 | 2625.13 | 2625.13 |  |  |  | 1 | 1 |  |  |  |  | 139727.26 | 2625.13 | 139727.26 | 2625.13 | 9.1358 | [5 empty] | 101.8895
24.11.2007 16:00 | 3600 | 2 | 758.64 | GGB | 767.033 | 772.219 | 768.498 | 259.94 | GGB | 10976.8 | GGB | 9.86 | GGB | 1012.72 | GGB | 60.59 | GGB | 170496.23 | GGB | 139492.15 | GGB | 0 | 0 | 2636 | 3600 | 2621.07 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 72590.01 | GGB | 72590.93 | 2621.07 | 2621.07 |  |  |  | 1 | 1 |  |  |  |  | 139492.15 | 2621.07 | 139492.15 | 2621.07 | 9.1336 | [5 empty] | 101.5607
24.11.2007 17:00 | 3600 | 2 | 758.72 | GGB | 767.033 | 772.172 | 769.597 | 259.48 | GGB | 10971.2 | GGB | 9.86 | GGB | 1012.49 | GGB | 60.39 | GGB | 170475.33 | GGB | 139523.87 | GGB | 0 | 0 | 2628 | 3600 | 2612.79 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 72630.29 | GGB | 72631.21 | 2612.79 | 2612.79 |  |  |  | 1 | 1 |  |  |  |  | 139523.87 | 2612.79 | 139523.87 | 2612.79 | 9.0503 | [5 empty] | 101.2629
24.11.2007 18:00 | 3600 | 2 | 758.42 | GGB | 764.835 | 770.906 | 767.033 | 259.15 | GGB | 10966.1 | GGB | 9.85 | GGB | 1012.07 | GGB | 59.69 | GGB | 170440.12 | GGB | 139731.12 | GGB | 0 | 0 | 2627 | 3600 | 2611.25 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 72669.99 | GGB | 72670.91 | 2611.25 | 2611.25 |  |  |  | 1 | 1 |  |  |  |  | 139731.12 | 2611.25 | 139731.12 | 2611.25 | 9.1908 | [5 empty] | 101.3536
24.11.2007 19:00 | 3600 | 2 | 757.9 | GGB | 765.934 | 772.031 | 768.498 | 260.94 | GGB | 10984.3 | GGB | 9.85 | GGB | 1012.69 | GGB | 58.71 | GGB | 172484.54 | GGB | 141911.67 | GGB | 0 | 0 | 2650 | 3600 | 2634.82 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 72710.43 | GGB | 72711.35 | 2634.82 | 2634.82 |  |  |  | 1 | 1 |  |  |  |  | 141911.67 | 2634.82 | 141911.67 | 2634.82 | 9.2461 | [5 empty] | 103.8644
24.11.2007 20:00 | 3600 | 2 | 758.51 | GGB | 765.934 | 771.961 | 768.498 | 260.66 | GGB | 11031.3 | GGB | 9.86 | GGB | 1012.54 | GGB | 59.2 | GGB | 172002.6 | GGB | 141286.99 | GGB | 0 | 0 | 2644 | 3600 | 2628.54 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 72749.97 | GGB | 72750.89 | 2628.54 | 2628.54 |  |  |  | 1 | 1 |  |  |  |  | 141286.99 | 2628.54 | 141286.99 | 2628.54 | 9.3925 | [5 empty] | 103.1607
24.11.2007 21:00 | 3600 | 2 | 758.26 | GGB | 764.835 | 770.953 | 767.033 | 260.63 | GGB | 11017.7 | GGB | 9.85 | GGB | 1012.41 | GGB | 59.77 | GGB | 171837.55 | GGB | 140890.28 | GGB | 0 | 0 | 2653 | 3600 | 2638.11 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 72790.26 | GGB | 72791.18 | 2638.11 | 2638.11 |  |  |  | 1 | 1 |  |  |  |  | 140890.28 | 2638.11 | 140890.28 | 2638.11 | 9.2252 | [5 empty] | 103.2456
24.11.2007 22:00 | 3600 | 2 | 758.28 | GGB | 765.934 | 770.883 | 768.498 | 261.51 | GGB | 11053.5 | GGB | 9.86 | GGB | 1012.54 | GGB | 59.4 | GGB | 172665 | GGB | 141745.68 | GGB | 0 | 0 | 2685 | 3600 | 2669.8 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 72831.08 | GGB | 72832 | 2669.8 | 2669.8 |  |  |  | 1 | 1 |  |  |  |  | 141745.68 | 2669.8 | 141745.68 | 2669.8 | 9.2708 | [5 empty] | 105.1202 | 2666.24
24.11.2007 23:00 | 3600 | 2 | 758.19 | GGB | 764.835 | 770.953 | 767.033 | 260.86 | GGB | 11061.4 | GGB | 9.86 | GGB | 1012.79 | GGB | 59.2 | GGB | 173132.64 | GGB | 142248.47 | GGB | 0 | 0 | 2677 | 3600 | 2661.21 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 72870.24 | GGB | 72871.16 | 2661.21 | 2661.21 |  |  |  | 1 | 1 |  |  |  |  | 142248.47 | 2661.21 | 142248.47 | 2661.21 | 9.6668 | [5 empty] | 105.1536 | 2656.8159
24.11.2007 24:00 | 3600 | 2 | 757.66 | GGB | 764.835 | 770.156 | 767.033 | 262.39 | GGB | 11060 | GGB | 9.85 | GGB | 1013.08 | GGB | 59.25 | GGB | 173605.79 | GGB | 142656.61 | GGB | 0 | 0 | 2715 | 3600 | 2699.81 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 72911.37 | GGB | 72912.29 | 2699.81 | 2699.81 |  |  |  | 1 | 1 |  |  |  |  | 142656.61 | 2699.81 | 142656.61 | 2699.81 | 9.3641 | [5 empty] | 106.9849 | 2649.2148
25.11.2007 01:00 | 3600 | 2 | 757.67 | GGB | 765.934 | 771.211 | 768.132 | 262.89 | GGB | 11091.9 | GGB | 9.85 | GGB | 1012.97 | GGB | 59.03 | GGB | 174324.31 | GGB | 143329.47 | GGB | 0 | 0 | 2719 | 3600 | 2703.84 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 72951.76 | GGB | 72952.68 | 2703.84 | 2703.84 |  |  |  | 1 | 1 |  |  |  |  | 143329.47 | 2703.84 | 143329.47 | 2703.84 | 9.5949 | [5 empty] | 107.65 | 2636.778
25.11.2007 02:00 | 3600 | 2 | 757.6 | GGB | 765.934 | 771.094 | 768.132 | 263.21 | GGB | 11111.5 | GGB | 9.85 | GGB | 1012.84 | GGB | 58.73 | GGB | 174684.12 | GGB | 143735.92 | GGB | 0 | 0 | 2731 | 3600 | 2715.82 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 72992.26 | GGB | 72993.19 | 2715.82 | 2715.82 |  |  |  | 1 | 1 |  |  |  |  | 143735.92 | 2715.82 | 143735.92 | 2715.82 | 9.6362 | [5 empty] | 108.4336 | 2629.3219
25.11.2007 03:00 | 3600 | 2 | 757.89 | GGB | 765.934 | 771.047 | 768.132 | 263.15 | GGB | 11116.6 | GGB | 9.86 | GGB | 1012.61 | GGB | 58.87 | GGB | 174626.9 | GGB | 143593.59 | GGB | 0 | 0 | 2724 | 3600 | 2708.36 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 73033.18 | GGB | 73034.11 | 2708.36 | 2708.36 |  |  |  | 1 | 1 |  |  |  |  | 143593.59 | 2708.36 | 143593.59 | 2708.36 | 9.504 | [5 empty] | 108.0286 | 2631.9281
25.11.2007 04:00 | 3600 | 2 | 757.85 | GGB | 765.934 | 771 | 768.498 | 263.32 | GGB | 11115.7 | GGB | 9.86 | GGB | 1012.25 | GGB | 59.1 | GGB | 174844.77 | GGB | 143624.39 | GGB | 0 | 0 | 2726 | 3600 | 2710.83 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 73073.37 | GGB | 73074.29 | 2710.83 | 2710.83 |  |  |  | 1 | 1 |  |  |  |  | 143624.39 | 2710.83 | 143624.39 | 2710.83 | 9.6899 | [5 empty] | 108.1504 | 2631.3637
25.11.2007 05:00 | 3600 | 2 | 757.86 | GGB | 764.835 | 771 | 767.033 | 262.72 | GGB | 11106.3 | GGB | 9.86 | GGB | 1011.62 | GGB | 58.94 | GGB | 174442.05 | GGB | 143274.52 | GGB | 0 | 0 | 2714 | 3600 | 2698.68 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 73114.25 | GGB | 73115.17 | 2698.68 | 2698.68 |  |  |  | 1 | 1 |  |  |  |  | 143274.52 | 2698.68 | 143274.52 | 2698.68 | 9.4582 | [5 empty] | 107.4034 | 2637.7893
25.11.2007 06:00 | 3600 | 2 | 757.85 | GGB | 765.934 | 770.977 | 767.033 | 262.71 | GGB | 11101.1 | GGB | 9.86 | GGB | 1011.23 | GGB | 58.87 | GGB | 174242.88 | GGB | 143081.57 | GGB | 0 | 0 | 2716 | 3600 | 2700.27 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 73154.38 | GGB | 73155.3 | 2700.27 | 2700.27 |  |  |  | 1 | 1 |  |  |  |  | 143081.57 | 2700.27 | 143081.57 | 2700.27 | 9.6277 | [5 empty] | 107.3219 | 2641.3465
25.11.2007 07:00 | 3600 | 2 | 757.71 | GGB | 765.934 | 772.148 | 767.033 | 262.66 | GGB | 11100.2 | GGB | 9.85 | GGB | 1010.96 | GGB | 58.83 | GGB | 174478.36 | GGB | 143257.38 | GGB | 0 | 0 | 2718 | 3600 | 2702.47 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 73194.89 | GGB | 73195.81 | 2702.47 | 2702.47 |  |  |  | 1 | 1 |  |  |  |  | 143257.38 | 2702.47 | 143257.38 | 2702.47 | 9.5569 | [5 empty] | 107.5413 | 2638.1049
25.11.2007 08:00 | 3600 | 2 | 757.6 | GGB | 765.934 | 771.047 | 767.033 | 263.21 | GGB | 11105.5 | GGB | 9.85 | GGB | 1010.44 | GGB | 58.92 | GGB | 174805.16 | GGB | 143412.39 | GGB | 0 | 0 | 2732 | 3600 | 2716.46 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 73235.32 | GGB | 73236.24 | 2716.46 | 2716.46 |  |  |  | 1 | 1 |  |  |  |  | 143412.39 | 2716.46 | 143412.39 | 2716.46 | 9.6358 | [5 empty] | 108.215 | 2635.2535
25.11.2007 09:00 | 3600 | 2 | 757.73 | GGB | 765.934 | 771.375 | 768.132 | 263.15 | GGB | 11113.8 | GGB | 9.86 | GGB | 1009.74 | GGB | 58.83 | GGB | 174947.1 | GGB | 143469.9 | GGB | 0 | 0 | 2721 | 3600 | 2706.01 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 73275.72 | GGB | 73276.64 | 2706.01 | 2706.01 |  |  |  | 1 | 1 |  |  |  |  | 143469.9 | 2706.01 | 143469.9 | 2706.01 | 9.6097 | [5 empty] | 107.8419 | 2634.1971
25.11.2007 10:00 | 3600 | 2 | 757.7 | GGB | 764.835 | 771.188 | 767.033 | 262.86 | GGB | 11112.1 | GGB | 9.86 | GGB | 1008.82 | GGB | 58.7 | GGB | 175288.21 | GGB | 143674.4 | GGB | 0 | 0 | 2714 | 3600 | 2698.6 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 73316.84 | GGB | 73317.76 | 2698.6 | 2698.6 |  |  |  | 1 | 1 |  |  |  |  | 143674.4 | 2698.6 | 143674.4 | 2698.6 | 9.429 | [5 empty] | 107.6999 | 2630.4477
25.11.2007 11:00 | 3600 | 2 | 757.58 | GGB | 765.934 | 771.188 | 768.132 | 262.61 | GGB | 11110.4 | GGB | 9.86 | GGB | 1007.91 | GGB | 58.41 | GGB | 175346.52 | GGB | 143714.28 | GGB | 0 | 0 | 2716 | 3600 | 2700.13 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 73356.73 | GGB | 73357.65 | 2700.13 | 2700.13 |  |  |  | 1 | 1 |  |  |  |  | 143714.28 | 2700.13 | 143714.28 | 2700.13 | 9.7279 | [5 empty] | 107.7909 | 2629.7178
25.11.2007 12:00 | 3600 | 2 | 757.71 | GGB | 765.934 | 771.07 | 768.132 | 262.59 | GGB | 11118.5 | GGB | 9.86 | GGB | 1006.8 | GGB | 58.37 | GGB | 175747.05 | GGB | 143903.17 | GGB | 0 | 0 | 2716 | 3600 | 2700.95 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 73397.9 | GGB | 73398.82 | 2700.95 | 2700.95 |  |  |  | 1 | 1 |  |  |  |  | 143903.17 | 2700.95 | 143903.17 | 2700.95 | 9.4407 | [5 empty] | 107.9654 | 2626.266
25.11.2007 13:00 | 3600 | 2 | 757.66 | GGB | 765.934 | 771.164 | 768.132 | 262.29 | GGB | 11113 | GGB | 9.86 | GGB | 1005.81 | GGB | 58.16 | GGB | 175690.93 | GGB | 143806.32 | GGB | 0 | 0 | 2709 | 3600 | 2693.69 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 73438 | GGB | 73438.92 | 2693.69 | 2693.69 |  |  |  | 1 | 1 |  |  |  |  | 143806.32 | 2693.69 | 143806.32 | 2693.69 | 9.6601 | [5 empty] | 107.6027 | 2628.0347
25.11.2007 14:00 | 3600 | 2 | 757.73 | GGB | 765.934 | 772.125 | 768.132 | 261.73 | GGB | 11098.1 | GGB | 9.86 | GGB | 1004.56 | GGB | 58.21 | GGB | 175326.72 | GGB | 143308.3 | GGB | 0 | 0 | 2694 | 3600 | 2678.88 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 73478.55 | GGB | 73479.47 | 2678.88 | 2678.88 |  |  |  | 1 | 1 |  |  |  |  | 143308.3 | 2678.88 | 143308.3 | 2678.88 | 9.4675 | [5 empty] | 106.6405 | 2637.1676
25.11.2007 15:00 | 3600 | 2 | 757.74 | GGB | 765.934 | 771.117 | 767.033 | 261.23 | GGB | 11087.7 | GGB | 9.86 | GGB | 1003.45 | GGB | 57.9 | GGB | 175084.64 | GGB | 143087.58 | GGB | 0 | 0 | 2686 | 3600 | 2670.97 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 73519.16 | GGB | 73520.08 | 2670.97 | 2670.97 |  |  |  | 1 | 1 |  |  |  |  | 143087.58 | 2670.97 | 143087.58 | 2670.97 | 9.411 | [5 empty] | 106.1618 | 2641.2355
25.11.2007 16:00 | 3600 | 2 | 757.57 | GGB | 764.835 | 771.328 | 767.033 | 260.99 | GGB | 11088 | GGB | 9.86 | GGB | 1002.88 | GGB | 58.06 | GGB | 175161.67 | GGB | 142999.79 | GGB | 0 | 0 | 2692 | 3600 | 2676.74 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 73559.24 | GGB | 73560.16 | 2676.74 | 2676.74 |  |  |  | 1 | 1 |  |  |  |  | 142999.79 | 2676.74 | 142999.79 | 2676.74 | 9.5502 | [5 empty] | 106.3259 | 2642.857
25.11.2007 17:00 | 3600 | 2 | 757.53 | GGB | 765.934 | 771.375 | 768.132 | 260.9 | GGB | 11094.8 | GGB | 9.86 | GGB | 1001.93 | GGB | 58.03 | GGB | 175249.69 | GGB | 142950.4 | GGB | 0 | 0 | 2698 | 3600 | 2682.7 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 73600.25 | GGB | 73601.17 | 2682.7 | 2682.7 |  |  |  | 1 | 1 |  |  |  |  | 142950.4 | 2682.7 | 142950.4 | 2682.7 | 9.3512 | [5 empty] | 106.5258 | 2643.7701
25.11.2007 18:00 | 3600 | 2 | 757.31 | GGB | 764.835 | 770.25 | 767.033 | 260.62 | GGB | 11097.4 | GGB | 9.86 | GGB | 1001.36 | GGB | 57.94 | GGB | 175245.29 | GGB | 142903.22 | GGB | 0 | 0 | 2711 | 3600 | 2695.15 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 73640.41 | GGB | 73641.33 | 2695.15 | 2695.15 |  |  |  | 1 | 1 |  |  |  |  | 142903.22 | 2695.15 | 142903.22 | 2695.15 | 9.5903 | [5 empty] | 106.9849 | 2644.643
25.11.2007 19:00 | 3600 | 2 | 757.19 | GGB | 764.835 | 770.203 | 767.033 | 260.86 | GGB | 11106.7 | GGB | 9.85 | GGB | 1000.71 | GGB | 57.7 | GGB | 175573.19 | GGB | 143180.36 | GGB | 0 | 0 | 2733 | 3600 | 2718.05 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 73681.13 | GGB | 73682.05 | 2718.05 | 2718.05 |  |  |  | 1 | 1 |  |  |  |  | 143180.36 | 2718.05 | 143180.36 | 2718.05 | 9.5573 | [5 empty] | 108.1032 | 2639.524
25.11.2007 20:00 | 3600 | 2 | 757.37 | GGB | 764.835 | 771.469 | 767.033 | 260.36 | GGB | 11108.2 | GGB | 9.86 | GGB | 1000.61 | GGB | 57.71 | GGB | 175335.52 | GGB | 142966.83 | GGB | 0 | 0 | 2719 | 3600 | 2703.32 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 73721.78 | GGB | 73722.7 | 2703.32 | 2703.32 |  |  |  | 1 | 1 |  |  |  |  | 142966.83 | 2703.32 | 142966.83 | 2703.32 | 9.5076 | [5 empty] | 107.357 | 2643.4663
25.11.2007 21:00 | 3600 | 2 | 757.24 | GGB | 764.835 | 770.391 | 767.033 | 259.84 | GGB | 11088.2 | GGB | 9.85 | GGB | 1000.18 | GGB | 57.54 | GGB | 174818.36 | GGB | 142560.11 | GGB | 0 | 0 | 2716 | 3600 | 2700.42 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 73761.76 | GGB | 73762.67 | 2700.42 | 2700.42 |  |  |  | 1 | 1 |  |  |  |  | 142560.11 | 2700.42 | 142560.11 | 2700.42 | 9.6315 | [5 empty] | 106.9367 | 2651.0081
25.11.2007 22:00 | 3600 | 2 | 757.47 | GGB | 764.835 | 770.391 | 767.033 | 259.26 | GGB | 11076.9 | GGB | 9.86 | GGB | 999.87 | GGB | 57.62 | GGB | 174292.4 | GGB | 142053.57 | GGB | 0 | 0 | 2697 | 3600 | 2681.15 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 73802.47 | GGB | 73803.38 | 2681.15 | 2681.15 |  |  |  | 1 | 1 |  |  |  |  | 142053.57 | 2681.15 | 142053.57 | 2681.15 | 9.3556 | [5 empty] | 105.7964 | 2660.4611
25.11.2007 23:00 | 3600 | 2 | 757.35 | GGB | 765.934 | 771.422 | 768.132 | 259.21 | GGB | 11065.1 | GGB | 9.86 | GGB | 999.57 | GGB | 57.71 | GGB | 173995.31 | GGB | 141729.71 | GGB | 0 | 0 | 2696 | 3600 | 2680.31 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 73842.79 | GGB | 73843.7 | 2680.31 | 2680.31 |  |  |  | 1 | 1 |  |  |  |  | 141729.71 | 2680.31 | 141729.71 | 2680.31 | 9.4216 | [5 empty] | 105.5221 | 2666.5404
25.11.2007 24:00 | 3600 | 2 | 757.41 | GGB | 764.835 | 771.305 | 767.033 | 259.12 | GGB | 11052.2 | GGB | 9.86 | GGB | 999.15 | GGB | 57.94 | GGB | 173720.22 | GGB | 141345.12 | GGB | 0 | 0 | 2690 | 3600 | 2674.67 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 73883.32 | GGB | 73884.23 | 2674.67 | 2674.67 |  |  |  | 1 | 1 |  |  |  |  | 141345.12 | 2674.67 | 141345.12 | 2674.67 | 9.3277 | [5 empty] | 105.0143 | 2673.7959
26.11.2007 01:00 | 3600 | 2 | 757.48 | GGB | 765.934 | 771.305 | 767.033 | 258.8 | GGB | 11037.3 | GGB | 9.86 | GGB | 998.5 | GGB | 58.07 | GGB | 173299.89 | GGB | 140855.36 | GGB | 0 | 0 | 2674 | 3600 | 2658.9 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 73922.85 | GGB | 73923.76 | 2658.9 | 2658.9 |  |  |  | 1 | 1 |  |  |  |  | 140855.36 | 2658.9 | 140855.36 | 2658.9 | 9.4743 | [5 empty] | 104.0334
26.11.2007 02:00 | 3600 | 2 | 757.5 | GGB | 765.934 | 771.164 | 768.132 | 258.54 | GGB | 11026.2 | GGB | 9.86 | GGB | 997.76 | GGB | 58.16 | GGB | 173033.61 | GGB | 140499.48 | GGB | 0 | 0 | 2668 | 3600 | 2652.62 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 73963.46 | GGB | 73964.37 | 2652.62 | 2652.62 |  |  |  | 1 | 1 |  |  |  |  | 140499.48 | 2652.62 | 140499.48 | 2652.62 | 9.1773 | [5 empty] | 103.5255
26.11.2007 03:00 | 3600 | 2 | 757.64 | GGB | 765.934 | 771.258 | 768.132 | 258 | GGB | 11001.4 | GGB | 9.86 | GGB | 997.27 | GGB | 58.31 | GGB | 172417.42 | GGB | 139867.26 | GGB | 0 | 0 | 2651 | 3600 | 2636.08 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 74003.67 | GGB | 74004.58 | 2636.08 | 2636.08 |  |  |  | 1 | 1 |  |  |  |  | 139867.26 | 2636.08 | 139867.26 | 2636.08 | 9.1694 | [5 empty] | 102.417
26.11.2007 04:00 | 3600 | 2 | 757.4 | GGB | 764.835 | 771.188 | 767.033 | 257.16 | GGB | 10948.6 | GGB | 9.86 | GGB | 996.7 | GGB | 58.47 | GGB | 171361.1 | GGB | 138865.5 | GGB | 0 | 0 | 2642 | 3600 | 2627.01 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 74043.56 | GGB | 74044.47 | 2627.01 | 2627.01 |  |  |  | 1 | 1 |  |  |  |  | 138865.5 | 2627.01 | 138865.5 | 2627.01 | 9.1452 | [5 empty] | 101.3336
26.11.2007 05:00 | 3600 | 2 | 757.7 | GGB | 765.934 | 772.242 | 768.132 | 257.99 | GGB | 10932 | GGB | 9.86 | GGB | 996.14 | GGB | 58.06 | GGB | 172487.85 | GGB | 139869.92 | GGB | 0 | 0 | 2619 | 3600 | 2603.97 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 74083.77 | GGB | 74084.68 | 2603.97 | 2603.97 |  |  |  | 1 | 1 |  |  |  |  | 139869.92 | 2603.97 | 139869.92 | 2603.97 | 9.0579 | [5 empty] | 101.1714
26.11.2007 06:00 | 3600 | 2 | 757.33 | GGB | 764.835 | 771.164 | 767.033 | 257.73 | GGB | 10917.6 | GGB | 9.85 | GGB | 995.68 | GGB | 58.1 | GGB | 172141.24 | GGB | 139506.75 | GGB | 0 | 0 | 2629 | 3600 | 2613.98 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 74123.79 | GGB | 74124.7 | 2613.98 | 2613.98 |  |  |  | 1 | 1 |  |  |  |  | 139506.75 | 2613.98 | 139506.75 | 2613.98 | 9.1121 | [5 empty] | 101.2966
26.11.2007 07:00 | 3600 | 2 | 757.71 | GGB | 764.835 | 771.07 | 767.033 | 257.03 | GGB | 10935.9 | GGB | 9.86 | GGB | 995.43 | GGB | 58.11 | GGB | 171483.24 | GGB | 138934.1 | GGB | 0 | 0 | 2617 | 3600 | 2602.16 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 74163.07 | GGB | 74163.98 | 2602.16 | 2602.16 |  |  |  | 1 | 1 |  |  |  |  | 138934.1 | 2602.16 | 138934.1 | 2602.16 | 9.2039 | [5 empty] | 100.4247
26.11.2007 08:00 | 3600 | 2 | 756.14 | GGB | 764.469 | 770.578 | 767.033 | 260.93 | GGB | 11017.1 | GGB | 9.84 | GGB | 995.69 | GGB | 57.71 | GGB | 174583.99 | GGB | 141655.56 | GGB | 0 | 0 | 2752 | 3600 | 2736.77 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 74203.76 | GGB | 74204.66 | 2736.77 | 2736.77 |  |  |  | 1 | 1 |  |  |  |  | 141655.56 | 2736.77 | 141655.56 | 2736.77 | 9.53 | [5 empty] | 107.6885 | 2667.9362
26.11.2007 09:00 | 3600 | 2 | 756.84 | GGB | 763.37 | 770.531 | 765.934 | 260.91 | GGB | 11063.8 | GGB | 9.85 | GGB | 995.57 | GGB | 57.88 | GGB | 174445.35 | GGB | 141453 | GGB | 0 | 0 | 2750 | 3600 | 2734.79 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 74243.84 | GGB | 74244.75 | 2734.79 | 2734.79 |  |  |  | 0 | 1 | [14 empty] | 107.4567 | 2671.7567
26.11.2007 10:00 | 3600 | 2 | 756.61 | GGB | 764.469 | 769.641 | 767.033 | 261.37 | GGB | 11080.1 | GGB | 9.85 | GGB | 995.98 | GGB | 57.54 | GGB | 175058.23 | GGB | 142153.18 | GGB | 0 | 0 | 2766 | 3600 | 2750.7 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 74283.89 | GGB | 74284.8 | 2750.7 | 2750.7 |  |  |  | 1 | 1 |  |  |  |  | 142153.18 | 2750.7 | 142153.18 | 2750.7 | 9.7633 | [5 empty] | 108.6169 | 2658.5969
26.11.2007 11:00 | 3600 | 2 | 756.61 | GGB | 764.835 | 770.719 | 767.033 | 262.26 | GGB | 11058.8 | GGB | 9.85 | GGB | 996.15 | GGB | 56.89 | GGB | 176474.37 | GGB | 143613.09 | GGB | 0 | 0 | 2744 | 3600 | 2728.36 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 74325.06 | GGB | 74325.97 | 2728.36 | 2728.36 |  |  |  | 1 | 1 |  |  |  |  | 143613.09 | 2728.36 | 143613.09 | 2728.36 | 9.5173 | [5 empty] | 108.8412 | 2631.5707
26.11.2007 12:00 | 3600 | 2 | 756.87 | GGB | 764.469 | 770.602 | 767.033 | 262.83 | GGB | 11058.6 | GGB | 9.85 | GGB | 996.48 | GGB | 56.61 | GGB | 177429.46 | GGB | 144558.65 | GGB | 0 | 0 | 2728 | 3600 | 2712.69 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 74364.57 | GGB | 74365.47 | 2712.69 | 2712.69 |  |  |  | 1 | 1 |  |  |  |  | 144558.65 | 2712.69 | 144558.65 | 2712.69 | 9.9277 | [5 empty] | 108.9286 | 2614.3576
26.11.2007 13:00 | 3600 | 2 | 757.31 | GGB | 764.469 | 769.594 | 767.033 | 261.01 | GGB | 11087.8 | GGB | 9.87 | GGB | 995.6 | GGB | 57.15 | GGB | 175207.88 | GGB | 142389.91 | GGB | 0 | 0 | 2727 | 3244 | 2711.9 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 74404.92 | GGB | 74405.83 | 2711.9 | 2711.9 |  |  |  | 1 | 1 |  |  |  |  | 142389.91 | 2711.9 | 142389.91 | 2711.9 | 9.5676 | [5 empty] | 107.2631 | 2654.1768
26.11.2007 14:00 | 3600 | 2 | 756.69 | GGB | 764.835 | 770.578 | 767.033 | 261.02 | GGB | 11076 | GGB | 9.85 | GGB | 995.83 | GGB | 57.6 | GGB | 175054.93 | GGB | 142105.24 | GGB | 0 | 0 | 2752 | 3600 | 2736.28 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 74445.32 | GGB | 74446.23 | 2736.28 | 2736.28 |  |  |  | 1 | 1 |  |  |  |  | 142105.24 | 2736.28 | 142105.24 | 2736.28 | 9.6247 | [5 empty] | 108.011 | 2659.4938
26.11.2007 15:00 | 3600 | 2 | 756.83 | GGB | 764.469 | 769.664 | 765.934 | 261.23 | GGB | 11083.6 | GGB | 9.86 | GGB | 995.3 | GGB | 57.79 | GGB | 175249.69 | GGB | 142105.38 | GGB | 0 | 0 | 2753 | 3600 | 2737.92 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 74485.19 | GGB | 74486.1 | 2737.92 | 2737.92 |  |  |  | 1 | 1 |  |  |  |  | 142105.38 | 2737.92 | 142105.38 | 2737.92 | 9.7585 | [5 empty] | 108.0759 | 2659.4911
26.11.2007 16:00 | 3600 | 2 | 756.9 | GGB | 765.934 | 771.281 | 767.033 | 262.44 | GGB | 11065.2 | GGB | 9.85 | GGB | 995.34 | GGB | 57.03 | GGB | 177067.45 | GGB | 143917.93 | GGB | 0 | 0 | 2732 | 3600 | 2716.82 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 74526.13 | GGB | 74527.04 | 2716.82 | 2716.82 |  |  |  | 1 | 1 |  |  |  |  | 143917.93 | 2716.82 | 143917.93 | 2716.82 | 9.5505 | [5 empty] | 108.6109 | 2625.9966
26.11.2007 17:00 | 3600 | 2 | 756.95 | GGB | 764.835 | 770.273 | 767.033 | 261.22 | GGB | 11092.4 | GGB | 9.86 | GGB | 995.58 | GGB | 57.59 | GGB | 175380.63 | GGB | 142339.19 | GGB | 0 | 0 | 2748 | 3600 | 2732.89 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 74565.95 | GGB | 74566.86 | 2732.89 | 2732.89 |  |  |  | 1 | 1 |  |  |  |  | 142339.19 | 2732.89 | 142339.19 | 2732.89 | 9.7689 | [5 empty] | 108.0548 | 2655.1226
26.11.2007 18:00 | 3600 | 2 | 756.55 | GGB | 764.835 | 770.273 | 765.934 | 262.7 | GGB | 11065.9 | GGB | 9.85 | GGB | 995.87 | GGB | 57.08 | GGB | 177276.52 | GGB | 144143.3 | GGB | 0 | 0 | 2751 | 3600 | 2735.77 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 74606.42 | GGB | 74607.33 | 2735.77 | 2735.77 |  |  |  | 1 | 1 |  |  |  |  | 144143.3 | 2735.77 | 144143.3 | 2735.77 | 9.7441 | [5 empty] | 109.5397 | 2621.8909
26.11.2007 19:00 | 3600 | 2 | 756.87 | GGB | 764.469 | 770.438 | 767.033 | 263.23 | GGB | 11091 | GGB | 9.85 | GGB | 995.91 | GGB | 56.79 | GGB | 177997.24 | GGB | 144859.78 | GGB | 0 | 0 | 2752 | 3600 | 2736.48 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 74646.93 | GGB | 74647.84 | 2736.48 | 2736.48 |  |  |  | 1 | 1 |  |  |  |  | 144859.78 | 2736.48 | 144859.78 | 2736.48 | 9.7854 | [5 empty] | 110.1127 | 2608.9229
26.11.2007 20:00 | 3600 | 2 | 756.62 | GGB | 764.469 | 769.547 | 767.033 | 262.62 | GGB | 11141.9 | GGB | 9.86 | GGB | 996.13 | GGB | 57.5 | GGB | 176695.54 | GGB | 143522.67 | GGB | 0 | 0 | 2800 | 3600 | 2784.87 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 74687.39 | GGB | 74688.3 | 2784.87 | 2784.87 |  |  |  | 1 | 1 |  |  |  |  | 143522.67 | 2784.87 | 143522.67 | 2784.87 | 9.8787 | [5 empty] | 111.0255 | 2633.2286
26.11.2007 21:00 | 3600 | 2 | 756.1 | GGB | 763.37 | 768.328 | 765.934 | 263.02 | GGB | 11146.4 | GGB | 9.85 | GGB | 996.49 | GGB | 57.35 | GGB | 177160.98 | GGB | 144020.4 | GGB | 0 | 0 | 2834 | 3600 | 2818.51 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 74728.15 | GGB | 74729.06 | 2818.51 | 2818.51 |  |  |  | 0 | 1 | [14 empty] | 112.7564 | 2624.1282
26.11.2007 22:00 | 3600 | 2 | 756.06 | GGB | 763.37 | 768.305 | 764.835 | 264.02 | GGB | 11172.8 | GGB | 9.85 | GGB | 996.95 | GGB | 56.52 | GGB | 178611.23 | GGB | 145632.76 | GGB | 0 | 0 | 2846 | 3600 | 2830.76 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 74768.34 | GGB | 74769.24 | 2830.76 | 2830.76 |  |  |  | 0 | 1 | [14 empty] | 114.5143 | 2595.0754
26.11.2007 23:00 | 3600 | 2 | 756.67 | GGB | 765.934 | 771.586 | 768.132 | 265 | GGB | 11199.5 | GGB | 9.86 | GGB | 997.17 | GGB | 55.98 | GGB | 179874.41 | GGB | 146933.17 | GGB | 0 | 0 | 2830 | 3600 | 2814.62 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 74809.15 | GGB | 74810.06 | 2814.62 | 2814.62 |  |  |  | 1 | 1 |  |  |  |  | 146933.17 | 2814.62 | 146933.17 | 2814.62 | 10.1313 | [5 empty] | 114.8781 | 2572.1081
26.11.2007 24:00 | 3600 | 2 | 756.86 | GGB | 764.835 | 770.367 | 767.033 | 263.95 | GGB | 11190.9 | GGB | 9.87 | GGB | 997.38 | GGB | 55.89 | GGB | 179955.84 | GGB | 147071.87 | GGB | 0 | 0 | 2806 | 3600 | 2790.65 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 74849.81 | GGB | 74850.72 | 2790.65 | 2790.65 |  |  |  | 1 | 1 |  |  |  |  | 147071.87 | 2790.65 | 147071.87 | 2790.65 | 10.0941 | [5 empty] | 114.0073 | 2569.6824
27.11.2007 01:00 | 3600 | 2 | 756.71 | GGB | 764.469 | 769.242 | 765.934 | 262.06 | GGB | 11166.2 | GGB | 9.86 | GGB | 997.26 | GGB | 56.99 | GGB | 176831.98 | GGB | 144021.03 | GGB | 0 | 0 | 2818 | 3600 | 2802.86 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 74891.18 | GGB | 74892.09 | 2802.86 | 2802.86 |  |  |  | 1 | 1 |  |  |  |  | 144021.03 | 2802.86 | 144021.03 | 2802.86 | 9.7576 | [5 empty] | 112.1308 | 2624.1168
27.11.2007 02:00 | 3600 | 2 | 756.34 | GGB | 764.469 | 769.43 | 765.934 | 262.5 | GGB | 11155.9 | GGB | 9.85 | GGB | 997.26 | GGB | 56.86 | GGB | 177076.25 | GGB | 144276.41 | GGB | 0 | 0 | 2837 | 3600 | 2821.97 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 74931.54 | GGB | 74932.45 | 2821.97 | 2821.97 |  |  |  | 1 | 1 |  |  |  |  | 144276.41 | 2821.97 | 144276.41 | 2821.97 | 10.0878 | [5 empty] | 113.0955 | 2619.4719
27.11.2007 03:00 | 3600 | 2 | 756.35 | GGB | 764.469 | 769.148 | 767.033 | 262.95 | GGB | 11176.8 | GGB | 9.85 | GGB | 997.75 | GGB | 56.56 | GGB | 177614.32 | GGB | 144919.4 | GGB | 0 | 0 | 2838 | 3600 | 2822.61 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 74972.42 | GGB | 74973.33 | 2822.61 | 2822.61 |  |  |  | 1 | 1 |  |  |  |  | 144919.4 | 2822.61 | 144919.4 | 2822.61 | 10.0061 | [5 empty] | 113.6253 | 2607.8496
27.11.2007 04:00 | 3600 | 2 | 756.37 | GGB | 764.835 | 770.367 | 767.033 | 264.58 | GGB | 11152.6 | GGB | 9.85 | GGB | 997.97 | GGB | 55.7 | GGB | 179841.4 | GGB | 147152.35 | GGB | 0 | 0 | 2809 | 3600 | 2793.55 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 75013.28 | GGB | 75014.19 | 2793.55 | 2793.55 |  |  |  | 1 | 1 |  |  |  |  | 147152.35 | 2793.55 | 147152.35 | 2793.55 | 10.0606 | [5 empty] | 114.1882 | 2568.277
27.11.2007 05:00 | 3600 | 2 | 756.87 | GGB | 764.835 | 770.391 | 767.033 | 263.86 | GGB | 11179.1 | GGB | 9.86 | GGB | 997.92 | GGB | 55.52 | GGB | 179260.42 | GGB | 146748.55 | GGB | 0 | 0 | 2800 | 3600 | 2784.27 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 75053.81 | GGB | 75054.72 | 2784.27 | 2784.27 |  |  |  | 1 | 1 |  |  |  |  | 146748.55 | 2784.27 | 146748.55 | 2784.27 | 10.0811 | [5 empty] | 113.4966 | 2575.344
27.11.2007 06:00 | 3600 | 2 | 756.27 | GGB | 764.469 | 769.406 | 767.033 | 263.14 | GGB | 11182.4 | GGB | 9.85 | GGB | 997.8 | GGB | 56.2 | GGB | 177795.87 | GGB | 145229.97 | GGB | 0 | 0 | 2839 | 3600 | 2823.85 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 75094.68 | GGB | 75095.59 | 2823.85 | 2823.85 |  |  |  | 1 | 1 |  |  |  |  | 145229.97 | 2823.85 | 145229.97 | 2823.85 | 10.0344 | [5 empty] | 113.9188 | 2602.2728
27.11.2007 07:00 | 3600 | 2 | 756.42 | GGB | 764.469 | 770.367 | 767.033 | 263.27 | GGB | 11195.5 | GGB | 9.86 | GGB | 997.75 | GGB | 56.15 | GGB | 177868.5 | GGB | 145306.86 | GGB | 0 | 0 | 2839 | 3600 | 2823.5 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 75134.97 | GGB | 75135.88 | 2823.5 | 2823.5 |  |  |  | 1 | 1 |  |  |  |  | 145306.86 | 2823.5 | 145306.86 | 2823.5 | 10.183 | [5 empty] | 113.965 | 2600.8958
27.11.2007 08:00 | 3600 | 2 | 756.46 | GGB | 764.469 | 770.367 | 765.934 | 263.39 | GGB | 11165.4 | GGB | 9.85 | GGB | 998.09 | GGB | 55.91 | GGB | 178270.12 | GGB | 145789.96 | GGB | 0 | 0 | 2822 | 3600 | 2806.04 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 75176.35 | GGB | 75177.26 | 2806.04 | 2806.04 |  |  |  | 1 | 1 |  |  |  |  | 145789.96 | 2806.04 | 145789.96 | 2806.04 | 9.8862 | [5 empty] | 113.6368 | 2592.2773
27.11.2007 09:00 | 3600 | 2 | 756.26 | GGB | 764.469 | 770.344 | 767.033 | 265.18 | GGB | 11138.3 | GGB | 9.85 | GGB | 998.67 | GGB | 55.14 | GGB | 179280.23 | GGB | 147041.66 | GGB | 0 | 0 | 2816 | 3600 | 2800.66 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 75216.36 | GGB | 75217.28 | 2800.66 | 2800.66 |  |  |  | 1 | 1 |  |  |  |  | 147041.66 | 2800.66 | 147041.66 | 2800.66 | 10.2902 | [5 empty] | 114.3927 | 2570.2104
27.11.2007 10:00 | 3600 | 2 | 756.56 | GGB | 765.201 | 770.461 | 767.033 | 265.21 | GGB | 11150.5 | GGB | 9.86 | GGB | 999.46 | GGB | 55.05 | GGB | 179224.11 | GGB | 147154.93 | GGB | 0 | 0 | 2810 | 3600 | 2794.03 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 75257.51 | GGB | 75258.43 | 2794.03 | 2794.03 |  |  |  | 1 | 1 |  |  |  |  | 147154.93 | 2794.03 | 147154.93 | 2794.03 | 9.9916 | [5 empty] | 114.2098 | 2568.232
27.11.2007 11:00 | 3600 | 2 | 756.86 | GGB | 765.201 | 770.414 | 767.033 | 264.89 | GGB | 11145 | GGB | 9.86 | GGB | 1000.12 | GGB | 55.33 | GGB | 178775.18 | GGB | 146759.31 | GGB | 0 | 0 | 2785 | 3600 | 2769.68 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 75298 | GGB | 75298.92 | 2769.68 | 2769.68 |  |  |  | 1 | 1 |  |  |  |  | 146759.31 | 2769.68 | 146759.31 | 2769.68 | 10.0389 | [5 empty] | 112.9101 | 2575.1552
27.11.2007 12:00 | 3600 | 2 | 756.88 | GGB | 765.201 | 770.039 | 767.033 | 264.67 | GGB | 11127.4 | GGB | 9.86 | GGB | 1000.28 | GGB | 55.67 | GGB | 178457.18 | GGB | 146370.18 | GGB | 0 | 0 | 2778 | 3600 | 2762.95 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 75338.42 | GGB | 75339.33 | 2762.95 | 2762.95 |  |  |  | 1 | 1 |  |  |  |  | 146370.18 | 2762.95 | 146370.18 | 2762.95 | 10.0078 | [5 empty] | 112.3371 | 2582.0013
27.11.2007 13:00 | 3600 | 2 | 757.19 | GGB | 765.201 | 770.086 | 767.033 | 263.1 | GGB | 11140.5 | GGB | 9.87 | GGB | 999.63 | GGB | 56.03 | GGB | 176592.11 | GGB | 144587.87 | GGB | 0 | 0 | 2767 | 3600 | 2751.88 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 75379.19 | GGB | 75380.11 | 2751.88 | 2751.88 |  |  |  | 1 | 1 |  |  |  |  | 144587.87 | 2751.88 | 144587.87 | 2751.88 | 9.757 | [5 empty] | 110.5246 | 2613.8292
27.11.2007 14:00 | 3600 | 2 | 756.83 | GGB | 765.201 | 770.086 | 767.033 | 262.38 | GGB | 11128.1 | GGB | 9.85 | GGB | 999.91 | GGB | 56.51 | GGB | 175563.29 | GGB | 143577.9 | GGB | 0 | 0 | 2798 | 3600 | 2782.85 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 75419.73 | GGB | 75420.65 | 2782.85 | 2782.85 |  |  |  | 1 | 1 |  |  |  |  | 143577.9 | 2782.85 | 143577.9 | 2782.85 | 9.8558 | [5 empty] | 110.9877 | 2632.2157
27.11.2007 15:00 | 3600 | 2 | 756.96 | GGB | 764.102 | 770.086 | 765.934 | 262.38 | GGB | 11134.4 | GGB | 9.86 | GGB | 1000.21 | GGB | 56.13 | GGB | 175709.63 | GGB | 143905.26 | GGB | 0 | 0 | 2796 | 3600 | 2780.68 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 75460.17 | GGB | 75461.09 | 2780.68 | 2780.68 |  |  |  | 1 | 1 |  |  |  |  | 143905.26 | 2780.68 | 143905.26 | 2780.68 | 9.895 | [5 empty] | 111.154 | 2626.2278
27.11.2007 16:00 | 3600 | 2 | 756.58 | GGB | 765.201 | 770.297 | 767.033 | 264.28 | GGB | 11103.5 | GGB | 9.84 | GGB | 1000.86 | GGB | 55.85 | GGB | 178186.49 | GGB | 146152.64 | GGB | 0 | 0 | 2794 | 3600 | 2778.84 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 75501 | GGB | 75501.92 | 2778.84 | 2778.84 |  |  |  | 1 | 1 |  |  |  |  | 146152.64 | 2778.84 | 146152.64 | 2778.84 | 9.947 | [5 empty] | 112.8152 | 2585.8445
27.11.2007 17:00 | 3600 | 2 | 757.16 | GGB | 765.201 | 770.508 | 767.033 | 263.52 | GGB | 11161 | GGB | 9.86 | GGB | 1001.2 | GGB | 56 | GGB | 177120.27 | GGB | 145262.1 | GGB | 0 | 0 | 2791 | 3600 | 2775.3 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 75541.06 | GGB | 75541.98 | 2775.3 | 2775.3 |  |  |  | 1 | 1 |  |  |  |  | 145262.1 | 2775.3 | 145262.1 | 2775.3 | 10.0636 | [5 empty] | 111.985 | 2601.6972
27.11.2007 18:00 | 3600 | 2 | 756.69 | GGB | 764.102 | 770.625 | 767.033 | 263.38 | GGB | 11181.9 | GGB | 9.86 | GGB | 1001.85 | GGB | 56.09 | GGB | 177005.83 | GGB | 145220.85 | GGB | 0 | 0 | 2815 | 3600 | 2799.68 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 75582 | GGB | 75582.92 | 2799.68 | 2799.68 |  |  |  | 1 | 1 |  |  |  |  | 145220.85 | 2799.68 | 145220.85 | 2799.68 | 9.9309 | [5 empty] | 112.9366 | 2602.4362
27.11.2007 19:00 | 3600 | 2 | 756.32 | GGB | 764.102 | 769.641 | 767.033 | 264.84 | GGB | 11167.7 | GGB | 9.85 | GGB | 1002.8 | GGB | 55.56 | GGB | 178866.5 | GGB | 147120.88 | GGB | 0 | 0 | 2838 | 3600 | 2822.09 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 75622.85 | GGB | 75623.77 | 2822.09 | 2822.09 |  |  |  | 1 | 1 |  |  |  |  | 147120.88 | 2822.09 | 147120.88 | 2822.09 | 10.1637 | [5 empty] | 115.3301 | 2568.8264
27.11.2007 20:00 | 3600 | 2 | 756.78 | GGB | 764.102 | 769.57 | 765.934 | 264.45 | GGB | 11216.8 | GGB | 9.86 | GGB | 1003.38 | GGB | 55.47 | GGB | 178341.64 | GGB | 146814.91 | GGB | 0 | 0 | 2836 | 3600 | 2820.18 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 75662.82 | GGB | 75663.74 | 2820.18 | 2820.18 |  |  |  | 1 | 1 |  |  |  |  | 146814.91 | 2820.18 | 146814.91 | 2820.18 | 10.3589 | [5 empty] | 115.0124 | 2574.18
27.11.2007 21:00 | 3600 | 2 | 756.47 | GGB | 764.102 | 769.617 | 765.201 | 265.6 | GGB | 11199.9 | GGB | 9.85 | GGB | 1004.43 | GGB | 55.66 | GGB | 178753.17 | GGB | 147222.91 | GGB | 0 | 0 | 2861 | 3600 | 2845.24 | GGB | 100 | GGB | 41.75 | GGB | 41.75 | GGB | 75704.58 | GGB | 75705.49 | 2845.24 | 2845.24 |  |  |  | 1 | 1 |  |  |  |  | 147222.91 | 2845.24 | 147222.91 | 2845.24 | 10.0332 | [5 empty] | 116.3568 | 2567.0461
27.11.2007 22:00 | 3600 | 2 | 756.72 | GGB | 764.102 | 769.57 | 766.3 | 267.2 | GGB | 11181.3 | GGB | 9.85 | GGB | 1004.83 | GGB | 55.54 | GGB | 180191.31 | GGB | 148524.22 | GGB | 0 | 0 | 2837 | 3600 | 2821.41 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 75744.9 | GGB | 75745.82 | 2821.41 | 2821.41 |  |  |  | 1 | 1 |  |  |  |  | 148524.22 | 2821.41 | 148524.22 | 2821.41 | 10.3905 | [5 empty] | 116.4021 | 2544.5547
27.11.2007 23:00 | 3600 | 2 | 756.89 | GGB | 766.3 | 771.539 | 767.766 | 267.22 | GGB | 11224.4 | GGB | 9.86 | GGB | 1005.86 | GGB | 55.52 | GGB | 180181.41 | GGB | 148675.89 | GGB | 0 | 0 | 2851 | 3600 | 2835.55 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 75785.42 | GGB | 75786.34 | 2835.55 | 2835.55 |  |  |  | 1 | 1 |  |  |  |  | 148675.89 | 2835.55 | 148675.89 | 2835.55 | 10.4042 | [5 empty] | 117.105 | 2541.9589
27.11.2007 24:00 | 3600 | 2 | 756.84 | GGB | 765.201 | 770.508 | 766.667 | 266.75 | GGB | 11230.7 | GGB | 9.86 | GGB | 1006 | GGB | 56.67 | GGB | 178226.11 | GGB | 146567.45 | GGB | 0 | 0 | 2865 | 3600 | 2849.07 | GGB | 100 | GGB | 41.62 | GGB | 41.62 | GGB | 75827.04 | GGB | 75827.96 | 2849.07 | 2849.07 |  |  |  | 1 | 1 |  |  |  |  | 146567.45 | 2849.07 | 146567.45 | 2849.07 | 10.0332 | [5 empty] | 115.9947 | 2578.5261
28.11.2007 01:00 | 3600 | 2 | 756.98 | GGB | 765.201 | 770.461 | 766.667 | 266.74 | GGB | 11222.6 | GGB | 9.85 | GGB | 1006.52 | GGB | 56.73 | GGB | 178178.79 | GGB | 146581.58 | GGB | 0 | 0 | 2864 | 3600 | 2848.28 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 75867.09 | GGB | 75868.01 | 2848.28 | 2848.28 |  |  |  | 1 | 1 |  |  |  |  | 146581.58 | 2848.28 | 146581.58 | 2848.28 | 10.4246 | [5 empty] | 115.9737 | 2578.2776
28.11.2007 02:00 | 3600 | 2 | 756.79 | GGB | 763.004 | 769.406 | 765.201 | 267.07 | GGB | 11223.3 | GGB | 9.85 | GGB | 1007.09 | GGB | 56.69 | GGB | 178307.53 | GGB | 146784.56 | GGB | 0 | 0 | 2868 | 3600 | 2851.99 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 75908.65 | GGB | 75909.57 | 2851.99 | 2851.99 |  |  |  | 0 | 1 | [14 empty] | 116.2856 | 2574.7122
28.11.2007 03:00 | 3600 | 2 | 756.78 | GGB | 765.201 | 771.539 | 767.766 | 268.75 | GGB | 11235.4 | GGB | 9.85 | GGB | 1008.34 | GGB | 55.94 | GGB | 180384.97 | GGB | 149019.43 | GGB | 0 | 0 | 2867 | 3600 | 2851.33 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 75948.86 | GGB | 75949.78 | 2851.33 | 2851.33 |  |  |  | 1 | 1 |  |  |  |  | 149019.43 | 2851.33 | 149019.43 | 2851.33 | 10.5671 | [5 empty] | 118.0288 | 2536.0988
28.11.2007 04:00 | 3600 | 2 | 757.03 | GGB | 765.201 | 770.484 | 767.766 | 267.41 | GGB | 11256.5 | GGB | 9.86 | GGB | 1008.28 | GGB | 56.34 | GGB | 178687.15 | GGB | 147426.86 | GGB | 0 | 0 | 2867 | 3600 | 2851.54 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 75990.13 | GGB | 75991.05 | 2851.54 | 2851.54 |  |  |  | 1 | 1 |  |  |  |  | 147426.86 | 2851.54 | 147426.86 | 2851.54 | 10.1864 | [5 empty] | 116.776 | 2563.4949
28.11.2007 05:00 | 3600 | 2 | 756.76 | GGB | 764.102 | 770.484 | 766.667 | 268.62 | GGB | 11221.5 | GGB | 9.85 | GGB | 1008.81 | GGB | 55.98 | GGB | 180354.16 | GGB | 149045.45 | GGB | 0 | 0 | 2860 | 3600 | 2844.37 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 76031.15 | GGB | 76032.07 | 2844.37 | 2844.37 |  |  |  | 1 | 1 |  |  |  |  | 149045.45 | 2844.37 | 149045.45 | 2844.37 | 10.335 | [5 empty] | 117.7612 | 2535.6561
28.11.2007 06:00 | 3600 | 2 | 757.16 | GGB | 763.004 | 768.398 | 765.201 | 268.37 | GGB | 11255.5 | GGB | 9.86 | GGB | 1009.02 | GGB | 56.09 | GGB | 179788.59 | GGB | 148561.28 | GGB | 0 | 0 | 2859 | 3600 | 2843.36 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 76071.43 | GGB | 76072.35 | 2843.36 | 2843.36 |  |  |  | 0 | 1 | [14 empty] | 117.337 | 2543.9199
28.11.2007 07:00 | 3600 | 2 | 757.01 | GGB | 766.3 | 771.727 | 768.864 | 268.27 | GGB | 11281.6 | GGB | 9.86 | GGB | 1009.31 | GGB | 56.28 | GGB | 179458.49 | GGB | 148244.38 | GGB | 0 | 0 | 2889 | 3600 | 2873.05 | GGB | 100 | GGB | 41.65 | GGB | 41.65 | GGB | 76113.08 | GGB | 76114 | 2873.05 | 2873.05 |  |  |  | 1 | 1 |  |  |  |  | 148244.38 | 2873.05 | 148244.38 | 2873.05 | 10.226 | [5 empty] | 118.3093 | 2549.358
28.11.2007 08:00 | 3600 | 2 | 756.91 | GGB | 765.201 | 770.648 | 767.766 | 269.25 | GGB | 11230 | GGB | 9.85 | GGB | 1009.84 | GGB | 55.72 | GGB | 180776.69 | GGB | 149665.26 | GGB | 0 | 0 | 2860 | 3600 | 2844.31 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 76153.91 | GGB | 76154.83 | 2844.31 | 2844.31 |  |  |  | 1 | 1 |  |  |  |  | 149665.26 | 2844.31 | 149665.26 | 2844.31 | 10.426 | [5 empty] | 118.2484 | 2525.1551
28.11.2007 09:00 | 3600 | 2 | 756.68 | GGB | 767.766 | 771.75 | 768.864 | 270.49 | GGB | 11272.4 | GGB | 9.85 | GGB | 1011.04 | GGB | 55.56 | GGB | 181991.46 | GGB | 150924.51 | GGB | 0 | 0 | 2895 | 3600 | 2879.23 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 76194.39 | GGB | 76195.31 | 2879.23 | 2879.23 |  |  |  | 1 | 1 |  |  |  |  | 150924.51 | 2879.23 | 150924.51 | 2879.23 | 10.7348 | [5 empty] | 120.7073 | 2504.0863
28.11.2007 10:00 | 3600 | 2 | 756.99 | GGB | 764.102 | 769.711 | 766.667 | 269.47 | GGB | 11338.1 | GGB | 9.86 | GGB | 1011.95 | GGB | 56 | GGB | 180518.11 | GGB | 149634.68 | GGB | 0 | 0 | 2913 | 3600 | 2896.97 | GGB | 100 | GGB | 41.76 | GGB | 41.76 | GGB | 76236.15 | GGB | 76237.07 | 2896.97 | 2896.97 |  |  |  | 1 | 1 |  |  |  |  | 149634.68 | 2896.97 | 149634.68 | 2896.97 | 10.3804 | [5 empty] | 120.4131 | 2525.6712
28.11.2007 11:00 | 3600 | 2 | 757.18 | GGB | 765.201 | 770.836 | 767.766 | 268.93 | GGB | 11361.2 | GGB | 9.87 | GGB | 1012.42 | GGB | 55.47 | GGB | 180787.69 | GGB | 150171.63 | GGB | 0 | 0 | 2903 | 3600 | 2887.3 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 76276.86 | GGB | 76277.78 | 2887.3 | 2887.3 |  |  |  | 1 | 1 |  |  |  |  | 150171.63 | 2887.3 | 150171.63 | 2887.3 | 10.6507 | [5 empty] | 120.4418 | 2516.6405
28.11.2007 12:00 | 3600 | 2 | 756.94 | GGB | 765.201 | 769.922 | 766.667 | 268.18 | GGB | 11314.7 | GGB | 9.86 | GGB | 1012.51 | GGB | 55.42 | GGB | 180706.27 | GGB | 150140.43 | GGB | 0 | 0 | 2896 | 3600 | 2879.97 | GGB | 100 | GGB | 42.04 | GGB | 42.04 | GGB | 76318.9 | GGB | 76319.82 | 2879.97 | 2879.97 |  |  |  | 1 | 1 |  |  |  |  | 150140.43 | 2879.97 | 150140.43 | 2879.97 | 10.2854 | [5 empty] | 120.1111 | 2517.1634
28.11.2007 13:00 | 3600 | 2 | 757.17 | GGB | 763.004 | 768.75 | 765.201 | 268.09 | GGB | 11264.2 | GGB | 9.86 | GGB | 1012.5 | GGB | 54.97 | GGB | 181537.02 | GGB | 151034.81 | GGB | 0 | 0 | 2847 | 3600 | 2830.98 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 76359.8 | GGB | 76360.71 | 2830.98 | 2830.98 |  |  |  | 0 | 1 | [14 empty] | 118.7713 | 2502.2576
28.11.2007 14:00 | 3600 | 2 | 757.87 | GGB | 765.201 | 770.883 | 767.033 | 266.33 | GGB | 11283.1 | GGB | 9.87 | GGB | 1012.31 | GGB | 55.74 | GGB | 178549.61 | GGB | 148174.98 | GGB | 0 | 0 | 2823 | 3600 | 2807.52 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 76400.81 | GGB | 76401.72 | 2807.52 | 2807.52 |  |  |  | 1 | 1 |  |  |  |  | 148174.98 | 2807.52 | 148174.98 | 2807.52 | 10.144 | [5 empty] | 115.5567 | 2550.5521
28.11.2007 15:00 | 3600 | 2 | 756.54 | GGB | 764.102 | 770.063 | 767.033 | 267.12 | GGB | 11254 | GGB | 9.85 | GGB | 1012.72 | GGB | 55.88 | GGB | 178478.08 | GGB | 148112.47 | GGB | 0 | 0 | 2891 | 3600 | 2875.51 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 76442.17 | GGB | 76443.08 | 2875.51 | 2875.51 |  |  |  | 1 | 1 |  |  |  |  | 148112.47 | 2875.51 | 148112.47 | 2875.51 | 10.2974 | [5 empty] | 118.3052 | 2551.6285
28.11.2007 16:00 | 3600 | 2 | 756.95 | GGB | 765.201 | 770.016 | 766.667 | 267.61 | GGB | 11262.3 | GGB | 9.86 | GGB | 1013.18 | GGB | 56.31 | GGB | 178291.03 | GGB | 147829.98 | GGB | 0 | 0 | 2888 | 3600 | 2872.01 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 76482.9 | GGB | 76483.81 | 2872.01 | 2872.01 |  |  |  | 1 | 1 |  |  |  |  | 147829.98 | 2872.01 | 147829.98 | 2872.01 | 10.424 | [5 empty] | 117.9359 | 2556.5044
28.11.2007 17:00 | 3600 | 2 | 756.36 | GGB | 764.102 | 770.016 | 765.201 | 268.28 | GGB | 11261 | GGB | 9.85 | GGB | 1013.12 | GGB | 56.21 | GGB | 178524.3 | GGB | 148061.78 | GGB | 0 | 0 | 2922 | 3600 | 2906.31 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 76524.1 | GGB | 76525.02 | 2906.31 | 2906.31 |  |  |  | 1 | 1 |  |  |  |  | 148061.78 | 2906.31 | 148061.78 | 2906.31 | 10.442 | [5 empty] | 119.5315 | 2552.5021
28.11.2007 18:00 | 3600 | 2 | 756.59 | GGB | 764.102 | 770.016 | 766.3 | 269.16 | GGB | 11285.3 | GGB | 9.85 | GGB | 1013.07 | GGB | 56.2 | GGB | 179204.31 | GGB | 148622.65 | GGB | 0 | 0 | 2924 | 3600 | 2908.78 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 76565.16 | GGB | 76566.08 | 2908.78 | 2908.78 |  |  |  | 1 | 1 |  |  |  |  | 148622.65 | 2908.78 | 148622.65 | 2908.78 | 10.5288 | [5 empty] | 120.0863 | 2542.8695
28.11.2007 19:00 | 3600 | 2 | 757.02 | GGB | 764.102 | 768.914 | 765.201 | 269.01 | GGB | 11292.6 | GGB | 9.86 | GGB | 1013.46 | GGB | 56.33 | GGB | 179132.79 | GGB | 148558.09 | GGB | 0 | 0 | 2900 | 3600 | 2884.56 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 76606.02 | GGB | 76606.94 | 2884.56 | 2884.56 |  |  |  | 1 | 1 |  |  |  |  | 148558.09 | 2884.56 | 148558.09 | 2884.56 | 10.4876 | [5 empty] | 119.0346 | 2543.9745
28.11.2007 20:00 | 3600 | 2 | 756.42 | GGB | 764.102 | 769.922 | 766.3 | 268.9 | GGB | 11278.2 | GGB | 9.85 | GGB | 1013.43 | GGB | 56.1 | GGB | 179228.51 | GGB | 148740.76 | GGB | 0 | 0 | 2921 | 3600 | 2905.26 | GGB | 100 | GGB | 41.52 | GGB | 41.52 | GGB | 76647.54 | GGB | 76648.46 | 2905.26 | 2905.26 |  |  |  | 1 | 1 |  |  |  |  | 148740.76 | 2905.26 | 148740.76 | 2905.26 | 10.4078 | [5 empty] | 120.0363 | 2540.8503
28.11.2007 21:00 | 3600 | 2 | 756.37 | GGB | 764.102 | 768.984 | 765.201 | 270.13 | GGB | 11289.7 | GGB | 9.84 | GGB | 1013.65 | GGB | 56.7 | GGB | 180814.1 | GGB | 149817.23 | GGB | 0 | 0 | 2930 | 3600 | 2914.31 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 76688.24 | GGB | 76689.16 | 2914.31 | 2914.31 |  |  |  | 1 | 1 |  |  |  |  | 149817.23 | 2914.31 | 149817.23 | 2914.31 | 10.7276 | [5 empty] | 121.2816 | 2522.5937
28.11.2007 22:00 | 3600 | 2 | 756.72 | GGB | 766.3 | 771.164 | 767.766 | 271.47 | GGB | 11306 | GGB | 9.85 | GGB | 1013.99 | GGB | 56.07 | GGB | 183140.22 | GGB | 152084.6 | GGB | 0 | 0 | 2907 | 3600 | 2891.87 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 76729.51 | GGB | 76730.43 | 2891.87 | 2891.87 |  |  |  | 1 | 1 |  |  |  |  | 152084.6 | 2891.87 | 152084.6 | 2891.87 | 10.6569 | [5 empty] | 122.1691 | 2484.9853
28.11.2007 23:00 | 3600 | 2 | 758.55 | GGB | 766.667 | 771.984 | 768.864 | 268.49 | GGB | 11309.3 | GGB | 9.89 | GGB | 1013.39 | GGB | 56.31 | GGB | 180499.4 | GGB | 149692.29 | GGB | 0 | 0 | 2802 | 3600 | 2786.69 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 76770.5 | GGB | 76771.42 | 2786.69 | 2786.69 |  |  |  | 1 | 1 |  |  |  |  | 149692.29 | 2786.69 | 149692.29 | 2786.69 | 10.1768 | [5 empty] | 115.8739 | 2524.6992
28.11.2007 24:00 | 3600 | 2 | 757.11 | GGB | 765.201 | 769.898 | 767.766 | 267.16 | GGB | 11276.6 | GGB | 9.85 | GGB | 1012.86 | GGB | 56.74 | GGB | 178965.53 | GGB | 148151.94 | GGB | 0 | 0 | 2868 | 3600 | 2851.96 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 76811.59 | GGB | 76812.51 | 2851.96 | 2851.96 |  |  |  | 1 | 1 |  |  |  |  | 148151.94 | 2851.96 | 148151.94 | 2851.96 | 10.2829 | [5 empty] | 117.3676 | 2550.9487
29.11.2007 01:00 | 3600 | 2 | 756.87 | GGB | 765.201 | 769.852 | 766.3 | 267.43 | GGB | 11253.2 | GGB | 9.85 | GGB | 1012.31 | GGB | 56.51 | GGB | 179550.91 | GGB | 148656.73 | GGB | 0 | 0 | 2861 | 3600 | 2845.1 | GGB | 100 | GGB | 42.05 | GGB | 42.05 | GGB | 76853.64 | GGB | 76854.56 | 2845.1 | 2845.1 |  |  |  | 1 | 1 |  |  |  |  | 148656.73 | 2845.1 | 148656.73 | 2845.1 | 10.0581 | [5 empty] | 117.4842 | 2542.2865
29.11.2007 02:00 | 3600 | 2 | 757.59 | GGB | 767.766 | 772.031 | 768.864 | 267.4 | GGB | 11239.2 | GGB | 9.87 | GGB | 1012.17 | GGB | 56.07 | GGB | 179939.33 | GGB | 149155.03 | GGB | 0 | 0 | 2810 | 3600 | 2794.42 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 76893.95 | GGB | 76894.86 | 2794.42 | 2794.42 |  |  |  | 1 | 1 |  |  |  |  | 149155.03 | 2794.42 | 149155.03 | 2794.42 | 10.3425 | [5 empty] | 115.7783 | 2533.7932
29.11.2007 03:00 | 3600 | 2 | 757.63 | GGB | 765.201 | 769.875 | 767.766 | 264.81 | GGB | 11229.4 | GGB | 9.87 | GGB | 1011.3 | GGB | 56.81 | GGB | 176803.37 | GGB | 146101.75 | GGB | 0 | 0 | 2802 | 3600 | 2786.2 | GGB | 100 | GGB | 41.68 | GGB | 41.68 | GGB | 76935.63 | GGB | 76936.54 | 2786.2 | 2786.2 |  |  |  | 1 | 1 |  |  |  |  | 146101.75 | 2786.2 | 146101.75 | 2786.2 | 9.7665 | [5 empty] | 113.0746 | 2586.7452
29.11.2007 04:00 | 3600 | 2 | 757.2 | GGB | 764.102 | 769.922 | 766.667 | 264.75 | GGB | 11200 | GGB | 9.85 | GGB | 1010.65 | GGB | 56.86 | GGB | 176545.89 | GGB | 145773.15 | GGB | 0 | 0 | 2810 | 3600 | 2794.63 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 76975.94 | GGB | 76976.85 | 2794.63 | 2794.63 |  |  |  | 1 | 1 |  |  |  |  | 145773.15 | 2794.63 | 145773.15 | 2794.63 | 10.1062 | [5 empty] | 113.1617 | 2592.5762
29.11.2007 05:00 | 3600 | 2 | 756.96 | GGB | 764.102 | 768.938 | 765.201 | 264.91 | GGB | 11198.3 | GGB | 9.85 | GGB | 1009.78 | GGB | 56.78 | GGB | 176554.69 | GGB | 145692.77 | GGB | 0 | 0 | 2826 | 3600 | 2810.65 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 77017.21 | GGB | 77018.12 | 2810.65 | 2810.65 |  |  |  | 1 | 1 |  |  |  |  | 145692.77 | 2810.65 | 145692.77 | 2810.65 | 9.9223 | [5 empty] | 113.7476 | 2594.0066
29.11.2007 06:00 | 3600 | 2 | 757.21 | GGB | 764.102 | 769.031 | 766.667 | 264.93 | GGB | 11205.6 | GGB | 9.86 | GGB | 1009.07 | GGB | 56.75 | GGB | 176698.84 | GGB | 145721.28 | GGB | 0 | 0 | 2819 | 3600 | 2803.46 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 77058.11 | GGB | 77059.02 | 2803.46 | 2803.46 |  |  |  | 1 | 1 |  |  |  |  | 145721.28 | 2803.46 | 145721.28 | 2803.46 | 9.9884 | [5 empty] | 113.4788 | 2593.499
29.11.2007 07:00 | 3600 | 2 | 756.65 | GGB | 765.201 | 770.18 | 766.667 | 265.55 | GGB | 11169.6 | GGB | 9.85 | GGB | 1008.44 | GGB | 56.63 | GGB | 177394.25 | GGB | 146257.82 | GGB | 0 | 0 | 2829 | 3600 | 2813.77 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 77098.93 | GGB | 77099.84 | 2813.77 | 2813.77 |  |  |  | 1 | 1 |  |  |  |  | 146257.82 | 2813.77 | 146257.82 | 2813.77 | 10.0817 | [5 empty] | 114.3155 | 2583.9849
29.11.2007 08:00 | 3600 | 2 | 757.52 | GGB | 765.201 | 771.188 | 767.766 | 265.49 | GGB | 11149.1 | GGB | 9.87 | GGB | 1008.04 | GGB | 56.23 | GGB | 178022.54 | GGB | 146895.6 | GGB | 0 | 0 | 2759 | 3600 | 2743.36 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 77139.8 | GGB | 77140.71 | 2743.36 | 2743.36 |  |  |  | 1 | 1 |  |  |  |  | 146895.6 | 2743.36 | 146895.6 | 2743.36 | 9.8602 | [5 empty] | 111.941 | 2572.766
29.11.2007 09:00 | 3600 | 2 | 757.05 | GGB | 764.102 | 768.773 | 766.3 | 263.68 | GGB | 11162.2 | GGB | 9.86 | GGB | 1007.4 | GGB | 56.9 | GGB | 175414.74 | GGB | 144359.04 | GGB | 0 | 0 | 2801 | 3600 | 2785.1 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 77180.3 | GGB | 77181.21 | 2785.1 | 2785.1 |  |  |  | 1 | 1 |  |  |  |  | 144359.04 | 2785.1 | 144359.04 | 2785.1 | 9.9273 | [5 empty] | 111.6818 | 2617.9725
29.11.2007 10:00 | 3600 | 2 | 757.19 | GGB | 764.102 | 769.969 | 766.667 | 263.58 | GGB | 11175.5 | GGB | 9.86 | GGB | 1006.62 | GGB | 56.72 | GGB | 175586.4 | GGB | 144466.49 | GGB | 0 | 0 | 2805 | 3600 | 2789.67 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 77221.28 | GGB | 77222.2 | 2789.67 | 2789.67 |  |  |  | 1 | 1 |  |  |  |  | 144466.49 | 2789.67 | 144466.49 | 2789.67 | 9.832 | [5 empty] | 111.9483 | 2616.0253
29.11.2007 11:00 | 3600 | 2 | 756.55 | GGB | 765.201 | 769.898 | 767.766 | 264.18 | GGB | 11138 | GGB | 9.85 | GGB | 1006.23 | GGB | 56.37 | GGB | 176813.27 | GGB | 145573.32 | GGB | 0 | 0 | 2799 | 3600 | 2783.9 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 77262.09 | GGB | 77263.01 | 2783.9 | 2783.9 |  |  |  | 1 | 1 |  |  |  |  | 145573.32 | 2783.9 | 145573.32 | 2783.9 | 9.9304 | [5 empty] | 112.5727 | 2596.1351
29.11.2007 12:00 | 3600 | 2 | 756.77 | GGB | 764.102 | 769.922 | 766.667 | 264.51 | GGB | 11121.5 | GGB | 9.86 | GGB | 1005.74 | GGB | 56.02 | GGB | 177481.18 | GGB | 146208.19 | GGB | 0 | 0 | 2758 | 3600 | 2742.29 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 77302.27 | GGB | 77303.18 | 2742.29 | 2742.29 |  |  |  | 1 | 1 |  |  |  |  | 146208.19 | 2742.29 | 146208.19 | 2742.29 | 9.9812 | [5 empty] | 111.3737 | 2584.862
29.11.2007 13:00 | 3600 | 2 | 756.76 | GGB | 765.201 | 769.922 | 767.766 | 264.19 | GGB | 11124.6 | GGB | 9.86 | GGB | 1004.91 | GGB | 55.26 | GGB | 177195.09 | GGB | 146189.69 | GGB | 0 | 0 | 2759 | 3600 | 2743.47 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 77343.45 | GGB | 77344.37 | 2743.47 | 2743.47 |  |  |  | 1 | 1 |  |  |  |  | 146189.69 | 2743.47 | 146189.69 | 2743.47 | 9.737 | [5 empty] | 111.4075 | 2585.1891
29.11.2007 14:00 | 3600 | 2 | 756.81 | GGB | 765.201 | 769.945 | 766.667 | 262.15 | GGB | 11143.5 | GGB | 9.86 | GGB | 1004.13 | GGB | 56.34 | GGB | 174656.61 | GGB | 143512.95 | GGB | 0 | 0 | 2778 | 3600 | 2762.1 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 77383.87 | GGB | 77384.79 | 2762.1 | 2762.1 |  |  |  | 1 | 1 |  |  |  |  | 143512.95 | 2762.1 | 143512.95 | 2762.1 | 9.807 | [5 empty] | 110.1103 | 2633.407
29.11.2007 15:00 | 3600 | 2 | 756.05 | GGB | 762.637 | 768.586 | 765.201 | 263.05 | GGB | 11131.9 | GGB | 9.85 | GGB | 1003.74 | GGB | 56.48 | GGB | 175091.24 | GGB | 143751.26 | GGB | 0 | 0 | 2821 | 3600 | 2805.55 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 77423.95 | GGB | 77424.87 | 2805.55 | 2805.55 |  |  |  | 0 | 1 | [14 empty] | 112.0282 | 2629.0413
29.11.2007 16:00 | 3600 | 2 | 757.2 | GGB | 765.201 | 770.813 | 767.766 | 263.27 | GGB | 11103.9 | GGB | 9.87 | GGB | 1003.24 | GGB | 57.26 | GGB | 173851.16 | GGB | 142325.84 | GGB | 0 | 0 | 2759 | 3600 | 2743.27 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 77464.67 | GGB | 77465.59 | 2743.27 | 2743.27 |  |  |  | 1 | 1 |  |  |  |  | 142325.84 | 2743.27 | 142325.84 | 2743.27 | 9.5884 | [5 empty] | 108.4551 | 2655.3716
29.11.2007 17:00 | 3600 | 2 | 755.72 | GNB | 765.201 | 769.734 | 766.3 | 264.05 | GGB | 11060.4 | GGB | 9.84 | GGB | 1002.91 | GGB | 57.18 | GGB | 173920.49 | GGB | 142369.89 | GGB | 0 | 0 | 2811 | 3600 | 2795.74 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 77505.29 | GGB | 77506.21 | 2795.74 | 2795.74 |  |  |  | 0 | 1 | [14 empty] | 110.5637 | 2654.5501
29.11.2007 18:00 | 3600 | 2 | 757.11 | GGB | 765.201 | 770.789 | 767.766 | 264.4 | GGB | 11099.7 | GGB | 9.87 | GGB | 1002.95 | GGB | 56.95 | GGB | 174054.73 | GGB | 142585.01 | GGB | 0 | 0 | 2772 | 3600 | 2756.29 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 77545.06 | GGB | 77545.98 | 2756.29 | 2756.29 |  |  |  | 1 | 1 |  |  |  |  | 142585.01 | 2756.29 | 142585.01 | 2756.29 | 9.882 | [5 empty] | 109.1682 | 2650.5451
29.11.2007 19:00 | 3600 | 2 | 756.65 | GGB | 764.102 | 769.453 | 766.667 | 264.04 | GGB | 11075.9 | GGB | 9.85 | GGB | 1002.65 | GGB | 57.12 | GGB | 173995.31 | GGB | 142417.77 | GGB | 0 | 0 | 2780 | 3600 | 2764.96 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 77585.92 | GGB | 77586.84 | 2764.96 | 2764.96 |  |  |  | 1 | 1 |  |  |  |  | 142417.77 | 2764.96 | 142417.77 | 2764.96 | 9.6373 | [5 empty] | 109.3832 | 2653.6576
29.11.2007 20:00 | 3600 | 2 | 756.65 | GGB | 764.102 | 769.594 | 766.3 | 264.46 | GGB | 11102.9 | GGB | 9.85 | GGB | 1002.26 | GGB | 57.16 | GGB | 174436.54 | GGB | 142707.38 | GGB | 0 | 0 | 2789 | 3600 | 2773.88 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 77625.58 | GGB | 77626.5 | 2773.88 | 2773.88 |  |  |  | 1 | 1 |  |  |  |  | 142707.38 | 2773.88 | 142707.38 | 2773.88 | 9.9812 | [5 empty] | 109.9592 | 2648.2723
29.11.2007 21:00 | 3600 | 2 | 757.06 | GGB | 764.102 | 770.602 | 766.667 | 264.19 | GGB | 11114.8 | GGB | 9.86 | GGB | 1001.9 | GGB | 57.07 | GGB | 174861.27 | GGB | 143042.59 | GGB | 0 | 0 | 2771 | 3600 | 2755.29 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 77666.59 | GGB | 77667.51 | 2755.29 | 2755.29 |  |  |  | 1 | 1 |  |  |  |  | 143042.59 | 2755.29 | 143042.59 | 2755.29 | 9.6104 | [5 empty] | 109.4788 | 2642.0663
29.11.2007 22:00 | 3600 | 2 | 756.43 | GGB | 764.102 | 769.5 | 766.3 | 264.33 | GGB | 11125.9 | GGB | 9.85 | GGB | 1001.54 | GGB | 56.65 | GGB | 175806.46 | GGB | 143945.07 | GGB | 0 | 0 | 2802 | 3600 | 2786.51 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 77706.92 | GGB | 77707.84 | 2786.51 | 2786.51 |  |  |  | 1 | 1 |  |  |  |  | 143945.07 | 2786.51 | 143945.07 | 2786.51 | 9.9456 | [5 empty] | 111.4179 | 2625.5015
29.11.2007 23:00 | 3600 | 2 | 757.37 | GGB | 764.102 | 770.508 | 766.667 | 264.1 | GGB | 11128 | GGB | 9.87 | GGB | 1000.92 | GGB | 56.81 | GGB | 175412.54 | GGB | 143468.6 | GGB | 0 | 0 | 2754 | 3600 | 2738.54 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 77747.74 | GGB | 77748.66 | 2738.54 | 2738.54 |  |  |  | 1 | 1 |  |  |  |  | 143468.6 | 2738.54 | 143468.6 | 2738.54 | 9.625 | [5 empty] | 109.1374 | 2634.221
29.11.2007 24:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 769.547 | 766.667 | 263.8 | GGB | 11112.2 | GGB | 9.86 | GGB | 1000.53 | GGB | 56.75 | GGB | 175196.88 | GGB | 143260.26 | GGB | 0 | 0 | 2765 | 3600 | 2749.16 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 77787.61 | GGB | 77788.53 | 2749.16 | 2749.16 |  |  |  | 1 | 1 |  |  |  |  | 143260.26 | 2749.16 | 143260.26 | 2749.16 | 9.8782 | [5 empty] | 109.4015 | 2638.0519
30.11.2007 01:00 | 3600 | 2 | 756.97 | GGB | 765.201 | 770.414 | 766.667 | 263.58 | GGB | 11098.1 | GGB | 9.86 | GGB | 1000.42 | GGB | 56.9 | GGB | 174870.08 | GGB | 142912.96 | GGB | 0 | 0 | 2763 | 3600 | 2747.95 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 77828.41 | GGB | 77829.33 | 2747.95 | 2747.95 |  |  |  | 1 | 1 |  |  |  |  | 142912.96 | 2747.95 | 142912.96 | 2747.95 | 9.6254 | [5 empty] | 109.0882 | 2644.4628
30.11.2007 02:00 | 3600 | 2 | 756.92 | GGB | 765.201 | 770.391 | 767.766 | 263.4 | GGB | 11088.2 | GGB | 9.86 | GGB | 999.96 | GGB | 56.88 | GGB | 174634.6 | GGB | 142662.99 | GGB | 0 | 0 | 2761 | 3600 | 2745.05 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 77868.62 | GGB | 77869.54 | 2745.05 | 2745.05 |  |  |  | 1 | 1 |  |  |  |  | 142662.99 | 2745.05 | 142662.99 | 2745.05 | 9.7393 | [5 empty] | 108.7825 | 2649.0963
30.11.2007 03:00 | 3600 | 2 | 757.21 | GGB | 765.201 | 770.438 | 767.766 | 263.26 | GGB | 11081.2 | GGB | 9.86 | GGB | 999.56 | GGB | 57.27 | GGB | 174248.39 | GGB | 142123.56 | GGB | 0 | 0 | 2739 | 3600 | 2723.52 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 77908.99 | GGB | 77909.91 | 2723.52 | 2723.52 |  |  |  | 1 | 1 |  |  |  |  | 142123.56 | 2723.52 | 142123.56 | 2723.52 | 9.5882 | [5 empty] | 107.5212 | 2659.151
30.11.2007 04:00 | 3600 | 2 | 756.94 | GGB | 765.201 | 770.344 | 767.766 | 262.98 | GGB | 11075.8 | GGB | 9.86 | GGB | 999.06 | GGB | 56.97 | GGB | 174214.28 | GGB | 142150.63 | GGB | 0 | 0 | 2755 | 3600 | 2739.98 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 77949.86 | GGB | 77950.78 | 2739.98 | 2739.98 |  |  |  | 1 | 1 |  |  |  |  | 142150.63 | 2739.98 | 142150.63 | 2739.98 | 9.53 | [5 empty] | 108.1916 | 2658.6446
30.11.2007 05:00 | 3600 | 2 | 756.9 | GGB | 765.201 | 770.367 | 766.667 | 262.79 | GGB | 11065.7 | GGB | 9.86 | GGB | 998.76 | GGB | 57.04 | GGB | 173951.29 | GGB | 141864.86 | GGB | 0 | 0 | 2751 | 3600 | 2735.56 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 77989.75 | GGB | 77990.67 | 2735.56 | 2735.56 |  |  |  | 1 | 1 |  |  |  |  | 141864.86 | 2735.56 | 141864.86 | 2735.56 | 9.7287 | [5 empty] | 107.8 | 2664.0001
30.11.2007 06:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 771.234 | 767.033 | 262.56 | GGB | 11056.7 | GGB | 9.86 | GGB | 998.65 | GGB | 57.4 | GGB | 173440.74 | GGB | 141280.51 | GGB | 0 | 0 | 2741 | 3600 | 2725.82 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 78030.5 | GGB | 78031.41 | 2725.82 | 2725.82 |  |  |  | 1 | 1 |  |  |  |  | 141280.51 | 2725.82 | 141280.51 | 2725.82 | 9.4528 | [5 empty] | 106.9737 | 2675.0187
30.11.2007 07:00 | 3600 | 2 | 756.83 | GGB | 765.201 | 770.203 | 767.033 | 262.45 | GGB | 11039.4 | GGB | 9.86 | GGB | 998.28 | GGB | 57.62 | GGB | 173412.13 | GGB | 141110.27 | GGB | 0 | 0 | 2743 | 3600 | 2727.1 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 78070.41 | GGB | 78071.32 | 2727.1 | 2727.1 |  |  |  | 1 | 1 |  |  |  |  | 141110.27 | 2727.1 | 141110.27 | 2727.1 | 9.6422 | [5 empty] | 106.8949 | 2678.2459
30.11.2007 08:00 | 3600 | 2 | 756.88 | GGB | 766.3 | 771.305 | 768.132 | 262.49 | GGB | 11035.2 | GGB | 9.86 | GGB | 997.86 | GGB | 57.56 | GGB | 173106.24 | GGB | 140828.49 | GGB | 0 | 0 | 2736 | 3209 | 2720.54 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 78110.64 | GGB | 78111.56 | 2720.54 | 2720.54 |  |  |  | 1 | 1 |  |  |  |  | 140828.49 | 2720.54 | 140828.49 | 2720.54 | 9.5211 | [5 empty] | 106.4249 | 2683.6047
30.11.2007 09:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 770.977 | 767.033 | 262.8 | GGB | 11016.7 | GGB | 9.86 | GGB | 998.12 | GGB | 57.93 | GGB | 172762.93 | GGB | 140425.06 | GGB | 0 | 0 | 2721 | 3600 | 2705.35 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 78150.97 | GGB | 78151.89 | 2705.35 | 2705.35 |  |  |  | 1 | 1 |  |  |  |  | 140425.06 | 2705.35 | 140425.06 | 2705.35 | 9.4198 | [5 empty] | 105.5275 | 2691.3145
30.11.2007 10:00 | 3600 | 2 | 756.8 | GGB | 765.201 | 770.789 | 767.033 | 262.76 | GGB | 11012.6 | GGB | 9.85 | GGB | 998.11 | GGB | 58.05 | GGB | 172773.93 | GGB | 140385.15 | GGB | 0 | 0 | 2725 | 3600 | 2709.37 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 78190.6 | GGB | 78191.52 | 2709.37 | 2709.37 |  |  |  | 1 | 1 |  |  |  |  | 140385.15 | 2709.37 | 140385.15 | 2709.37 | 9.5977 | [5 empty] | 105.6543 | 2692.0796
30.11.2007 11:00 | 3600 | 2 | 756.63 | GGB | 764.102 | 770.766 | 767.033 | 262.68 | GGB | 11015.3 | GGB | 9.86 | GGB | 998.04 | GGB | 58.04 | GGB | 172628.69 | GGB | 140261.5 | GGB | 0 | 0 | 2717 | 3600 | 2701.09 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 78231.13 | GGB | 78232.05 | 2701.09 | 2701.09 |  |  |  | 1 | 1 |  |  |  |  | 140261.5 | 2701.09 | 140261.5 | 2701.09 | 9.3476 | [5 empty] | 105.2386 | 2694.4529
30.11.2007 12:00 | 3600 | 2 | 756.5 | GGB | 764.102 | 769.617 | 767.033 | 262.74 | GGB | 11013.9 | GGB | 9.85 | GGB | 997.79 | GGB | 57.9 | GGB | 172747.53 | GGB | 140381.87 | GGB | 0 | 0 | 2731 | 3600 | 2715.27 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 78270.94 | GGB | 78271.86 | 2715.27 | 2715.27 |  |  |  | 1 | 1 |  |  |  |  | 140381.87 | 2715.27 | 140381.87 | 2715.27 | 9.5748 | [5 empty] | 105.8819 | 2692.1425
30.11.2007 13:00 | 3600 | 2 | 756.49 | GGB | 764.102 | 769.758 | 767.033 | 262.86 | GGB | 11038.8 | GGB | 9.86 | GGB | 997.6 | GGB | 57.5 | GGB | 173173.36 | GGB | 140870.12 | GGB | 0 | 0 | 2745 | 3600 | 2729.29 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 78310.98 | GGB | 78311.9 | 2729.29 | 2729.29 |  |  |  | 1 | 1 |  |  |  |  | 140870.12 | 2729.29 | 140870.12 | 2729.29 | 9.6023 | [5 empty] | 106.7987 | 2682.8117
30.11.2007 14:00 | 3600 | 2 | 756.61 | GGB | 764.102 | 769.195 | 767.033 | 262.62 | GGB | 11037.4 | GGB | 9.85 | GGB | 997.3 | GGB | 57.39 | GGB | 173209.67 | GGB | 140904.13 | GGB | 0 | 0 | 2747 | 3600 | 2731.35 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 78351.63 | GGB | 78352.55 | 2731.35 | 2731.35 |  |  |  | 1 | 1 |  |  |  |  | 140904.13 | 2731.35 | 140904.13 | 2731.35 | 9.4676 | [5 empty] | 106.9051 | 2682.1641
30.11.2007 15:00 | 3600 | 2 | 756.93 | GGB | 764.102 | 770.086 | 767.766 | 262.41 | GGB | 11038.9 | GGB | 9.86 | GGB | 997.53 | GGB | 57.87 | GGB | 173126.04 | GGB | 140663.7 | GGB | 0 | 0 | 2728 | 3600 | 2712.27 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 78391.29 | GGB | 78392.21 | 2712.27 | 2712.27 |  |  |  | 1 | 1 |  |  |  |  | 140663.7 | 2712.27 | 140663.7 | 2712.27 | 9.6197 | [5 empty] | 105.9772 | 2686.7486
30.11.2007 16:00 | 3600 | 2 | 756.82 | GGB | 764.102 | 770.18 | 766.667 | 262.35 | GGB | 11029.6 | GGB | 9.86 | GGB | 997.61 | GGB | 57.9 | GGB | 172897.17 | GGB | 140477.83 | GGB | 0 | 0 | 2730 | 3600 | 2714.21 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 78431.8 | GGB | 78432.72 | 2714.21 | 2714.21 |  |  |  | 1 | 1 |  |  |  |  | 140477.83 | 2714.21 | 140477.83 | 2714.21 | 9.4122 | [5 empty] | 105.9129 | 2690.3035
30.11.2007 17:00 | 3600 | 2 | 756.65 | GGB | 765.201 | 770.18 | 766.667 | 262.42 | GGB | 11028.1 | GGB | 9.85 | GGB | 997.8 | GGB | 57.74 | GGB | 172951.09 | GGB | 140617.72 | GGB | 0 | 0 | 2736 | 3600 | 2720.56 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 78471.84 | GGB | 78472.76 | 2720.56 | 2720.56 |  |  |  | 1 | 1 |  |  |  |  | 140617.72 | 2720.56 | 140617.72 | 2720.56 | 9.5544 | [5 empty] | 106.2664 | 2687.6271
30.11.2007 18:00 | 3600 | 2 | 756.61 | GGB | 764.102 | 770.18 | 766.667 | 262.74 | GGB | 11040.1 | GGB | 9.85 | GGB | 997.93 | GGB | 57.5 | GGB | 173242.68 | GGB | 140973.71 | GGB | 0 | 0 | 2750 | 3600 | 2734.08 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 78512.1 | GGB | 78513.02 | 2734.08 | 2734.08 |  |  |  | 1 | 1 |  |  |  |  | 140973.71 | 2734.08 | 140973.71 | 2734.08 | 9.5736 | [5 empty] | 107.0648 | 2680.8403
30.11.2007 19:00 | 3600 | 2 | 756.58 | GGB | 765.201 | 770.438 | 766.667 | 262.99 | GGB | 11040.6 | GGB | 9.86 | GGB | 998.24 | GGB | 57.51 | GGB | 173203.07 | GGB | 140979.63 | GGB | 0 | 0 | 2751 | 3600 | 2736.01 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 78552.28 | GGB | 78553.2 | 2736.01 | 2736.01 |  |  |  | 1 | 1 |  |  |  |  | 140979.63 | 2736.01 | 140979.63 | 2736.01 | 9.5998 | [5 empty] | 107.1449 | 2680.7277
30.11.2007 20:00 | 3600 | 2 | 756.78 | GGB | 765.201 | 770.414 | 767.766 | 263.21 | GGB | 11044 | GGB | 9.86 | GGB | 998.71 | GGB | 57.57 | GGB | 173256.98 | GGB | 141063.17 | GGB | 0 | 0 | 2749 | 3600 | 2733.3 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 78592.26 | GGB | 78593.18 | 2733.3 | 2733.3 |  |  |  | 1 | 1 |  |  |  |  | 141063.17 | 2733.3 | 141063.17 | 2733.3 | 9.644 | [5 empty] | 107.1022 | 2679.1401
30.11.2007 21:00 | 3600 | 2 | 756.71 | GGB | 764.102 | 770.414 | 766.667 | 263.35 | GGB | 11045.5 | GGB | 9.85 | GGB | 999 | GGB | 57.55 | GGB | 173431.94 | GGB | 141259.66 | GGB | 0 | 0 | 2761 | 3600 | 2745.15 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 78632.59 | GGB | 78633.52 | 2745.15 | 2745.15 |  |  |  | 1 | 1 |  |  |  |  | 141259.66 | 2745.15 | 141259.66 | 2745.15 | 9.6128 | [5 empty] | 107.7164 | 2675.4135
30.11.2007 22:00 | 3600 | 2 | 757.02 | GGB | 765.201 | 770.203 | 767.766 | 263.24 | GGB | 11053.2 | GGB | 9.86 | GGB | 999.64 | GGB | 57.83 | GGB | 173364.81 | GGB | 141172.51 | GGB | 0 | 0 | 2749 | 3600 | 2733.67 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 78672.64 | GGB | 78673.57 | 2733.67 | 2733.67 |  |  |  | 1 | 1 |  |  |  |  | 141172.51 | 2733.67 | 141172.51 | 2733.67 | 9.6359 | [5 empty] | 107.1997 | 2677.0651
30.11.2007 23:00 | 3600 | 2 | 756.72 | GGB | 762.637 | 768.188 | 764.102 | 262.8 | GGB | 11058.2 | GGB | 9.85 | GGB | 999.97 | GGB | 57.71 | GGB | 173782.94 | GGB | 141612.47 | GGB | 0 | 0 | 2751 | 3600 | 2735.58 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 78711.21 | GGB | 78712.14 | 2735.58 | 2735.58 |  |  |  | 0 | 1 | [14 empty] | 107.609 | 2668.748
30.11.2007 24:00 | 3600 | 2 | 756.73 | GGB | 765.201 | 770.297 | 767.766 | 263.29 | GGB | 11058.1 | GGB | 9.86 | GGB | 1000.37 | GGB | 57.91 | GGB | 173731.23 | GGB | 141539.19 | GGB | 0 | 0 | 2763 | 3600 | 2747.82 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 78752.49 | GGB | 78753.42 | 2747.82 | 2747.82 |  |  |  | 1 | 1 |  |  |  |  | 141539.19 | 2747.82 | 141539.19 | 2747.82 | 9.4216 | [5 empty] | 108.0345 | 2670.1297
01.12.2007 01:00 | 3600 | 2 | 756.9 | GGB | 764.102 | 770.391 | 766.667 | 263.24 | GGB | 11057.5 | GGB | 9.86 | GGB | 1000.64 | GGB | 57.86 | GGB | 173690.51 | GGB | 141567.49 | GGB | 0 | 0 | 2750 | 3600 | 2734.99 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 78792.83 | GGB | 78793.76 | 2734.99 | 2734.99 |  |  |  | 1 | 1 |  |  |  |  | 141567.49 | 2734.99 | 141567.49 | 2734.99 | 9.5981 | [5 empty] | 107.5516 | 2669.596
01.12.2007 02:00 | 3600 | 2 | 756.83 | GGB | 765.201 | 771.375 | 767.766 | 263.58 | GGB | 11058 | GGB | 9.85 | GGB | 1001.48 | GGB | 57.85 | GGB | 173758.74 | GGB | 141744.14 | GGB | 0 | 0 | 2765 | 3600 | 2749.35 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 78833.4 | GGB | 78834.33 | 2749.35 | 2749.35 |  |  |  | 1 | 1 |  |  |  |  | 141744.14 | 2749.35 | 141744.14 | 2749.35 | 9.6057 | [5 empty] | 108.2512 | 2666.269
01.12.2007 03:00 | 3600 | 2 | 756.01 | GGB | 764.102 | 769.031 | 765.201 | 264.15 | GGB | 11065.6 | GGB | 9.85 | GGB | 1002.41 | GGB | 57.84 | GGB | 174172.46 | GGB | 142218.8 | GGB | 0 | 0 | 2801 | 3600 | 2785.31 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 78873.66 | GGB | 78874.58 | 2785.31 | 2785.31 |  |  |  | 1 | 1 |  |  |  |  | 142218.8 | 2785.31 | 142218.8 | 2785.31 | 9.8416 | [5 empty] | 110.0343 | 2657.3702
01.12.2007 04:00 | 3600 | 2 | 756.31 | GGB | 763.004 | 769.102 | 765.201 | 263.31 | GGB | 11058 | GGB | 9.86 | GGB | 1002.68 | GGB | 57.89 | GGB | 173404.43 | GGB | 141607.98 | GGB | 0 | 0 | 2773 | 3600 | 2757.32 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 78913.67 | GGB | 78914.59 | 2757.32 | 2757.32 |  |  |  | 0 | 1 | [14 empty] | 108.4607 | 2668.8326
01.12.2007 05:00 | 3600 | 2 | 755.86 | GNB | 764.102 | 770.203 | 766.3 | 264.02 | GGB | 11057.5 | GGB | 9.85 | GGB | 1003.41 | GGB | 57.84 | GGB | 174043.72 | GGB | 142257.32 | GGB | 0 | 0 | 2804 | 3600 | 2788.73 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 78954.11 | GGB | 78955.03 | 2788.73 | 2788.73 |  |  |  | 0 | 1 | [14 empty] | 110.1992 | 2656.6506
01.12.2007 06:00 | 3600 | 2 | 757.01 | GGB | 764.102 | 770.227 | 766.3 | 263.59 | GGB | 11060.7 | GGB | 9.86 | GGB | 1004.03 | GGB | 58 | GGB | 173514.46 | GGB | 141841.02 | GGB | 0 | 0 | 2745 | 3600 | 2729.93 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 78994.02 | GGB | 78994.94 | 2729.93 | 2729.93 |  |  |  | 1 | 1 |  |  |  |  | 141841.02 | 2729.93 | 141841.02 | 2729.93 | 9.7022 | [5 empty] | 107.56 | 2664.4478
01.12.2007 07:00 | 3600 | 2 | 757.08 | GGB | 765.201 | 770.227 | 767.766 | 264.21 | GGB | 11085.9 | GGB | 9.86 | GGB | 1004.49 | GGB | 57.91 | GGB | 174179.06 | GGB | 142489.01 | GGB | 0 | 0 | 2755 | 3600 | 2739.76 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 79034.65 | GGB | 79035.57 | 2739.76 | 2739.76 |  |  |  | 1 | 1 |  |  |  |  | 142489.01 | 2739.76 | 142489.01 | 2739.76 | 9.6083 | [5 empty] | 108.4405 | 2652.3309
01.12.2007 08:00 | 3600 | 2 | 756.7 | GGB | 765.201 | 770.25 | 767.766 | 264.06 | GGB | 11086.6 | GGB | 9.85 | GGB | 1004.99 | GGB | 57.87 | GGB | 174135.05 | GGB | 142541.51 | GGB | 0 | 0 | 2768 | 3600 | 2752.78 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 79074.85 | GGB | 79075.77 | 2752.78 | 2752.78 |  |  |  | 1 | 1 |  |  |  |  | 142541.51 | 2752.78 | 142541.51 | 2752.78 | 9.7608 | [5 empty] | 108.9959 | 2651.354
01.12.2007 09:00 | 3600 | 2 | 756.85 | GGB | 765.201 | 771.445 | 767.766 | 266.43 | GGB | 11072 | GGB | 9.85 | GGB | 1006.61 | GGB | 57 | GGB | 176887 | GGB | 145412.73 | GGB | 0 | 0 | 2757 | 3600 | 2741.15 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 79114.99 | GGB | 79115.91 | 2741.15 | 2741.15 |  |  |  | 1 | 1 |  |  |  |  | 145412.73 | 2741.15 | 145412.73 | 2741.15 | 9.9302 | [5 empty] | 110.7217 | 2599.0022
01.12.2007 10:00 | 3600 | 2 | 757.44 | GGB | 765.201 | 770.508 | 766.667 | 265.84 | GGB | 11078.9 | GGB | 9.86 | GGB | 1006.76 | GGB | 56.78 | GGB | 176684.53 | GGB | 145364.16 | GGB | 0 | 0 | 2724 | 3600 | 2708.37 | GGB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 79155.97 | GGB | 79156.89 | 2708.37 | 2708.37 |  |  |  | 1 | 1 |  |  |  |  | 145364.16 | 2708.37 | 145364.16 | 2708.37 | 9.6071 | [5 empty] | 109.3611 | 2599.8706
01.12.2007 11:00 | 3600 | 2 | 757.08 | GGB | 764.102 | 770.438 | 766.667 | 266.26 | GGB | 11080.6 | GGB | 9.86 | GGB | 1007.73 | GGB | 56.9 | GGB | 176653.72 | GGB | 145425.94 | GGB | 0 | 0 | 2727 | 3600 | 2711.59 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 79195.59 | GGB | 79196.51 | 2711.59 | 2711.59 |  |  |  | 1 | 1 |  |  |  |  | 145425.94 | 2711.59 | 145425.94 | 2711.59 | 9.9529 | [5 empty] | 109.5376 | 2598.7661
01.12.2007 12:00 | 3600 | 2 | 757.32 | GGB | 766.667 | 772.383 | 768.864 | 265.66 | GGB | 11089.3 | GGB | 9.87 | GGB | 1007.95 | GGB | 57.16 | GGB | 176148.67 | GGB | 144924.78 | GGB | 0 | 0 | 2710 | 3600 | 2694.24 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 79236.31 | GGB | 79237.24 | 2694.24 | 2694.24 |  |  |  | 1 | 1 |  |  |  |  | 144924.78 | 2694.24 | 144924.78 | 2694.24 | 9.5866 | [5 empty] | 108.4617 | 2607.7528
01.12.2007 13:00 | 3600 | 2 | 756.8 | GGB | 766.3 | 772.477 | 768.864 | 264.33 | GGB | 11064.3 | GGB | 9.86 | GGB | 1007.35 | GGB | 58.13 | GGB | 173415.43 | GGB | 142174.05 | GGB | 0 | 0 | 2735 | 3600 | 2719.61 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 79276.41 | GGB | 79277.34 | 2719.61 | 2719.61 |  |  |  | 1 | 1 |  |  |  |  | 142174.05 | 2719.61 | 142174.05 | 2719.61 | 9.6423 | [5 empty] | 107.405 | 2658.2066
01.12.2007 14:00 | 3600 | 2 | 756.95 | GGB | 765.201 | 770.508 | 766.667 | 263.75 | GGB | 11063 | GGB | 9.86 | GGB | 1007.13 | GGB | 58.19 | GGB | 173065.52 | GGB | 141830.78 | GGB | 0 | 0 | 2729 | 3600 | 2713.37 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 79316.78 | GGB | 79317.71 | 2713.37 | 2713.37 |  |  |  | 1 | 1 |  |  |  |  | 141830.78 | 2713.37 | 141830.78 | 2713.37 | 9.5328 | [5 empty] | 106.8998 | 2664.6402
01.12.2007 15:00 | 3600 | 2 | 756.67 | GGB | 766.3 | 771.539 | 768.132 | 263.84 | GGB | 11064 | GGB | 9.86 | GGB | 1007.44 | GGB | 58.18 | GGB | 173346.11 | GGB | 142107.83 | GGB | 0 | 0 | 2744 | 3600 | 2728.99 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 79357.17 | GGB | 79358.09 | 2728.99 | 2728.99 |  |  |  | 1 | 1 |  |  |  |  | 142107.83 | 2728.99 | 142107.83 | 2728.99 | 9.604 | [5 empty] | 107.7252 | 2659.4453
01.12.2007 16:00 | 3600 | 2 | 756.79 | GGB | 765.201 | 770.414 | 767.033 | 263.86 | GGB | 11066.5 | GGB | 9.85 | GGB | 1008.06 | GGB | 58.09 | GGB | 173381.32 | GGB | 142263.51 | GGB | 0 | 0 | 2742 | 3600 | 2726.63 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 79397.59 | GGB | 79398.51 | 2726.63 | 2726.63 |  |  |  | 1 | 1 |  |  |  |  | 142263.51 | 2726.63 | 142263.51 | 2726.63 | 9.5967 | [5 empty] | 107.75 | 2656.535
01.12.2007 17:00 | 3600 | 2 | 756.79 | GGB | 764.102 | 770.461 | 765.934 | 263.86 | GGB | 11066.3 | GGB | 9.85 | GGB | 1008.25 | GGB | 57.84 | GGB | 173437.44 | GGB | 142442.54 | GGB | 0 | 0 | 2745 | 3600 | 2729.13 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 79437.94 | GGB | 79438.86 | 2729.13 | 2729.13 |  |  |  | 1 | 1 |  |  |  |  | 142442.54 | 2729.13 | 142442.54 | 2729.13 | 9.6343 | [5 empty] | 107.9845 | 2653.1962
01.12.2007 18:00 | 3600 | 2 | 756.95 | GGB | 765.201 | 770.508 | 766.667 | 263.65 | GGB | 11063.7 | GGB | 9.86 | GGB | 1007.79 | GGB | 57.96 | GGB | 173203.07 | GGB | 142134.34 | GGB | 0 | 0 | 2737 | 3600 | 2721.55 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 79478.25 | GGB | 79479.17 | 2721.55 | 2721.55 |  |  |  | 1 | 1 |  |  |  |  | 142134.34 | 2721.55 | 142134.34 | 2721.55 | 9.5963 | [5 empty] | 107.4516 | 2658.9493
01.12.2007 19:00 | 3600 | 2 | 756.98 | GGB | 765.201 | 770.578 | 767.033 | 263.5 | GGB | 11056.6 | GGB | 9.86 | GGB | 1007.43 | GGB | 58 | GGB | 173379.12 | GGB | 142214.42 | GGB | 0 | 0 | 2737 | 3600 | 2721.87 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 79518.54 | GGB | 79519.47 | 2721.87 | 2721.87 |  |  |  | 1 | 1 |  |  |  |  | 142214.42 | 2721.87 | 142214.42 | 2721.87 | 9.6052 | [5 empty] | 107.5248 | 2657.452
01.12.2007 20:00 | 3600 | 2 | 756.85 | GGB | 765.201 | 770.578 | 767.033 | 263.45 | GGB | 11049.4 | GGB | 9.86 | GGB | 1007.27 | GGB | 57.97 | GGB | 173138.15 | GGB | 142007.26 | GGB | 0 | 0 | 2739 | 3600 | 2723.26 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 79559.17 | GGB | 79560.1 | 2723.26 | 2723.26 |  |  |  | 1 | 1 |  |  |  |  | 142007.26 | 2723.26 | 142007.26 | 2723.26 | 9.5182 | [5 empty] | 107.423 | 2661.3287
01.12.2007 21:00 | 3600 | 2 | 756.83 | GGB | 765.201 | 770.578 | 767.033 | 263.58 | GGB | 11040.3 | GGB | 9.85 | GGB | 1007.83 | GGB | 58.12 | GGB | 173106.24 | GGB | 141992.98 | GGB | 0 | 0 | 2740 | 3600 | 2724.33 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 79599.08 | GGB | 79600.01 | 2724.33 | 2724.33 |  |  |  | 1 | 1 |  |  |  |  | 141992.98 | 2724.33 | 141992.98 | 2724.33 | 9.6927 | [5 empty] | 107.4544 | 2661.5964
01.12.2007 22:00 | 3600 | 2 | 757.12 | GGB | 764.102 | 770.273 | 767.033 | 263.37 | GGB | 11047.8 | GGB | 9.86 | GGB | 1007.12 | GGB | 58.17 | GGB | 173076.53 | GGB | 141849.02 | GGB | 0 | 0 | 2723 | 3600 | 2707.51 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 79639.6 | GGB | 79640.53 | 2707.51 | 2707.51 |  |  |  | 1 | 1 |  |  |  |  | 141849.02 | 2707.51 | 141849.02 | 2707.51 | 9.4782 | [5 empty] | 106.6827 | 2664.2976
01.12.2007 23:00 | 3600 | 2 | 756.98 | GGB | 763.004 | 768.258 | 764.835 | 262.45 | GGB | 11043.7 | GGB | 9.86 | GGB | 1006.29 | GGB | 58 | GGB | 173209.67 | GGB | 141912.24 | GGB | 0 | 0 | 2721 | 3600 | 2705.63 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 79679.49 | GGB | 79680.41 | 2705.63 | 2705.63 |  |  |  | 0 | 1 | [14 empty] | 106.6561 | 2663.1107
01.12.2007 24:00 | 3600 | 2 | 756.82 | GGB | 765.201 | 770.672 | 767.033 | 262.8 | GGB | 11032.9 | GGB | 9.85 | GGB | 1006.27 | GGB | 57.95 | GGB | 172828.95 | GGB | 141620.94 | GGB | 0 | 0 | 2736 | 3600 | 2720.12 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 79720.44 | GGB | 79721.37 | 2720.12 | 2720.12 |  |  |  | 1 | 1 |  |  |  |  | 141620.94 | 2720.12 | 141620.94 | 2720.12 | 9.4049 | [5 empty] | 107.0072 | 2668.5884
02.12.2007 01:00 | 3600 | 2 | 756.85 | GGB | 765.201 | 770.672 | 767.033 | 264.09 | GGB | 11017 | GGB | 9.84 | GGB | 1006.47 | GGB | 57.48 | GGB | 174367.22 | GGB | 143110.23 | GGB | 0 | 0 | 2727 | 3600 | 2711.28 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 79760.04 | GGB | 79760.96 | 2711.28 | 2711.28 |  |  |  | 1 | 1 |  |  |  |  | 143110.23 | 2711.28 | 143110.23 | 2711.28 | 9.8008 | [5 empty] | 107.7811 | 2640.8175
02.12.2007 02:00 | 3600 | 2 | 757.57 | GGB | 765.201 | 771.984 | 768.498 | 264.03 | GGB | 11047.1 | GGB | 9.87 | GGB | 1006.25 | GGB | 57.47 | GGB | 174098.74 | GGB | 142864.32 | GGB | 0 | 0 | 2691 | 3600 | 2675.54 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 79800.25 | GGB | 79801.18 | 2675.54 | 2675.54 |  |  |  | 1 | 1 |  |  |  |  | 142864.32 | 2675.54 | 142864.32 | 2675.54 | 9.5037 | [5 empty] | 106.1776 | 2645.3631
02.12.2007 03:00 | 3600 | 2 | 757.03 | GGB | 764.102 | 769.875 | 767.033 | 263.42 | GGB | 11017.9 | GGB | 9.85 | GGB | 1006.2 | GGB | 57.84 | GGB | 173525.46 | GGB | 142226.27 | GGB | 0 | 0 | 2716 | 3600 | 2700.08 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 79840.75 | GGB | 79841.67 | 2700.08 | 2700.08 |  |  |  | 1 | 1 |  |  |  |  | 142226.27 | 2700.08 | 142226.27 | 2700.08 | 9.4844 | [5 empty] | 106.6729 | 2657.2306
02.12.2007 04:00 | 3600 | 2 | 757.3 | GGB | 764.102 | 770.203 | 767.033 | 263.84 | GGB | 11010.7 | GGB | 9.85 | GGB | 1006.28 | GGB | 57.79 | GGB | 173942.49 | GGB | 142601.24 | GGB | 0 | 0 | 2697 | 3600 | 2681.84 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 79880.29 | GGB | 79881.21 | 2681.84 | 2681.84 |  |  |  | 1 | 1 |  |  |  |  | 142601.24 | 2681.84 | 142601.24 | 2681.84 | 9.6721 | [5 empty] | 106.2316 | 2650.2434
02.12.2007 05:00 | 3600 | 2 | 757.35 | GGB | 766.3 | 771.352 | 768.132 | 263.96 | GGB | 11009.9 | GGB | 9.86 | GGB | 1006.34 | GGB | 58.09 | GGB | 173558.47 | GGB | 142167.05 | GGB | 0 | 0 | 2702 | 3600 | 2686.17 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 79921.49 | GGB | 79922.42 | 2686.17 | 2686.17 |  |  |  | 1 | 1 |  |  |  |  | 142167.05 | 2686.17 | 142167.05 | 2686.17 | 9.2668 | [5 empty] | 106.0791 | 2658.3375
02.12.2007 06:00 | 3600 | 2 | 757.89 | GGB | 766.3 | 772.336 | 768.498 | 264.05 | GGB | 11018.1 | GGB | 9.87 | GGB | 1006.34 | GGB | 58.12 | GGB | 173650.9 | GGB | 142230.59 | GGB | 0 | 0 | 2672 | 3600 | 2656.54 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 79960.47 | GGB | 79961.4 | 2656.54 | 2656.54 |  |  |  | 1 | 1 |  |  |  |  | 142230.59 | 2656.54 | 142230.59 | 2656.54 | 9.6932 | [5 empty] | 104.9559
02.12.2007 07:00 | 3600 | 2 | 757.14 | GGB | 765.201 | 771.328 | 767.766 | 263.1 | GGB | 11012.5 | GGB | 9.85 | GGB | 1006.29 | GGB | 58.65 | GGB | 172173.15 | GGB | 140786.95 | GGB | 0 | 0 | 2709 | 3600 | 2694.05 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 80001.52 | GGB | 80002.45 | 2694.05 | 2694.05 |  |  |  | 1 | 1 |  |  |  |  | 140786.95 | 2694.05 | 140786.95 | 2694.05 | 9.2396 | [5 empty] | 105.3575 | 2684.3965
02.12.2007 08:00 | 3600 | 2 | 757.21 | GGB | 766.3 | 772.219 | 768.864 | 264.43 | GGB | 10973.4 | GGB | 9.85 | GGB | 1006.43 | GGB | 58.25 | GGB | 173646.5 | GGB | 142182.2 | GGB | 0 | 0 | 2691 | 3600 | 2675.95 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 80041.84 | GGB | 80042.77 | 2675.95 | 2675.95 |  |  |  | 1 | 1 |  |  |  |  | 142182.2 | 2675.95 | 142182.2 | 2675.95 | 9.4363 | [5 empty] | 105.6868 | 2658.0542
02.12.2007 09:00 | 3600 | 2 | 757.72 | GGB | 766.3 | 772.195 | 768.864 | 263.68 | GGB | 10986.8 | GGB | 9.86 | GGB | 1006.63 | GGB | 58.48 | GGB | 172671.6 | GGB | 141316.33 | GGB | 0 | 0 | 2669 | 3600 | 2653.29 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 80081.28 | GGB | 80082.21 | 2653.29 | 2653.29 |  |  |  | 1 | 1 |  |  |  |  | 141316.33 | 2653.29 | 141316.33 | 2653.29 | 9.5069 | [5 empty] | 104.1537
02.12.2007 10:00 | 3600 | 2 | 757.55 | GGB | 765.201 | 772.172 | 767.766 | 262.63 | GGB | 10982.1 | GGB | 9.86 | GGB | 1006.08 | GGB | 58.97 | GGB | 171289.58 | GGB | 139898.03 | GGB | 0 | 0 | 2686 | 3600 | 2670.65 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 80121.71 | GGB | 80122.64 | 2670.65 | 2670.65 |  |  |  | 1 | 1 |  |  |  |  | 139898.03 | 2670.65 | 139898.03 | 2670.65 | 9.2411 | [5 empty] | 103.783
02.12.2007 11:00 | 3600 | 2 | 757.26 | GGB | 766.3 | 772.336 | 768.864 | 262.71 | GGB | 10964.6 | GGB | 9.85 | GGB | 1005.95 | GGB | 59.13 | GGB | 171186.15 | GGB | 139730.34 | GGB | 0 | 0 | 2695 | 3600 | 2679.34 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 80161.15 | GGB | 80162.08 | 2679.34 | 2679.34 |  |  |  | 1 | 1 |  |  |  |  | 139730.34 | 2679.34 | 139730.34 | 2679.34 | 9.4925 | [5 empty] | 103.9959
02.12.2007 12:00 | 3600 | 2 | 757.81 | GGB | 766.3 | 772.242 | 768.864 | 262.68 | GGB | 10947.8 | GGB | 9.86 | GGB | 1005.98 | GGB | 58.83 | GGB | 171101.42 | GGB | 139791.17 | GGB | 0 | 0 | 2642 | 3600 | 2626.83 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 80201.37 | GGB | 80202.3 | 2626.83 | 2626.83 |  |  |  | 1 | 1 |  |  |  |  | 139791.17 | 2626.83 | 139791.17 | 2626.83 | 9.13 | [5 empty] | 102.0021
02.12.2007 13:00 | 3600 | 2 | 757.42 | GGB | 764.102 | 771.188 | 766.3 | 261.15 | GGB | 10909.1 | GGB | 9.85 | GGB | 1005.2 | GGB | 59.4 | GGB | 169454.21 | GGB | 138102.6 | GGB | 0 | 0 | 2652 | 3600 | 2636.2 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 80241.2 | GGB | 80242.13 | 2636.2 | 2636.2 |  |  |  | 1 | 1 |  |  |  |  | 138102.6 | 2636.2 | 138102.6 | 2636.2 | 9.1405 | [5 empty] | 101.1295
02.12.2007 14:00 | 3600 | 2 | 758.34 | GGB | 766.3 | 772.266 | 768.864 | 259.81 | GGB | 10915.2 | GGB | 9.87 | GGB | 1004.09 | GGB | 59.5 | GGB | 168867.73 | GGB | 137432.39 | GGB | 0 | 0 | 2611 | 3600 | 2596.11 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 80280.82 | GGB | 80281.75 | 2596.11 | 2596.11 |  |  |  | 1 | 1 |  |  |  |  | 137432.39 | 2596.11 | 137432.39 | 2596.11 | 9.0053 | [5 empty] | 99.1082
02.12.2007 15:00 | 3600 | 2 | 757.61 | GGB | 766.3 | 772.266 | 768.864 | 259.97 | GGB | 10872.1 | GGB | 9.85 | GGB | 1003.65 | GGB | 59.59 | GGB | 168532.13 | GGB | 137058.38 | GGB | 0 | 0 | 2627 | 3600 | 2611.77 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 80321.27 | GGB | 80322.2 | 2611.77 | 2611.77 |  |  |  | 1 | 1 |  |  |  |  | 137058.38 | 2611.77 | 137058.38 | 2611.77 | 8.8496 | [5 empty] | 99.4347
02.12.2007 16:00 | 3600 | 2 | 757.9 | GGB | 766.3 | 772.313 | 767.766 | 260.05 | GGB | 10873.7 | GGB | 9.86 | GGB | 1002.91 | GGB | 59.68 | GGB | 168299.96 | GGB | 136733.59 | GGB | 0 | 0 | 2618 | 3600 | 2602.43 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 80360.77 | GGB | 80361.7 | 2602.43 | 2602.43 |  |  |  | 1 | 1 |  |  |  |  | 136733.59 | 2602.43 | 136733.59 | 2602.43 | 9.0086 | [5 empty] | 98.8443
02.12.2007 17:00 | 3600 | 2 | 757.65 | GGB | 766.3 | 771.281 | 767.766 | 260.38 | GGB | 10884.9 | GGB | 9.85 | GGB | 1002.01 | GGB | 59.52 | GGB | 168730.19 | GGB | 137026.72 | GGB | 0 | 0 | 2633 | 3600 | 2617.26 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 80400.08 | GGB | 80401.01 | 2617.26 | 2617.26 |  |  |  | 1 | 1 |  |  |  |  | 137026.72 | 2617.26 | 137026.72 | 2617.26 | 9.1232 | [5 empty] | 99.6207
02.12.2007 18:00 | 3600 | 2 | 757.76 | GGB | 766.3 | 772.523 | 768.864 | 260.25 | GGB | 10886.8 | GGB | 9.86 | GGB | 1001.41 | GGB | 59.45 | GGB | 168810.52 | GGB | 137037.57 | GGB | 0 | 0 | 2631 | 3600 | 2616.01 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 80440.07 | GGB | 80441 | 2616.01 | 2616.01 |  |  |  | 1 | 1 |  |  |  |  | 137037.57 | 2616.01 | 137037.57 | 2616.01 | 8.9645 | [5 empty] | 99.581
02.12.2007 19:00 | 3600 | 2 | 757.76 | GGB | 766.3 | 772.523 | 767.766 | 259.82 | GGB | 10881.1 | GGB | 9.86 | GGB | 1000.8 | GGB | 59.45 | GGB | 168663.07 | GGB | 136831.73 | GGB | 0 | 0 | 2621 | 3600 | 2605.31 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 80479.82 | GGB | 80480.75 | 2605.31 | 2605.31 |  |  |  | 1 | 1 |  |  |  |  | 136831.73 | 2605.31 | 136831.73 | 2605.31 | 8.9683 | [5 empty] | 99.0247
02.12.2007 20:00 | 3600 | 2 | 757.54 | GGB | 765.201 | 770.297 | 767.766 | 259.52 | GGB | 10870.2 | GGB | 9.85 | GGB | 1000.42 | GGB | 59.28 | GGB | 168562.94 | GGB | 136772.14 | GGB | 0 | 0 | 2627 | 3600 | 2611.84 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 80519.17 | GGB | 80520.1 | 2611.84 | 2611.84 |  |  |  | 1 | 1 |  |  |  |  | 136772.14 | 2611.84 | 136772.14 | 2611.84 | 9.0782 | [5 empty] | 99.2297
02.12.2007 21:00 | 3600 | 2 | 758.02 | GGB | 766.667 | 773.602 | 768.864 | 259.53 | GGB | 10876.3 | GGB | 9.86 | GGB | 999.42 | GGB | 59.29 | GGB | 168546.44 | GGB | 136618.1 | GGB | 0 | 0 | 2617 | 3600 | 2601.41 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 80559.19 | GGB | 80560.12 | 2601.41 | 2601.41 |  |  |  | 1 | 1 |  |  |  |  | 136618.1 | 2601.41 | 136618.1 | 2601.41 | 8.8806 | [5 empty] | 98.7221
02.12.2007 22:00 | 3600 | 2 | 757.65 | GGB | 765.201 | 771.422 | 767.766 | 259.43 | GGB | 10861.1 | GGB | 9.86 | GGB | 998.56 | GGB | 59.5 | GGB | 168601.45 | GGB | 136455.39 | GGB | 0 | 0 | 2614 | 3600 | 2598.99 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 80597.77 | GGB | 80598.7 | 2598.99 | 2598.99 |  |  |  | 1 | 1 |  |  |  |  | 136455.39 | 2598.99 | 136455.39 | 2598.99 | 9.1925 | [5 empty] | 98.5128
02.12.2007 23:00 | 3600 | 2 | 757.73 | GGB | 768.864 | 774.469 | 771.429 | 259.71 | GGB | 10839.2 | GGB | 9.86 | GGB | 997.9 | GGB | 59.11 | GGB | 169733.7 | GGB | 137444.51 | GGB | 0 | 0 | 2597 | 3600 | 2581.45 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 80636.79 | GGB | 80637.72 | 2581.45 | 2581.45 |  |  |  | 1 | 1 |  |  |  |  | 137444.51 | 2581.45 | 137444.51 | 2581.45 | 9.0929 | [5 empty] | 98.5573
02.12.2007 24:00 | 3600 | 2 | 758.26 | GGB | 765.201 | 771.633 | 767.766 | 260.55 | GGB | 10804.1 | GGB | 9.85 | GGB | 997.42 | GGB | 58.94 | GGB | 169899.85 | GGB | 137583.08 | GGB | 0 | 0 | 2560 | 3600 | 2545.2 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 80676.65 | GGB | 80677.58 | 2545.2 | 2545.2 |  |  |  | 1 | 1 |  |  |  |  | 137583.08 | 2545.2 | 137583.08 | 2545.2 | 8.7852 | [5 empty] | 97.2712
03.12.2007 01:00 | 3600 | 2 | 758.55 | GGB | 766.667 | 772.617 | 768.864 | 259.23 | GGB | 10824.6 | GGB | 9.87 | GGB | 996.45 | GGB | 59.26 | GGB | 168627.86 | GGB | 136289.11 | GGB | 0 | 0 | 2549 | 3600 | 2533.84 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 80716.64 | GGB | 80717.57 | 2533.84 | 2533.84 |  |  |  | 1 | 1 |  |  |  |  | 136289.11 | 2533.84 | 136289.11 | 2533.84 | 8.6355 | [5 empty] | 95.9263
03.12.2007 02:00 | 3600 | 2 | 757.94 | GGB | 765.201 | 771.375 | 767.766 | 258.37 | GGB | 10801.4 | GGB | 9.85 | GGB | 995.46 | GGB | 59.63 | GGB | 167575.94 | GGB | 135151.32 | GGB | 0 | 0 | 2571 | 3600 | 2556.07 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 80755.66 | GGB | 80756.59 | 2556.07 | 2556.07 |  |  |  | 1 | 1 |  |  |  |  | 135151.32 | 2556.07 | 135151.32 | 2556.07 | 8.8533 | [5 empty] | 95.9601
03.12.2007 03:00 | 3600 | 2 | 758.19 | GGB | 766.3 | 772.547 | 768.864 | 259.36 | GGB | 10771.1 | GGB | 9.85 | GGB | 994.54 | GGB | 59.04 | GGB | 169312.27 | GGB | 136669.6 | GGB | 0 | 0 | 2542 | 3600 | 2526.48 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 80795.95 | GGB | 80796.88 | 2526.48 | 2526.48 |  |  |  | 1 | 1 |  |  |  |  | 136669.6 | 2526.48 | 136669.6 | 2526.48 | 8.5702 | [5 empty] | 95.9147
03.12.2007 04:00 | 3600 | 2 | 758.05 | GGB | 766.667 | 773.813 | 768.864 | 259.36 | GGB | 10771.2 | GGB | 9.86 | GGB | 993.06 | GGB | 58.85 | GGB | 169607.16 | GGB | 136782.83 | GGB | 0 | 0 | 2539 | 3600 | 2523.7 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 80834.71 | GGB | 80835.64 | 2523.7 | 2523.7 |  |  |  | 1 | 1 |  |  |  |  | 136782.83 | 2523.7 | 136782.83 | 2523.7 | 8.9061 | [5 empty] | 95.8886
03.12.2007 05:00 | 3600 | 2 | 758.06 | GGB | 766.3 | 772.734 | 768.864 | 259.04 | GGB | 10782.5 | GGB | 9.86 | GGB | 991.39 | GGB | 58.78 | GGB | 169147.22 | GGB | 136212.38 | GGB | 0 | 0 | 2542 | 3600 | 2526.55 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 80874 | GGB | 80874.93 | 2526.55 | 2526.55 |  |  |  | 1 | 1 |  |  |  |  | 136212.38 | 2526.55 | 136212.38 | 2526.55 | 8.7592 | [5 empty] | 95.5965
03.12.2007 06:00 | 3600 | 2 | 757.58 | GGB | 765.201 | 771.656 | 767.766 | 257.92 | GGB | 10807.9 | GGB | 9.86 | GGB | 989.59 | GGB | 58.97 | GGB | 167934.65 | GGB | 134913.91 | GGB | 0 | 0 | 2578 | 3600 | 2562.86 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 80913.52 | GGB | 80914.45 | 2562.86 | 2562.86 |  |  |  | 1 | 1 |  |  |  |  | 134913.91 | 2562.86 | 134913.91 | 2562.86 | 8.7491 | [5 empty] | 96.046
03.12.2007 07:00 | 3600 | 2 | 757.43 | GGB | 764.102 | 771.07 | 766.667 | 258.89 | GGB | 10786.8 | GGB | 9.85 | GGB | 987.98 | GGB | 57.96 | GGB | 169633.57 | GGB | 136469 | GGB | 0 | 0 | 2578 | 3600 | 2562.89 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 80952.42 | GGB | 80953.35 | 2562.89 | 2562.89 |  |  |  | 1 | 1 |  |  |  |  | 136469 | 2562.89 | 136469 | 2562.89 | 8.9911 | [5 empty] | 97.1542
03.12.2007 08:00 | 3600 | 2 | 757.31 | GGB | 765.201 | 770.203 | 766.667 | 259.75 | GGB | 10796.2 | GGB | 9.85 | GGB | 986.74 | GGB | 57.77 | GGB | 170505.04 | GGB | 137078.33 | GGB | 0 | 0 | 2584 | 3600 | 2569.08 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 80992.34 | GGB | 80993.28 | 2569.08 | 2569.08 |  |  |  | 1 | 1 |  |  |  |  | 137078.33 | 2569.08 | 137078.33 | 2569.08 | 8.8196 | [5 empty] | 97.8237
03.12.2007 09:00 | 3600 | 2 | 757.54 | GGB | 764.102 | 770.32 | 766.667 | 259.01 | GGB | 10825.3 | GGB | 9.86 | GGB | 986.41 | GGB | 57.79 | GGB | 169470.72 | GGB | 136191.23 | GGB | 0 | 0 | 2590 | 3600 | 2574.87 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 81030.7 | GGB | 81031.64 | 2574.87 | 2574.87 |  |  |  | 1 | 1 |  |  |  |  | 136191.23 | 2574.87 | 136191.23 | 2574.87 | 9.1417 | [5 empty] | 97.4096
03.12.2007 10:00 | 3600 | 2 | 757.11 | GGB | 764.102 | 771.188 | 766.667 | 257.68 | GGB | 10820.1 | GGB | 9.86 | GGB | 985.68 | GGB | 58.52 | GGB | 167880.73 | GGB | 134518.23 | GGB | 0 | 0 | 2614 | 3600 | 2598.4 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 81070.91 | GGB | 81071.85 | 2598.4 | 2598.4 |  |  |  | 1 | 1 |  |  |  |  | 134518.23 | 2598.4 | 134518.23 | 2598.4 | 8.6927 | [5 empty] | 97.0923
03.12.2007 11:00 | 3600 | 2 | 757.2 | GGB | 766.3 | 772.359 | 768.498 | 257.43 | GGB | 10808.7 | GGB | 9.86 | GGB | 985.26 | GGB | 58.7 | GGB | 167656.26 | GGB | 134206.74 | GGB | 0 | 0 | 2604 | 3600 | 2588.67 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 81109.71 | GGB | 81110.66 | 2588.67 | 2588.67 |  |  |  | 1 | 1 |  |  |  |  | 134206.74 | 2588.67 | 134206.74 | 2588.67 | 8.9517 | [5 empty] | 96.5047
03.12.2007 12:00 | 3600 | 2 | 757.31 | GGB | 765.201 | 771.141 | 767.033 | 256.85 | GGB | 10793.9 | GGB | 9.86 | GGB | 984.67 | GGB | 58.65 | GGB | 167116 | GGB | 133715.46 | GGB | 0 | 0 | 2593 | 3600 | 2577.23 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 81149.3 | GGB | 81150.25 | 2577.23 | 2577.23 |  |  |  | 1 | 1 |  |  |  |  | 133715.46 | 2577.23 | 133715.46 | 2577.23 | 8.7046 | [5 empty] | 95.7265
03.12.2007 13:00 | 3600 | 2 | 757.36 | GGB | 764.102 | 770.344 | 767.033 | 257.18 | GGB | 10764.7 | GGB | 9.85 | GGB | 983.73 | GGB | 59 | GGB | 166961.95 | GGB | 133322.69 | GGB | 0 | 0 | 2586 | 3094 | 2570.7 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 81188.58 | GGB | 81189.53 | 2570.7 | 2570.7 |  |  |  | 1 | 1 |  |  |  |  | 133322.69 | 2570.7 | 133322.69 | 2570.7 | 8.7254 | [5 empty] | 95.2035
03.12.2007 14:00 | 3600 | 2 | 757.91 | GGB | 764.102 | 769.945 | 765.934 | 257.58 | GGB | 10740 | GGB | 9.86 | GGB | 982.28 | GGB | 58.25 | GGB | 169169.23 | GGB | 135194.68 | GGB | 0 | 0 | 2529 | 3600 | 2514.02 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 81227.99 | GGB | 81228.94 | 2514.02 | 2514.02 |  |  |  | 1 | 1 |  |  |  |  | 135194.68 | 2514.02 | 135194.68 | 2514.02 | 8.6243 | [5 empty] | 94.4117
03.12.2007 15:00 | 3600 | 2 | 757.71 | GGB | 766.3 | 772.078 | 768.864 | 257.06 | GGB | 10728.9 | GGB | 9.86 | GGB | 981.8 | GGB | 58.09 | GGB | 168788.51 | GGB | 134886.5 | GGB | 0 | 0 | 2541 | 3600 | 2526.16 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 81266.75 | GGB | 81267.7 | 2526.16 | 2526.16 |  |  |  | 1 | 1 |  |  |  |  | 134886.5 | 2526.16 | 134886.5 | 2526.16 | 8.7911 | [5 empty] | 94.6514
03.12.2007 16:00 | 3600 | 2 | 757.54 | GGB | 766.3 | 772.922 | 768.498 | 256.35 | GGB | 10727.9 | GGB | 9.86 | GGB | 981.76 | GGB | 58.54 | GGB | 167983.06 | GGB | 134056.27 | GGB | 0 | 0 | 2539 | 3600 | 2523.28 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 81306.18 | GGB | 81307.13 | 2523.28 | 2523.28 |  |  |  | 1 | 1 |  |  |  |  | 134056.27 | 2523.28 | 134056.27 | 2523.28 | 8.5788 | [5 empty] | 93.9615
03.12.2007 17:00 | 3600 | 2 | 757.86 | GGB | 767.766 | 773.227 | 769.597 | 256.59 | GGB | 10727.1 | GGB | 9.86 | GGB | 981.62 | GGB | 58.31 | GGB | 168538.73 | GGB | 134573.95 | GGB | 0 | 0 | 2521 | 3600 | 2505.78 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 81345.3 | GGB | 81346.25 | 2505.78 | 2505.78 |  |  |  | 1 | 1 |  |  |  |  | 134573.95 | 2505.78 | 134573.95 | 2505.78 | 8.62 | [5 empty] | 93.6702
03.12.2007 18:00 | 3600 | 2 | 757.8 | GGB | 766.3 | 773.227 | 768.498 | 255.43 | GGB | 10737.5 | GGB | 9.86 | GGB | 981.28 | GGB | 58.43 | GGB | 167167.71 | GGB | 133384.07 | GGB | 0 | 0 | 2528 | 3600 | 2513 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 81384.82 | GGB | 81385.77 | 2513 | 2513 |  |  |  | 1 | 1 |  |  |  |  | 133384.07 | 2513 | 133384.07 | 2513 | 8.4816 | [5 empty] | 93.1095
03.12.2007 19:00 | 3600 | 2 | 757.49 | GGB | 765.201 | 772.148 | 768.132 | 254.77 | GGB | 10735.8 | GGB | 9.85 | GGB | 980.81 | GGB | 58.69 | GGB | 165993.65 | GGB | 132281.31 | GGB | 0 | 0 | 2558 | 3600 | 2542.8 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 81423.45 | GGB | 81424.4 | 2542.8 | 2542.8 |  |  |  | 1 | 1 |  |  |  |  | 132281.31 | 2542.8 | 132281.31 | 2542.8 | 8.7073 | [5 empty] | 93.4347
03.12.2007 20:00 | 3600 | 2 | 757.65 | GGB | 766.3 | 772.969 | 768.498 | 256.09 | GGB | 10713.9 | GGB | 9.85 | GGB | 980.87 | GGB | 58.31 | GGB | 167689.27 | GGB | 133794.66 | GGB | 0 | 0 | 2530 | 3600 | 2514.75 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 81463.04 | GGB | 81464 | 2514.75 | 2514.75 |  |  |  | 1 | 1 |  |  |  |  | 133794.66 | 2514.75 | 133794.66 | 2514.75 | 8.4965 | [5 empty] | 93.4611
03.12.2007 21:00 | 3600 | 2 | 757.91 | GGB | 766.3 | 772.992 | 768.132 | 256.09 | GGB | 10710.5 | GGB | 9.86 | GGB | 980.7 | GGB | 58.13 | GGB | 167909.34 | GGB | 134020.14 | GGB | 0 | 0 | 2516 | 3600 | 2500.5 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 81501.81 | GGB | 81502.77 | 2500.5 | 2500.5 |  |  |  | 1 | 1 |  |  |  |  | 134020.14 | 2500.5 | 134020.14 | 2500.5 | 8.6437 | [5 empty] | 93.0882
03.12.2007 22:00 | 3600 | 2 | 757.93 | GGB | 766.3 | 772.945 | 768.498 | 255.48 | GGB | 10705.8 | GGB | 9.86 | GGB | 980.46 | GGB | 58.68 | GGB | 167130.3 | GGB | 133143.76 | GGB | 0 | 0 | 2515 | 3600 | 2499.33 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 81540.61 | GGB | 81541.57 | 2499.33 | 2499.33 |  |  |  | 1 | 1 |  |  |  |  | 133143.76 | 2499.33 | 133143.76 | 2499.33 | 8.5766 | [5 empty] | 92.4362
03.12.2007 23:00 | 3600 | 2 | 757.74 | GGB | 765.201 | 771.727 | 767.033 | 254.36 | GGB | 10717.3 | GGB | 9.85 | GGB | 980.81 | GGB | 58.96 | GGB | 165316.94 | GGB | 131636.02 | GGB | 0 | 0 | 2532 | 3600 | 2516.85 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 81579.66 | GGB | 81580.62 | 2516.85 | 2516.85 |  |  |  | 1 | 1 |  |  |  |  | 131636.02 | 2516.85 | 131636.02 | 2516.85 | 8.4842 | [5 empty] | 92.03
03.12.2007 24:00 | 3600 | 2 | 757.74 | GGB | 766.3 | 771.82 | 768.498 | 255.63 | GGB | 10743.1 | GGB | 9.86 | GGB | 982.24 | GGB | 58.6 | GGB | 166554.82 | GGB | 132959.27 | GGB | 0 | 0 | 2541 | 3600 | 2525.69 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 81619.3 | GGB | 81620.26 | 2525.69 | 2525.69 |  |  |  | 1 | 1 |  |  |  |  | 132959.27 | 2525.69 | 132959.27 | 2525.69 | 8.4716 | [5 empty] | 93.2816
04.12.2007 01:00 | 3600 | 2 | 757.75 | GGB | 766.667 | 772.242 | 768.498 | 257.44 | GGB | 10726.5 | GGB | 9.85 | GGB | 983.39 | GGB | 58.15 | GGB | 168869.94 | GGB | 135147.32 | GGB | 0 | 0 | 2529 | 3600 | 2513.61 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 81658.11 | GGB | 81659.07 | 2513.61 | 2513.61 |  |  |  | 1 | 1 |  |  |  |  | 135147.32 | 2513.61 | 135147.32 | 2513.61 | 8.7531 | [5 empty] | 94.3632
04.12.2007 02:00 | 3600 | 2 | 757.73 | GGB | 765.201 | 772.195 | 768.498 | 257.81 | GGB | 10739.4 | GGB | 9.85 | GGB | 984.13 | GGB | 58.05 | GGB | 169185.73 | GGB | 135542.15 | GGB | 0 | 0 | 2532 | 3600 | 2516.51 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 81697.66 | GGB | 81698.62 | 2516.51 | 2516.51 |  |  |  | 1 | 1 |  |  |  |  | 135542.15 | 2516.51 | 135542.15 | 2516.51 | 8.6244 | [5 empty] | 94.7481
04.12.2007 03:00 | 3600 | 2 | 757.8 | GGB | 766.667 | 772.266 | 768.498 | 257.15 | GGB | 10776.6 | GGB | 9.86 | GGB | 984.64 | GGB | 58.34 | GGB | 168473.81 | GGB | 134924.84 | GGB | 0 | 0 | 2541 | 3600 | 2526.06 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 81736.43 | GGB | 81737.39 | 2526.06 | 2526.06 |  |  |  | 1 | 1 |  |  |  |  | 134924.84 | 2526.06 | 134924.84 | 2526.06 | 8.791 | [5 empty] | 94.6745
04.12.2007 04:00 | 3600 | 2 | 757.4 | GGB | 766.3 | 771.164 | 768.132 | 256.64 | GGB | 10789.5 | GGB | 9.85 | GGB | 985.48 | GGB | 58.65 | GGB | 167643.06 | GGB | 134248.15 | GGB | 0 | 0 | 2575 | 3600 | 2560.09 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 81775.74 | GGB | 81776.7 | 2560.09 | 2560.09 |  |  |  | 1 | 1 |  |  |  |  | 134248.15 | 2560.09 | 134248.15 | 2560.09 | 8.743 | [5 empty] | 95.4687
04.12.2007 05:00 | 3600 | 2 | 757.52 | GGB | 765.201 | 771.164 | 767.033 | 256.83 | GGB | 10805.7 | GGB | 9.85 | GGB | 985.96 | GGB | 58.62 | GGB | 167876.33 | GGB | 134510.99 | GGB | 0 | 0 | 2579 | 3600 | 2564.17 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 81814.56 | GGB | 81815.52 | 2564.17 | 2564.17 |  |  |  | 1 | 1 |  |  |  |  | 134510.99 | 2564.17 | 134510.99 | 2564.17 | 8.8848 | [5 empty] | 95.8081
04.12.2007 06:00 | 3600 | 2 | 757.62 | GGB | 766.3 | 772.219 | 768.132 | 258.37 | GGB | 10794.7 | GGB | 9.85 | GGB | 986.75 | GGB | 58.25 | GGB | 169626.97 | GGB | 136176.33 | GGB | 0 | 0 | 2577 | 3600 | 2561.87 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 81854.42 | GGB | 81855.39 | 2561.87 | 2561.87 |  |  |  | 1 | 1 |  |  |  |  | 136176.33 | 2561.87 | 136176.33 | 2561.87 | 8.7501 | [5 empty] | 96.9072
04.12.2007 07:00 | 3600 | 2 | 757.87 | GGB | 765.201 | 772.219 | 768.498 | 258.97 | GGB | 10796.1 | GGB | 9.86 | GGB | 987.44 | GGB | 58.07 | GGB | 170310.28 | GGB | 136895.27 | GGB | 0 | 0 | 2556 | 3600 | 2540.26 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 81893.25 | GGB | 81894.22 | 2540.26 | 2540.26 |  |  |  | 1 | 1 |  |  |  |  | 136895.27 | 2540.26 | 136895.27 | 2540.26 | 8.9557 | [5 empty] | 96.5971
04.12.2007 08:00 | 3600 | 2 | 757.83 | GGB | 766.3 | 772.898 | 768.498 | 258.02 | GGB | 10827.3 | GGB | 9.86 | GGB | 988.14 | GGB | 57.82 | GGB | 169964.77 | GGB | 136814.82 | GGB | 0 | 0 | 2567 | 3600 | 2551.7 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 81932.71 | GGB | 81933.67 | 2551.7 | 2551.7 |  |  |  | 1 | 1 |  |  |  |  | 136814.82 | 2551.7 | 136814.82 | 2551.7 | 8.8494 | [5 empty] | 96.9751
04.12.2007 09:00 | 3600 | 2 | 757.44 | GGB | 766.3 | 771.656 | 768.132 | 256.44 | GGB | 10866.3 | GGB | 9.86 | GGB | 989.21 | GGB | 57.94 | GGB | 168851.23 | GGB | 136019.87 | GGB | 0 | 0 | 2605 | 3600 | 2589.72 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 81972.76 | GGB | 81973.73 | 2589.72 | 2589.72 |  |  |  | 1 | 1 |  |  |  |  | 136019.87 | 2589.72 | 136019.87 | 2589.72 | 8.7931 | [5 empty] | 97.8482
04.12.2007 10:00 | 3600 | 2 | 757.26 | GGB | 764.102 | 770.297 | 766.667 | 256.45 | GGB | 10878.5 | GGB | 9.85 | GGB | 990.38 | GGB | 57.83 | GGB | 169238.55 | GGB | 136536.79 | GGB | 0 | 0 | 2625 | 3600 | 2609.42 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 82011.83 | GGB | 82012.8 | 2609.42 | 2609.42 |  |  |  | 1 | 1 |  |  |  |  | 136536.79 | 2609.42 | 136536.79 | 2609.42 | 9.1191 | [5 empty] | 98.9672
04.12.2007 11:00 | 3600 | 2 | 757.01 | GGB | 764.102 | 770.625 | 767.033 | 256.48 | GGB | 10893.4 | GGB | 9.86 | GGB | 991.92 | GGB | 57.37 | GGB | 169052.59 | GGB | 136789.64 | GGB | 0 | 0 | 2638 | 3600 | 2623.09 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 82052.42 | GGB | 82053.4 | 2623.09 | 2623.09 |  |  |  | 1 | 1 |  |  |  |  | 136789.64 | 2623.09 | 136789.64 | 2623.09 | 8.8377 | [5 empty] | 99.6699
04.12.2007 12:00 | 3600 | 2 | 757.09 | GGB | 765.201 | 771.633 | 767.766 | 257.78 | GGB | 10893.2 | GGB | 9.86 | GGB | 993.06 | GGB | 56.74 | GGB | 170679.99 | GGB | 138528.41 | GGB | 0 | 0 | 2634 | 3600 | 2618.39 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 82091.74 | GGB | 82092.72 | 2618.39 | 2618.39 |  |  |  | 1 | 1 |  |  |  |  | 138528.41 | 2618.39 | 138528.41 | 2618.39 | 9.2249 | [5 empty] | 100.7559
04.12.2007 13:00 | 3600 | 2 | 756.96 | GGB | 764.102 | 770.484 | 766.3 | 257.11 | GGB | 10906.3 | GGB | 9.86 | GGB | 993.66 | GGB | 57.29 | GGB | 169347.48 | GGB | 137303.51 | GGB | 0 | 0 | 2655 | 3600 | 2639.87 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 82131.79 | GGB | 82132.78 | 2639.87 | 2639.87 |  |  |  | 1 | 1 |  |  |  |  | 137303.51 | 2639.87 | 137303.51 | 2639.87 | 9.048 | [5 empty] | 100.6843
04.12.2007 14:00 | 3600 | 2 | 756.7 | GGB | 766.3 | 771.727 | 768.864 | 259.14 | GGB | 10881.3 | GGB | 9.85 | GGB | 994.57 | GGB | 57.4 | GGB | 171386.41 | GGB | 139036.65 | GGB | 0 | 0 | 2655 | 3600 | 2639.87 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 82171.76 | GGB | 82172.75 | 2639.87 | 2639.87 |  |  |  | 1 | 1 |  |  |  |  | 139036.65 | 2639.87 | 139036.65 | 2639.87 | 9.1829 | [5 empty] | 101.9552
04.12.2007 15:00 | 3600 | 2 | 758.02 | GGB | 765.201 | 771.68 | 766.667 | 258.43 | GGB | 10857.1 | GGB | 9.86 | GGB | 994.77 | GGB | 57.65 | GGB | 171001.29 | GGB | 138647.56 | GGB | 0 | 0 | 2566 | 3600 | 2551.09 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 82211.52 | GGB | 82212.51 | 2551.09 | 2551.09 |  |  |  | 1 | 1 |  |  |  |  | 138647.56 | 2551.09 | 138647.56 | 2551.09 | 8.8959 | [5 empty] | 98.2507
04.12.2007 16:00 | 3600 | 2 | 758.31 | GGB | 766.3 | 771.563 | 768.498 | 258.12 | GGB | 10874.4 | GGB | 9.86 | GGB | 995.48 | GGB | 57.96 | GGB | 170195.84 | GGB | 137960.31 | GGB | 0 | 0 | 2567 | 3600 | 2552.17 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 82250.92 | GGB | 82251.91 | 2552.17 | 2552.17 |  |  |  | 1 | 1 |  |  |  |  | 137960.31 | 2552.17 | 137960.31 | 2552.17 | 8.9365 | [5 empty] | 97.805
04.12.2007 17:00 | 3600 | 2 | 757.35 | GGB | 765.201 | 770.672 | 767.033 | 257.97 | GGB | 10892.3 | GGB | 9.85 | GGB | 996.39 | GGB | 58.24 | GGB | 169253.95 | GGB | 137208.53 | GGB | 0 | 0 | 2626 | 3600 | 2610.2 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 82291 | GGB | 82292 | 2610.2 | 2610.2 |  |  |  | 1 | 1 |  |  |  |  | 137208.53 | 2610.2 | 137208.53 | 2610.2 | 8.9334 | [5 empty] | 99.4838
04.12.2007 18:00 | 3600 | 2 | 757.56 | GGB | 765.201 | 770.602 | 767.033 | 259.18 | GGB | 10932 | GGB | 9.85 | GGB | 997.6 | GGB | 57.65 | GGB | 169996.68 | GGB | 138221.2 | GGB | 0 | 0 | 2656 | 3600 | 2640.8 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 82330.76 | GGB | 82331.76 | 2640.8 | 2640.8 |  |  |  | 1 | 1 |  |  |  |  | 138221.2 | 2640.8 | 138221.2 | 2640.8 | 9.1804 | [5 empty] | 101.3929
04.12.2007 19:00 | 3600 | 2 | 757.32 | GGB | 765.201 | 771.703 | 767.033 | 261.6 | GGB | 10911.5 | GGB | 9.85 | GGB | 999 | GGB | 56.52 | GGB | 172373.41 | GGB | 140832.37 | GGB | 0 | 0 | 2655 | 3600 | 2639.35 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 82370.33 | GGB | 82371.33 | 2639.35 | 2639.35 |  |  |  | 1 | 1 |  |  |  |  | 140832.37 | 2639.35 | 140832.37 | 2639.35 | 9.3936 | [5 empty] | 103.2516
04.12.2007 20:00 | 3600 | 2 | 757.53 | GGB | 765.201 | 771.727 | 768.132 | 262.1 | GGB | 10920.3 | GGB | 9.85 | GGB | 1000.2 | GGB | 56.59 | GGB | 172252.37 | GGB | 140873.99 | GGB | 0 | 0 | 2644 | 3600 | 2628.95 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 82409.38 | GGB | 82410.38 | 2628.95 | 2628.95 |  |  |  | 1 | 1 |  |  |  |  | 140873.99 | 2628.95 | 140873.99 | 2628.95 | 9.484 | [5 empty] | 102.8752
04.12.2007 21:00 | 3600 | 2 | 757.6 | GGB | 765.201 | 770.531 | 767.033 | 262.16 | GGB | 10925.3 | GGB | 9.86 | GGB | 1001.14 | GGB | 56.35 | GGB | 172004.8 | GGB | 140907.07 | GGB | 0 | 0 | 2647 | 3600 | 2631.87 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 82449.9 | GGB | 82450.9 | 2631.87 | 2631.87 |  |  |  | 1 | 1 |  |  |  |  | 140907.07 | 2631.87 | 140907.07 | 2631.87 | 9.1522 | [5 empty] | 103.0136
04.12.2007 22:00 | 3600 | 2 | 757.4 | GGB | 765.201 | 771.75 | 767.033 | 262.79 | GGB | 10920.4 | GGB | 9.85 | GGB | 1002.29 | GGB | 56.85 | GGB | 172009.2 | GGB | 140857.75 | GGB | 0 | 0 | 2667 | 3600 | 2651.65 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 82489.67 | GGB | 82490.67 | 2651.65 | 2651.65 |  |  |  | 1 | 1 |  |  |  |  | 140857.75 | 2651.65 | 140857.75 | 2651.65 | 9.3916 | [5 empty] | 103.7515
04.12.2007 23:00 | 3600 | 2 | 757.57 | GGB | 765.201 | 771.656 | 767.033 | 262 | GGB | 10957.8 | GGB | 9.86 | GGB | 1003.6 | GGB | 57.92 | GGB | 170040.69 | GGB | 138978.87 | GGB | 0 | 0 | 2690 | 3600 | 2675.06 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 82529.73 | GGB | 82530.73 | 2675.06 | 2675.06 |  |  |  | 1 | 1 |  |  |  |  | 138978.87 | 2675.06 | 138978.87 | 2675.06 | 9.2805 | [5 empty] | 103.2713
04.12.2007 24:00 | 3600 | 2 | 757.77 | GGB | 766.3 | 771.68 | 768.132 | 262.47 | GGB | 10954.3 | GGB | 9.86 | GGB | 1005.15 | GGB | 58.56 | GGB | 170129.82 | GGB | 138996.85 | GGB | 0 | 0 | 2691 | 3600 | 2675.18 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 82569.47 | GGB | 82570.47 | 2675.18 | 2675.18 |  |  |  | 1 | 1 |  |  |  |  | 138996.85 | 2675.18 | 138996.85 | 2675.18 | 9.3569 | [5 empty] | 103.2893
05.12.2007 01:00 | 3600 | 2 | 757.58 | GGB | 766.3 | 772.711 | 768.498 | 263.59 | GGB | 10912.5 | GGB | 9.85 | GGB | 1006.78 | GGB | 58.67 | GGB | 170882.45 | GGB | 139792.21 | GGB | 0 | 0 | 2679 | 3600 | 2663.78 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 82609.36 | GGB | 82610.36 | 2663.78 | 2663.78 |  |  |  | 1 | 1 |  |  |  |  | 139792.21 | 2663.78 | 139792.21 | 2663.78 | 9.3351 | [5 empty] | 103.4377
05.12.2007 02:00 | 3600 | 2 | 758.5 | GGB | 766.3 | 772.477 | 768.132 | 263.97 | GGB | 10912.6 | GGB | 9.86 | GGB | 1008.19 | GGB | 58.44 | GGB | 171956.38 | GGB | 140965.13 | GGB | 0 | 0 | 2638 | 3600 | 2622.17 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 82649.17 | GGB | 82650.17 | 2622.17 | 2622.17 |  |  |  | 1 | 1 |  |  |  |  | 140965.13 | 2622.17 | 140965.13 | 2622.17 | 9.285 | [5 empty] | 102.6763
05.12.2007 03:00 | 3600 | 2 | 757.75 | GGB | 766.3 | 772.617 | 768.498 | 265.06 | GGB | 10928.3 | GGB | 9.84 | GGB | 1009.39 | GGB | 58.15 | GGB | 172736.52 | GGB | 141897.34 | GGB | 0 | 0 | 2687 | 3600 | 2671.68 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 82689.09 | GGB | 82690.1 | 2671.68 | 2671.68 |  |  |  | 1 | 1 |  |  |  |  | 141897.34 | 2671.68 | 141897.34 | 2671.68 | 9.4942 | [5 empty] | 105.3067 | 2663.3903
05.12.2007 04:00 | 3600 | 2 | 758.25 | GGB | 765.201 | 770.555 | 768.132 | 264.12 | GGB | 10992.9 | GGB | 9.86 | GGB | 1010.32 | GGB | 58.89 | GGB | 171256.57 | GGB | 140496.23 | GGB | 0 | 0 | 2702 | 3600 | 2686.62 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 82728.69 | GGB | 82729.7 | 2686.62 | 2686.62 |  |  |  | 1 | 1 |  |  |  |  | 140496.23 | 2686.62 | 140496.23 | 2686.62 | 9.5318 | [5 empty] | 104.85
05.12.2007 05:00 | 3600 | 2 | 758.14 | GGB | 766.3 | 771.609 | 768.132 | 264.31 | GGB | 11021.7 | GGB | 9.86 | GGB | 1011.37 | GGB | 58.71 | GGB | 171606.48 | GGB | 141004.32 | GGB | 0 | 0 | 2713 | 3600 | 2697.22 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 82769.18 | GGB | 82770.19 | 2697.22 | 2697.22 |  |  |  | 1 | 1 |  |  |  |  | 141004.32 | 2697.22 | 141004.32 | 2697.22 | 9.3929 | [5 empty] | 105.6444 | 2680.2583
05.12.2007 06:00 | 3600 | 2 | 757.67 | GGB | 765.201 | 771.609 | 767.033 | 264.63 | GGB | 11026.2 | GGB | 9.85 | GGB | 1012.36 | GGB | 58.77 | GGB | 172109.33 | GGB | 141532.85 | GGB | 0 | 0 | 2734 | 3600 | 2718.56 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 82809.06 | GGB | 82810.08 | 2718.56 | 2718.56 |  |  |  | 1 | 1 |  |  |  |  | 141532.85 | 2718.56 | 141532.85 | 2718.56 | 9.6457 | [5 empty] | 106.8793 | 2670.2493
05.12.2007 07:00 | 3600 | 2 | 757.86 | GGB | 766.667 | 772.664 | 768.498 | 266.11 | GGB | 11017 | GGB | 9.85 | GGB | 1013.66 | GGB | 58.31 | GGB | 173876.47 | GGB | 143367.99 | GGB | 0 | 0 | 2731 | 3600 | 2715.08 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 82849.73 | GGB | 82850.75 | 2715.08 | 2715.08 |  |  |  | 1 | 1 |  |  |  |  | 143367.99 | 2715.08 | 143367.99 | 2715.08 | 9.5711 | [5 empty] | 108.1265 | 2636.0696
05.12.2007 08:00 | 3600 | 2 | 758.14 | GGB | 766.667 | 772.641 | 768.498 | 266.97 | GGB | 11020 | GGB | 9.85 | GGB | 1014.63 | GGB | 58.16 | GGB | 174810.66 | GGB | 144341.46 | GGB | 0 | 0 | 2714 | 3600 | 2698.96 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 82889.37 | GGB | 82890.39 | 2698.96 | 2698.96 |  |  |  | 1 | 1 |  |  |  |  | 144341.46 | 2698.96 | 144341.46 | 2698.96 | 9.8277 | [5 empty] | 108.2144 | 2618.2914
05.12.2007 09:00 | 3600 | 2 | 758.31 | GGB | 766.667 | 772.641 | 768.498 | 266.97 | GGB | 11030.9 | GGB | 9.86 | GGB | 1015.39 | GGB | 58.12 | GGB | 174857.97 | GGB | 144506.87 | GGB | 0 | 0 | 2707 | 3600 | 2692.05 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 82929.99 | GGB | 82931.01 | 2692.05 | 2692.05 |  |  |  | 1 | 1 |  |  |  |  | 144506.87 | 2692.05 | 144506.87 | 2692.05 | 9.577 | [5 empty] | 108.061 | 2615.2943
05.12.2007 10:00 | 3600 | 2 | 758.22 | GGB | 765.201 | 771.586 | 767.033 | 267 | GGB | 11027.2 | GGB | 9.85 | GGB | 1015.78 | GGB | 58.14 | GGB | 174917.39 | GGB | 144602.5 | GGB | 0 | 0 | 2710 | 3600 | 2694.74 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 82970.13 | GGB | 82971.15 | 2694.74 | 2694.74 |  |  |  | 1 | 1 |  |  |  |  | 144602.5 | 2694.74 | 144602.5 | 2694.74 | 9.7077 | [5 empty] | 108.2406 | 2613.5648
05.12.2007 11:00 | 3600 | 2 | 758.02 | GGB | 766.667 | 772.945 | 769.597 | 266.67 | GGB | 11034.4 | GGB | 9.86 | GGB | 1016.51 | GGB | 58.19 | GGB | 174867.88 | GGB | 144641.51 | GGB | 0 | 0 | 2717 | 3600 | 2701.8 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 83010.41 | GGB | 83011.43 | 2701.8 | 2701.8 |  |  |  | 1 | 1 |  |  |  |  | 144641.51 | 2701.8 | 144641.51 | 2701.8 | 9.7019 | [5 empty] | 108.5535 | 2612.8599
05.12.2007 12:00 | 3600 | 2 | 758.82 | GGB | 768.864 | 774.07 | 770.696 | 265.77 | GGB | 11045.3 | GGB | 9.87 | GGB | 1016.59 | GGB | 58.32 | GGB | 174146.05 | GGB | 144000.4 | GGB | 0 | 0 | 2684 | 3600 | 2668.69 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 83051.13 | GGB | 83052.14 | 2668.69 | 2668.69 |  |  |  | 1 | 1 |  |  |  |  | 144000.4 | 2668.69 | 144000.4 | 2668.69 | 9.4398 | [5 empty] | 106.7479 | 2624.4927
05.12.2007 13:00 | 3600 | 2 | 758.9 | GGB | 766.3 | 771.844 | 768.498 | 263.8 | GGB | 11038.5 | GGB | 9.86 | GGB | 1016.3 | GGB | 59.19 | GGB | 171632.88 | GGB | 141509.08 | GGB | 0 | 0 | 2686 | 3600 | 2671.08 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 83090.83 | GGB | 83091.84 | 2671.08 | 2671.08 |  |  |  | 1 | 1 |  |  |  |  | 141509.08 | 2671.08 | 141509.08 | 2671.08 | 9.521 | [5 empty] | 104.995 | 2670.6979
05.12.2007 14:00 | 3600 | 2 | 758.63 | GGB | 767.766 | 772.781 | 769.597 | 263.7 | GGB | 11022.5 | GGB | 9.86 | GGB | 1016.35 | GGB | 59.35 | GGB | 171357.8 | GGB | 141224.74 | GGB | 0 | 0 | 2696 | 3600 | 2680.38 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 83131.35 | GGB | 83132.36 | 2680.38 | 2680.38 |  |  |  | 1 | 1 |  |  |  |  | 141224.74 | 2680.38 | 141224.74 | 2680.38 | 9.342 | [5 empty] | 105.1489 | 2676.075
05.12.2007 15:00 | 3600 | 2 | 758.4 | GGB | 766.667 | 773.695 | 769.597 | 264.83 | GGB | 10985.4 | GGB | 9.85 | GGB | 1016.71 | GGB | 58.97 | GGB | 172618.79 | GGB | 142473.36 | GGB | 0 | 0 | 2682 | 3600 | 2666.43 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 83171.54 | GGB | 83172.54 | 2666.43 | 2666.43 |  |  |  | 1 | 1 |  |  |  |  | 142473.36 | 2666.43 | 142473.36 | 2666.43 | 9.4548 | [5 empty] | 105.5265 | 2652.6222
05.12.2007 16:00 | 3600 | 2 | 758.27 | GGB | 765.201 | 772.5 | 768.498 | 265.68 | GGB | 10997.3 | GGB | 9.85 | GGB | 1016.83 | GGB | 58.48 | GGB | 174164.76 | GGB | 143982.2 | GGB | 0 | 0 | 2687 | 3600 | 2672.04 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 83211.15 | GGB | 83212.16 | 2672.04 | 2672.04 |  |  |  | 1 | 1 |  |  |  |  | 143982.2 | 2672.04 | 143982.2 | 2672.04 | 9.7104 | [5 empty] | 106.8684 | 2624.8245
05.12.2007 17:00 | 3600 | 2 | 758.37 | GGB | 765.201 | 772.523 | 768.498 | 265.21 | GGB | 11096.7 | GGB | 9.86 | GGB | 1016.64 | GGB | 58.19 | GGB | 174365.02 | GGB | 144243.72 | GGB | 0 | 0 | 2723 | 3600 | 2707.87 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 83252.16 | GGB | 83253.16 | 2707.87 | 2707.87 |  |  |  | 1 | 1 |  |  |  |  | 144243.72 | 2707.87 | 144243.72 | 2707.87 | 9.5267 | [5 empty] | 108.4981 | 2620.0655
05.12.2007 18:00 | 3600 | 2 | 757.92 | GGB | 765.201 | 772.453 | 767.033 | 264.98 | GGB | 11129.9 | GGB | 9.85 | GGB | 1016.83 | GGB | 58.1 | GGB | 174433.24 | GGB | 144367.7 | GGB | 0 | 0 | 2759 | 3600 | 2743.32 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 83291.95 | GGB | 83292.95 | 2743.32 | 2743.32 |  |  |  | 1 | 1 |  |  |  |  | 144367.7 | 2743.32 | 144367.7 | 2743.32 | 9.9534 | [5 empty] | 110.013 | 2617.8155
05.12.2007 19:00 | 3600 | 2 | 758.14 | GGB | 766.667 | 773.273 | 768.498 | 264.98 | GGB | 11144 | GGB | 9.86 | GGB | 1017.01 | GGB | 58.08 | GGB | 174613.7 | GGB | 144552.86 | GGB | 0 | 0 | 2757 | 3600 | 2741.08 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 83333.31 | GGB | 83334.31 | 2741.08 | 2741.08 |  |  |  | 1 | 1 |  |  |  |  | 144552.86 | 2741.08 | 144552.86 | 2741.08 | 9.5801 | [5 empty] | 110.0642 | 2614.4623
05.12.2007 20:00 | 3600 | 2 | 758.13 | GGB | 766.667 | 773.063 | 768.498 | 265.7 | GGB | 11108.7 | GGB | 9.85 | GGB | 1016.61 | GGB | 57.29 | GGB | 175892.29 | GGB | 145902.55 | GGB | 0 | 0 | 2733 | 3600 | 2717.65 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 83373.45 | GGB | 83374.46 | 2717.65 | 2717.65 |  |  |  | 1 | 1 |  |  |  |  | 145902.55 | 2717.65 | 145902.55 | 2717.65 | 9.8758 | [5 empty] | 110.1422 | 2590.2769
05.12.2007 21:00 | 3600 | 2 | 758.38 | GGB | 765.201 | 772.008 | 768.498 | 265.66 | GGB | 11107.1 | GGB | 9.86 | GGB | 1016.56 | GGB | 56.76 | GGB | 176348.93 | GGB | 146508.62 | GGB | 0 | 0 | 2713 | 3600 | 2698.02 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 83414.23 | GGB | 83415.23 | 2698.02 | 2698.02 |  |  |  | 1 | 1 |  |  |  |  | 146508.62 | 2698.02 | 146508.62 | 2698.02 | 9.6954 | [5 empty] | 109.8009 | 2579.5615
05.12.2007 22:00 | 3600 | 2 | 758.44 | GGB | 765.201 | 771.07 | 768.132 | 264.05 | GGB | 11139.9 | GGB | 9.86 | GGB | 1016.23 | GGB | 57.25 | GGB | 174108.64 | GGB | 144385.02 | GGB | 0 | 0 | 2737 | 3600 | 2721.93 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 83454.96 | GGB | 83455.97 | 2721.93 | 2721.93 |  |  |  | 1 | 1 |  |  |  |  | 144385.02 | 2721.93 | 144385.02 | 2721.93 | 9.6467 | [5 empty] | 109.1683 | 2617.5015
05.12.2007 23:00 | 3600 | 2 | 758.06 | GGB | 766.3 | 772.453 | 768.132 | 264.15 | GGB | 11134.2 | GGB | 9.86 | GGB | 1016.34 | GGB | 57.58 | GGB | 174246.19 | GGB | 144371.73 | GGB | 0 | 0 | 2756 | 3600 | 2740.34 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 83495.31 | GGB | 83496.32 | 2740.34 | 2740.34 |  |  |  | 1 | 1 |  |  |  |  | 144371.73 | 2740.34 | 144371.73 | 2740.34 | 9.8049 | [5 empty] | 109.8966 | 2617.7424
05.12.2007 24:00 | 3600 | 2 | 758.13 | GGB | 766.3 | 772.922 | 768.498 | 263.67 | GGB | 11130 | GGB | 9.86 | GGB | 1015.74 | GGB | 57.68 | GGB | 174077.83 | GGB | 144101.94 | GGB | 0 | 0 | 2747 | 3600 | 2731.48 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 83536.55 | GGB | 83537.55 | 2731.48 | 2731.48 |  |  |  | 1 | 1 |  |  |  |  | 144101.94 | 2731.48 | 144101.94 | 2731.48 | 9.5467 | [5 empty] | 109.3365 | 2622.6434
06.12.2007 01:00 | 3600 | 2 | 757.99 | GGB | 766.3 | 772.031 | 768.132 | 265.38 | GGB | 11075.4 | GGB | 9.85 | GGB | 1015.18 | GGB | 56.98 | GGB | 176274.11 | GGB | 146149.98 | GGB | 0 | 0 | 2729 | 3600 | 2713.93 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 83576.45 | GGB | 83577.46 | 2713.93 | 2713.93 |  |  |  | 1 | 1 |  |  |  |  | 146149.98 | 2713.93 | 146149.98 | 2713.93 | 9.9384 | [5 empty] | 110.178 | 2585.8916
06.12.2007 02:00 | 3600 | 2 | 758.29 | GGB | 766.3 | 772.031 | 768.132 | 265.25 | GGB | 11078.9 | GGB | 9.86 | GGB | 1014.76 | GGB | 56.83 | GGB | 176048.54 | GGB | 145969.77 | GGB | 0 | 0 | 2713 | 3600 | 2697.84 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 83618.09 | GGB | 83619.1 | 2697.84 | 2697.84 |  |  |  | 1 | 1 |  |  |  |  | 145969.77 | 2697.84 | 145969.77 | 2697.84 | 9.4573 | [5 empty] | 109.3897 | 2589.084
06.12.2007 03:00 | 3600 | 2 | 758.62 | GGB | 765.201 | 771.938 | 768.498 | 264.58 | GGB | 11104.6 | GGB | 9.86 | GGB | 1013.97 | GGB | 57.26 | GGB | 175035.13 | GGB | 144827.01 | GGB | 0 | 0 | 2713 | 3600 | 2697.67 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 83656.89 | GGB | 83657.9 | 2697.67 | 2697.67 |  |  |  | 1 | 1 |  |  |  |  | 144827.01 | 2697.67 | 144827.01 | 2697.67 | 10.0695 | [5 empty] | 108.5265 | 2609.5132
06.12.2007 04:00 | 3600 | 2 | 757.88 | GGB | 766.3 | 771.938 | 768.132 | 263.49 | GGB | 11114.7 | GGB | 9.86 | GGB | 1013.33 | GGB | 57.66 | GGB | 173770.84 | GGB | 143516.05 | GGB | 0 | 0 | 2757 | 3600 | 2741.94 | GGB | 100 | GGB | 42.6 | GGB | 42.6 | GGB | 83699.49 | GGB | 83700.5 | 2741.94 | 2741.94 |  |  |  | 1 | 1 |  |  |  |  | 143516.05 | 2741.94 | 143516.05 | 2741.94 | 9.2374 | [5 empty] | 109.309 | 2633.3501
06.12.2007 05:00 | 3600 | 2 | 758.01 | GGB | 765.201 | 771.773 | 767.033 | 263.11 | GGB | 11108.9 | GGB | 9.86 | GGB | 1012.9 | GGB | 57.59 | GGB | 173707.02 | GGB | 143431.29 | GGB | 0 | 0 | 2750 | 3600 | 2734.33 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 83738.94 | GGB | 83739.95 | 2734.33 | 2734.33 |  |  |  | 1 | 1 |  |  |  |  | 143431.29 | 2734.33 | 143431.29 | 2734.33 | 9.9414 | [5 empty] | 108.9412 | 2634.9062
06.12.2007 06:00 | 3600 | 2 | 757.77 | GGB | 766.3 | 771.773 | 768.132 | 263.44 | GGB | 11105.6 | GGB | 9.85 | GGB | 1012.76 | GGB | 57.61 | GGB | 173955.7 | GGB | 143609.58 | GGB | 0 | 0 | 2768 | 3600 | 2752.5 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 83779.93 | GGB | 83780.94 | 2752.5 | 2752.5 |  |  |  | 1 | 1 |  |  |  |  | 143609.58 | 2752.5 | 143609.58 | 2752.5 | 9.6435 | [5 empty] | 109.8015 | 2631.635
06.12.2007 07:00 | 3600 | 2 | 758 | GGB | 765.201 | 771.82 | 767.033 | 263.49 | GGB | 11109.4 | GGB | 9.86 | GGB | 1012.7 | GGB | 57.57 | GGB | 173994.21 | GGB | 143649.07 | GGB | 0 | 0 | 2753 | 3600 | 2737.44 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 83820.8 | GGB | 83821.8 | 2737.44 | 2737.44 |  |  |  | 1 | 1 |  |  |  |  | 143649.07 | 2737.44 | 143649.07 | 2737.44 | 9.6239 | [5 empty] | 109.2308 | 2630.9116
06.12.2007 08:00 | 3600 | 2 | 758.04 | GGB | 766.3 | 772.875 | 768.498 | 263.35 | GGB | 11111.9 | GGB | 9.86 | GGB | 1012.53 | GGB | 57.52 | GGB | 174087.74 | GGB | 143722.75 | GGB | 0 | 0 | 2750 | 3600 | 2734.92 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 83860.71 | GGB | 83861.71 | 2734.92 | 2734.92 |  |  |  | 1 | 1 |  |  |  |  | 143722.75 | 2734.92 | 143722.75 | 2734.92 | 9.8489 | [5 empty] | 109.1862 | 2629.5628
06.12.2007 09:00 | 3600 | 2 | 758.06 | GGB | 766.3 | 771.797 | 768.132 | 263 | GGB | 11100.8 | GGB | 9.86 | GGB | 1012.19 | GGB | 57.33 | GGB | 173847.86 | GGB | 143559.09 | GGB | 0 | 0 | 2746 | 3600 | 2730.59 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 83902.08 | GGB | 83903.08 | 2730.59 | 2730.59 |  |  |  | 1 | 1 |  |  |  |  | 143559.09 | 2730.59 | 143559.09 | 2730.59 | 9.4755 | [5 empty] | 108.8892 | 2632.5606
06.12.2007 10:00 | 3600 | 2 | 757.93 | GGB | 766.3 | 771.75 | 767.033 | 262.71 | GGB | 11090.1 | GGB | 9.86 | GGB | 1012.02 | GGB | 57.36 | GGB | 173622.29 | GGB | 143336.32 | GGB | 0 | 0 | 2738 | 3600 | 2722.55 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 83941.96 | GGB | 83942.96 | 2722.55 | 2722.55 |  |  |  | 1 | 1 |  |  |  |  | 143336.32 | 2722.55 | 143336.32 | 2722.55 | 9.7854 | [5 empty] | 108.4001 | 2636.652
06.12.2007 11:00 | 3600 | 2 | 758.08 | GGB | 766.3 | 772.734 | 768.132 | 262.94 | GGB | 11088.1 | GGB | 9.86 | GGB | 1012.53 | GGB | 57.55 | GGB | 173507.86 | GGB | 143232.66 | GGB | 0 | 0 | 2737 | 3600 | 2721.59 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 83982.73 | GGB | 83983.74 | 2721.59 | 2721.59 |  |  |  | 1 | 1 |  |  |  |  | 143232.66 | 2721.59 | 143232.66 | 2721.59 | 9.5591 | [5 empty] | 108.2835 | 2638.5602
06.12.2007 12:00 | 3600 | 2 | 758.18 | GGB | 765.201 | 771.656 | 767.033 | 262.89 | GGB | 11085.6 | GGB | 9.86 | GGB | 1012.04 | GGB | 57.64 | GGB | 173456.14 | GGB | 143080.77 | GGB | 0 | 0 | 2728 | 3600 | 2712.38 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 84023.49 | GGB | 84024.5 | 2712.38 | 2712.38 |  |  |  | 1 | 1 |  |  |  |  | 143080.77 | 2712.38 | 143080.77 | 2712.38 | 9.5213 | [5 empty] | 107.8026 | 2641.3612
06.12.2007 13:00 | 3600 | 2 | 758.04 | GGB | 766.3 | 771.609 | 768.132 | 263.03 | GGB | 11073.6 | GGB | 9.86 | GGB | 1011.9 | GGB | 57.74 | GGB | 173194.26 | GGB | 142805.54 | GGB | 0 | 0 | 2734 | 3600 | 2718.78 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 84063.75 | GGB | 84064.76 | 2718.78 | 2718.78 |  |  |  | 1 | 1 |  |  |  |  | 142805.54 | 2718.78 | 142805.54 | 2718.78 | 9.6437 | [5 empty] | 107.8491 | 2646.452
06.12.2007 14:00 | 3600 | 2 | 758.08 | GGB | 766.3 | 772.898 | 768.498 | 263.24 | GGB | 11062 | GGB | 9.86 | GGB | 1011.73 | GGB | 57.85 | GGB | 172629.79 | GGB | 142266.86 | GGB | 0 | 0 | 2731 | 3600 | 2716.05 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 84104.83 | GGB | 84105.83 | 2716.05 | 2716.05 |  |  |  | 1 | 1 |  |  |  |  | 142266.86 | 2716.05 | 142266.86 | 2716.05 | 9.4084 | [5 empty] | 107.3344 | 2656.4725
06.12.2007 15:00 | 3600 | 2 | 758.11 | GGB | 766.3 | 772.922 | 768.132 | 262.98 | GGB | 11055.5 | GGB | 9.86 | GGB | 1011.33 | GGB | 57.85 | GGB | 172674.9 | GGB | 142247.21 | GGB | 0 | 0 | 2725 | 3600 | 2710.03 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 84144.87 | GGB | 84145.87 | 2710.03 | 2710.03 |  |  |  | 1 | 1 |  |  |  |  | 142247.21 | 2710.03 | 142247.21 | 2710.03 | 9.6277 | [5 empty] | 107.0817 | 2656.8395
06.12.2007 16:00 | 3600 | 2 | 758.19 | GGB | 765.201 | 770.742 | 767.033 | 263.05 | GGB | 11057 | GGB | 9.85 | GGB | 1010.9 | GGB | 57.8 | GGB | 172576.97 | GGB | 142128.64 | GGB | 0 | 0 | 2731 | 3600 | 2715.92 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 84185.66 | GGB | 84186.67 | 2715.92 | 2715.92 |  |  |  | 1 | 1 |  |  |  |  | 142128.64 | 2715.92 | 142128.64 | 2715.92 | 9.461 | [5 empty] | 107.225 | 2659.0559
06.12.2007 17:00 | 3600 | 2 | 757.51 | GGB | 766.3 | 771.656 | 768.132 | 264.07 | GGB | 11082.1 | GGB | 9.85 | GGB | 1011.25 | GGB | 57.5 | GGB | 173372.52 | GGB | 142961.77 | GGB | 0 | 0 | 2787 | 3600 | 2771.79 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 84226.05 | GGB | 84227.06 | 2771.79 | 2771.79 |  |  |  | 1 | 1 |  |  |  |  | 142961.77 | 2771.79 | 142961.77 | 2771.79 | 9.8108 | [5 empty] | 110.0722 | 2643.5599
06.12.2007 18:00 | 3600 | 2 | 757.6 | GGB | 765.201 | 771.539 | 767.033 | 264.12 | GGB | 11097.3 | GGB | 9.85 | GGB | 1010.98 | GGB | 57.23 | GGB | 173605.79 | GGB | 143232.7 | GGB | 0 | 0 | 2784 | 3600 | 2768.7 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 84266.49 | GGB | 84267.5 | 2768.7 | 2768.7 |  |  |  | 1 | 1 |  |  |  |  | 143232.7 | 2768.7 | 143232.7 | 2768.7 | 9.8063 | [5 empty] | 110.1579 | 2638.5595
06.12.2007 19:00 | 3600 | 2 | 757.53 | GGB | 765.201 | 771.586 | 766.667 | 264.26 | GGB | 11099.3 | GGB | 9.86 | GGB | 1010.7 | GGB | 57.37 | GGB | 173565.08 | GGB | 143101.47 | GGB | 0 | 0 | 2783 | 3600 | 2767.17 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 84307.14 | GGB | 84308.16 | 2767.17 | 2767.17 |  |  |  | 1 | 1 |  |  |  |  | 143101.47 | 2767.17 | 143101.47 | 2767.17 | 9.739 | [5 empty] | 109.9961 | 2640.9792
06.12.2007 20:00 | 3600 | 2 | 757.69 | GGB | 766.667 | 772.594 | 768.864 | 264.43 | GGB | 11100.9 | GGB | 9.86 | GGB | 1010.5 | GGB | 57.42 | GGB | 173688.31 | GGB | 143152.7 | GGB | 0 | 0 | 2776 | 3600 | 2760.95 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 84347.42 | GGB | 84348.44 | 2760.95 | 2760.95 |  |  |  | 1 | 1 |  |  |  |  | 143152.7 | 2760.95 | 143152.7 | 2760.95 | 9.8123 | [5 empty] | 109.7882 | 2640.034
06.12.2007 21:00 | 3600 | 2 | 757.53 | GGB | 765.201 | 771.539 | 767.766 | 264.39 | GGB | 11085.6 | GGB | 9.85 | GGB | 1010.28 | GGB | 57.5 | GGB | 173467.15 | GGB | 142903.52 | GGB | 0 | 0 | 2781 | 3600 | 2765.31 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 84388.26 | GGB | 84389.28 | 2765.31 | 2765.31 |  |  |  | 1 | 1 |  |  |  |  | 142903.52 | 2765.31 | 142903.52 | 2765.31 | 9.6761 | [5 empty] | 109.7701 | 2644.6374
06.12.2007 22:00 | 3600 | 2 | 757.59 | GGB | 765.201 | 771.539 | 766.667 | 264.31 | GGB | 11081.6 | GGB | 9.86 | GGB | 1009.65 | GGB | 57.51 | GGB | 173413.23 | GGB | 142764.03 | GGB | 0 | 0 | 2770 | 3600 | 2754.07 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 84428.35 | GGB | 84429.36 | 2754.07 | 2754.07 |  |  |  | 1 | 1 |  |  |  |  | 142764.03 | 2754.07 | 142764.03 | 2754.07 | 9.8099 | [5 empty] | 109.2173 | 2647.2214
06.12.2007 23:00 | 3600 | 2 | 757.74 | GGB | 764.102 | 770.32 | 766.667 | 263.65 | GGB | 11093.5 | GGB | 9.86 | GGB | 1009.19 | GGB | 57.36 | GGB | 173533.17 | GGB | 142863.3 | GGB | 0 | 0 | 2770 | 3600 | 2754.09 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 84468.65 | GGB | 84469.66 | 2754.09 | 2754.09 |  |  |  | 1 | 1 |  |  |  |  | 142863.3 | 2754.09 | 142863.3 | 2754.09 | 9.7632 | [5 empty] | 109.294 | 2645.382
06.12.2007 24:00 | 3600 | 2 | 757.58 | GGB | 765.201 | 772.406 | 767.766 | 264.13 | GGB | 11085.2 | GGB | 9.86 | GGB | 1008.77 | GGB | 57.42 | GGB | 173364.81 | GGB | 142640.18 | GGB | 0 | 0 | 2781 | 3600 | 2765.44 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 84510.03 | GGB | 84511.04 | 2765.44 | 2765.44 |  |  |  | 1 | 1 |  |  |  |  | 142640.18 | 2765.44 | 142640.18 | 2765.44 | 9.5327 | [5 empty] | 109.573 | 2649.5199
07.12.2007 01:00 | 3600 | 2 | 757.63 | GGB | 766.3 | 772.383 | 768.864 | 265.59 | GGB | 11049.5 | GGB | 9.85 | GGB | 1008.48 | GGB | 56.69 | GGB | 175573.19 | GGB | 144735.48 | GGB | 0 | 0 | 2752 | 3600 | 2736.11 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 84549.59 | GGB | 84550.59 | 2736.11 | 2736.11 |  |  |  | 1 | 1 |  |  |  |  | 144735.48 | 2736.11 | 144735.48 | 2736.11 | 10.013 | [5 empty] | 110.0034 | 2611.1635
07.12.2007 02:00 | 3600 | 2 | 757.97 | GGB | 765.201 | 771.492 | 767.766 | 264.09 | GGB | 11075.3 | GGB | 9.86 | GGB | 1007.94 | GGB | 57.22 | GGB | 173811.55 | GGB | 142977.84 | GGB | 0 | 0 | 2741 | 3600 | 2725.13 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 84590.33 | GGB | 84591.33 | 2725.13 | 2725.13 |  |  |  | 1 | 1 |  |  |  |  | 142977.84 | 2725.13 | 142977.84 | 2725.13 | 9.5639 | [5 empty] | 108.2314 | 2643.2628
07.12.2007 03:00 | 3600 | 2 | 757.71 | GGB | 765.201 | 770.625 | 767.766 | 263.39 | GGB | 11065.2 | GGB | 9.86 | GGB | 1007.02 | GGB | 57.36 | GGB | 173139.25 | GGB | 142230.82 | GGB | 0 | 0 | 2755 | 3600 | 2739.3 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 84630.85 | GGB | 84631.85 | 2739.3 | 2739.3 |  |  |  | 1 | 1 |  |  |  |  | 142230.82 | 2739.3 | 142230.82 | 2739.3 | 9.6153 | [5 empty] | 108.2258 | 2657.1456
07.12.2007 04:00 | 3600 | 2 | 757.69 | GGB | 765.201 | 771.633 | 767.766 | 262.84 | GGB | 11054.6 | GGB | 9.86 | GGB | 1006.24 | GGB | 57.53 | GGB | 172601.18 | GGB | 141607.77 | GGB | 0 | 0 | 2750 | 3600 | 2734.31 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 84670.83 | GGB | 84671.83 | 2734.31 | 2734.31 |  |  |  | 1 | 1 |  |  |  |  | 141607.77 | 2734.31 | 141607.77 | 2734.31 | 9.6848 | [5 empty] | 107.5554 | 2668.8366
07.12.2007 05:00 | 3600 | 2 | 757.59 | GGB | 766.3 | 771.609 | 767.766 | 262.38 | GGB | 11043.6 | GGB | 9.86 | GGB | 1005.15 | GGB | 57.53 | GGB | 172268.88 | GGB | 141180.94 | GGB | 0 | 0 | 2750 | 3600 | 2734.26 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 84711.37 | GGB | 84712.37 | 2734.26 | 2734.26 |  |  |  | 1 | 1 |  |  |  |  | 141180.94 | 2734.26 | 141180.94 | 2734.26 | 9.5221 | [5 empty] | 107.2293 | 2676.9053
07.12.2007 06:00 | 3600 | 2 | 757.72 | GGB | 766.3 | 771.633 | 767.766 | 261.77 | GGB | 11028.5 | GGB | 9.86 | GGB | 1004.13 | GGB | 57.65 | GGB | 171926.67 | GGB | 140709.13 | GGB | 0 | 0 | 2735 | 3600 | 2719.08 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 84751.57 | GGB | 84752.57 | 2719.08 | 2719.08 |  |  |  | 1 | 1 |  |  |  |  | 140709.13 | 2719.08 | 140709.13 | 2719.08 | 9.5174 | [5 empty] | 106.2776 | 2685.8812
07.12.2007 07:00 | 3600 | 2 | 757.53 | GGB | 766.3 | 772.711 | 768.864 | 262.03 | GGB | 11015 | GGB | 9.85 | GGB | 1004.07 | GGB | 57.8 | GGB | 171756.12 | GGB | 140494.82 | GGB | 0 | 0 | 2736 | 3600 | 2720.24 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 84791.99 | GGB | 84792.99 | 2720.24 | 2720.24 |  |  |  | 1 | 1 |  |  |  |  | 140494.82 | 2720.24 | 140494.82 | 2720.24 | 9.4552 | [5 empty] | 106.161 | 2689.9782
07.12.2007 08:00 | 3600 | 2 | 757.69 | GGB | 766.3 | 771.586 | 767.766 | 261.95 | GGB | 11009.4 | GGB | 9.86 | GGB | 1003.34 | GGB | 57.84 | GGB | 171619.68 | GGB | 140263.77 | GGB | 0 | 0 | 2755 | 3208 | 2739.52 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 84832.07 | GGB | 84833.08 | 2739.52 | 2739.52 |  |  |  | 1 | 1 |  |  |  |  | 140263.77 | 2739.52 | 140263.77 | 2739.52 | 9.5848 | [5 empty] | 106.7376 | 2694.4093
07.12.2007 09:00 | 3600 | 2 | 757.71 | GGB | 765.201 | 771.586 | 767.766 | 261.33 | GGB | 10997.2 | GGB | 9.86 | GGB | 1002.92 | GGB | 57.8 | GGB | 171301.68 | GGB | 139964.16 | GGB | 0 | 0 | 2755 | 3600 | 2739.73 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 84872.19 | GGB | 84873.2 | 2739.73 | 2739.73 |  |  |  | 1 | 1 |  |  |  |  | 139964.16 | 2739.73 | 139964.16 | 2739.73 | 9.5579 | [5 empty] | 106.5178 | 2700.177
07.12.2007 10:00 | 3600 | 2 | 757.76 | GGB | 765.201 | 771.867 | 768.132 | 260.85 | GGB | 10981.4 | GGB | 9.86 | GGB | 1002.43 | GGB | 57.91 | GGB | 170905.56 | GGB | 139524.65 | GGB | 0 | 0 | 2744 | 3600 | 2728.47 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 84912.68 | GGB | 84913.69 | 2728.47 | 2728.47 |  |  |  | 1 | 1 |  |  |  |  | 139524.65 | 2728.47 | 139524.65 | 2728.47 | 9.402 | [5 empty] | 105.7469 | 2708.6827
07.12.2007 11:00 | 3600 | 2 | 757.67 | GGB | 765.201 | 771.656 | 767.033 | 260.47 | GGB | 10967.2 | GGB | 9.86 | GGB | 1001.49 | GGB | 57.8 | GGB | 170744.91 | GGB | 139311.99 | GGB | 0 | 0 | 2739 | 3600 | 2724.03 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 84952.47 | GGB | 84953.48 | 2724.03 | 2724.03 |  |  |  | 1 | 1 |  |  |  |  | 139311.99 | 2724.03 | 139311.99 | 2724.03 | 9.5373 | [5 empty] | 105.4139 | 2712.8175
07.12.2007 12:00 | 3600 | 2 | 757.63 | GGB | 766.3 | 772.523 | 768.498 | 260.85 | GGB | 10942.1 | GGB | 9.86 | GGB | 1000.07 | GGB | 57.25 | GGB | 171550.36 | GGB | 140003.34 | GGB | 0 | 0 | 2731 | 3600 | 2715.57 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 84993.26 | GGB | 84994.27 | 2715.57 | 2715.57 |  |  |  | 1 | 1 |  |  |  |  | 140003.34 | 2715.57 | 140003.34 | 2715.57 | 9.3206 | [5 empty] | 105.608 | 2699.4213
07.12.2007 13:00 | 3600 | 2 | 758.07 | GGB | 765.201 | 771.352 | 767.033 | 259.37 | GGB | 10942.6 | GGB | 9.86 | GGB | 998.32 | GGB | 57.4 | GGB | 170166.13 | GGB | 138564.58 | GGB | 0 | 0 | 2701 | 3600 | 2685.67 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 85032.44 | GGB | 85033.44 | 2685.67 | 2685.67 |  |  |  | 1 | 1 |  |  |  |  | 138564.58 | 2685.67 | 138564.58 | 2685.67 | 9.5006 | [5 empty] | 103.3719
07.12.2007 14:00 | 3600 | 2 | 757.94 | GGB | 765.201 | 771.328 | 768.132 | 258.38 | GGB | 10919.4 | GGB | 9.86 | GGB | 996.55 | GGB | 57.55 | GGB | 169384.89 | GGB | 137623.54 | GGB | 0 | 0 | 2697 | 3600 | 2681.16 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 85072.68 | GGB | 85073.68 | 2681.16 | 2681.16 |  |  |  | 1 | 1 |  |  |  |  | 137623.54 | 2681.16 | 137623.54 | 2681.16 | 9.1697 | [5 empty] | 102.4974
07.12.2007 15:00 | 3600 | 2 | 757.95 | GGB | 765.201 | 772.383 | 768.132 | 257.71 | GGB | 10883.7 | GGB | 9.86 | GGB | 994.82 | GGB | 57.58 | GGB | 168908.45 | GGB | 136986.3 | GGB | 0 | 0 | 2682 | 3600 | 2666.64 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 85112.07 | GGB | 85113.07 | 2666.64 | 2666.64 |  |  |  | 1 | 1 |  |  |  |  | 136986.3 | 2666.64 | 136986.3 | 2666.64 | 9.2738 | [5 empty] | 101.4703
07.12.2007 16:00 | 3600 | 2 | 757.87 | GGB | 766.3 | 772.219 | 768.498 | 258.1 | GGB | 10841.5 | GGB | 9.85 | GGB | 993.62 | GGB | 57.39 | GGB | 169474.02 | GGB | 137358.68 | GGB | 0 | 0 | 2664 | 3600 | 2648.9 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 85151.41 | GGB | 85152.41 | 2648.9 | 2648.9 |  |  |  | 1 | 1 |  |  |  |  | 137358.68 | 2648.9 | 137358.68 | 2648.9 | 9.2488 | [5 empty] | 101.0693
07.12.2007 17:00 | 3600 | 2 | 758.14 | GGB | 765.201 | 772.219 | 767.033 | 258.48 | GGB | 10829.1 | GGB | 9.86 | GGB | 992.47 | GGB | 56.86 | GGB | 170035.19 | GGB | 137873.05 | GGB | 0 | 0 | 2630 | 3600 | 2615.03 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 85191.4 | GGB | 85192.4 | 2615.03 | 2615.03 |  |  |  | 1 | 1 |  |  |  |  | 137873.05 | 2615.03 | 137873.05 | 2615.03 | 9.0158 | [5 empty] | 100.1506
07.12.2007 18:00 | 3600 | 2 | 757.76 | GGB | 765.201 | 771.188 | 768.132 | 256.76 | GGB | 10858.7 | GGB | 9.86 | GGB | 991.82 | GGB | 57.11 | GGB | 167855.42 | GGB | 135912.38 | GGB | 0 | 0 | 2661 | 3600 | 2645.58 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 85230.11 | GGB | 85231.12 | 2645.58 | 2645.58 |  |  |  | 1 | 1 |  |  |  |  | 135912.38 | 2645.58 | 135912.38 | 2645.58 | 9.2863 | [5 empty] | 99.8797
07.12.2007 19:00 | 3600 | 2 | 757.34 | GGB | 766.3 | 772.219 | 767.766 | 257.99 | GGB | 10858.9 | GGB | 9.85 | GGB | 991.52 | GGB | 56.11 | GGB | 169575.25 | GGB | 137680.71 | GGB | 0 | 0 | 2684 | 3600 | 2668.16 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 85270.83 | GGB | 85271.83 | 2668.16 | 2668.16 |  |  |  | 1 | 1 |  |  |  |  | 137680.71 | 2668.16 | 137680.71 | 2668.16 | 9.0237 | [5 empty] | 102.0428
07.12.2007 20:00 | 3600 | 2 | 757.68 | GGB | 766.3 | 772.242 | 767.766 | 258.82 | GGB | 10851.7 | GGB | 9.86 | GGB | 990.91 | GGB | 56.4 | GGB | 170749.31 | GGB | 138428.07 | GGB | 0 | 0 | 2658 | 3600 | 2642.35 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 85309.86 | GGB | 85310.86 | 2642.35 | 2642.35 |  |  |  | 1 | 1 |  |  |  |  | 138428.07 | 2642.35 | 138428.07 | 2642.35 | 9.3716 | [5 empty] | 101.6043
07.12.2007 21:00 | 3600 | 2 | 757.84 | GGB | 765.201 | 771.211 | 767.766 | 256.91 | GGB | 10864 | GGB | 9.86 | GGB | 989.63 | GGB | 57.34 | GGB | 168140.41 | GGB | 135749.81 | GGB | 0 | 0 | 2669 | 3600 | 2653.21 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 85349.35 | GGB | 85350.35 | 2653.21 | 2653.21 |  |  |  | 1 | 1 |  |  |  |  | 135749.81 | 2653.21 | 135749.81 | 2653.21 | 9.1206 | [5 empty] | 100.048
07.12.2007 22:00 | 3600 | 2 | 757.83 | GGB | 765.201 | 771.328 | 767.766 | 256.48 | GGB | 10829.7 | GGB | 9.86 | GGB | 988.94 | GGB | 57.78 | GGB | 167367.97 | GGB | 134850.52 | GGB | 0 | 0 | 2660 | 3600 | 2644.39 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 85389.54 | GGB | 85390.54 | 2644.39 | 2644.39 |  |  |  | 1 | 1 |  |  |  |  | 134850.52 | 2644.39 | 134850.52 | 2644.39 | 8.8728 | [5 empty] | 99.0548
07.12.2007 23:00 | 3600 | 2 | 758 | GGB | 766.3 | 772.477 | 767.766 | 257.55 | GGB | 10780.9 | GGB | 9.85 | GGB | 989.09 | GGB | 57.7 | GGB | 168844.63 | GGB | 136096.4 | GGB | 0 | 0 | 2630 | 3600 | 2614.54 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 85428.41 | GGB | 85429.4 | 2614.54 | 2614.54 |  |  |  | 1 | 1 |  |  |  |  | 136096.4 | 2614.54 | 136096.4 | 2614.54 | 9.1567 | [5 empty] | 98.8415
07.12.2007 24:00 | 3600 | 2 | 758.04 | GGB | 766.3 | 772.547 | 768.498 | 256.64 | GGB | 10775.4 | GGB | 9.86 | GGB | 989.1 | GGB | 57.29 | GGB | 168614.66 | GGB | 136079.43 | GGB | 0 | 0 | 2609 | 3600 | 2593.97 | GGB | 100 | GGB | 37.31 | GGB | 37.31 | GGB | 85465.72 | GGB | 85466.71 | 2593.97 | 2593.97 |  |  |  | 1 | 1 |  |  |  |  | 136079.43 | 2593.97 | 136079.43 | 2593.97 | 9.4609 | [5 empty] | 98.0517
08.12.2007 01:00 | 3600 | 2 | 758.6 | GGB | 766.667 | 772.523 | 768.498 | 255.11 | GGB | 10766.7 | GGB | 9.86 | GGB | 989.15 | GGB | 58.7 | GGB | 165486.4 | GGB | 132994.62 | GGB | 0 | 0 | 2597 | 3600 | 2581.36 | GGB | 100 | GGB | 41.61 | GGB | 41.61 | GGB | 85507.33 | GGB | 85508.32 | 2581.36 | 2581.36 |  |  |  | 1 | 1 |  |  |  |  | 132994.62 | 2581.36 | 132994.62 | 2581.36 | 8.2506 | [5 empty] | 95.3631
08.12.2007 02:00 | 3600 | 2 | 758.31 | GGB | 766.3 | 772.523 | 768.498 | 255.18 | GGB | 10742.3 | GGB | 9.85 | GGB | 989.46 | GGB | 58.97 | GGB | 165358.76 | GGB | 132827.26 | GGB | 0 | 0 | 2594 | 3600 | 2578.93 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 85545.84 | GGB | 85546.83 | 2578.93 | 2578.93 |  |  |  | 1 | 1 |  |  |  |  | 132827.26 | 2578.93 | 132827.26 | 2578.93 | 8.8951 | [5 empty] | 95.1534
08.12.2007 03:00 | 3600 | 2 | 758.31 | GGB | 767.766 | 773.531 | 769.597 | 255.66 | GGB | 10746.4 | GGB | 9.85 | GGB | 990.25 | GGB | 59.05 | GGB | 165276.23 | GGB | 132833.16 | GGB | 0 | 0 | 2599 | 3600 | 2583.34 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 85585.55 | GGB | 85586.54 | 2583.34 | 2583.34 |  |  |  | 1 | 1 |  |  |  |  | 132833.16 | 2583.34 | 132833.16 | 2583.34 | 8.6415 | [5 empty] | 95.3203
08.12.2007 04:00 | 3600 | 2 | 758.68 | GGB | 766.667 | 773.531 | 768.498 | 255.23 | GGB | 10737.2 | GGB | 9.86 | GGB | 991.17 | GGB | 59.12 | GGB | 164912.02 | GGB | 132632.91 | GGB | 0 | 0 | 2580 | 3600 | 2564.52 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 85625.43 | GGB | 85626.43 | 2564.52 | 2564.52 |  |  |  | 1 | 1 |  |  |  |  | 132632.91 | 2564.52 | 132632.91 | 2564.52 | 8.5269 | [5 empty] | 94.4833
08.12.2007 05:00 | 3600 | 2 | 758.9 | GGB | 766.667 | 773.531 | 769.597 | 255.17 | GGB | 10729.2 | GGB | 9.86 | GGB | 992.03 | GGB | 59.19 | GGB | 164738.17 | GGB | 132583.42 | GGB | 0 | 0 | 2574 | 3600 | 2558.6 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 85663.74 | GGB | 85664.73 | 2558.6 | 2558.6 |  |  |  | 1 | 1 |  |  |  |  | 132583.42 | 2558.6 | 132583.42 | 2558.6 | 8.8571 | [5 empty] | 94.23
08.12.2007 06:00 | 3600 | 2 | 758.75 | GGB | 766.667 | 772.523 | 768.864 | 255.39 | GGB | 10724.8 | GGB | 9.85 | GGB | 992.71 | GGB | 59.36 | GGB | 164686.45 | GGB | 132565.47 | GGB | 0 | 0 | 2575 | 3600 | 2559.53 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 85704.02 | GGB | 85705.02 | 2559.53 | 2559.53 |  |  |  | 1 | 1 |  |  |  |  | 132565.47 | 2559.53 | 132565.47 | 2559.53 | 8.4216 | [5 empty] | 94.2515
08.12.2007 07:00 | 3600 | 2 | 758.57 | GGB | 766.667 | 772.5 | 768.132 | 256.11 | GGB | 10741.5 | GGB | 9.85 | GGB | 993.57 | GGB | 59.31 | GGB | 165271.83 | GGB | 133170.51 | GGB | 0 | 0 | 2592 | 3600 | 2576.88 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 85742.85 | GGB | 85743.85 | 2576.88 | 2576.88 |  |  |  | 1 | 1 |  |  |  |  | 133170.51 | 2576.88 | 133170.51 | 2576.88 | 8.8376 | [5 empty] | 95.3235
08.12.2007 08:00 | 3600 | 2 | 758.53 | GGB | 766.3 | 772.219 | 768.498 | 258.12 | GGB | 10754.3 | GGB | 9.85 | GGB | 994.91 | GGB | 59.17 | GGB | 167381.18 | GGB | 135107.14 | GGB | 0 | 0 | 2603 | 3600 | 2588.1 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 85782.06 | GGB | 85783.06 | 2588.1 | 2588.1 |  |  |  | 1 | 1 |  |  |  |  | 135107.14 | 2588.1 | 135107.14 | 2588.1 | 8.9179 | [5 empty] | 97.1308
08.12.2007 09:00 | 3600 | 2 | 758.95 | GGB | 765.201 | 771.914 | 768.498 | 257.6 | GGB | 10783.5 | GGB | 9.86 | GGB | 995.59 | GGB | 59.22 | GGB | 166773.79 | GGB | 134690.45 | GGB | 0 | 0 | 2590 | 3600 | 2574.26 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 85820.87 | GGB | 85821.87 | 2574.26 | 2574.26 |  |  |  | 1 | 1 |  |  |  |  | 134690.45 | 2574.26 | 134690.45 | 2574.26 | 8.934 | [5 empty] | 96.3134
08.12.2007 10:00 | 3600 | 2 | 758.34 | GGB | 766.3 | 772.969 | 768.498 | 258.17 | GGB | 10803.9 | GGB | 9.85 | GGB | 996.52 | GGB | 59.35 | GGB | 167118.2 | GGB | 135043.05 | GGB | 0 | 0 | 2628 | 3600 | 2612.6 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 85860.37 | GGB | 85861.37 | 2612.6 | 2612.6 |  |  |  | 1 | 1 |  |  |  |  | 135043.05 | 2612.6 | 135043.05 | 2612.6 | 8.932 | [5 empty] | 98.0037
08.12.2007 11:00 | 3600 | 2 | 758.45 | GGB | 766.3 | 772.969 | 768.498 | 258.58 | GGB | 10827.1 | GGB | 9.85 | GGB | 997.21 | GGB | 59.2 | GGB | 167570.44 | GGB | 135560.53 | GGB | 0 | 0 | 2635 | 3600 | 2619.18 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 85899.8 | GGB | 85900.8 | 2619.18 | 2619.18 |  |  |  | 1 | 1 |  |  |  |  | 135560.53 | 2619.18 | 135560.53 | 2619.18 | 9.0048 | [5 empty] | 98.6271
08.12.2007 12:00 | 3600 | 2 | 758.44 | GGB | 766.3 | 772.969 | 768.498 | 258.62 | GGB | 10840.7 | GGB | 9.86 | GGB | 997.99 | GGB | 58.98 | GGB | 167821.31 | GGB | 135960.13 | GGB | 0 | 0 | 2638 | 3600 | 2622.77 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 85938.97 | GGB | 85939.97 | 2622.77 | 2622.77 |  |  |  | 1 | 1 |  |  |  |  | 135960.13 | 2622.77 | 135960.13 | 2622.77 | 9.1037 | [5 empty] | 99.0534
08.12.2007 13:00 | 3600 | 2 | 758.51 | GGB | 766.667 | 772.875 | 768.498 | 258.58 | GGB | 10834.3 | GGB | 9.85 | GGB | 998.46 | GGB | 58.99 | GGB | 167729.99 | GGB | 135946.02 | GGB | 0 | 0 | 2631 | 3600 | 2615.59 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 85978.98 | GGB | 85979.98 | 2615.59 | 2615.59 |  |  |  | 1 | 1 |  |  |  |  | 135946.02 | 2615.59 | 135946.02 | 2615.59 | 8.8873 | [5 empty] | 98.772
08.12.2007 14:00 | 3600 | 2 | 758.76 | GGB | 766.667 | 772.641 | 768.498 | 258.67 | GGB | 10844.2 | GGB | 9.86 | GGB | 998.24 | GGB | 58.9 | GGB | 168003.97 | GGB | 136174.04 | GGB | 0 | 0 | 2629 | 3600 | 2613.43 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 86018 | GGB | 86019 | 2613.43 | 2613.43 |  |  |  | 1 | 1 |  |  |  |  | 136174.04 | 2613.43 | 136174.04 | 2613.43 | 9.1205 | [5 empty] | 98.8559
08.12.2007 15:00 | 3600 | 2 | 758.61 | GGB | 766.667 | 772.828 | 769.597 | 259.93 | GGB | 10829.7 | GGB | 9.85 | GGB | 998.81 | GGB | 58.22 | GGB | 169692.99 | GGB | 137907.59 | GGB | 0 | 0 | 2626 | 3600 | 2610.26 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 86058.09 | GGB | 86059.09 | 2610.26 | 2610.26 |  |  |  | 1 | 1 |  |  |  |  | 137907.59 | 2610.26 | 137907.59 | 2610.26 | 8.9792 | [5 empty] | 99.993
08.12.2007 16:00 | 3600 | 2 | 758.84 | GGB | 767.766 | 773.484 | 769.597 | 259.8 | GGB | 10844.3 | GGB | 9.86 | GGB | 999.17 | GGB | 57.73 | GGB | 169926.26 | GGB | 138351.84 | GGB | 0 | 0 | 2617 | 3600 | 2601.93 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 86097.45 | GGB | 86098.45 | 2601.93 | 2601.93 |  |  |  | 1 | 1 |  |  |  |  | 138351.84 | 2601.93 | 138351.84 | 2601.93 | 9.1459 | [5 empty] | 99.9949
08.12.2007 17:00 | 3600 | 2 | 758.03 | GGB | 765.201 | 771.234 | 768.132 | 259.32 | GGB | 10875.3 | GGB | 9.85 | GGB | 1000.15 | GGB | 58.15 | GGB | 168777.51 | GGB | 137373.48 | GGB | 0 | 0 | 2679 | 3600 | 2663.13 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 86137.13 | GGB | 86138.13 | 2663.13 | 2663.13 |  |  |  | 1 | 1 |  |  |  |  | 137373.48 | 2663.13 | 137373.48 | 2663.13 | 9.2198 | [5 empty] | 101.6232
08.12.2007 18:00 | 3600 | 2 | 758.22 | GGB | 767.766 | 773.344 | 769.597 | 259.62 | GGB | 10897.3 | GGB | 9.86 | GGB | 1000.75 | GGB | 58.2 | GGB | 169088.9 | GGB | 137688.08 | GGB | 0 | 0 | 2680 | 3600 | 2664.43 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 86177.59 | GGB | 86178.59 | 2664.43 | 2664.43 |  |  |  | 1 | 1 |  |  |  |  | 137688.08 | 2664.43 | 137688.08 | 2664.43 | 9.0672 | [5 empty] | 101.9056
08.12.2007 19:00 | 3600 | 2 | 758.13 | GGB | 767.766 | 773.227 | 768.864 | 260.36 | GGB | 10869.4 | GGB | 9.85 | GGB | 1001.07 | GGB | 58.04 | GGB | 169902.05 | GGB | 138464.31 | GGB | 0 | 0 | 2666 | 3600 | 2650.61 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 86217.12 | GGB | 86218.13 | 2650.61 | 2650.61 |  |  |  | 1 | 1 |  |  |  |  | 138464.31 | 2650.61 | 138464.31 | 2650.61 | 9.2821 | [5 empty] | 101.9486
08.12.2007 20:00 | 3600 | 2 | 758.74 | GGB | 766.3 | 772.242 | 768.864 | 260.92 | GGB | 10866.7 | GGB | 9.86 | GGB | 1001.35 | GGB | 57.73 | GGB | 170657.98 | GGB | 139250.05 | GGB | 0 | 0 | 2639 | 3600 | 2623.76 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 86256.67 | GGB | 86257.68 | 2623.76 | 2623.76 |  |  |  | 1 | 1 |  |  |  |  | 139250.05 | 2623.76 | 139250.05 | 2623.76 | 9.2379 | [5 empty] | 101.4885
08.12.2007 21:00 | 3600 | 2 | 758.54 | GGB | 766.3 | 772.172 | 768.864 | 259.5 | GGB | 10891.7 | GGB | 9.86 | GGB | 1001.13 | GGB | 58.32 | GGB | 168928.25 | GGB | 137562.09 | GGB | 0 | 0 | 2667 | 3600 | 2651.14 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 86296.75 | GGB | 86297.76 | 2651.14 | 2651.14 |  |  |  | 1 | 1 |  |  |  |  | 137562.09 | 2651.14 | 137562.09 | 2651.14 | 9.0992 | [5 empty] | 101.3045
08.12.2007 22:00 | 3600 | 2 | 758.32 | GGB | 766.3 | 772.289 | 768.864 | 259.81 | GGB | 10891.8 | GGB | 9.85 | GGB | 1001.67 | GGB | 58.37 | GGB | 169084.5 | GGB | 137743.35 | GGB | 0 | 0 | 2674 | 3600 | 2658.47 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 86336.09 | GGB | 86337.1 | 2658.47 | 2658.47 |  |  |  | 1 | 1 |  |  |  |  | 137743.35 | 2658.47 | 137743.35 | 2658.47 | 9.3083 | [5 empty] | 101.7185
08.12.2007 23:00 | 3600 | 2 | 758.33 | GGB | 766.3 | 772.289 | 768.864 | 259.28 | GGB | 10895.9 | GGB | 9.86 | GGB | 1002.23 | GGB | 58.33 | GGB | 168955.76 | GGB | 137731.67 | GGB | 0 | 0 | 2671 | 3600 | 2655.82 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 86376.16 | GGB | 86377.17 | 2655.82 | 2655.82 |  |  |  | 1 | 1 |  |  |  |  | 137731.67 | 2655.82 | 137731.67 | 2655.82 | 9.1288 | [5 empty] | 101.6085
08.12.2007 24:00 | 3600 | 2 | 758.19 | GGB | 766.3 | 772.43 | 767.766 | 260.13 | GGB | 10903.3 | GGB | 9.85 | GGB | 1002.69 | GGB | 58.32 | GGB | 169325.47 | GGB | 138101.01 | GGB | 0 | 0 | 2691 | 3600 | 2675.65 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 86415.73 | GGB | 86416.74 | 2675.65 | 2675.65 |  |  |  | 1 | 1 |  |  |  |  | 138101.01 | 2675.65 | 138101.01 | 2675.65 | 9.3381 | [5 empty] | 102.6417
09.12.2007 01:00 | 3600 | 2 | 757.91 | GGB | 765.201 | 771.375 | 767.766 | 261.82 | GGB | 10925.6 | GGB | 9.85 | GGB | 1002.79 | GGB | 58.32 | GGB | 170909.96 | GGB | 139404.53 | GGB | 0 | 0 | 2715 | 3600 | 2699.86 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 86455.87 | GGB | 86456.89 | 2699.86 | 2699.86 |  |  |  | 1 | 1 |  |  |  |  | 139404.53 | 2699.86 | 139404.53 | 2699.86 | 9.3742 | [5 empty] | 104.548
09.12.2007 02:00 | 3600 | 2 | 757.9 | GGB | 766.3 | 771.586 | 767.766 | 262.88 | GGB | 10978.4 | GGB | 9.85 | GGB | 1002.89 | GGB | 57.93 | GGB | 172102.73 | GGB | 140557.5 | GGB | 0 | 0 | 2748 | 3600 | 2732.24 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 86495.92 | GGB | 86496.93 | 2732.24 | 2732.24 |  |  |  | 1 | 1 |  |  |  |  | 140557.5 | 2732.24 | 140557.5 | 2732.24 | 9.5913 | [5 empty] | 106.6769 | 2688.7786
09.12.2007 03:00 | 3600 | 2 | 757.65 | GGB | 765.201 | 771.586 | 767.766 | 263.11 | GGB | 11016 | GGB | 9.85 | GGB | 1003.06 | GGB | 57.84 | GGB | 172361.31 | GGB | 140831.9 | GGB | 0 | 0 | 2774 | 3600 | 2758.84 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 86535.84 | GGB | 86536.85 | 2758.84 | 2758.84 |  |  |  | 1 | 1 |  |  |  |  | 140831.9 | 2758.84 | 140831.9 | 2758.84 | 9.7328 | [5 empty] | 107.9257 | 2683.5397
09.12.2007 04:00 | 3600 | 2 | 757.79 | GGB | 766.3 | 771.516 | 767.766 | 263.77 | GGB | 10997.8 | GGB | 9.85 | GGB | 1003.29 | GGB | 57.6 | GGB | 173324.1 | GGB | 141753.47 | GGB | 0 | 0 | 2765 | 3600 | 2749.13 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 86576.73 | GGB | 86577.74 | 2749.13 | 2749.13 |  |  |  | 1 | 1 |  |  |  |  | 141753.47 | 2749.13 | 141753.47 | 2749.13 | 9.5304 | [5 empty] | 108.2496 | 2666.0935
09.12.2007 05:00 | 3600 | 2 | 758.44 | GGB | 766.3 | 771.469 | 767.766 | 263.31 | GGB | 11003.5 | GGB | 9.87 | GGB | 1003.47 | GGB | 57.81 | GGB | 172868.56 | GGB | 141318.21 | GGB | 0 | 0 | 2730 | 3600 | 2715.05 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 86615.73 | GGB | 86616.74 | 2715.05 | 2715.05 |  |  |  | 1 | 1 |  |  |  |  | 141318.21 | 2715.05 | 141318.21 | 2715.05 | 9.8381 | [5 empty] | 106.5794 | 2674.305
09.12.2007 06:00 | 3600 | 2 | 757.93 | GGB | 765.201 | 771.609 | 767.766 | 262.39 | GGB | 10996.4 | GGB | 9.86 | GGB | 1003.33 | GGB | 58.02 | GGB | 171594.37 | GGB | 140165.93 | GGB | 0 | 0 | 2753 | 3600 | 2737.54 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 86656.88 | GGB | 86657.89 | 2737.54 | 2737.54 |  |  |  | 1 | 1 |  |  |  |  | 140165.93 | 2737.54 | 140165.93 | 2737.54 | 9.3247 | [5 empty] | 106.5861 | 2696.29
09.12.2007 07:00 | 3600 | 2 | 757.86 | GGB | 766.3 | 772.664 | 767.766 | 262.28 | GGB | 11002.6 | GGB | 9.86 | GGB | 1003.07 | GGB | 58.04 | GGB | 171801.23 | GGB | 140293.69 | GGB | 0 | 0 | 2753 | 3600 | 2737.33 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 86696.6 | GGB | 86697.62 | 2737.33 | 2737.33 |  |  |  | 1 | 1 |  |  |  |  | 140293.69 | 2737.33 | 140293.69 | 2737.33 | 9.666 | [5 empty] | 106.675 | 2693.8346
09.12.2007 08:00 | 3600 | 2 | 758 | GGB | 765.201 | 771.633 | 767.766 | 262.25 | GGB | 11001.4 | GGB | 9.85 | GGB | 1003.03 | GGB | 57.91 | GGB | 171888.16 | GGB | 140413.96 | GGB | 0 | 0 | 2754 | 3600 | 2738.1 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 86736.87 | GGB | 86737.89 | 2738.1 | 2738.1 |  |  |  | 1 | 1 |  |  |  |  | 140413.96 | 2738.1 | 140413.96 | 2738.1 | 9.5472 | [5 empty] | 106.7965 | 2691.5273
09.12.2007 09:00 | 3600 | 2 | 757.86 | GGB | 765.201 | 771.633 | 767.766 | 262.35 | GGB | 11010.6 | GGB | 9.85 | GGB | 1003.25 | GGB | 57.77 | GGB | 172148.94 | GGB | 140716.53 | GGB | 0 | 0 | 2766 | 3600 | 2750.66 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 86777.02 | GGB | 86778.04 | 2750.66 | 2750.66 |  |  |  | 1 | 1 |  |  |  |  | 140716.53 | 2750.66 | 140716.53 | 2750.66 | 9.6404 | [5 empty] | 107.5176 | 2685.7399
09.12.2007 10:00 | 3600 | 2 | 757.78 | GGB | 765.201 | 771.656 | 767.766 | 262.35 | GGB | 10996.2 | GGB | 9.85 | GGB | 1003.51 | GGB | 57.56 | GGB | 172424.03 | GGB | 141066.01 | GGB | 0 | 0 | 2757 | 3600 | 2741.41 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 86817.64 | GGB | 86818.66 | 2741.41 | 2741.41 |  |  |  | 1 | 1 |  |  |  |  | 141066.01 | 2741.41 | 141066.01 | 2741.41 | 9.5204 | [5 empty] | 107.4222 | 2679.0862
09.12.2007 11:00 | 3600 | 2 | 758.16 | GGB | 766.3 | 772.758 | 768.864 | 263.48 | GGB | 10970.7 | GGB | 9.86 | GGB | 1003.78 | GGB | 56.79 | GGB | 174104.24 | GGB | 142813.4 | GGB | 0 | 0 | 2722 | 3600 | 2706.46 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 86857.4 | GGB | 86858.42 | 2706.46 | 2706.46 |  |  |  | 1 | 1 |  |  |  |  | 142813.4 | 2706.46 | 142813.4 | 2706.46 | 9.7213 | [5 empty] | 107.3663 | 2646.3063
09.12.2007 12:00 | 3600 | 2 | 758.51 | GGB | 766.3 | 772.758 | 768.864 | 261.66 | GGB | 10976.5 | GGB | 9.87 | GGB | 1003.52 | GGB | 57.45 | GGB | 171607.58 | GGB | 140445.72 | GGB | 0 | 0 | 2713 | 3600 | 2697.31 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 86897.41 | GGB | 86898.42 | 2697.31 | 2697.31 |  |  |  | 1 | 1 |  |  |  |  | 140445.72 | 2697.31 | 140445.72 | 2697.31 | 9.4706 | [5 empty] | 105.2293 | 2690.9186
09.12.2007 13:00 | 3600 | 2 | 758.42 | GGB | 765.201 | 771.703 | 767.766 | 260.47 | GGB | 10937.2 | GGB | 9.86 | GGB | 1003.13 | GGB | 58.05 | GGB | 170029.69 | GGB | 138849.03 | GGB | 0 | 0 | 2699 | 3600 | 2683.75 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 86937.63 | GGB | 86938.65 | 2683.75 | 2683.75 |  |  |  | 1 | 1 |  |  |  |  | 138849.03 | 2683.75 | 138849.03 | 2683.75 | 9.2626 | [5 empty] | 103.51
09.12.2007 14:00 | 3600 | 2 | 758.42 | GGB | 766.667 | 772.875 | 768.864 | 260.11 | GGB | 10915.9 | GGB | 9.86 | GGB | 1002.67 | GGB | 58.16 | GGB | 169623.67 | GGB | 138405.5 | GGB | 0 | 0 | 2685 | 3600 | 2669.5 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 86977.33 | GGB | 86978.34 | 2669.5 | 2669.5 |  |  |  | 1 | 1 |  |  |  |  | 138405.5 | 2669.5 | 138405.5 | 2669.5 | 9.309 | [5 empty] | 102.6315
09.12.2007 15:00 | 3600 | 2 | 758.33 | GGB | 766.3 | 773.016 | 768.864 | 260.25 | GGB | 10914.8 | GGB | 9.85 | GGB | 1002.15 | GGB | 58.14 | GGB | 169617.06 | GGB | 138339.06 | GGB | 0 | 0 | 2690 | 3600 | 2674.37 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 87017.32 | GGB | 87018.33 | 2674.37 | 2674.37 |  |  |  | 1 | 1 |  |  |  |  | 138339.06 | 2674.37 | 138339.06 | 2674.37 | 9.2516 | [5 empty] | 102.7694
09.12.2007 16:00 | 3600 | 2 | 757.83 | GGB | 765.201 | 772.734 | 767.766 | 262.13 | GGB | 10905 | GGB | 9.84 | GGB | 1002.24 | GGB | 57.39 | GGB | 171848.55 | GGB | 140489.72 | GGB | 0 | 0 | 2712 | 3600 | 2696.27 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 87057.64 | GGB | 87058.65 | 2696.27 | 2696.27 |  |  |  | 1 | 1 |  |  |  |  | 140489.72 | 2696.27 | 140489.72 | 2696.27 | 9.3948 | [5 empty] | 105.2217 | 2690.0758
09.12.2007 17:00 | 3600 | 2 | 758.58 | GGB | 765.201 | 771.609 | 767.033 | 261.83 | GGB | 10947.2 | GGB | 9.86 | GGB | 1002.29 | GGB | 57.42 | GGB | 171448.03 | GGB | 140156.94 | GGB | 0 | 0 | 2700 | 3600 | 2685.02 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 87096.85 | GGB | 87097.86 | 2685.02 | 2685.02 |  |  |  | 1 | 1 |  |  |  |  | 140156.94 | 2685.02 | 140156.94 | 2685.02 | 9.5977 | [5 empty] | 104.5345
09.12.2007 18:00 | 3600 | 2 | 757.94 | GGB | 765.201 | 772.922 | 768.498 | 261.37 | GGB | 10964.7 | GGB | 9.85 | GGB | 1002.13 | GGB | 57.6 | GGB | 170940.77 | GGB | 139642.74 | GGB | 0 | 0 | 2736 | 3600 | 2720.68 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 87137.52 | GGB | 87138.54 | 2720.68 | 2720.68 |  |  |  | 1 | 1 |  |  |  |  | 139642.74 | 2720.68 | 139642.74 | 2720.68 | 9.3393 | [5 empty] | 105.5342 | 2706.392
09.12.2007 19:00 | 3600 | 2 | 758.21 | GGB | 766.3 | 772.898 | 768.132 | 261.19 | GGB | 10965.3 | GGB | 9.86 | GGB | 1001.56 | GGB | 57.67 | GGB | 170743.81 | GGB | 139371.54 | GGB | 0 | 0 | 2730 | 3600 | 2714.28 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 87177.33 | GGB | 87178.35 | 2714.28 | 2714.28 |  |  |  | 1 | 1 |  |  |  |  | 139371.54 | 2714.28 | 139371.54 | 2714.28 | 9.5025 | [5 empty] | 105.0815 | 2711.6583
09.12.2007 20:00 | 3600 | 2 | 758.07 | GGB | 766.3 | 772.945 | 768.498 | 260.73 | GGB | 10942.9 | GGB | 9.86 | GGB | 1001.72 | GGB | 57.76 | GGB | 169980.18 | GGB | 138733.21 | GGB | 0 | 0 | 2720 | 3600 | 2705.04 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 87217.54 | GGB | 87218.56 | 2705.04 | 2705.04 |  |  |  | 1 | 1 |  |  |  |  | 138733.21 | 2705.04 | 138733.21 | 2705.04 | 9.333 | [5 empty] | 104.2441
09.12.2007 21:00 | 3600 | 2 | 758.21 | GGB | 766.3 | 772.922 | 768.132 | 260.63 | GGB | 10932.3 | GGB | 9.86 | GGB | 1001.73 | GGB | 58 | GGB | 169620.37 | GGB | 138342.24 | GGB | 0 | 0 | 2716 | 3600 | 2700.42 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 87257.5 | GGB | 87258.52 | 2700.42 | 2700.42 |  |  |  | 1 | 1 |  |  |  |  | 138342.24 | 2700.42 | 138342.24 | 2700.42 | 9.3489 | [5 empty] | 103.7728
09.12.2007 22:00 | 3600 | 2 | 758.18 | GGB | 765.201 | 771.68 | 767.033 | 259.94 | GGB | 10937.6 | GGB | 9.86 | GGB | 1001.49 | GGB | 58.15 | GGB | 169999.98 | GGB | 138555.81 | GGB | 0 | 0 | 2714 | 3600 | 2698.25 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 87296.29 | GGB | 87297.31 | 2698.25 | 2698.25 |  |  |  | 1 | 1 |  |  |  |  | 138555.81 | 2698.25 | 138555.81 | 2698.25 | 9.638 | [5 empty] | 103.8495
09.12.2007 23:00 | 3600 | 2 | 757.88 | GGB | 766.3 | 772.758 | 768.498 | 261.92 | GGB | 10893.3 | GGB | 9.85 | GGB | 1001.62 | GGB | 57.47 | GGB | 171585.57 | GGB | 140154.46 | GGB | 0 | 0 | 2716 | 3600 | 2700.58 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 87336.88 | GGB | 87337.91 | 2700.58 | 2700.58 |  |  |  | 1 | 1 |  |  |  |  | 140154.46 | 2700.58 | 140154.46 | 2700.58 | 9.3226 | [5 empty] | 105.1384 | 2696.5107
09.12.2007 24:00 | 3600 | 2 | 758.55 | GGB | 765.201 | 772.758 | 768.498 | 260.87 | GGB | 10929 | GGB | 9.86 | GGB | 1001.37 | GGB | 57.82 | GGB | 170419.21 | GGB | 139019.71 | GGB | 0 | 0 | 2700 | 3600 | 2684.82 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 87375.98 | GGB | 87377.01 | 2684.82 | 2684.82 |  |  |  | 1 | 1 |  |  |  |  | 139019.71 | 2684.82 | 139019.71 | 2684.82 | 9.5459 | [5 empty] | 103.6786
10.12.2007 01:00 | 3600 | 2 | 758.17 | GGB | 766.3 | 772.828 | 768.498 | 260.58 | GGB | 10930.8 | GGB | 9.85 | GGB | 1001.62 | GGB | 58.12 | GGB | 169712.79 | GGB | 138353.31 | GGB | 0 | 0 | 2720 | 3600 | 2704.56 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 87417.26 | GGB | 87418.29 | 2704.56 | 2704.56 |  |  |  | 1 | 1 |  |  |  |  | 138353.31 | 2704.56 | 138353.31 | 2704.56 | 9.0646 | [5 empty] | 103.9402
10.12.2007 02:00 | 3600 | 2 | 758.08 | GGB | 765.201 | 772.805 | 768.132 | 260.82 | GGB | 10925 | GGB | 9.85 | GGB | 1001.94 | GGB | 58.12 | GGB | 169917.46 | GGB | 138564.35 | GGB | 0 | 0 | 2717 | 3600 | 2701.39 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 87456.34 | GGB | 87457.37 | 2701.39 | 2701.39 |  |  |  | 1 | 1 |  |  |  |  | 138564.35 | 2701.39 | 138564.35 | 2701.39 | 9.5782 | [5 empty] | 103.9768
10.12.2007 03:00 | 3600 | 2 | 757.94 | GGB | 766.3 | 771.867 | 768.132 | 261.71 | GGB | 10921.1 | GGB | 9.85 | GGB | 1002.22 | GGB | 58.06 | GGB | 170951.77 | GGB | 139470.19 | GGB | 0 | 0 | 2725 | 3600 | 2709.79 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 87496.7 | GGB | 87497.73 | 2709.79 | 2709.79 |  |  |  | 1 | 1 |  |  |  |  | 139470.19 | 2709.79 | 139470.19 | 2709.79 | 9.3641 | [5 empty] | 104.9819 | 2709.7403
10.12.2007 04:00 | 3600 | 2 | 758.41 | GGB | 766.3 | 772.898 | 768.498 | 262.84 | GGB | 10915.6 | GGB | 9.86 | GGB | 1002.19 | GGB | 57.58 | GGB | 172462.54 | GGB | 140903.59 | GGB | 0 | 0 | 2699 | 3600 | 2683.42 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 87536.12 | GGB | 87537.15 | 2683.42 | 2683.42 |  |  |  | 1 | 1 |  |  |  |  | 140903.59 | 2683.42 | 140903.59 | 2683.42 | 9.5917 | [5 empty] | 105.0288 | 2682.1744
10.12.2007 05:00 | 3600 | 2 | 758.52 | GGB | 767.766 | 772.828 | 768.498 | 261.22 | GGB | 10941.9 | GGB | 9.86 | GGB | 1002.23 | GGB | 58.08 | GGB | 170440.12 | GGB | 139046.27 | GGB | 0 | 0 | 2711 | 3600 | 2695.27 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 87576.36 | GGB | 87577.39 | 2695.27 | 2695.27 |  |  |  | 1 | 1 |  |  |  |  | 139046.27 | 2695.27 | 139046.27 | 2695.27 | 9.3133 | [5 empty] | 104.102
10.12.2007 06:00 | 3600 | 2 | 758.28 | GGB | 765.201 | 771.656 | 768.498 | 261.02 | GGB | 10931.3 | GGB | 9.86 | GGB | 1002.28 | GGB | 58.21 | GGB | 170105.61 | GGB | 138726.41 | GGB | 0 | 0 | 2711 | 3600 | 2695.45 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 87615.98 | GGB | 87617.01 | 2695.45 | 2695.45 |  |  |  | 1 | 1 |  |  |  |  | 138726.41 | 2695.45 | 138726.41 | 2695.45 | 9.4379 | [5 empty] | 103.8695
10.12.2007 07:00 | 3600 | 2 | 758.45 | GGB | 766.667 | 772.758 | 768.498 | 262.59 | GGB | 10900.4 | GGB | 9.85 | GGB | 1002.58 | GGB | 57.76 | GGB | 172129.14 | GGB | 140610.29 | GGB | 0 | 0 | 2695 | 3600 | 2679.69 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 87656.13 | GGB | 87657.16 | 2679.69 | 2679.69 |  |  |  | 1 | 1 |  |  |  |  | 140610.29 | 2679.69 | 140610.29 | 2679.69 | 9.3846 | [5 empty] | 104.6644
10.12.2007 08:00 | 3600 | 2 | 758.81 | GGB | 766.3 | 771.727 | 768.132 | 261.34 | GGB | 10925.5 | GGB | 9.86 | GGB | 1002.65 | GGB | 58.17 | GGB | 170660.18 | GGB | 139245.74 | GGB | 0 | 0 | 2685 | 3600 | 2669.9 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 87695.56 | GGB | 87696.59 | 2669.9 | 2669.9 |  |  |  | 1 | 1 |  |  |  |  | 139245.74 | 2669.9 | 139245.74 | 2669.9 | 9.4287 | [5 empty] | 103.2701
10.12.2007 09:00 | 3600 | 2 | 758.46 | GGB | 766.3 | 772.734 | 768.498 | 260.51 | GGB | 10925.5 | GGB | 9.86 | GGB | 1003.07 | GGB | 58.41 | GGB | 169597.26 | GGB | 138338.8 | GGB | 0 | 0 | 2705 | 3600 | 2689.99 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 87735.82 | GGB | 87736.85 | 2689.99 | 2689.99 |  |  |  | 1 | 1 |  |  |  |  | 138338.8 | 2689.99 | 138338.8 | 2689.99 | 9.2432 | [5 empty] | 103.3694
10.12.2007 10:00 | 3600 | 2 | 758.44 | GGB | 766.667 | 773.93 | 768.498 | 261.59 | GGB | 10901.8 | GGB | 9.85 | GGB | 1003.65 | GGB | 58.2 | GGB | 170896.76 | GGB | 139566.83 | GGB | 0 | 0 | 2698 | 3600 | 2683.03 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 87776.01 | GGB | 87777.04 | 2683.03 | 2683.03 |  |  |  | 1 | 1 |  |  |  |  | 139566.83 | 2683.03 | 139566.83 | 2683.03 | 9.3173 | [5 empty] | 104.0172
10.12.2007 11:00 | 3600 | 2 | 758.79 | GGB | 767.766 | 773.742 | 768.864 | 262.31 | GGB | 10898.2 | GGB | 9.86 | GGB | 1004.56 | GGB | 57.82 | GGB | 171596.57 | GGB | 140424.44 | GGB | 0 | 0 | 2673 | 3600 | 2657.97 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 87815.69 | GGB | 87816.72 | 2657.97 | 2657.97 |  |  |  | 1 | 1 |  |  |  |  | 140424.44 | 2657.97 | 140424.44 | 2657.97 | 9.4063 | [5 empty] | 103.6789
10.12.2007 12:00 | 3600 | 2 | 759.01 | GGB | 766.667 | 772.805 | 768.498 | 260.42 | GGB | 10924.5 | GGB | 9.86 | GGB | 1004.65 | GGB | 58.57 | GGB | 169196.74 | GGB | 138160.51 | GGB | 0 | 0 | 2684 | 3600 | 2668.47 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 87855.42 | GGB | 87856.45 | 2668.47 | 2668.47 |  |  |  | 1 | 1 |  |  |  |  | 138160.51 | 2668.47 | 138160.51 | 2668.47 | 9.2796 | [5 empty] | 102.4103
10.12.2007 13:00 | 3600 | 2 | 758.65 | GGB | 766.667 | 772.875 | 768.498 | 261.79 | GGB | 10876.9 | GGB | 9.85 | GGB | 1005.16 | GGB | 58.11 | GGB | 171145.43 | GGB | 140020.01 | GGB | 0 | 0 | 2669 | 3600 | 2653.97 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 87895.46 | GGB | 87896.49 | 2653.97 | 2653.97 |  |  |  | 1 | 1 |  |  |  |  | 140020.01 | 2653.97 | 140020.01 | 2653.97 | 9.2809 | [5 empty] | 103.2247
10.12.2007 14:00 | 3600 | 2 | 759.02 | GGB | 766.667 | 772.758 | 767.033 | 260.66 | GGB | 10901.6 | GGB | 9.86 | GGB | 1005.2 | GGB | 58.61 | GGB | 169409.1 | GGB | 138394.78 | GGB | 0 | 0 | 2669 | 3600 | 2653.74 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 87934.77 | GGB | 87935.8 | 2653.74 | 2653.74 |  |  |  | 1 | 1 |  |  |  |  | 138394.78 | 2653.74 | 138394.78 | 2653.74 | 9.3428 | [5 empty] | 102.0177
10.12.2007 15:00 | 3600 | 2 | 759.31 | GGB | 767.766 | 774.867 | 769.597 | 261.08 | GGB | 10882.7 | GGB | 9.86 | GGB | 1005.43 | GGB | 58.31 | GGB | 170074.8 | GGB | 139093.24 | GGB | 0 | 0 | 2651 | 3600 | 2635.33 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 87974.72 | GGB | 87975.75 | 2635.33 | 2635.33 |  |  |  | 1 | 1 |  |  |  |  | 139093.24 | 2635.33 | 139093.24 | 2635.33 | 9.1754 | [5 empty] | 101.8213
10.12.2007 16:00 | 3600 | 2 | 758.85 | GGB | 766.667 | 772.688 | 768.498 | 260.27 | GGB | 10879.1 | GGB | 9.85 | GGB | 1005.33 | GGB | 59.03 | GGB | 168594.85 | GGB | 137573.33 | GGB | 0 | 0 | 2671 | 3600 | 2656.02 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 88014.59 | GGB | 88015.62 | 2656.02 | 2656.02 |  |  |  | 1 | 1 |  |  |  |  | 137573.33 | 2656.02 | 137573.33 | 2656.02 | 9.1647 | [5 empty] | 101.4993
10.12.2007 17:00 | 3600 | 2 | 759.15 | GGB | 766.667 | 773.766 | 769.597 | 261.56 | GGB | 10853.6 | GGB | 9.85 | GGB | 1006.24 | GGB | 58.52 | GGB | 170183.74 | GGB | 139208.25 | GGB | 0 | 0 | 2642 | 3600 | 2626.9 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 88054.47 | GGB | 88055.5 | 2626.9 | 2626.9 |  |  |  | 1 | 1 |  |  |  |  | 139208.25 | 2626.9 | 139208.25 | 2626.9 | 9.1697 | [5 empty] | 101.5795
10.12.2007 18:00 | 3600 | 2 | 759.47 | GGB | 766.667 | 773.766 | 768.498 | 260.83 | GGB | 10879 | GGB | 9.86 | GGB | 1006.37 | GGB | 58.86 | GGB | 169016.28 | GGB | 138129.19 | GGB | 0 | 0 | 2646 | 3600 | 2630.84 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 88093.75 | GGB | 88094.78 | 2630.84 | 2630.84 |  |  |  | 1 | 1 |  |  |  |  | 138129.19 | 2630.84 | 138129.19 | 2630.84 | 9.2514 | [5 empty] | 100.9433
10.12.2007 19:00 | 3600 | 2 | 758.67 | GGB | 766.667 | 773.672 | 768.132 | 260.38 | GGB | 10882.5 | GGB | 9.85 | GGB | 1005.77 | GGB | 59.25 | GGB | 168046.88 | GGB | 137093.46 | GGB | 0 | 0 | 2697 | 3600 | 2681.62 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 88134.09 | GGB | 88135.12 | 2681.62 | 2681.62 |  |  |  | 1 | 1 |  |  |  |  | 137093.46 | 2681.62 | 137093.46 | 2681.62 | 9.1134 | [5 empty] | 102.1202
10.12.2007 20:00 | 3600 | 2 | 759.19 | GGB | 766.667 | 772.664 | 768.498 | 260.24 | GGB | 10870.6 | GGB | 9.86 | GGB | 1005.96 | GGB | 59.45 | GGB | 167419.69 | GGB | 136524.09 | GGB | 0 | 0 | 2683 | 3600 | 2668.1 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 88172.93 | GGB | 88173.96 | 2668.1 | 2668.1 |  |  |  | 1 | 1 |  |  |  |  | 136524.09 | 2668.1 | 136524.09 | 2668.1 | 9.3785 | [5 empty] | 101.1833
10.12.2007 21:00 | 3600 | 2 | 759.06 | GGB | 767.766 | 773.93 | 769.597 | 259.97 | GGB | 10857.1 | GGB | 9.86 | GGB | 1006.03 | GGB | 59.68 | GGB | 167009.26 | GGB | 136104.41 | GGB | 0 | 0 | 2677 | 3600 | 2661.36 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 88213.36 | GGB | 88214.4 | 2661.36 | 2661.36 |  |  |  | 1 | 1 |  |  |  |  | 136104.41 | 2661.36 | 136104.41 | 2661.36 | 8.957 | [5 empty] | 100.6175
10.12.2007 22:00 | 3600 | 2 | 759.03 | GGB | 766.667 | 772.852 | 768.864 | 260.1 | GGB | 10819.1 | GGB | 9.85 | GGB | 1006.82 | GGB | 59.77 | GGB | 167286.55 | GGB | 136401.87 | GGB | 0 | 0 | 2656 | 3600 | 2640.43 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 88251.98 | GGB | 88253.01 | 2640.43 | 2640.43 |  |  |  | 1 | 1 |  |  |  |  | 136401.87 | 2640.43 | 136401.87 | 2640.43 | 9.3281 | [5 empty] | 100.0443
10.12.2007 23:00 | 3600 | 2 | 759.23 | GGB | 767.766 | 773.93 | 769.963 | 260.09 | GGB | 10820.5 | GGB | 9.86 | GGB | 1007.23 | GGB | 59.22 | GGB | 168755.5 | GGB | 137885.21 | GGB | 0 | 0 | 2634 | 3600 | 2618.8 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 88290.62 | GGB | 88291.65 | 2618.8 | 2618.8 |  |  |  | 1 | 1 |  |  |  |  | 137885.21 | 2618.8 | 137885.21 | 2618.8 | 9.3451 | [5 empty] | 100.3038
10.12.2007 24:00 | 3600 | 2 | 759.35 | GGB | 766.667 | 773.906 | 768.864 | 259.37 | GGB | 10830.1 | GGB | 9.86 | GGB | 1007.87 | GGB | 60.02 | GGB | 166592.24 | GGB | 135876.06 | GGB | 0 | 0 | 2647 | 3600 | 2632.01 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 88331.37 | GGB | 88332.4 | 2632.01 | 2632.01 |  |  |  | 1 | 1 |  |  |  |  | 135876.06 | 2632.01 | 135876.06 | 2632.01 | 8.7761 | [5 empty] | 99.3409
11.12.2007 01:00 | 3600 | 2 | 759 | GGB | 767.766 | 773.93 | 769.963 | 260.96 | GGB | 10810 | GGB | 9.85 | GGB | 1008.12 | GGB | 59.68 | GGB | 168443 | GGB | 137558.62 | GGB | 0 | 0 | 2650 | 3600 | 2634.45 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 88370.71 | GGB | 88371.74 | 2634.45 | 2634.45 |  |  |  | 1 | 1 |  |  |  |  | 137558.62 | 2634.45 | 137558.62 | 2634.45 | 9.2118 | [5 empty] | 100.6643
11.12.2007 02:00 | 3600 | 2 | 759.32 | GGB | 766.667 | 773.719 | 768.864 | 259.85 | GGB | 10851 | GGB | 9.86 | GGB | 1008.39 | GGB | 59.58 | GGB | 166910.23 | GGB | 136384.74 | GGB | 0 | 0 | 2653 | 3600 | 2637.18 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 88410.49 | GGB | 88411.52 | 2637.18 | 2637.18 |  |  |  | 1 | 1 |  |  |  |  | 136384.74 | 2637.18 | 136384.74 | 2637.18 | 9.0415 | [5 empty] | 99.9086
11.12.2007 03:00 | 3600 | 2 | 758.86 | GGB | 767.766 | 773.742 | 769.963 | 261.51 | GGB | 10817.5 | GGB | 9.85 | GGB | 1009.28 | GGB | 59.32 | GGB | 168863.33 | GGB | 138209.55 | GGB | 0 | 0 | 2662 | 3600 | 2647.1 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 88450.68 | GGB | 88451.71 | 2647.1 | 2647.1 |  |  |  | 1 | 1 |  |  |  |  | 138209.55 | 2647.1 | 138209.55 | 2647.1 | 9.1031 | [5 empty] | 101.6262
11.12.2007 04:00 | 3600 | 2 | 759.46 | GGB | 766.667 | 772.664 | 768.864 | 261.04 | GGB | 10852.4 | GGB | 9.86 | GGB | 1009.65 | GGB | 59.51 | GGB | 168137.11 | GGB | 137587.83 | GGB | 0 | 0 | 2649 | 3600 | 2633.98 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 88488.99 | GGB | 88490.02 | 2633.98 | 2633.98 |  |  |  | 1 | 1 |  |  |  |  | 137587.83 | 2633.98 | 137587.83 | 2633.98 | 9.4598 | [5 empty] | 100.6677
11.12.2007 05:00 | 3600 | 2 | 759 | GGB | 766.667 | 773.719 | 768.864 | 260.58 | GGB | 10872.3 | GGB | 9.85 | GGB | 1009.91 | GGB | 59.8 | GGB | 167424.09 | GGB | 136922.89 | GGB | 0 | 0 | 2685 | 3600 | 2669.21 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 88529.89 | GGB | 88530.92 | 2669.21 | 2669.21 |  |  |  | 1 | 1 |  |  |  |  | 136922.89 | 2669.21 | 136922.89 | 2669.21 | 8.9358 | [5 empty] | 101.5211
11.12.2007 06:00 | 3600 | 2 | 758.83 | GGB | 766.667 | 772.617 | 767.766 | 262.6 | GGB | 10853.7 | GGB | 9.85 | GGB | 1010.48 | GGB | 59.12 | GGB | 170129.82 | GGB | 139497.55 | GGB | 0 | 0 | 2677 | 3600 | 2661.93 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 88568.52 | GGB | 88569.55 | 2661.93 | 2661.93 |  |  |  | 1 | 1 |  |  |  |  | 139497.55 | 2661.93 | 139497.55 | 2661.93 | 9.6125 | [5 empty] | 103.148
11.12.2007 07:00 | 3600 | 2 | 758.96 | GGB | 766.667 | 772.664 | 768.864 | 262.3 | GGB | 10900.8 | GGB | 9.86 | GGB | 1010.9 | GGB | 59.03 | GGB | 169691.89 | GGB | 139233.68 | GGB | 0 | 0 | 2692 | 3600 | 2676.34 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 88608.57 | GGB | 88609.6 | 2676.34 | 2676.34 |  |  |  | 1 | 1 |  |  |  |  | 139233.68 | 2676.34 | 139233.68 | 2676.34 | 9.3043 | [5 empty] | 103.5102
11.12.2007 08:00 | 3600 | 2 | 758.46 | GGB | 765.201 | 772.664 | 767.766 | 262.04 | GGB | 10923.2 | GGB | 9.85 | GGB | 1011.47 | GGB | 59.22 | GGB | 169256.15 | GGB | 138873.05 | GGB | 0 | 0 | 2727 | 3600 | 2711.23 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 88648.31 | GGB | 88649.34 | 2711.23 | 2711.23 |  |  |  | 1 | 1 |  |  |  |  | 138873.05 | 2711.23 | 138873.05 | 2711.23 | 9.4745 | [5 empty] | 104.588
11.12.2007 09:00 | 3600 | 2 | 758.58 | GGB | 766.667 | 772.664 | 768.864 | 262.56 | GGB | 10948.5 | GGB | 9.85 | GGB | 1012.48 | GGB | 59.13 | GGB | 169636.87 | GGB | 139365.34 | GGB | 0 | 0 | 2739 | 3600 | 2723.19 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 88688.01 | GGB | 88689.03 | 2723.19 | 2723.19 |  |  |  | 1 | 1 |  |  |  |  | 139365.34 | 2723.19 | 139365.34 | 2723.19 | 9.5621 | [5 empty] | 105.4218 | 2711.779
11.12.2007 10:00 | 3600 | 2 | 758.4 | GGB | 766.3 | 772.781 | 768.864 | 263.21 | GGB | 10968.6 | GGB | 9.85 | GGB | 1013.48 | GGB | 59.05 | GGB | 170439.02 | GGB | 140195.01 | GGB | 0 | 0 | 2751 | 3600 | 2735.39 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 88728.65 | GGB | 88729.68 | 2735.39 | 2735.39 |  |  |  | 1 | 1 |  |  |  |  | 140195.01 | 2735.39 | 140195.01 | 2735.39 | 9.4339 | [5 empty] | 106.5245 | 2695.7308
11.12.2007 11:00 | 3600 | 2 | 758.63 | GGB | 766.667 | 772.711 | 768.864 | 264.01 | GGB | 10999.2 | GGB | 9.85 | GGB | 1014.51 | GGB | 58.95 | GGB | 171361.1 | GGB | 141141.23 | GGB | 0 | 0 | 2755 | 3600 | 2739.69 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 88768.02 | GGB | 88769.04 | 2739.69 | 2739.69 |  |  |  | 1 | 1 |  |  |  |  | 141141.23 | 2739.69 | 141141.23 | 2739.69 | 9.8243 | [5 empty] | 107.412 | 2677.6584
11.12.2007 12:00 | 3600 | 2 | 758.8 | GGB | 767.766 | 773.836 | 768.864 | 265.12 | GGB | 10976.1 | GGB | 9.85 | GGB | 1014.9 | GGB | 58.16 | GGB | 173390.12 | GGB | 143208.93 | GGB | 0 | 0 | 2729 | 3600 | 2713.8 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 88808.8 | GGB | 88809.83 | 2713.8 | 2713.8 |  |  |  | 1 | 1 |  |  |  |  | 143208.93 | 2713.8 | 143208.93 | 2713.8 | 9.5278 | [5 empty] | 107.9557 | 2638.9974
11.12.2007 13:00 | 3600 | 2 | 758.96 | GGB | 766.667 | 773.883 | 768.864 | 265.16 | GGB | 10992.8 | GGB | 9.86 | GGB | 1015.05 | GGB | 57.95 | GGB | 173646.5 | GGB | 143529.64 | GGB | 0 | 0 | 2720 | 3600 | 2704.81 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 88848.61 | GGB | 88849.64 | 2704.81 | 2704.81 |  |  |  | 1 | 1 |  |  |  |  | 143529.64 | 2704.81 | 143529.64 | 2704.81 | 9.7518 | [5 empty] | 107.839 | 2633.1007
11.12.2007 14:00 | 3600 | 2 | 758.88 | GGB | 766.3 | 771.867 | 767.766 | 264.39 | GGB | 11024 | GGB | 9.86 | GGB | 1015.28 | GGB | 58.28 | GGB | 172501.05 | GGB | 142474.15 | GGB | 0 | 0 | 2745 | 3600 | 2729.84 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 88888.59 | GGB | 88889.62 | 2729.84 | 2729.84 |  |  |  | 1 | 1 |  |  |  |  | 142474.15 | 2729.84 | 142474.15 | 2729.84 | 9.7282 | [5 empty] | 108.0366 | 2652.6075
11.12.2007 15:00 | 3600 | 2 | 758.19 | GGB | 766.3 | 772.805 | 768.864 | 265.39 | GGB | 11025.2 | GGB | 9.84 | GGB | 1015.73 | GGB | 58.03 | GGB | 173506.76 | GGB | 143474.45 | GGB | 0 | 0 | 2785 | 3600 | 2769.59 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 88929.65 | GGB | 88930.68 | 2769.59 | 2769.59 |  |  |  | 1 | 1 |  |  |  |  | 143474.45 | 2769.59 | 143474.45 | 2769.59 | 9.6777 | [5 empty] | 110.3793 | 2634.1136
11.12.2007 16:00 | 3600 | 2 | 758.77 | GGB | 766.667 | 772.688 | 768.864 | 266.88 | GGB | 11041.1 | GGB | 9.85 | GGB | 1016.58 | GGB | 57.47 | GGB | 175069.24 | GGB | 145133.4 | GGB | 0 | 0 | 2762 | 3600 | 2746.52 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 88969.06 | GGB | 88970.09 | 2746.52 | 2746.52 |  |  |  | 1 | 1 |  |  |  |  | 145133.4 | 2746.52 | 145133.4 | 2746.52 | 10.1145 | [5 empty] | 110.7255 | 2604.0043
11.12.2007 17:00 | 3600 | 2 | 758.79 | GGB | 766.3 | 772.945 | 768.864 | 265.32 | GGB | 11085.3 | GGB | 9.86 | GGB | 1017.03 | GGB | 58.19 | GGB | 173061.12 | GGB | 143221.57 | GGB | 0 | 0 | 2783 | 3600 | 2767.84 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 89010.01 | GGB | 89011.04 | 2767.84 | 2767.84 |  |  |  | 1 | 1 |  |  |  |  | 143221.57 | 2767.84 | 143221.57 | 2767.84 | 9.6804 | [5 empty] | 110.1151 | 2638.7645
11.12.2007 18:00 | 3600 | 2 | 758.46 | GGB | 766.667 | 772.898 | 768.864 | 265.73 | GGB | 11095.2 | GGB | 9.85 | GGB | 1017.45 | GGB | 58.09 | GGB | 173244.88 | GGB | 143474.5 | GGB | 0 | 0 | 2814 | 3600 | 2798.58 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 89050.22 | GGB | 89051.25 | 2798.58 | 2798.58 |  |  |  | 1 | 1 |  |  |  |  | 143474.5 | 2798.58 | 143474.5 | 2798.58 | 9.9857 | [5 empty] | 111.5347 | 2634.1127
11.12.2007 19:00 | 3600 | 2 | 758.46 | GGB | 766.3 | 772.945 | 768.864 | 265.81 | GGB | 11094.9 | GGB | 9.85 | GGB | 1017.95 | GGB | 58.04 | GGB | 173109.54 | GGB | 143457.67 | GGB | 0 | 0 | 2819 | 3600 | 2803.58 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 89090.75 | GGB | 89091.78 | 2803.58 | 2803.58 |  |  |  | 1 | 1 |  |  |  |  | 143457.67 | 2803.58 | 143457.67 | 2803.58 | 9.9234 | [5 empty] | 111.7208 | 2634.4217
11.12.2007 20:00 | 3600 | 2 | 758.57 | GGB | 766.3 | 772.758 | 768.864 | 265.11 | GGB | 11114.5 | GGB | 9.86 | GGB | 1018.44 | GGB | 57.78 | GGB | 173428.63 | GGB | 143904.81 | GGB | 0 | 0 | 2811 | 3600 | 2795.02 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 89131.34 | GGB | 89132.37 | 2795.02 | 2795.02 |  |  |  | 1 | 1 |  |  |  |  | 143904.81 | 2795.02 | 143904.81 | 2795.02 | 9.9093 | [5 empty] | 111.7269 | 2626.2361
11.12.2007 21:00 | 3600 | 2 | 758.1 | GGB | 766.3 | 772.922 | 767.766 | 266.86 | GGB | 11083.4 | GGB | 9.85 | GGB | 1018.89 | GGB | 57.84 | GGB | 173755.43 | GGB | 144212.67 | GGB | 0 | 0 | 2828 | 3600 | 2812.28 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 89172.49 | GGB | 89173.52 | 2812.28 | 2812.28 |  |  |  | 1 | 1 |  |  |  |  | 144212.67 | 2812.28 | 144212.67 | 2812.28 | 9.8558 | [5 empty] | 112.6573 | 2620.6297
11.12.2007 22:00 | 3600 | 2 | 758.47 | GGB | 766.3 | 772.852 | 767.766 | 268.14 | GGB | 11117.9 | GGB | 9.85 | GGB | 1019.45 | GGB | 57.51 | GGB | 174734.74 | GGB | 145247.74 | GGB | 0 | 0 | 2827 | 3600 | 2811.97 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 89212.57 | GGB | 89213.61 | 2811.97 | 2811.97 |  |  |  | 1 | 1 |  |  |  |  | 145247.74 | 2811.97 | 145247.74 | 2811.97 | 10.1879 | [5 empty] | 113.4534 | 2601.9544
11.12.2007 23:00 | 3600 | 2 | 758.18 | GGB | 765.201 | 771.563 | 766.667 | 268.72 | GGB | 11109.6 | GGB | 9.85 | GGB | 1020.49 | GGB | 57.21 | GGB | 175499.47 | GGB | 146164.84 | GGB | 0 | 0 | 2840 | 3600 | 2824.91 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 89253.02 | GGB | 89254.06 | 2824.91 | 2824.91 |  |  |  | 1 | 1 |  |  |  |  | 146164.84 | 2824.91 | 146164.84 | 2824.91 | 10.2077 | [5 empty] | 114.6951 | 2585.6287
11.12.2007 24:00 | 3600 | 2 | 758.78 | GGB | 766.667 | 772.594 | 768.864 | 267.87 | GGB | 11165.7 | GGB | 9.87 | GGB | 1020.93 | GGB | 57.6 | GGB | 174544.38 | GGB | 145260.56 | GGB | 0 | 0 | 2840 | 3600 | 2824.35 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 89293.29 | GGB | 89294.34 | 2824.35 | 2824.35 |  |  |  | 1 | 1 |  |  |  |  | 145260.56 | 2824.35 | 145260.56 | 2824.35 | 10.1854 | [5 empty] | 113.963 | 2601.7248
12.12.2007 01:00 | 3600 | 2 | 757.93 | GGB | 765.201 | 771.609 | 766.667 | 268.53 | GGB | 11151.9 | GGB | 9.84 | GGB | 1021.09 | GGB | 57.35 | GGB | 175301.41 | GGB | 146026.19 | GGB | 0 | 0 | 2879 | 3600 | 2863.54 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 89334.67 | GGB | 89335.72 | 2863.54 | 2863.54 |  |  |  | 1 | 1 |  |  |  |  | 146026.19 | 2863.54 | 146026.19 | 2863.54 | 10.1052 | [5 empty] | 116.1533 | 2588.0837
12.12.2007 02:00 | 3600 | 2 | 758.42 | GGB | 765.201 | 771.563 | 767.766 | 270.26 | GGB | 11152.6 | GGB | 9.85 | GGB | 1021.77 | GGB | 56.59 | GGB | 177672.64 | GGB | 148441.24 | GGB | 0 | 0 | 2852 | 3600 | 2836.33 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 89374.69 | GGB | 89375.73 | 2836.33 | 2836.33 |  |  |  | 1 | 1 |  |  |  |  | 148441.24 | 2836.33 | 148441.24 | 2836.33 | 10.5231 | [5 empty] | 116.9523 | 2545.9771
12.12.2007 03:00 | 3600 | 2 | 758.73 | GGB | 765.201 | 771.492 | 767.766 | 268.98 | GGB | 11211.5 | GGB | 9.86 | GGB | 1021.82 | GGB | 57.28 | GGB | 175744.85 | GGB | 146528.27 | GGB | 0 | 0 | 2868 | 3600 | 2852.44 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 89415.99 | GGB | 89417.03 | 2852.44 | 2852.44 |  |  |  | 1 | 1 |  |  |  |  | 146528.27 | 2852.44 | 146528.27 | 2852.44 | 10.1202 | [5 empty] | 116.1009 | 2579.2156
12.12.2007 04:00 | 3600 | 2 | 758.59 | GGB | 766.3 | 772.406 | 768.864 | 269.08 | GGB | 11219.4 | GGB | 9.86 | GGB | 1022.44 | GGB | 57.22 | GGB | 175972.62 | GGB | 146837.03 | GGB | 0 | 0 | 2883 | 3600 | 2867.2 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 89456.39 | GGB | 89457.44 | 2867.2 | 2867.2 |  |  |  | 1 | 1 |  |  |  |  | 146837.03 | 2867.2 | 146837.03 | 2867.2 | 10.4185 | [5 empty] | 116.9475 | 2573.7922
12.12.2007 05:00 | 3600 | 2 | 758.51 | GGB | 766.667 | 772.523 | 768.864 | 268.52 | GGB | 11205.4 | GGB | 9.86 | GGB | 1022.26 | GGB | 57.16 | GGB | 175583.1 | GGB | 146513.6 | GGB | 0 | 0 | 2879 | 3600 | 2863.09 | GGB | 100 | GGB | 41.63 | GGB | 41.63 | GGB | 89498.02 | GGB | 89499.07 | 2863.09 | 2863.09 |  |  |  | 1 | 1 |  |  |  |  | 146513.6 | 2863.09 | 146513.6 | 2863.09 | 10.0764 | [5 empty] | 116.5227 | 2579.4739
12.12.2007 06:00 | 3600 | 2 | 758.14 | GGB | 766.3 | 772.523 | 767.766 | 268.4 | GGB | 11200 | GGB | 9.85 | GGB | 1022.49 | GGB | 57.14 | GGB | 175640.31 | GGB | 146601.47 | GGB | 0 | 0 | 2889 | 3600 | 2873.08 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 89538.53 | GGB | 89539.57 | 2873.08 | 2873.08 |  |  |  | 1 | 1 |  |  |  |  | 146601.47 | 2873.08 | 146601.47 | 2873.08 | 10.3999 | [5 empty] | 116.9994 | 2577.9278
12.12.2007 07:00 | 3600 | 2 | 758.43 | GGB | 765.201 | 771.375 | 766.667 | 268.01 | GGB | 11197.4 | GGB | 9.86 | GGB | 1022.79 | GGB | 57.3 | GGB | 175364.13 | GGB | 146342.47 | GGB | 0 | 0 | 2877 | 3600 | 2861.33 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 89579.9 | GGB | 89580.94 | 2861.33 | 2861.33 |  |  |  | 1 | 1 |  |  |  |  | 146342.47 | 2861.33 | 146342.47 | 2861.33 | 10.1217 | [5 empty] | 116.315 | 2582.4902
12.12.2007 08:00 | 3600 | 2 | 758.05 | GGB | 766.3 | 772.336 | 768.132 | 268.89 | GGB | 11212.4 | GGB | 9.85 | GGB | 1023.17 | GGB | 57.11 | GGB | 175929.7 | GGB | 146952.19 | GGB | 0 | 0 | 2909 | 3600 | 2892.93 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 89620.54 | GGB | 89621.58 | 2892.93 | 2892.93 |  |  |  | 1 | 1 |  |  |  |  | 146952.19 | 2892.93 | 146952.19 | 2892.93 | 10.4607 | [5 empty] | 118.0896 | 2571.7752
12.12.2007 09:00 | 3600 | 2 | 758.78 | GGB | 766.667 | 772.336 | 768.498 | 268.37 | GGB | 11217.5 | GGB | 9.86 | GGB | 1023.47 | GGB | 57.12 | GGB | 175442.25 | GGB | 146586.23 | GGB | 0 | 0 | 2873 | 3600 | 2857.21 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 89661.83 | GGB | 89662.87 | 2857.21 | 2857.21 |  |  |  | 1 | 1 |  |  |  |  | 146586.23 | 2857.21 | 146586.23 | 2857.21 | 10.1436 | [5 empty] | 116.341 | 2578.1958
12.12.2007 10:00 | 3600 | 2 | 758.6 | GGB | 765.201 | 771.328 | 767.033 | 268.39 | GGB | 11219.9 | GGB | 9.86 | GGB | 1023.78 | GGB | 57.04 | GGB | 175605.1 | GGB | 146799.79 | GGB | 0 | 0 | 2888 | 3600 | 2872.87 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 89702.67 | GGB | 89703.71 | 2872.87 | 2872.87 |  |  |  | 1 | 1 |  |  |  |  | 146799.79 | 2872.87 | 146799.79 | 2872.87 | 10.3266 | [5 empty] | 117.1491 | 2574.4451
12.12.2007 11:00 | 3600 | 2 | 758.18 | GGB | 767.766 | 772.617 | 769.597 | 268.33 | GGB | 11224.7 | GGB | 9.86 | GGB | 1024.26 | GGB | 56.89 | GGB | 175223.29 | GGB | 146615.65 | GGB | 0 | 0 | 2881 | 3600 | 2865.65 | GGB | 100 | GGB | 41.54 | GGB | 41.54 | GGB | 89744.21 | GGB | 89745.25 | 2865.65 | 2865.65 |  |  |  | 1 | 1 |  |  |  |  | 146615.65 | 2865.65 | 146615.65 | 2865.65 | 10.1143 | [5 empty] | 116.7081 | 2577.6784
12.12.2007 12:00 | 3600 | 2 | 757.93 | GGB | 766.3 | 771.75 | 769.597 | 268.68 | GGB | 11161.2 | GGB | 9.85 | GGB | 1024.45 | GGB | 56.99 | GGB | 175517.08 | GGB | 146846.12 | GGB | 0 | 0 | 2863 | 3600 | 2846.99 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 89784.59 | GGB | 89785.63 | 2846.99 | 2846.99 |  |  |  | 1 | 1 |  |  |  |  | 146846.12 | 2846.99 | 146846.12 | 2846.99 | 10.3534 | [5 empty] | 116.1304 | 2573.6329
12.12.2007 13:00 | 3600 | 2 | 759.16 | GGB | 765.201 | 771.633 | 768.132 | 267.58 | GGB | 11136.1 | GGB | 9.87 | GGB | 1024.29 | GGB | 57.52 | GGB | 173680.61 | GGB | 145055.71 | GGB | 0 | 0 | 2797 | 3600 | 2781.62 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 89825.41 | GGB | 89826.45 | 2781.62 | 2781.62 |  |  |  | 1 | 1 |  |  |  |  | 145055.71 | 2781.62 | 145055.71 | 2781.62 | 9.8846 | [5 empty] | 112.0805 | 2605.399
12.12.2007 14:00 | 3600 | 2 | 758.59 | GGB | 766.3 | 771.938 | 769.597 | 266.8 | GGB | 11116.4 | GGB | 9.86 | GGB | 1024.2 | GGB | 58.19 | GGB | 172529.66 | GGB | 143786.45 | GGB | 0 | 0 | 2818 | 3600 | 2802.2 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 89866.37 | GGB | 89867.41 | 2802.2 | 2802.2 |  |  |  | 1 | 1 |  |  |  |  | 143786.45 | 2802.2 | 143786.45 | 2802.2 | 9.8369 | [5 empty] | 111.9218 | 2628.3979
12.12.2007 15:00 | 3600 | 2 | 758.39 | GGB | 766.667 | 771.891 | 768.498 | 268.56 | GGB | 11078.1 | GGB | 9.85 | GGB | 1024.69 | GGB | 57.24 | GGB | 174974.61 | GGB | 146317.51 | GGB | 0 | 0 | 2801 | 3600 | 2785.26 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 89906.85 | GGB | 89907.89 | 2785.26 | 2785.26 |  |  |  | 1 | 1 |  |  |  |  | 146317.51 | 2785.26 | 146317.51 | 2785.26 | 10.0675 | [5 empty] | 113.2034 | 2582.9308
12.12.2007 16:00 | 3600 | 2 | 759.15 | GGB | 766.667 | 772.781 | 769.597 | 267.08 | GGB | 11135.1 | GGB | 9.87 | GGB | 1024.64 | GGB | 57.96 | GGB | 173098.53 | GGB | 144427.5 | GGB | 0 | 0 | 2793 | 3600 | 2777.07 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 89948.06 | GGB | 89949.1 | 2777.07 | 2777.07 |  |  |  | 1 | 1 |  |  |  |  | 144427.5 | 2777.07 | 144427.5 | 2777.07 | 9.7327 | [5 empty] | 111.4126 | 2616.7316
12.12.2007 17:00 | 3600 | 2 | 758.73 | GGB | 766.667 | 772.781 | 768.864 | 267.36 | GGB | 11121.3 | GGB | 9.86 | GGB | 1024.49 | GGB | 57.62 | GGB | 173974.4 | GGB | 145286.41 | GGB | 0 | 0 | 2802 | 3600 | 2786.9 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 89988.73 | GGB | 89989.76 | 2786.9 | 2786.9 |  |  |  | 1 | 1 |  |  |  |  | 145286.41 | 2786.9 | 145286.41 | 2786.9 | 9.9582 | [5 empty] | 112.4719 | 2601.2619
12.12.2007 18:00 | 3600 | 2 | 758.59 | GGB | 766.667 | 772.805 | 768.864 | 267.04 | GGB | 11142.5 | GGB | 9.85 | GGB | 1024.98 | GGB | 57.68 | GGB | 173389.02 | GGB | 144838.11 | GGB | 0 | 0 | 2832 | 3600 | 2816.56 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 90030 | GGB | 90031.04 | 2816.56 | 2816.56 |  |  |  | 1 | 1 |  |  |  |  | 144838.11 | 2816.56 | 144838.11 | 2816.56 | 9.8824 | [5 empty] | 113.3181 | 2609.3133
12.12.2007 19:00 | 3600 | 2 | 758.44 | GGB | 766.667 | 772.781 | 768.864 | 267.45 | GGB | 11191.1 | GGB | 9.86 | GGB | 1025.67 | GGB | 56.78 | GGB | 175095.65 | GGB | 146761.54 | GGB | 0 | 0 | 2844 | 3600 | 2828.24 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 90070.54 | GGB | 90071.58 | 2828.24 | 2828.24 |  |  |  | 1 | 1 |  |  |  |  | 146761.54 | 2828.24 | 146761.54 | 2828.24 | 10.2387 | [5 empty] | 115.2991 | 2575.1161
12.12.2007 20:00 | 3600 | 2 | 758.01 | GGB | 766.667 | 772.711 | 768.864 | 269.62 | GGB | 11175.1 | GGB | 9.84 | GGB | 1026.55 | GGB | 56.38 | GGB | 177025.64 | GGB | 148688.8 | GGB | 0 | 0 | 2866 | 3600 | 2850.75 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 90110.69 | GGB | 90111.73 | 2850.75 | 2850.75 |  |  |  | 1 | 1 |  |  |  |  | 148688.8 | 2850.75 | 148688.8 | 2850.75 | 10.5573 | [5 empty] | 117.7429 | 2541.7382
12.12.2007 21:00 | 3600 | 2 | 757.36 | GGB | 765.201 | 771.398 | 767.766 | 270.57 | GGB | 11251.4 | GGB | 9.83 | GGB | 1026.89 | GGB | 56.29 | GGB | 177732.06 | GGB | 149372.28 | GGB | 0 | 0 | 2941 | 3600 | 2925.8 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 90152.05 | GGB | 90153.1 | 2925.8 | 2925.8 |  |  |  | 1 | 1 |  |  |  |  | 149372.28 | 2925.8 | 149372.28 | 2925.8 | 10.564 | [5 empty] | 121.3982 | 2530.108
12.12.2007 22:00 | 3600 | 2 | 757.9 | GGB | 767.766 | 773.672 | 770.33 | 272.72 | GGB | 11314.7 | GGB | 9.85 | GGB | 1028.08 | GGB | 55.79 | GGB | 180424.58 | GGB | 152039.73 | GGB | 0 | 0 | 2930 | 3600 | 2914.24 | GGB | 100 | GGB | 41.04 | GGB | 41.04 | GGB | 90193.09 | GGB | 90194.14 | 2914.24 | 2914.24 |  |  |  | 1 | 1 |  |  |  |  | 152039.73 | 2914.24 | 152039.73 | 2914.24 | 10.7963 | [5 empty] | 123.0779 | 2485.7187
12.12.2007 23:00 | 3600 | 2 | 757.49 | GGB | 765.201 | 770.438 | 766.667 | 272.34 | GGB | 11363 | GGB | 9.84 | GGB | 1028.39 | GGB | 55.79 | GGB | 180105.48 | GGB | 151816.08 | GGB | 0 | 0 | 2978 | 3600 | 2962.28 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 90234.47 | GGB | 90235.52 | 2962.28 | 2962.28 |  |  |  | 1 | 1 |  |  |  |  | 151816.08 | 2962.28 | 151816.08 | 2962.28 | 10.8681 | [5 empty] | 124.9227 | 2489.3806
12.12.2007 24:00 | 3600 | 2 | 757.81 | GGB | 766.3 | 771.703 | 768.864 | 272.64 | GGB | 11404.3 | GGB | 9.86 | GGB | 1029.2 | GGB | 55.4 | GGB | 180716.17 | GGB | 152633.67 | GGB | 0 | 0 | 2981 | 3600 | 2965.76 | GGB | 100 | GGB | 41.83 | GGB | 41.83 | GGB | 90276.3 | GGB | 90277.35 | 2965.76 | 2965.76 |  |  |  | 1 | 1 |  |  |  |  | 152633.67 | 2965.76 | 152633.67 |  | 10.8218 | [5 empty] | 125.743 | 2476.0461
13.12.2007 01:00 | 3600 | 2 | 757.37 | GGB | 765.201 | 770.414 | 767.766 | 274.41 | GGB | 11370.2 | GGB | 9.84 | GGB | 1029.77 | GGB | 54.94 | GGB | 183538.54 | GGB | 155321.65 | GNB | 0 | 0 | 2990 | 3600 | 2974.33 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 90317.16 | GGB | 90318.21 | 2974.33 | 2974.33 |  |  |  | 1 | 1 |  |  |  |  | 155321.65 | 2974.33 |  |  | 11.3064 | [5 empty] | 128.3272 | 2433.1959
13.12.2007 02:00 | 3600 | 2 | 758.19 | GGB | 765.201 | 771.234 | 767.766 | 273.52 | GGB | 11433.5 | GGB | 9.87 | GGB | 1029.91 | GGB | 54.92 | GGB | 182493.22 | GGB | 154463.74 | GNB | 0 | 0 | 2975 | 3600 | 2958.93 | GGB | 100 | GGB | 41.97 | GGB | 41.97 | GGB | 90359.13 | GGB | 90360.18 | 2958.93 | 2958.93 |  |  |  | 1 | 1 |  |  |  |  | 154463.74 | 2958.93 |  | 2958.93 | 10.8899 | [5 empty] | 126.9576 | 2446.7101
13.12.2007 03:00 | 3600 | 2 | 757.45 | GGB | 766.3 | 771.305 | 767.766 | 273.27 | GGB | 11440.4 | GGB | 9.85 | GGB | 1029.5 | GGB | 68.33 | GGB | 182053.08 | GGB | 147979.21 | GGB | 0 | 0 | 3027 | 3600 | 3011.23 | GGB | 100 | GGB | 42.15 | GGB | 42.15 | GGB | 90401.28 | GGB | 90402.33 | 3011.23 | 3011.23 |  |  |  | 1 | 1 |  |  |  |  | 147979.21 | 3011.23 | 147979.21 |  | 10.5718 | [5 empty] | 123.7776 | 2553.9263
13.12.2007 04:00 | 3600 | 2 | 757.78 | GGB | 766.3 | 771.492 | 768.864 | 273.28 | GGB | 11459.4 | GGB | 9.86 | GGB | 1029.2 | GGB | 71.26 | GGB | 182232.44 | GGB | 146821.04 | GGB | 0 | 0 | 3015 | 3600 | 2998.93 | GGB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 90443.16 | GGB | 90444.21 | 2998.93 | 2998.93 |  |  |  | 1 | 1 |  |  |  |  | 146821.04 | 2998.93 | 146821.04 |  | 10.5135 | [5 empty] | 122.3072 | 2574.0725
13.12.2007 05:00 | 3600 | 2 | 757.88 | GGB | 765.201 | 771.211 | 767.766 | 272.83 | GGB | 11462.6 | GGB | 9.86 | GGB | 1029.09 | GGB | 56.44 | GGB | 182113.6 | GGB | 153312.83 | GNB | 0 | 0 | 3009 | 3600 | 2992.87 | GGB | 100 | GGB | 41.74 | GGB | 41.74 | GGB | 90484.9 | GGB | 90485.95 | 2992.87 | 2992.87 |  |  |  | 1 | 1 |  |  |  |  | 153312.83 | 2992.87 |  |  | 10.9929 | [5 empty] | 127.457 | 2465.0774
13.12.2007 06:00 | 3600 | 2 | 757.65 | GGB | 765.201 | 769.945 | 766.667 | 272.32 | GGB | 11429.1 | GGB | 9.86 | GGB | 1028.94 | GGB | 54.69 | GGB | 181364.27 | GGB | 153471.81 | GNB | 0 | 0 | 3005 | 3600 | 2989.82 | GGB | 100 | GGB | 41.91 | GGB | 41.91 | GGB | 90526.8 | GGB | 90527.86 | 2989.82 | 2989.82 |  |  |  | 1 | 1 |  |  |  |  | 153471.81 | 2989.82 |  |  | 10.9485 | [5 empty] | 127.4592 | 2462.5239
13.12.2007 07:00 | 3600 | 2 | 757.14 | GGB | 765.201 | 770.086 | 766.667 | 273.45 | GGB | 11433.9 | GGB | 9.85 | GGB | 1028.84 | GGB | 54.52 | GGB | 181819.81 | GGB | 153922.4 | GNB | 0 | 0 | 3043 | 3600 | 3027.5 | GGB | 100 | GGB | 41.7 | GGB | 41.7 | GGB | 90568.51 | GGB | 90569.56 | 3027.5 | 3027.5 |  |  |  | 1 | 1 |  |  |  |  | 153922.4 | 3027.5 |  |  | 11.1751 | [5 empty] | 129.4445 | 2455.3151
13.12.2007 08:00 | 3600 | 2 | 757.66 | GGB | 766.3 | 771.305 | 768.864 | 273.73 | GGB | 11454.4 | GGB | 9.86 | GGB | 1029.23 | GGB | 54.34 | GGB | 182158.71 | GGB | 154354.32 | GNB | 0 | 0 | 3030 | 3600 | 3014.19 | GGB | 100 | GGB | 41.97 | GGB | 41.97 | GGB | 90610.48 | GGB | 90611.53 | 3014.19 | 3014.19 |  |  |  | 1 | 1 |  |  |  |  | 154354.32 | 3014.19 |  |  | 11.0854 | [5 empty] | 129.237 | 2448.4446
13.12.2007 09:00 | 3600 | 2 | 757.69 | GGB | 764.102 | 770.367 | 766.667 | 273.23 | GGB | 11417.4 | GGB | 9.85 | GGB | 1029.42 | GGB | 54.87 | GGB | 181286.15 | GGB | 153393.44 | GNB | 0 | 0 | 3018 | 3600 | 3001.94 | GGB | 100 | GGB | 41.62 | GGB | 41.62 | GGB | 90652.1 | GGB | 90653.15 | 3001.94 | 3001.94 |  |  |  | 1 | 1 |  |  |  |  | 153393.44 | 3001.94 |  |  | 11.0639 | [5 empty] | 127.9105 | 2463.782
13.12.2007 10:00 | 3600 | 2 | 757.89 | GGB | 766.3 | 772.453 | 768.864 | 273.39 | GGB | 11424.3 | GGB | 9.86 | GGB | 1029.9 | GGB | 55.12 | GGB | 180908.73 | GGB | 153027.82 | GNB | 0 | 0 | 3009 | 3600 | 2992.86 | GGB | 100 | GGB | 41.7 | GGB | 41.7 | GGB | 90693.8 | GGB | 90694.85 | 2992.86 | 2992.86 |  |  |  | 1 | 1 |  |  |  |  | 153027.82 | 2992.86 |  |  | 10.983 | [5 empty] | 127.2197 | 2469.6686
13.12.2007 11:00 | 3600 | 2 | 757.37 | GGB | 764.102 | 770.25 | 766.667 | 273.4 | GGB | 11390 | GGB | 9.85 | GGB | 1029.63 | GGB | 55.26 | GGB | 180510.41 | GGB | 152586.31 | GGB | 0 | 0 | 3016 | 3600 | 3000.61 | GGB | 100 | GGB | 41.73 | GGB | 41.73 | GGB | 90735.53 | GGB | 90736.58 | 3000.61 | 3000.61 |  |  |  | 1 | 1 |  |  |  |  | 152586.31 | 3000.61 | 152586.31 |  | 10.9718 | [5 empty] | 127.1811 | 2476.8146
13.12.2007 12:00 | 3600 | 2 | 757.22 | GGB | 765.201 | 771.211 | 767.766 | 273.68 | GGB | 11377.1 | GGB | 9.86 | GGB | 1029.89 | GGB | 55.45 | GGB | 180182.51 | GGB | 152261.75 | GGB | 0 | 0 | 3003 | 3600 | 2987.23 | GGB | 100 | GGB | 41.35 | GGB | 41.35 | GGB | 90776.87 | GGB | 90777.93 | 2987.23 | 2987.23 |  |  |  | 1 | 1 |  |  |  |  | 152261.75 | 2987.23 | 152261.75 |  | 10.9998 | [5 empty] | 126.3447 | 2482.0942
13.12.2007 13:00 | 3600 | 2 | 757.43 | GGB | 766.3 | 772.195 | 768.864 | 273.87 | GGB | 11369.7 | GGB | 9.86 | GGB | 1029.87 | GGB | 55.46 | GGB | 180003.15 | GGB | 152101.59 | GGB | 0 | 0 | 2995 | 3600 | 2979.52 | GGB | 100 | GGB | 41.9 | GGB | 41.9 | GGB | 90818.78 | GGB | 90819.83 | 2979.52 | 2979.52 |  |  |  | 1 | 1 |  |  |  |  | 152101.59 | 2979.52 | 152101.59 |  | 10.816 | [5 empty] | 125.886 | 2484.7078
13.12.2007 14:00 | 3600 | 2 | 757.8 | GGB | 766.3 | 771.516 | 767.766 | 274.2 | GGB | 11338.4 | GGB | 9.86 | GGB | 1030.09 | GGB | 55.54 | GGB | 179861.21 | GGB | 151979.17 | GGB | 0 | 0 | 2961 | 3600 | 2945.18 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 90859.35 | GGB | 90860.4 | 2945.18 | 2945.18 |  |  |  | 1 | 1 |  |  |  |  | 151979.17 | 2945.18 | 151979.17 | 2945.18 | 11.0329 | [5 empty] | 124.335 | 2486.7092
13.12.2007 15:00 | 3600 | 2 | 757.75 | GGB | 766.3 | 771.773 | 768.864 | 273.43 | GGB | 11328.4 | GGB | 9.86 | GGB | 1030.1 | GGB | 56.01 | GGB | 178910.52 | GGB | 150959.91 | GGB | 0 | 0 | 2960 | 3600 | 2944.4 | GGB | 100 | GGB | 42.13 | GGB | 42.13 | GGB | 90901.48 | GGB | 90902.53 | 2944.4 | 2944.4 |  |  |  | 1 | 1 |  |  |  |  | 150959.91 | 2944.4 | 150959.91 | 2944.4 | 10.5504 | [5 empty] | 123.4684 | 2503.4991
13.12.2007 16:00 | 3600 | 2 | 757.7 | GGB | 765.201 | 771.539 | 768.864 | 273.23 | GGB | 11317 | GGB | 9.86 | GGB | 1030.47 | GGB | 56.43 | GGB | 178898.41 | GGB | 150811.08 | GGB | 0 | 0 | 2961 | 3600 | 2945.68 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 90941.82 | GGB | 90942.87 | 2945.68 | 2945.68 |  |  |  | 1 | 1 |  |  |  |  | 150811.08 | 2945.68 | 150811.08 | 2945.68 | 11.0124 | [5 empty] | 123.4003 | 2505.9697
13.12.2007 17:00 | 3600 | 2 | 757.92 | GGB | 767.766 | 774.258 | 771.429 | 274.24 | GGB | 11306.1 | GGB | 9.86 | GGB | 1030.21 | GGB | 56.03 | GGB | 180141.79 | GGB | 152006.17 | GGB | 0 | 0 | 2952 | 3600 | 2935.92 | GGB | 100 | GGB | 42.41 | GGB | 42.41 | GGB | 90984.23 | GGB | 90985.28 | 2935.92 | 2935.92 |  |  |  | 1 | 1 |  |  |  |  | 152006.17 | 2935.92 | 152006.17 | 2935.92 | 10.5229 | [5 empty] | 123.9661 | 2486.2675
13.12.2007 18:00 | 3600 | 2 | 757.99 | GGB | 766.3 | 771.141 | 767.766 | 273.16 | GGB | 11318.3 | GGB | 9.86 | GGB | 1030.35 | GGB | 56.42 | GGB | 178730.06 | GGB | 150653.85 | GGB | 0 | 0 | 2956 | 3600 | 2939.91 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 91024.72 | GGB | 91025.78 | 2939.91 | 2939.91 |  |  |  | 1 | 1 |  |  |  |  | 150653.85 | 2939.91 | 150653.85 | 2939.91 | 10.936 | [5 empty] | 123.0302 | 2508.5851
13.12.2007 19:00 | 3600 | 2 | 757.63 | GGB | 766.3 | 771.117 | 768.864 | 273.73 | GGB | 11332.7 | GGB | 9.85 | GGB | 1030.48 | GGB | 56.31 | GGB | 179239.52 | GGB | 151155.5 | GGB | 0 | 0 | 2989 | 3600 | 2973.5 | GGB | 100 | GGB | 41.86 | GGB | 41.86 | GGB | 91066.58 | GGB | 91067.64 | 2973.5 | 2973.5 |  |  |  | 1 | 1 |  |  |  |  | 151155.5 | 2973.5 | 151155.5 |  | 10.7372 | [5 empty] | 124.8502 | 2500.2597
13.12.2007 20:00 | 3600 | 2 | 758.46 | GGB | 765.201 | 771.07 | 766.667 | 272.67 | GGB | 11339.3 | GGB | 9.87 | GGB | 1030.65 | GGB | 56.34 | GGB | 178989.74 | GGB | 150956.13 | GGB | 0 | 0 | 2936 | 3600 | 2920.38 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 91107.6 | GGB | 91108.66 | 2920.38 | 2920.38 |  |  |  | 1 | 1 |  |  |  |  | 150956.13 | 2920.38 | 150956.13 | 2920.38 | 10.7472 | [5 empty] | 122.4581 | 2503.5618
13.12.2007 21:00 | 3600 | 2 | 758.12 | GGB | 766.3 | 772.242 | 768.864 | 274.53 | GGB | 11266.8 | GGB | 9.84 | GGB | 1030.75 | GGB | 55.94 | GGB | 180980.25 | GGB | 152834.44 | GNB | 0 | 0 | 2923 | 3600 | 2907.07 | GGB | 100 | GGB | 41.8 | GGB | 41.8 | GGB | 91149.4 | GGB | 91150.46 | 2907.07 | 2907.07 |  |  |  | 1 | 1 |  |  |  |  | 152834.44 | 2907.07 |  | 2907.07 | 10.6292 | [5 empty] | 123.4168 | 2472.7934
13.12.2007 22:00 | 3600 | 2 | 758.77 | GGB | 765.201 | 771.141 | 767.766 | 273.24 | GGB | 11314.5 | GGB | 9.86 | GGB | 1031.05 | GGB | 56.59 | GGB | 178715.76 | GGB | 150667.93 | GGB | 0 | 0 | 2909 | 3600 | 2893.27 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 91190.55 | GGB | 91191.61 | 2893.27 | 2893.27 |  |  |  | 1 | 1 |  |  |  |  | 150667.93 | 2893.27 | 150667.93 | 2893.27 | 10.5935 | [5 empty] | 121.0897 | 2508.3506
13.12.2007 23:00 | 3600 | 2 | 757.84 | GGB | 766.3 | 772.289 | 769.963 | 274.26 | GGB | 11283.8 | GGB | 9.85 | GGB | 1031.48 | GGB | 56.36 | GGB | 180064.77 | GGB | 151974.06 | GGB | 0 | 0 | 2940 | 3600 | 2924.57 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 91231.72 | GGB | 91232.78 | 2924.57 | 2924.57 |  |  |  | 1 | 1 |  |  |  |  | 151974.06 | 2924.57 | 151974.06 | 2924.57 | 10.7957 | [5 empty] | 123.4608 | 2486.7928
13.12.2007 24:00 | 3600 | 2 | 758.67 | GGB | 766.667 | 772.43 | 768.864 | 275.03 | GGB | 11290.6 | GGB | 9.86 | GGB | 1031.75 | GGB | 55.93 | GGB | 181168.41 | GGB | 153146.56 | GNB | 0 | 0 | 2898 | 3600 | 2882.8 | GGB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 91273.6 | GGB | 91274.66 | 2882.8 | 2882.8 |  |  |  | 1 | 1 |  |  |  |  | 153146.56 | 2882.8 |  | 2882.8 | 10.5418 | [5 empty] | 122.6364 | 2467.7538
14.12.2007 01:00 | 3600 | 2 | 758.89 | GGB | 766.3 | 771.258 | 767.766 | 273.74 | GGB | 11325.1 | GGB | 9.86 | GGB | 1031.77 | GGB | 56.45 | GGB | 179428.78 | GGB | 151440.96 | GGB | 0 | 0 | 2906 | 3600 | 2890.1 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 91313.7 | GGB | 91314.76 | 2890.1 | 2890.1 |  |  |  | 1 | 1 |  |  |  |  | 151440.96 | 2890.1 | 151440.96 | 2890.1 | 10.9147 | [5 empty] | 121.5776 | 2495.5468
14.12.2007 02:00 | 3600 | 2 | 758.42 | GGB | 766.667 | 772.406 | 768.864 | 273.31 | GGB | 11340.2 | GGB | 9.86 | GGB | 1031.71 | GGB | 56.57 | GGB | 179147.09 | GGB | 151139.08 | GGB | 0 | 0 | 2936 | 3600 | 2920.51 | GGB | 100 | GGB | 42.83 | GGB | 42.83 | GGB | 91356.53 | GGB | 91357.59 | 2920.51 | 2920.51 |  |  |  | 1 | 1 |  |  |  |  | 151139.08 | 2920.51 | 151139.08 | 2920.51 | 10.3059 | [5 empty] | 122.612 | 2500.5313
14.12.2007 03:00 | 3600 | 2 | 758.26 | GGB | 765.201 | 771.117 | 767.766 | 273.49 | GGB | 11325 | GGB | 9.85 | GGB | 1031.81 | GGB | 56.55 | GGB | 179111.88 | GGB | 151132.34 | GGB | 0 | 0 | 2940 | 3600 | 2924.49 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 91396.7 | GGB | 91397.76 | 2924.49 | 2924.49 |  |  |  | 1 | 1 |  |  |  |  | 151132.34 | 2924.49 | 151132.34 | 2924.49 | 11.0029 | [5 empty] | 122.7736 | 2500.6428
14.12.2007 04:00 | 3600 | 2 | 758.19 | GGB | 765.201 | 771.516 | 766.667 | 273.62 | GGB | 11318 | GGB | 9.85 | GGB | 1031.72 | GGB | 56.7 | GGB | 179043.66 | GGB | 150991.26 | GGB | 0 | 0 | 2944 | 3600 | 2928.62 | GGB | 100 | GGB | 42.15 | GGB | 42.15 | GGB | 91438.85 | GGB | 91439.91 | 2928.62 | 2928.62 |  |  |  | 1 | 1 |  |  |  |  | 150991.26 | 2928.62 | 150991.26 | 2928.62 | 10.491 | [5 empty] | 122.8322 | 2502.9793
14.12.2007 05:00 | 3600 | 2 | 758.33 | GGB | 766.3 | 772.617 | 768.864 | 273.65 | GGB | 11329.7 | GGB | 9.86 | GGB | 1031.68 | GGB | 56.56 | GGB | 179064.56 | GGB | 151065.8 | GGB | 0 | 0 | 2942 | 3600 | 2926.86 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 91479.65 | GGB | 91480.71 | 2926.86 | 2926.86 |  |  |  | 1 | 1 |  |  |  |  | 151065.8 | 2926.86 | 151065.8 | 2926.86 | 10.837 | [5 empty] | 122.819 | 2501.7443
14.12.2007 06:00 | 3600 | 2 | 758.22 | GGB | 766.667 | 772.477 | 768.864 | 275.59 | GGB | 11281.7 | GGB | 9.85 | GGB | 1031.97 | GGB | 56.14 | GGB | 180993.46 | GGB | 152933.67 | GNB | 0 | 0 | 2928 | 3600 | 2912.32 | GGB | 100 | GGB | 42.07 | GGB | 42.07 | GGB | 91521.72 | GGB | 91522.78 | 2912.32 | 2912.32 |  |  |  | 1 | 1 |  |  |  |  | 152933.67 | 2912.32 |  | 2912.32 | 10.5869 | [5 empty] | 123.7199 | 2471.189
14.12.2007 07:00 | 3600 | 2 | 758.38 | GGB | 766.3 | 772.547 | 768.864 | 275.87 | GGB | 11284.9 | GGB | 9.85 | GGB | 1032.56 | GGB | 56.32 | GGB | 181334.56 | GGB | 153224.53 | GNB | 0 | 0 | 2917 | 3600 | 2901.38 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 91562.2 | GGB | 91563.26 | 2901.38 | 2901.38 |  |  |  | 1 | 1 |  |  |  |  | 153224.53 | 2901.38 |  | 2901.38 | 10.9823 | [5 empty] | 123.4896 | 2466.498
14.12.2007 08:00 | 3600 | 2 | 758.85 | GGB | 766.667 | 772.523 | 768.864 | 274.15 | GGB | 11334.1 | GGB | 9.86 | GGB | 1032.96 | GGB | 56.9 | GGB | 178951.23 | GGB | 151004.44 | GGB | 0 | 0 | 2939 | 3207 | 2923.01 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 91603.58 | GGB | 91604.64 | 2923.01 | 2923.01 |  |  |  | 1 | 1 |  |  |  |  | 151004.44 | 2923.01 | 151004.44 | 2923.01 | 10.6667 | [5 empty] | 122.6076 | 2502.7608
14.12.2007 09:00 | 3600 | 2 | 758.37 | GGB | 766.3 | 771.539 | 767.766 | 274.19 | GGB | 11328.1 | GGB | 9.85 | GGB | 1032.57 | GGB | 58.4 | GGB | 169804.12 | GGB | 142582.4 | GGB | 0 | 0 | 2961 | 3000 | 2945 | GGB | 100 | GGB | 41.69 | GGB | 41.69 | GGB | 91645.27 | GGB | 91646.33 | 2945 | 2945 |  |  |  | 1 | 1 |  |  |  |  | 142582.4 | 2945 | 142582.4 | 2945 | 10.0721 | [5 empty] | 116.6403 | 2650.5936
14.12.2007 10:00 | 3600 | 2 | 758.38 | GGB | 766.667 | 772.734 | 768.864 | 274.27 | GGB | 11336.8 | GGB | 9.86 | GGB | 1033.07 | GGB | 56.91 | GGB | 179297.84 | GGB | 151308.34 | GGB | 0 | 0 | 2968 | 3600 | 2952.18 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 91686.07 | GGB | 91687.13 | 2952.18 | 2952.18 |  |  |  | 1 | 1 |  |  |  |  | 151308.34 | 2952.18 | 151308.34 | 2952.18 | 10.9483 | [5 empty] | 124.0804 | 2497.7341
14.12.2007 11:00 | 3600 | 2 | 758.06 | GGB | 766.3 | 772.758 | 768.864 | 276.21 | GGB | 11306.8 | GGB | 9.85 | GGB | 1034.03 | GGB | 56.47 | GGB | 181551.33 | GGB | 153555.83 | GNB | 0 | 0 | 2955 | 3600 | 2939.85 | GGB | 100 | GGB | 42.36 | GGB | 42.36 | GGB | 91728.43 | GGB | 91729.49 | 2939.85 | 2939.85 |  |  |  | 1 | 1 |  |  |  |  | 153555.83 | 2939.85 |  | 2939.85 | 10.657 | [5 empty] | 125.3975 | 2461.1765
14.12.2007 12:00 | 3600 | 2 | 758.65 | GGB | 767.766 | 772.758 | 769.963 | 276.21 | GGB | 11317.9 | GGB | 9.86 | GGB | 1034.64 | GGB | 56.36 | GGB | 181721.88 | GGB | 153843.42 | GNB | 0 | 0 | 2920 | 3600 | 2904.82 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 91768.87 | GGB | 91769.93 | 2904.82 | 2904.82 |  |  |  | 1 | 1 |  |  |  |  | 153843.42 | 2904.82 |  | 2904.82 | 11.0506 | [5 empty] | 124.1354 | 2456.5757
14.12.2007 13:00 | 3600 | 2 | 758.65 | GGB | 766.3 | 771.82 | 768.864 | 274.43 | GGB | 11353.3 | GGB | 9.86 | GGB | 1034.06 | GGB | 57.03 | GGB | 179337.45 | GGB | 151430.57 | GGB | 0 | 0 | 2944 | 3600 | 2928 | GGB | 100 | GGB | 41.69 | GGB | 41.69 | GGB | 91810.56 | GGB | 91811.62 | 2928 | 2928 |  |  |  | 1 | 1 |  |  |  |  | 151430.57 | 2928 | 151430.57 | 2928 | 10.6354 | [5 empty] | 123.1635 | 2495.718
14.12.2007 14:00 | 3600 | 2 | 758.53 | GGB | 766.667 | 771.82 | 768.864 | 274.44 | GGB | 11349.1 | GGB | 9.86 | GGB | 1034.03 | GGB | 57.07 | GGB | 179338.55 | GGB | 151410.95 | GGB | 0 | 0 | 2955 | 3600 | 2939.06 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 91851.97 | GGB | 91853.03 | 2939.06 | 2939.06 |  |  |  | 1 | 1 |  |  |  |  | 151410.95 | 2939.06 | 151410.95 | 2939.06 | 10.7463 | [5 empty] | 123.6127 | 2496.0414
14.12.2007 15:00 | 3600 | 2 | 757.99 | GGB | 766.667 | 772.828 | 768.864 | 275.54 | GGB | 11306.5 | GGB | 9.85 | GGB | 1034.05 | GGB | 56.59 | GGB | 180880.12 | GGB | 152937.43 | GNB | 0 | 0 | 2955 | 3600 | 2939.74 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 91893.27 | GGB | 91894.33 | 2939.74 | 2939.74 |  |  |  | 1 | 1 |  |  |  |  | 152937.43 | 2939.74 |  | 2939.74 | 10.8861 | [5 empty] | 124.8879 | 2471.1282
14.12.2007 16:00 | 3600 | 2 | 758.81 | GGB | 767.766 | 773.766 | 769.963 | 275.92 | GGB | 11326.1 | GGB | 9.86 | GGB | 1034.52 | GGB | 56.43 | GGB | 181020.96 | GGB | 153201.14 | GNB | 0 | 0 | 2926 | 3600 | 2910.2 | GGB | 100 | GGB | 41.61 | GGB | 41.61 | GGB | 91934.89 | GGB | 91935.94 | 2910.2 | 2910.2 |  |  |  | 1 | 1 |  |  |  |  | 153201.14 | 2910.2 |  | 2910.2 | 10.7149 | [5 empty] | 123.8461 | 2466.8746
14.12.2007 17:00 | 3600 | 2 | 758.21 | GGB | 766.3 | 772.688 | 767.766 | 275.3 | GGB | 11346.1 | GGB | 9.85 | GGB | 1034.86 | GGB | 56.86 | GGB | 179392.46 | GGB | 151672.77 | GGB | 0 | 0 | 2969 | 3600 | 2953.17 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 91975.99 | GGB | 91977.04 | 2953.17 | 2953.17 |  |  |  | 1 | 1 |  |  |  |  | 151672.77 | 2953.17 | 151672.77 | 2953.17 | 10.8982 | [5 empty] | 124.421 | 2491.7327
14.12.2007 18:00 | 3600 | 2 | 758.08 | GGB | 766.3 | 772.688 | 767.766 | 275.82 | GGB | 11350.8 | GGB | 9.85 | GGB | 1035.16 | GGB | 56.92 | GGB | 179637.84 | GGB | 151895.91 | GGB | 0 | 0 | 2988 | 3600 | 2972.68 | GGB | 100 | GGB | 41.78 | GGB | 41.78 | GGB | 92017.77 | GGB | 92018.82 | 2972.68 | 2972.68 |  |  |  | 1 | 1 |  |  |  |  | 151895.91 | 2972.68 | 151895.91 |  | 10.8075 | [5 empty] | 125.4272 | 2488.0723
14.12.2007 19:00 | 3600 | 2 | 758.63 | GGB | 766.3 | 771.68 | 767.766 | 276.09 | GGB | 11372.8 | GGB | 9.86 | GGB | 1035.81 | GGB | 56.95 | GGB | 179888.72 | GGB | 152190.02 | GGB | 0 | 0 | 2979 | 3600 | 2963.02 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 92058.62 | GGB | 92059.67 | 2963.02 | 2963.02 |  |  |  | 1 | 1 |  |  |  |  | 152190.02 | 2963.02 | 152190.02 | 2963.02 | 11.039 | [5 empty] | 125.2617 | 2483.264
14.12.2007 20:00 | 3600 | 2 | 758.35 | GGB | 765.201 | 771.82 | 767.766 | 276.32 | GGB | 11373.5 | GGB | 9.85 | GGB | 1036.17 | GGB | 56.89 | GGB | 180077.98 | GGB | 152433.68 | GGB | 0 | 0 | 2995 | 3600 | 2979.04 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 92099.1 | GGB | 92100.15 | 2979.04 | 2979.04 |  |  |  | 1 | 1 |  |  |  |  | 152433.68 | 2979.04 | 152433.68 |  | 11.218 | [5 empty] | 126.1406 | 2479.2946
14.12.2007 21:00 | 3600 | 2 | 759.26 | GGB | 766.667 | 773.133 | 768.864 | 276.64 | GGB | 11347 | GGB | 9.87 | GGB | 1036.62 | GGB | 56.63 | GGB | 181162.91 | GGB | 153537.77 | GNB | 0 | 0 | 2939 | 3600 | 2923.49 | GGB | 100 | GGB | 41.52 | GGB | 41.52 | GGB | 92140.62 | GGB | 92141.67 | 2923.49 | 2923.49 |  |  |  | 1 | 1 |  |  |  |  | 153537.77 | 2923.49 |  | 2923.49 | 10.8108 | [5 empty] | 124.685 | 2461.466
14.12.2007 22:00 | 3600 | 2 | 759.24 | GGB | 768.864 | 774.117 | 771.429 | 275.7 | GGB | 11282.6 | GGB | 9.86 | GGB | 1036.9 | GGB | 56.72 | GGB | 179780.88 | GGB | 152367.24 | GGB | 0 | 0 | 2901 | 3600 | 2885.06 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 92181.48 | GGB | 92182.53 | 2885.06 | 2885.06 |  |  |  | 1 | 1 |  |  |  |  | 152367.24 | 2885.06 | 152367.24 | 2885.06 | 10.7584 | [5 empty] | 122.108 | 2480.3757
14.12.2007 23:00 | 3600 | 2 | 759.11 | GGB | 766.667 | 772.898 | 768.864 | 274.29 | GGB | 11309.7 | GGB | 9.86 | GGB | 1037.1 | GGB | 57.54 | GGB | 177824.48 | GGB | 150365.53 | GGB | 0 | 0 | 2918 | 3600 | 2902.25 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 92222.23 | GGB | 92223.28 | 2902.25 | 2902.25 |  |  |  | 1 | 1 |  |  |  |  | 150365.53 | 2902.25 | 150365.53 | 2902.25 | 10.7092 | [5 empty] | 121.2218 | 2513.3952
14.12.2007 24:00 | 3600 | 2 | 758.94 | GGB | 766.667 | 772.875 | 768.864 | 274.31 | GGB | 11295.7 | GGB | 9.85 | GGB | 1037.54 | GGB | 57.63 | GGB | 177848.69 | GGB | 150407.87 | GGB | 0 | 0 | 2935 | 3600 | 2919.67 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 92263.52 | GGB | 92264.57 | 2919.67 | 2919.67 |  |  |  | 1 | 1 |  |  |  |  | 150407.87 | 2919.67 | 150407.87 | 2919.67 | 10.6355 | [5 empty] | 121.9837 | 2512.6877
15.12.2007 01:00 | 3600 | 2 | 759.55 | GGB | 767.766 | 774.07 | 768.864 | 273.89 | GGB | 11298 | GGB | 9.87 | GGB | 1037.63 | GGB | 57.78 | GGB | 177252.31 | GGB | 149846.47 | GGB | 0 | 0 | 2894 | 3600 | 2878.76 | GGB | 100 | GGB | 41.53 | GGB | 41.53 | GGB | 92305.05 | GGB | 92306.1 | 2878.76 | 2878.76 |  |  |  | 1 | 1 |  |  |  |  | 149846.47 | 2878.76 | 149846.47 | 2878.76 | 10.387 | [5 empty] | 119.8256 | 2522.1015
15.12.2007 02:00 | 3600 | 2 | 758.35 | GGB | 766.3 | 772.078 | 768.864 | 274.28 | GGB | 11273.5 | GGB | 9.84 | GGB | 1037.52 | GGB | 57.68 | GGB | 177877.3 | GGB | 150407.52 | GGB | 0 | 0 | 2953 | 3600 | 2937.25 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 92346.09 | GGB | 92347.15 | 2937.25 | 2937.25 |  |  |  | 1 | 1 |  |  |  |  | 150407.52 | 2937.25 | 150407.52 | 2937.25 | 10.7621 | [5 empty] | 122.7179 | 2512.6935
15.12.2007 03:00 | 3600 | 2 | 758.56 | GGB | 764.102 | 771.023 | 766.667 | 275.26 | GGB | 11282.8 | GGB | 9.84 | GGB | 1038.31 | GGB | 57.42 | GGB | 179026.05 | GGB | 151609.67 | GGB | 0 | 0 | 2942 | 3600 | 2926.01 | GGB | 100 | GGB | 41.65 | GGB | 41.65 | GGB | 92387.74 | GGB | 92388.8 | 2926.01 | 2926.01 |  |  |  | 1 | 1 |  |  |  |  | 151609.67 | 2926.01 | 151609.67 | 2926.01 | 10.6509 | [5 empty] | 123.2254 | 2492.7698
15.12.2007 04:00 | 3600 | 2 | 758.83 | GGB | 767.766 | 772.945 | 769.963 | 276.6 | GGB | 11291.5 | GGB | 9.85 | GGB | 1038.64 | GGB | 56.56 | GGB | 180854.81 | GGB | 153607.08 | GNB | 0 | 0 | 2925 | 3600 | 2909.15 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 92428.53 | GGB | 92429.58 | 2909.15 | 2909.15 |  |  |  | 1 | 1 |  |  |  |  | 153607.08 | 2909.15 |  | 2909.15 | 10.958 | [5 empty] | 124.1295 | 2460.3553
15.12.2007 05:00 | 3600 | 2 | 758.96 | GGB | 766.3 | 771.867 | 768.864 | 276.08 | GGB | 11369.1 | GGB | 9.86 | GGB | 1038.79 | GGB | 56.78 | GGB | 179978.94 | GGB | 152785.29 | GNB | 0 | 0 | 2958 | 3600 | 2942.05 | GGB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 92470.4 | GGB | 92471.46 | 2942.05 | 2942.05 |  |  |  | 1 | 1 |  |  |  |  | 152785.29 | 2942.05 |  | 2942.05 | 10.7331 | [5 empty] | 124.8617 | 2473.5889
15.12.2007 06:00 | 3600 | 2 | 758.03 | GGB | 765.201 | 771.68 | 767.766 | 277.41 | GGB | 11406.4 | GGB | 9.84 | GGB | 1039.39 | GGB | 56.76 | GGB | 181264.14 | GGB | 153974.51 | GNB | 0 | 0 | 3034 | 3600 | 3018.21 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 92511.58 | GGB | 92512.64 | 3018.21 | 3018.21 |  |  |  | 1 | 1 |  |  |  |  | 153974.51 | 3018.21 |  |  | 11.2853 | [5 empty] | 129.0909 | 2454.4842
15.12.2007 07:00 | 3600 | 2 | 758.7 | GGB | 765.201 | 771.586 | 767.766 | 278.4 | GGB | 11463.2 | GGB | 9.85 | GGB | 1039.61 | GGB | 56.62 | GGB | 182354.57 | GGB | 154996.68 | GNB | 0 | 0 | 3031 | 3600 | 3015.44 | GGB | 100 | GGB | 42.08 | GGB | 42.08 | GGB | 92553.66 | GGB | 92554.72 | 3015.44 | 3015.44 |  |  |  | 1 | 1 |  |  |  |  | 154996.68 | 3015.44 |  |  | 11.107 | [5 empty] | 129.8287 | 2438.2974
15.12.2007 08:00 | 3600 | 2 | 758.59 | GGB | 766.667 | 772.922 | 768.864 | 279.06 | GGB | 11499.7 | GNB | 9.86 | GGB | 1040.8 | GGB | 56.32 | GGB | 183081.9 | GGB | 155938.76 | GGB | 0 | 0 | 3051 | 3600 | 3035.44 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 92594.78 | GGB | 92595.84 | 3035.44 | 3035.44 |  |  |  | 0 | 1 | [14 empty] | 131.4841 | 2423.5668
15.12.2007 09:00 | 3600 | 2 | 758.21 | GGB | 768.864 | 774.82 | 770.33 | 280.52 | GGB | 11472.2 | GGB | 9.85 | GGB | 1041.06 | GGB | 55.75 | GGB | 185211.05 | GGB | 158063.44 | GNB | 0 | 0 | 3060 | 3600 | 3044 | GGB | 100 | GGB | 42.77 | GGB | 42.77 | GGB | 92637.55 | GGB | 92638.61 | 3044 | 3044 |  |  |  | 1 | 1 |  |  |  |  | 158063.44 | 3044 |  |  | 11.2496 | [5 empty] | 133.6514 | 2390.9893
15.12.2007 10:00 | 3600 | 2 | 759.33 | GGB | 768.864 | 775.242 | 770.696 | 280.53 | GGB | 11533.5 | GNB | 9.87 | GGB | 1041.2 | GGB | 55.59 | GGB | 185332.09 | GGB | 158263.1 | GGB | 0 | 0 | 3023 | 3600 | 3007.35 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 92678.06 | GGB | 92679.12 | 3007.35 | 3007.35 |  |  |  | 0 | 1 | [14 empty] | 132.209 | 2387.9729
15.12.2007 11:00 | 3600 | 2 | 759.02 | GGB | 767.766 | 772.641 | 769.597 | 278.16 | GGB | 11515.3 | GNB | 9.86 | GGB | 1040.5 | GGB | 56.09 | GGB | 183172.13 | GGB | 156077.21 | GGB | 0 | 0 | 3043 | 3600 | 3027.2 | GGB | 100 | GGB | 43.36 | GGB | 43.36 | GGB | 92721.42 | GGB | 92722.48 | 3027.2 | 3027.2 |  |  |  | 0 | 1 | [14 empty] | 131.2436 | 2421.4169
15.12.2007 12:00 | 3600 | 2 | 759.08 | GGB | 767.766 | 773.719 | 770.696 | 277.57 | GGB | 11483 | GGB | 9.86 | GGB | 1040.34 | GGB | 56.3 | GGB | 182268.75 | GGB | 155186.63 | GNB | 0 | 0 | 3024 | 3600 | 3008.24 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 92762.65 | GGB | 92763.71 | 3008.24 | 3008.24 |  |  |  | 1 | 1 |  |  |  |  | 155186.63 | 3008.24 |  |  | 11.3228 | [5 empty] | 129.6774 | 2435.3129
15.12.2007 13:00 | 3600 | 2 | 759.02 | GGB | 768.132 | 773.508 | 770.696 | 276.85 | GGB | 11444.8 | GGB | 9.86 | GGB | 1040.39 | GGB | 56.56 | GGB | 181117.79 | GGB | 154092.04 | GNB | 0 | 0 | 2999 | 3600 | 2983.32 | GGB | 100 | GGB | 42.3 | GGB | 42.3 | GGB | 92804.95 | GGB | 92806.01 | 2983.32 | 2983.32 |  |  |  | 1 | 1 |  |  |  |  | 154092.04 | 2983.32 |  |  | 10.8678 | [5 empty] | 127.6961 | 2452.6121
15.12.2007 14:00 | 3600 | 2 | 759.24 | GGB | 767.033 | 773.555 | 769.597 | 276.06 | GGB | 11410.2 | GGB | 9.86 | GGB | 1039.9 | GGB | 56.68 | GGB | 180449.89 | GGB | 153393.4 | GNB | 0 | 0 | 2969 | 3600 | 2953.66 | GGB | 100 | GGB | 41.92 | GGB | 41.92 | GGB | 92846.87 | GGB | 92847.93 | 2953.66 | 2953.66 |  |  |  | 1 | 1 |  |  |  |  | 153393.4 | 2953.66 |  | 2953.66 | 10.808 | [5 empty] | 125.8533 | 2463.7827
15.12.2007 15:00 | 3600 | 2 | 759.21 | GGB | 767.033 | 772.336 | 769.597 | 275.86 | GGB | 11412 | GGB | 9.86 | GGB | 1039.45 | GGB | 56.5 | GGB | 180448.79 | GGB | 153413.23 | GNB | 0 | 0 | 2971 | 3600 | 2954.95 | GGB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 92888.44 | GGB | 92889.5 | 2954.95 | 2954.95 |  |  |  | 1 | 1 |  |  |  |  | 153413.23 | 2954.95 |  | 2954.95 | 10.9052 | [5 empty] | 125.9246 | 2463.4642
15.12.2007 16:00 | 3600 | 2 | 758.9 | GGB | 767.033 | 772.477 | 768.498 | 275.95 | GGB | 11403.9 | GGB | 9.85 | GGB | 1039.28 | GGB | 56.6 | GGB | 180419.08 | GGB | 153315.76 | GNB | 0 | 0 | 2987 | 3600 | 2971.4 | GGB | 100 | GGB | 42.33 | GGB | 42.33 | GGB | 92930.77 | GGB | 92931.83 | 2971.4 | 2971.4 |  |  |  | 1 | 1 |  |  |  |  | 153315.76 | 2971.4 |  |  | 10.7622 | [5 empty] | 126.5451 | 2465.0303
15.12.2007 17:00 | 3600 | 2 | 759.01 | GGB | 767.033 | 773.602 | 769.597 | 276.28 | GGB | 11414.7 | GGB | 9.86 | GGB | 1039.21 | GGB | 56.49 | GGB | 180829.51 | GGB | 153705.46 | GNB | 0 | 0 | 2991 | 3600 | 2974.91 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 92971.85 | GGB | 92972.92 | 2974.91 | 2974.91 |  |  |  | 1 | 1 |  |  |  |  | 153705.46 | 2974.91 |  |  | 11.1283 | [5 empty] | 127.0166 | 2458.7806
15.12.2007 18:00 | 3600 | 2 | 759.07 | GGB | 767.033 | 772.641 | 769.597 | 276.58 | GGB | 11426 | GGB | 9.86 | GGB | 1038.63 | GGB | 56.59 | GGB | 181072.68 | GGB | 153775.78 | GNB | 0 | 0 | 2995 | 3600 | 2979.78 | GGB | 100 | GGB | 42.54 | GGB | 42.54 | GGB | 93014.39 | GGB | 93015.46 | 2979.78 | 2979.78 |  |  |  | 1 | 1 |  |  |  |  | 153775.78 | 2979.78 |  |  | 10.7715 | [5 empty] | 127.2828 | 2457.6562
15.12.2007 19:00 | 3600 | 2 | 759.18 | GGB | 768.132 | 774.352 | 770.696 | 275.88 | GGB | 11407.3 | GGB | 9.86 | GGB | 1038.52 | GGB | 56.74 | GGB | 180442.19 | GGB | 153154.6 | GNB | 0 | 0 | 2979 | 3600 | 2962.91 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 93055.62 | GGB | 93056.69 | 2962.91 | 2962.91 |  |  |  | 1 | 1 |  |  |  |  | 153154.6 | 2962.91 |  | 2962.91 | 11.0061 | [5 empty] | 126.0509 | 2467.6242
15.12.2007 20:00 | 3600 | 2 | 758.99 | GGB | 767.033 | 772.336 | 768.498 | 275.85 | GGB | 11398 | GGB | 9.86 | GGB | 1038.44 | GGB | 56.77 | GGB | 180268.33 | GGB | 152984.05 | GNB | 0 | 0 | 2984 | 3600 | 2968.58 | GGB | 100 | GGB | 41.84 | GGB | 41.84 | GGB | 93097.46 | GGB | 93098.53 | 2968.58 | 2968.58 |  |  |  | 1 | 1 |  |  |  |  | 152984.05 | 2968.58 |  |  | 10.8543 | [5 empty] | 126.1515 | 2470.3752
15.12.2007 21:00 | 3600 | 2 | 759.66 | GGB | 767.033 | 772.5 | 768.498 | 274.79 | GGB | 11390.4 | GGB | 9.87 | GGB | 1038.14 | GGB | 56.84 | GGB | 179190 | GGB | 151994.11 | GGB | 0 | 0 | 2941 | 3600 | 2925.17 | GGB | 100 | GGB | 41.58 | GGB | 41.58 | GGB | 93139.04 | GGB | 93140.11 | 2925.17 | 2925.17 |  |  |  | 1 | 1 |  |  |  |  | 151994.11 | 2925.17 | 151994.11 | 2925.17 | 10.6928 | [5 empty] | 123.5024 | 2486.4648
15.12.2007 22:00 | 3600 | 2 | 758.64 | GGB | 767.033 | 772.219 | 768.132 | 274.07 | GGB | 11372.8 | GGB | 9.85 | GGB | 1037.92 | GGB | 56.53 | GGB | 179476.09 | GGB | 152345.41 | GGB | 0 | 0 | 2972 | 3600 | 2956.29 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 93179.98 | GGB | 93181.05 | 2956.29 | 2956.29 |  |  |  | 1 | 1 |  |  |  |  | 152345.41 | 2956.29 | 152345.41 | 2956.29 | 11.0009 | [5 empty] | 125.1048 | 2480.7311
15.12.2007 23:00 | 3600 | 2 | 759.22 | GGB | 767.033 | 772.336 | 769.597 | 274.31 | GGB | 11370.9 | GGB | 9.86 | GGB | 1037.53 | GGB | 56.7 | GGB | 178930.32 | GGB | 151746.92 | GGB | 0 | 0 | 2954 | 3600 | 2938.47 | GGB | 100 | GGB | 42.81 | GGB | 42.81 | GGB | 93222.79 | GGB | 93223.86 | 2938.47 | 2938.47 |  |  |  | 1 | 1 |  |  |  |  | 151746.92 | 2938.47 | 151746.92 | 2938.47 | 10.4159 | [5 empty] | 123.8622 | 2490.5151
15.12.2007 24:00 | 3600 | 2 | 759.03 | GGB | 767.033 | 773.344 | 769.597 | 275.13 | GGB | 11316.4 | GGB | 9.85 | GGB | 1037.47 | GGB | 56.14 | GGB | 180262.83 | GGB | 153129.94 | GNB | 0 | 0 | 2929 | 3600 | 2913.25 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 93263.6 | GGB | 93264.67 | 2913.25 | 2913.25 |  |  |  | 1 | 1 |  |  |  |  | 153129.94 | 2913.25 |  | 2913.25 | 10.9313 | [5 empty] | 123.9183 | 2468.0216
16.12.2007 01:00 | 3600 | 2 | 759.79 | GGB | 767.033 | 771.984 | 768.498 | 273.49 | GGB | 11339.4 | GGB | 9.87 | GGB | 1036.6 | GGB | 56.75 | GGB | 178084.16 | GGB | 150872.09 | GGB | 0 | 0 | 2909 | 3600 | 2893.86 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 93305.07 | GGB | 93306.14 | 2893.86 | 2893.86 |  |  |  | 1 | 1 |  |  |  |  | 150872.09 | 2893.86 | 150872.09 | 2893.86 | 10.5282 | [5 empty] | 121.2785 | 2504.9564
16.12.2007 02:00 | 3600 | 2 | 759.46 | GGB | 767.033 | 772.992 | 769.597 | 272.66 | GGB | 11305.9 | GGB | 9.86 | GGB | 1036.28 | GGB | 56.83 | GGB | 177112.57 | GGB | 149966.81 | GGB | 0 | 0 | 2912 | 3600 | 2895.97 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 93346.62 | GGB | 93347.7 | 2895.97 | 2895.97 |  |  |  | 1 | 1 |  |  |  |  | 149966.81 | 2895.97 | 149966.81 | 2895.97 | 10.4499 | [5 empty] | 120.6387 | 2520.0776
16.12.2007 03:00 | 3600 | 2 | 759.1 | GGB | 765.934 | 771.984 | 768.498 | 272.31 | GGB | 11276.3 | GGB | 9.86 | GGB | 1035.84 | GGB | 57.01 | GGB | 176460.06 | GGB | 149266.58 | GGB | 0 | 0 | 2912 | 3600 | 2896.35 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 93387.69 | GGB | 93388.77 | 2896.35 | 2896.35 |  |  |  | 1 | 1 |  |  |  |  | 149266.58 | 2896.35 | 149266.58 | 2896.35 | 10.5266 | [5 empty] | 120.0912 | 2531.8996
16.12.2007 04:00 | 3600 | 2 | 758.74 | GGB | 765.934 | 771.563 | 768.132 | 272.65 | GGB | 11242.6 | GGB | 9.85 | GGB | 1035.64 | GGB | 56.95 | GGB | 176861.69 | GGB | 149604.11 | GGB | 0 | 0 | 2922 | 3600 | 2906.78 | GGB | 100 | GGB | 41.62 | GGB | 41.62 | GGB | 93429.31 | GGB | 93430.39 | 2906.78 | 2906.78 |  |  |  | 1 | 1 |  |  |  |  | 149604.11 | 2906.78 | 149604.11 | 2906.78 | 10.4485 | [5 empty] | 120.7962 | 2526.1873
16.12.2007 05:00 | 3600 | 2 | 759.87 | GGB | 767.033 | 773.766 | 769.597 | 272.39 | GGB | 11250.9 | GGB | 9.87 | GGB | 1035.5 | GGB | 57.59 | GGB | 176489.77 | GGB | 148983.22 | GGB | 0 | 0 | 2858 | 3600 | 2842.67 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 93469.65 | GGB | 93470.73 | 2842.67 | 2842.67 |  |  |  | 1 | 1 |  |  |  |  | 148983.22 | 2842.67 | 148983.22 | 2842.67 | 10.4985 | [5 empty] | 117.6417 | 2536.7152
16.12.2007 06:00 | 3600 | 2 | 759.43 | GGB | 767.033 | 772.664 | 768.498 | 271.33 | GGB | 11220.6 | GGB | 9.86 | GGB | 1035.03 | GGB | 58.09 | GGB | 174877.78 | GGB | 147333.72 | GGB | 0 | 0 | 2891 | 3600 | 2874.99 | GGB | 100 | GGB | 41.94 | GGB | 41.94 | GGB | 93511.59 | GGB | 93512.67 | 2874.99 | 2874.99 |  |  |  | 1 | 1 |  |  |  |  | 147333.72 | 2874.99 | 147333.72 | 2874.99 | 10.0997 | [5 empty] | 117.6619 | 2565.1154
16.12.2007 07:00 | 3600 | 2 | 758.54 | GGB | 764.835 | 770.484 | 767.033 | 272.24 | GGB | 11199.2 | GGB | 9.84 | GGB | 1035.17 | GGB | 57.78 | GGB | 175715.14 | GGB | 148194.28 | GGB | 0 | 0 | 2921 | 3600 | 2905.2 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 93552.02 | GGB | 93553.1 | 2905.2 | 2905.2 |  |  |  | 1 | 1 |  |  |  |  | 148194.28 | 2905.2 | 148194.28 | 2905.2 | 10.6489 | [5 empty] | 119.5928 | 2550.2199
16.12.2007 08:00 | 3600 | 2 | 759.39 | GGB | 764.835 | 771.75 | 768.498 | 273 | GGB | 11255.5 | GGB | 9.86 | GGB | 1035.55 | GGB | 57.68 | GGB | 176851.79 | GGB | 149253.16 | GGB | 0 | 0 | 2897 | 3600 | 2880.94 | GGB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 93592.99 | GGB | 93594.08 | 2880.94 | 2880.94 |  |  |  | 1 | 1 |  |  |  |  | 149253.16 | 2880.94 | 149253.16 | 2880.94 | 10.4927 | [5 empty] | 119.4415 | 2532.1273
16.12.2007 09:00 | 3600 | 2 | 759.13 | GGB | 766.3 | 772.734 | 768.498 | 272.9 | GGB | 11244 | GGB | 9.85 | GGB | 1035.15 | GGB | 58.26 | GGB | 176282.91 | GGB | 148457.71 | GGB | 0 | 0 | 2918 | 3600 | 2902.09 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 93634.26 | GGB | 93635.34 | 2902.09 | 2902.09 |  |  |  | 1 | 1 |  |  |  |  | 148457.71 | 2902.09 | 148457.71 | 2902.09 | 10.442 | [5 empty] | 119.6771 | 2545.6947
16.12.2007 10:00 | 3600 | 2 | 759.14 | GGB | 766.667 | 772.711 | 768.498 | 274.53 | GGB | 11197.1 | GGB | 9.85 | GGB | 1035.74 | GGB | 57.67 | GGB | 178480.28 | GGB | 150662.28 | GGB | 0 | 0 | 2881 | 3600 | 2865.61 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 93674.8 | GGB | 93675.88 | 2865.61 | 2865.61 |  |  |  | 1 | 1 |  |  |  |  | 150662.28 | 2865.61 | 150662.28 | 2865.61 | 10.6497 | [5 empty] | 119.9276 | 2508.4447
16.12.2007 11:00 | 3600 | 2 | 759.65 | GGB | 767.766 | 774 | 769.597 | 274.17 | GGB | 11235.4 | GGB | 9.86 | GGB | 1035.79 | GGB | 57.61 | GGB | 177806.88 | GGB | 150124.84 | GGB | 0 | 0 | 2873 | 3600 | 2857.02 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 93716.03 | GGB | 93717.11 | 2857.02 | 2857.02 |  |  |  | 1 | 1 |  |  |  |  | 150124.84 | 2857.02 | 150124.84 | 2857.02 | 10.4029 | [5 empty] | 119.1416 | 2517.4248
16.12.2007 12:00 | 3600 | 2 | 759.47 | GGB | 766.667 | 773.133 | 769.597 | 273.13 | GGB | 11256.2 | GGB | 9.86 | GGB | 1035.87 | GGB | 58.17 | GGB | 176482.07 | GGB | 148767.06 | GGB | 0 | 0 | 2893 | 3600 | 2877.75 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 93756.79 | GGB | 93757.87 | 2877.75 | 2877.75 |  |  |  | 1 | 1 |  |  |  |  | 148767.06 | 2877.75 | 148767.06 | 2877.75 | 10.5033 | [5 empty] | 118.9207 | 2540.4011
16.12.2007 13:00 | 3600 | 2 | 759.24 | GGB | 765.201 | 770.063 | 767.033 | 272.95 | GGB | 11245.2 | GGB | 9.85 | GGB | 1036.08 | GGB | 58.21 | GGB | 176389.64 | GGB | 148703.04 | GGB | 0 | 0 | 2899 | 3600 | 2883.26 | GGB | 100 | GGB | 41.43 | GGB | 41.43 | GGB | 93798.22 | GGB | 93799.3 | 2883.26 | 2883.26 |  |  |  | 1 | 1 |  |  |  |  | 148703.04 | 2883.26 | 148703.04 | 2883.26 | 10.3488 | [5 empty] | 119.0971 | 2541.4948
16.12.2007 14:00 | 3600 | 2 | 759.36 | GGB | 766.3 | 771.539 | 768.498 | 273.41 | GGB | 11270.1 | GGB | 9.86 | GGB | 1035.7 | GGB | 57.99 | GGB | 177069.65 | GGB | 149319.97 | GGB | 0 | 0 | 2913 | 3600 | 2897.4 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 93838.87 | GGB | 93839.96 | 2897.4 | 2897.4 |  |  |  | 1 | 1 |  |  |  |  | 149319.97 | 2897.4 | 149319.97 | 2897.4 | 10.6404 | [5 empty] | 120.1777 | 2530.9943
16.12.2007 15:00 | 3600 | 2 | 759.47 | GGB | 766.667 | 772.805 | 768.498 | 273.41 | GGB | 11273.4 | GGB | 9.86 | GGB | 1035.71 | GGB | 57.98 | GGB | 177093.86 | GGB | 149346.65 | GGB | 0 | 0 | 2908 | 3600 | 2892.32 | GGB | 100 | GGB | 41.44 | GGB | 41.44 | GGB | 93880.32 | GGB | 93881.4 | 2892.32 | 2892.32 |  |  |  | 1 | 1 |  |  |  |  | 149346.65 | 2892.32 | 149346.65 | 2892.32 | 10.4237 | [5 empty] | 119.9884 | 2530.5422
16.12.2007 16:00 | 3600 | 2 | 759.04 | GGB | 765.201 | 771.984 | 768.498 | 274.89 | GGB | 11230.3 | GGB | 9.85 | GGB | 1036.01 | GGB | 57.34 | GGB | 178909.42 | GGB | 151212.48 | GGB | 0 | 0 | 2895 | 3600 | 2879.89 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 93921.57 | GGB | 93922.66 | 2879.89 | 2879.89 |  |  |  | 1 | 1 |  |  |  |  | 151212.48 | 2879.89 | 151212.48 | 2879.89 | 10.5544 | [5 empty] | 120.9654 | 2499.3175
16.12.2007 17:00 | 3600 | 2 | 759.51 | GGB | 765.201 | 771.563 | 767.033 | 274.46 | GGB | 11270.4 | GGB | 9.86 | GGB | 1036.58 | GGB | 57.41 | GGB | 178316.33 | GGB | 150762.35 | GGB | 0 | 0 | 2892 | 3600 | 2876.18 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 93962.15 | GGB | 93963.24 | 2876.18 | 2876.18 |  |  |  | 1 | 1 |  |  |  |  | 150762.35 | 2876.18 | 150762.35 | 2876.18 | 10.6856 | [5 empty] | 120.4499 | 2506.7797
16.12.2007 18:00 | 3600 | 2 | 759.34 | GGB | 766.667 | 772.688 | 768.498 | 274.12 | GGB | 11307.3 | GGB | 9.86 | GGB | 1036.95 | GGB | 57.77 | GGB | 177855.29 | GGB | 150261.54 | GGB | 0 | 0 | 2922 | 3600 | 2906.58 | GGB | 100 | GGB | 41.81 | GGB | 41.81 | GGB | 94003.96 | GGB | 94005.05 | 2906.58 | 2906.58 |  |  |  | 1 | 1 |  |  |  |  | 150261.54 | 2906.58 | 150261.54 | 2906.58 | 10.446 | [5 empty] | 121.3187 | 2515.1346
16.12.2007 19:00 | 3600 | 2 | 758.79 | GGB | 768.864 | 774.797 | 770.696 | 274.5 | GGB | 11312.2 | GGB | 9.85 | GGB | 1037.18 | GGB | 57.48 | GGB | 178359.25 | GGB | 150856.39 | GGB | 0 | 0 | 2957 | 3600 | 2941.27 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 94044.77 | GGB | 94045.85 | 2941.27 | 2941.27 |  |  |  | 1 | 1 |  |  |  |  | 150856.39 | 2941.27 | 150856.39 | 2941.27 | 10.8752 | [5 empty] | 123.2526 | 2505.217
16.12.2007 20:00 | 3600 | 2 | 758.93 | GGB | 765.201 | 771.586 | 767.033 | 275.33 | GGB | 11325 | GGB | 9.85 | GGB | 1037.59 | GGB | 57.17 | GGB | 179173.5 | GGB | 151744.1 | GGB | 0 | 0 | 2954 | 3600 | 2938.79 | GGB | 100 | GGB | 41.76 | GGB | 41.76 | GGB | 94086.53 | GGB | 94087.61 | 2938.79 | 2938.79 |  |  |  | 1 | 1 |  |  |  |  | 151744.1 | 2938.79 | 151744.1 | 2938.79 | 10.6787 | [5 empty] | 123.8733 | 2490.5614
16.12.2007 21:00 | 3600 | 2 | 759.91 | GGB | 766.667 | 773.508 | 768.498 | 275.95 | GGB | 11359 | GGB | 9.87 | GGB | 1037.87 | GGB | 56.92 | GGB | 180227.62 | GGB | 152796.66 | GNB | 0 | 0 | 2914 | 3600 | 2898.39 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 94127.44 | GGB | 94128.53 | 2898.39 | 2898.39 |  |  |  | 1 | 1 |  |  |  |  | 152796.66 | 2898.39 |  | 2898.39 | 10.8227 | [5 empty] | 123.0179 | 2473.4049
16.12.2007 22:00 | 3600 | 2 | 758.47 | GGB | 767.766 | 773.813 | 769.597 | 274.7 | GGB | 11354.9 | GGB | 9.84 | GGB | 1037.89 | GGB | 56.91 | GGB | 179566.32 | GGB | 152241.53 | GGB | 0 | 0 | 2990 | 3600 | 2974.81 | GGB | 100 | GGB | 41.43 | GGB | 41.43 | GGB | 94168.87 | GGB | 94169.96 | 2974.81 | 2974.81 |  |  |  | 1 | 1 |  |  |  |  | 152241.53 | 2974.81 | 152241.53 |  | 10.9314 | [5 empty] | 125.8027 | 2482.4238
16.12.2007 23:00 | 3600 | 2 | 759.48 | GGB | 767.766 | 774.422 | 769.597 | 275.01 | GGB | 11378.1 | GGB | 9.86 | GGB | 1038.09 | GGB | 57.17 | GGB | 179186.7 | GGB | 151827.83 | GGB | 0 | 0 | 2948 | 3600 | 2931.94 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 94210.02 | GGB | 94211.11 | 2931.94 | 2931.94 |  |  |  | 1 | 1 |  |  |  |  | 151827.83 | 2931.94 | 151827.83 | 2931.94 | 10.8177 | [5 empty] | 123.6528 | 2489.1879
16.12.2007 24:00 | 3600 | 2 | 759.33 | GGB | 766.3 | 772.359 | 769.597 | 274.91 | GGB | 11367 | GGB | 9.86 | GGB | 1038.3 | GGB | 57.27 | GGB | 179054.66 | GGB | 151703.14 | GGB | 0 | 0 | 2956 | 3600 | 2939.98 | GGB | 100 | GGB | 41.8 | GGB | 41.8 | GGB | 94251.83 | GGB | 94252.91 | 2939.98 | 2939.98 |  |  |  | 1 | 1 |  |  |  |  | 151703.14 | 2939.98 | 151703.14 | 2939.98 | 10.67 | [5 empty] | 123.8901 | 2491.2339
17.12.2007 01:00 | 3600 | 2 | 759.11 | GGB | 765.201 | 770.789 | 768.132 | 274.52 | GGB | 11358.5 | GGB | 9.85 | GGB | 1038.39 | GGB | 57.13 | GGB | 179092.07 | GGB | 151811.1 | GGB | 0 | 0 | 2960 | 3600 | 2944.41 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 94293.38 | GGB | 94294.47 | 2944.41 | 2944.41 |  |  |  | 1 | 1 |  |  |  |  | 151811.1 | 2944.41 | 151811.1 | 2944.41 | 10.7554 | [5 empty] | 124.165 | 2489.4622
17.12.2007 02:00 | 3600 | 2 | 759.24 | GGB | 768.864 | 774.797 | 770.696 | 276.16 | GGB | 11341.7 | GGB | 9.86 | GGB | 1038.26 | GGB | 56.44 | GGB | 180830.61 | GGB | 153586.85 | GNB | 0 | 0 | 2948 | 3600 | 2932.72 | GGB | 100 | GGB | 41.71 | GGB | 41.71 | GGB | 94335.1 | GGB | 94336.18 | 2932.72 | 2932.72 |  |  |  | 1 | 1 |  |  |  |  | 153586.85 | 2932.72 |  | 2932.72 | 10.799 | [5 empty] | 125.1187 | 2460.6794
17.12.2007 03:00 | 3600 | 2 | 759.5 | GGB | 768.864 | 774.703 | 771.795 | 276.26 | GGB | 11335 | GGB | 9.86 | GGB | 1038.6 | GGB | 56.1 | GGB | 181155.21 | GGB | 154071.71 | GNB | 0 | 0 | 2921 | 3600 | 2905.88 | GGB | 100 | GGB | 41.44 | GGB | 41.44 | GGB | 94376.53 | GGB | 94377.62 | 2905.88 | 2905.88 |  |  |  | 1 | 1 |  |  |  |  | 154071.71 | 2905.88 |  | 2905.88 | 10.8039 | [5 empty] | 124.365 | 2452.9357
17.12.2007 04:00 | 3600 | 2 | 759.36 | GGB | 767.766 | 772.266 | 769.597 | 276.15 | GGB | 11320.3 | GGB | 9.85 | GGB | 1038.56 | GGB | 56.14 | GGB | 181083.68 | GGB | 153987.92 | GNB | 0 | 0 | 2931 | 3600 | 2915.38 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 94417.8 | GGB | 94418.88 | 2915.38 | 2915.38 |  |  |  | 1 | 1 |  |  |  |  | 153987.92 | 2915.38 |  | 2915.38 | 10.8806 | [5 empty] | 124.7037 | 2454.2704
17.12.2007 05:00 | 3600 | 2 | 759.39 | GGB | 766.667 | 772.969 | 769.597 | 276.28 | GGB | 11326.2 | GGB | 9.85 | GGB | 1038.6 | GGB | 56.09 | GGB | 180925.24 | GGB | 153882.89 | GNB | 0 | 0 | 2927 | 3600 | 2911.23 | GGB | 100 | GGB | 41.66 | GGB | 41.66 | GGB | 94459.46 | GGB | 94460.54 | 2911.23 | 2911.23 |  |  |  | 1 | 1 |  |  |  |  | 153882.89 | 2911.23 |  | 2911.23 | 10.7534 | [5 empty] | 124.4412 | 2455.9456
17.12.2007 06:00 | 3600 | 2 | 759.57 | GGB | 768.864 | 774.047 | 770.696 | 276.28 | GGB | 11332.9 | GGB | 9.86 | GGB | 1038.59 | GGB | 56.13 | GGB | 180716.17 | GGB | 153682.25 | GNB | 0 | 0 | 2920 | 3600 | 2904.68 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 94500.48 | GGB | 94501.57 | 2904.68 | 2904.68 |  |  |  | 1 | 1 |  |  |  |  | 153682.25 | 2904.68 |  | 2904.68 | 10.8798 | [5 empty] | 123.9994 | 2459.1519
17.12.2007 07:00 | 3600 | 2 | 759.33 | GGB | 767.766 | 773.438 | 770.696 | 275.23 | GGB | 11334.2 | GGB | 9.86 | GGB | 1038.5 | GGB | 56.62 | GGB | 179300.04 | GGB | 152240.27 | GGB | 0 | 0 | 2941 | 3600 | 2925.42 | GGB | 100 | GGB | 41.61 | GGB | 41.61 | GGB | 94542.09 | GGB | 94543.18 | 2925.42 | 2925.42 |  |  |  | 1 | 1 |  |  |  |  | 152240.27 | 2925.42 | 152240.27 | 2925.42 | 10.7034 | [5 empty] | 123.713 | 2482.4444
17.12.2007 08:00 | 3600 | 2 | 759.84 | GGB | 768.864 | 774.281 | 770.696 | 275.88 | GGB | 11310.2 | GGB | 9.86 | GGB | 1038.78 | GGB | 56.38 | GGB | 179890.92 | GGB | 152892.53 | GNB | 0 | 0 | 2906 | 3600 | 2890.69 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 94583.2 | GGB | 94584.29 | 2890.69 | 2890.69 |  |  |  | 1 | 1 |  |  |  |  | 152892.53 | 2890.69 |  | 2890.69 | 10.7508 | [5 empty] | 122.768 | 2471.8539
17.12.2007 09:00 | 3600 | 2 | 760.03 | GGB | 766.667 | 772.102 | 769.597 | 274.3 | GGB | 11319.2 | GGB | 9.87 | GGB | 1038.53 | GGB | 56.93 | GGB | 177721.05 | GGB | 150761.63 | GGB | 0 | 0 | 2900 | 3600 | 2883.97 | GGB | 100 | GGB | 41.34 | GGB | 41.34 | GGB | 94624.54 | GGB | 94625.63 | 2883.97 | 2883.97 |  |  |  | 1 | 1 |  |  |  |  | 150761.63 | 2883.97 | 150761.63 | 2883.97 | 10.5175 | [5 empty] | 120.7756 | 2506.7917
17.12.2007 10:00 | 3600 | 2 | 759.44 | GGB | 767.766 | 773.227 | 769.597 | 273.5 | GGB | 11299.1 | GGB | 9.86 | GGB | 1037.65 | GGB | 57.07 | GGB | 176487.57 | GGB | 149523.28 | GGB | 0 | 0 | 2928 | 3600 | 2911.91 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 94666.06 | GGB | 94667.14 | 2911.91 | 2911.91 |  |  |  | 1 | 1 |  |  |  |  | 149523.28 | 2911.91 | 149523.28 | 2911.91 | 10.489 | [5 empty] | 120.944 | 2527.5529
17.12.2007 11:00 | 3600 | 2 | 759.21 | GGB | 767.766 | 774.117 | 770.696 | 274.58 | GGB | 11242.5 | GGB | 9.85 | GGB | 1037.64 | GGB | 56.59 | GGB | 177966.43 | GGB | 150995.03 | GGB | 0 | 0 | 2912 | 3600 | 2896.17 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 94707.29 | GGB | 94708.38 | 2896.17 | 2896.17 |  |  |  | 1 | 1 |  |  |  |  | 150995.03 | 2896.17 | 150995.03 | 2896.17 | 10.604 | [5 empty] | 121.4742 | 2502.9168
17.12.2007 12:00 | 3600 | 2 | 759.97 | GGB | 766.667 | 773.016 | 769.597 | 274.41 | GGB | 11233.2 | GGB | 9.86 | GGB | 1036.83 | GGB | 56.54 | GGB | 177953.22 | GGB | 150888.64 | GGB | 0 | 0 | 2862 | 3600 | 2846.62 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 94748.15 | GGB | 94749.24 | 2846.62 | 2846.62 |  |  |  | 1 | 1 |  |  |  |  | 150888.64 | 2846.62 | 150888.64 | 2846.62 | 10.5121 | [5 empty] | 119.3118 | 2504.6816
17.12.2007 13:00 | 3600 | 2 | 760.08 | GGB | 766.667 | 773.086 | 768.498 | 273.4 | GGB | 11180.5 | GGB | 9.87 | GGB | 1036.57 | GGB | 57 | GGB | 176148.67 | GGB | 149112.56 | GGB | 0 | 0 | 2839 | 3600 | 2823.57 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 94789.1 | GGB | 94790.18 | 2823.57 | 2823.57 |  |  |  | 1 | 1 |  |  |  |  | 149112.56 | 2823.57 | 149112.56 | 2823.57 | 10.2841 | [5 empty] | 116.9527 | 2534.5149
17.12.2007 14:00 | 3600 | 2 | 759.62 | GGB | 768.864 | 774.773 | 770.696 | 273.46 | GGB | 11171.2 | GGB | 9.86 | GGB | 1036.34 | GGB | 56.98 | GGB | 176143.17 | GGB | 149084.95 | GGB | 0 | 0 | 2859 | 3600 | 2843.59 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 94829.88 | GGB | 94830.97 | 2843.59 | 2843.59 |  |  |  | 1 | 1 |  |  |  |  | 149084.95 | 2843.59 | 149084.95 | 2843.59 | 10.3931 | [5 empty] | 117.7601 | 2534.9842
17.12.2007 15:00 | 3600 | 2 | 760.06 | GGB | 768.864 | 774.586 | 771.795 | 271.65 | GGB | 11203.2 | GGB | 9.87 | GGB | 1035.95 | GGB | 57.73 | GGB | 173951.29 | GGB | 146840.1 | GGB | 0 | 0 | 2854 | 3600 | 2838.14 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 94871.03 | GGB | 94872.12 | 2838.14 | 2838.14 |  |  |  | 1 | 1 |  |  |  |  | 146840.1 | 2838.14 | 146840.1 | 2838.14 | 10.1276 | [5 empty] | 115.7647 | 2573.7384
17.12.2007 16:00 | 3600 | 2 | 759.46 | GGB | 765.201 | 771.375 | 768.498 | 270.57 | GGB | 11153.2 | GGB | 9.85 | GGB | 1035.18 | GGB | 58.39 | GGB | 172789.34 | GGB | 145460.37 | GGB | 0 | 0 | 2868 | 3600 | 2852.15 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 94911.9 | GGB | 94912.99 | 2852.15 | 2852.15 |  |  |  | 1 | 1 |  |  |  |  | 145460.37 | 2852.15 | 145460.37 | 2852.15 | 10.1511 | [5 empty] | 115.243 | 2598.151
17.12.2007 17:00 | 3600 | 2 | 759.22 | GGB | 766.3 | 772.688 | 768.498 | 271.21 | GGB | 11134.3 | GGB | 9.85 | GGB | 1035.01 | GGB | 58.01 | GGB | 173846.76 | GGB | 146497.56 | GGB | 0 | 0 | 2870 | 3600 | 2854.59 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 94952.82 | GGB | 94953.91 | 2854.59 | 2854.59 |  |  |  | 1 | 1 |  |  |  |  | 146497.56 | 2854.59 | 146497.56 | 2854.59 | 10.2197 | [5 empty] | 116.164 | 2579.7563
17.12.2007 18:00 | 3600 | 2 | 759.62 | GGB | 766.667 | 773.953 | 769.597 | 272.11 | GGB | 11123.5 | GGB | 9.85 | GGB | 1034.99 | GGB | 57.35 | GGB | 175172.67 | GGB | 147905.42 | GGB | 0 | 0 | 2833 | 3600 | 2817.89 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 94993.49 | GGB | 94994.59 | 2817.89 | 2817.89 |  |  |  | 1 | 1 |  |  |  |  | 147905.42 | 2817.89 | 147905.42 | 2817.89 | 10.2454 | [5 empty] | 115.7726 | 2555.2005
17.12.2007 19:00 | 3600 | 2 | 759.9 | GGB | 767.766 | 773.086 | 769.597 | 271.87 | GGB | 11132 | GGB | 9.86 | GGB | 1034.88 | GGB | 57.24 | GGB | 175034.03 | GGB | 147818.55 | GGB | 0 | 0 | 2815 | 3600 | 2799.81 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 95034.37 | GGB | 95035.47 | 2799.81 | 2799.81 |  |  |  | 1 | 1 |  |  |  |  | 147818.55 | 2799.81 | 147818.55 | 2799.81 | 10.1239 | [5 empty] | 114.9622 | 2556.7021
17.12.2007 20:00 | 3600 | 2 | 759.98 | GGB | 767.766 | 774.234 | 770.696 | 271.58 | GGB | 11122 | GGB | 9.86 | GGB | 1034.72 | GGB | 57.23 | GGB | 174762.24 | GGB | 147574.82 | GGB | 0 | 0 | 2808 | 3600 | 2792.87 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 95074.95 | GGB | 95076.05 | 2792.87 | 2792.87 |  |  |  | 1 | 1 |  |  |  |  | 147574.82 | 2792.87 | 147574.82 | 2792.87 | 10.1567 | [5 empty] | 114.4881 | 2560.9247
17.12.2007 21:00 | 3600 | 2 | 759.62 | GGB | 766.3 | 773.016 | 769.597 | 271.66 | GGB | 11103.8 | GGB | 9.85 | GGB | 1034.33 | GGB | 57.12 | GGB | 174787.55 | GGB | 147587.97 | GGB | 0 | 0 | 2820 | 3600 | 2804.95 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 95115.67 | GGB | 95116.77 | 2804.95 | 2804.95 |  |  |  | 1 | 1 |  |  |  |  | 147587.97 | 2804.95 | 147587.97 | 2804.95 | 10.1664 | [5 empty] | 114.9936 | 2560.6965
17.12.2007 22:00 | 3600 | 2 | 759.82 | GGB | 766.667 | 772.898 | 768.498 | 271.8 | GGB | 11116.3 | GGB | 9.86 | GGB | 1034.52 | GGB | 57.17 | GGB | 174915.19 | GGB | 147702.52 | GGB | 0 | 0 | 2812 | 3600 | 2796.74 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 95155.92 | GGB | 95157.03 | 2796.74 | 2796.74 |  |  |  | 1 | 1 |  |  |  |  | 147702.52 | 2796.74 | 147702.52 | 2796.74 | 10.2604 | [5 empty] | 114.746 | 2558.7106
17.12.2007 23:00 | 3600 | 2 | 760.27 | GGB | 768.864 | 775.055 | 770.696 | 270.76 | GGB | 11161.6 | GGB | 9.88 | GGB | 1034.05 | GGB | 57.51 | GGB | 174407.93 | GGB | 147052.82 | GGB | 0 | 0 | 2807 | 3600 | 2791.03 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 95194.14 | GGB | 95195.25 | 2791.03 | 2791.03 |  |  |  | 1 | 1 |  |  |  |  | 147052.82 | 2791.03 | 147052.82 | 2791.03 | 10.7386 | [5 empty] | 114.008 | 2570.0153
17.12.2007 24:00 | 3600 | 2 | 759.38 | GGB | 767.766 | 772.219 | 769.597 | 269.87 | GGB | 11134.7 | GGB | 9.85 | GGB | 1033.58 | GGB | 58.4 | GGB | 172659.5 | GGB | 145121.68 | GGB | 0 | 0 | 2858 | 3600 | 2842.19 | GGB | 100 | GGB | 42.55 | GGB | 42.55 | GGB | 95236.69 | GGB | 95237.8 | 2842.19 | 2842.19 |  |  |  | 1 | 1 |  |  |  |  | 145121.68 | 2842.19 | 145121.68 | 2842.19 | 9.6936 | [5 empty] | 114.5732 | 2604.2146
18.12.2007 01:00 | 3600 | 2 | 759.6 | GGB | 767.766 | 773.273 | 768.864 | 269.97 | GGB | 11138.7 | GGB | 9.86 | GGB | 1033.38 | GGB | 58.56 | GGB | 172506.55 | GGB | 144895.72 | GGB | 0 | 0 | 2855 | 3600 | 2839.46 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 95277.48 | GGB | 95278.58 | 2839.46 | 2839.46 |  |  |  | 1 | 1 |  |  |  |  | 144895.72 | 2839.46 | 144895.72 | 2839.46 | 10.0889 | [5 empty] | 114.2849 | 2608.2758
18.12.2007 02:00 | 3600 | 2 | 759.5 | GGB | 767.766 | 774.234 | 769.963 | 269.99 | GGB | 11137.8 | GGB | 9.85 | GGB | 1033.73 | GGB | 58.39 | GGB | 172557.17 | GGB | 145062.19 | GGB | 0 | 0 | 2859 | 3600 | 2843.44 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 95318.4 | GGB | 95319.51 | 2843.44 | 2843.44 |  |  |  | 1 | 1 |  |  |  |  | 145062.19 | 2843.44 | 145062.19 | 2843.44 | 10.0776 | [5 empty] | 114.5766 | 2605.2826
18.12.2007 03:00 | 3600 | 2 | 759.62 | GGB | 767.766 | 773.18 | 769.963 | 269.86 | GGB | 11145 | GGB | 9.86 | GGB | 1033.64 | GGB | 58.28 | GGB | 172568.17 | GGB | 145104.51 | GGB | 0 | 0 | 2846 | 3600 | 2830.75 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 95359.21 | GGB | 95360.32 | 2830.75 | 2830.75 |  |  |  | 1 | 1 |  |  |  |  | 145104.51 | 2830.75 | 145104.51 | 2830.75 | 10.065 | [5 empty] | 114.0985 | 2604.5228
18.12.2007 04:00 | 3600 | 2 | 759.7 | GGB | 766.667 | 773.063 | 769.963 | 269.7 | GGB | 11138.6 | GGB | 9.86 | GGB | 1033.37 | GGB | 58.23 | GGB | 172298.59 | GGB | 144862.72 | GGB | 0 | 0 | 2843 | 3600 | 2827.07 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 95399.76 | GGB | 95400.87 | 2827.07 | 2827.07 |  |  |  | 1 | 1 |  |  |  |  | 144862.72 | 2827.07 | 144862.72 | 2827.07 | 10.0996 | [5 empty] | 113.7603 | 2608.87
18.12.2007 05:00 | 3600 | 2 | 759.72 | GGB | 766.667 | 773.156 | 768.864 | 269.75 | GGB | 11137.1 | GGB | 9.86 | GGB | 1033.01 | GGB | 58.22 | GGB | 172342.6 | GGB | 144857.32 | GGB | 0 | 0 | 2842 | 3600 | 2826.76 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 95440.88 | GGB | 95442 | 2826.76 | 2826.76 |  |  |  | 1 | 1 |  |  |  |  | 144857.32 | 2826.76 | 144857.32 | 2826.76 | 9.9557 | [5 empty] | 113.7436 | 2608.9672
18.12.2007 06:00 | 3600 | 2 | 759.71 | GGB | 767.766 | 773.344 | 769.963 | 269.38 | GGB | 11124.4 | GGB | 9.86 | GGB | 1033.03 | GGB | 58.43 | GGB | 171940.98 | GGB | 144429.54 | GGB | 0 | 0 | 2839 | 3600 | 2823.42 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 95481.05 | GGB | 95482.17 | 2823.42 | 2823.42 |  |  |  | 1 | 1 |  |  |  |  | 144429.54 | 2823.42 | 144429.54 | 2823.42 | 10.1515 | [5 empty] | 113.2737 | 2616.6946
18.12.2007 07:00 | 3600 | 2 | 759.69 | GGB | 766.667 | 773.32 | 768.864 | 269.34 | GGB | 11122.5 | GGB | 9.86 | GGB | 1033.17 | GGB | 58.55 | GGB | 172115.93 | GGB | 144543.58 | GGB | 0 | 0 | 2837 | 3600 | 2821.95 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 95522.24 | GGB | 95523.36 | 2821.95 | 2821.95 |  |  |  | 1 | 1 |  |  |  |  | 144543.58 | 2821.95 | 144543.58 | 2821.95 | 9.9028 | [5 empty] | 113.3041 | 2614.6301
18.12.2007 08:00 | 3600 | 2 | 759.47 | GGB | 766.667 | 772.266 | 768.864 | 269.91 | GGB | 11106.3 | GGB | 9.85 | GGB | 1032.96 | GGB | 58.38 | GGB | 172889.47 | GGB | 145237.08 | GGB | 0 | 0 | 2842 | 3600 | 2826.78 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 95562.68 | GGB | 95563.79 | 2826.78 | 2826.78 |  |  |  | 1 | 1 |  |  |  |  | 145237.08 | 2826.78 | 145237.08 | 2826.78 | 10.1547 | [5 empty] | 114.0426 | 2602.1454
18.12.2007 09:00 | 3600 | 2 | 759.55 | GGB | 766.667 | 772.313 | 768.864 | 271.43 | GGB | 11078.6 | GGB | 9.85 | GGB | 1033.17 | GGB | 57.95 | GGB | 174425.54 | GGB | 146748.67 | GGB | 0 | 0 | 2827 | 3600 | 2811.44 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 95603.41 | GGB | 95604.52 | 2811.44 | 2811.44 |  |  |  | 1 | 1 |  |  |  |  | 146748.67 | 2811.44 | 146748.67 | 2811.44 | 10.1295 | [5 empty] | 114.6042 | 2575.3419
18.12.2007 10:00 | 3600 | 2 | 759.35 | GGB | 767.766 | 774.375 | 769.963 | 271.92 | GGB | 11094.9 | GGB | 9.85 | GGB | 1033.56 | GGB | 57.61 | GGB | 174976.81 | GGB | 147417.3 | GGB | 0 | 0 | 2842 | 3600 | 2826.27 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 95644.09 | GGB | 95645.2 | 2826.27 | 2826.27 |  |  |  | 1 | 1 |  |  |  |  | 147417.3 | 2826.27 | 147417.3 | 2826.27 | 10.2419 | [5 empty] | 115.7336 | 2563.6611
18.12.2007 11:00 | 3600 | 2 | 759.64 | GGB | 767.766 | 773.367 | 769.963 | 272.43 | GGB | 11132.6 | GGB | 9.85 | GGB | 1034.07 | GGB | 57.31 | GGB | 175719.54 | GGB | 148253.02 | GGB | 0 | 0 | 2835 | 3600 | 2819.71 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 95684.57 | GGB | 95685.68 | 2819.71 | 2819.71 |  |  |  | 1 | 1 |  |  |  |  | 148253.02 | 2819.71 | 148253.02 | 2819.71 | 10.3268 | [5 empty] | 116.1196 | 2549.2095
18.12.2007 12:00 | 3600 | 2 | 759.81 | GGB | 767.766 | 774.352 | 769.963 | 272.19 | GGB | 11130.4 | GGB | 9.86 | GGB | 1033.95 | GGB | 57.44 | GGB | 175229.89 | GGB | 147764.3 | GGB | 0 | 0 | 2819 | 3600 | 2803.67 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 95725.35 | GGB | 95726.46 | 2803.67 | 2803.67 |  |  |  | 1 | 1 |  |  |  |  | 147764.3 | 2803.67 | 147764.3 | 2803.67 | 10.159 | [5 empty] | 115.0784 | 2557.6408
18.12.2007 13:00 | 3600 | 2 | 760.08 | GGB | 768.864 | 774.375 | 771.429 | 271.99 | GGB | 11116.7 | GGB | 9.86 | GGB | 1033.62 | GGB | 57.46 | GGB | 174776.55 | GGB | 147326.56 | GGB | 0 | 0 | 2805 | 3600 | 2789.19 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 95765.68 | GGB | 95766.79 | 2789.19 | 2789.19 |  |  |  | 1 | 1 |  |  |  |  | 147326.56 | 2789.19 | 147326.56 | 2789.19 | 10.189 | [5 empty] | 114.1449 | 2565.2401
18.12.2007 14:00 | 3600 | 2 | 760.16 | GGB | 767.766 | 773.156 | 768.864 | 270.88 | GGB | 11077.4 | GGB | 9.87 | GGB | 1033.3 | GGB | 57.95 | GGB | 173647.6 | GGB | 146113.14 | GGB | 0 | 0 | 2775 | 3600 | 2759.26 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 95806.44 | GGB | 95807.55 | 2759.26 | 2759.26 |  |  |  | 1 | 1 |  |  |  |  | 146113.14 | 2759.26 | 146113.14 | 2759.26 | 9.8912 | [5 empty] | 111.99 | 2586.5436
18.12.2007 15:00 | 3600 | 2 | 759.79 | GGB | 766.667 | 772.055 | 768.864 | 270.42 | GGB | 11052.4 | GGB | 9.86 | GGB | 1032.54 | GGB | 58.02 | GGB | 173233.87 | GGB | 145626.12 | GGB | 0 | 0 | 2781 | 3600 | 2765.71 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 95846.73 | GGB | 95847.84 | 2765.71 | 2765.71 |  |  |  | 1 | 1 |  |  |  |  | 145626.12 | 2765.71 | 145626.12 | 2765.71 | 9.9965 | [5 empty] | 111.8777 | 2595.1938
18.12.2007 16:00 | 3600 | 2 | 759.42 | GGB | 767.766 | 774 | 769.963 | 270.56 | GGB | 11049.9 | GGB | 9.85 | GGB | 1032.61 | GGB | 58 | GGB | 173530.97 | GGB | 145893.42 | GGB | 0 | 0 | 2801 | 3600 | 2785.99 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 95887.34 | GGB | 95888.45 | 2785.99 | 2785.99 |  |  |  | 1 | 1 |  |  |  |  | 145893.42 | 2785.99 | 145893.42 | 2785.99 | 10.0088 | [5 empty] | 112.9049 | 2590.439
18.12.2007 17:00 | 3600 | 2 | 759.89 | GGB | 766.667 | 772.711 | 769.963 | 268.97 | GGB | 11082.8 | GGB | 9.87 | GGB | 1031.94 | GGB | 58.59 | GGB | 171322.59 | GGB | 143689.33 | GGB | 0 | 0 | 2793 | 3600 | 2777.46 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 95927.48 | GGB | 95928.59 | 2777.46 | 2777.46 |  |  |  | 1 | 1 |  |  |  |  | 143689.33 | 2777.46 | 143689.33 | 2777.46 | 9.9425 | [5 empty] | 110.8587 | 2630.1744
18.12.2007 18:00 | 3600 | 2 | 759.66 | GGB | 768.864 | 774.844 | 771.429 | 269.85 | GGB | 11040.7 | GGB | 9.86 | GGB | 1031.91 | GGB | 58.32 | GGB | 172681.51 | GGB | 144943.71 | GGB | 0 | 0 | 2795 | 3600 | 2779.46 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 95968.68 | GGB | 95969.79 | 2779.46 | 2779.46 |  |  |  | 1 | 1 |  |  |  |  | 144943.71 | 2779.46 | 144943.71 | 2779.46 | 9.7783 | [5 empty] | 111.907 | 2607.4122
18.12.2007 19:00 | 3600 | 2 | 759.77 | GGB | 767.766 | 773.859 | 769.963 | 269.79 | GGB | 11020.7 | GGB | 9.86 | GGB | 1031.75 | GGB | 58.31 | GGB | 172581.37 | GGB | 144841.44 | GGB | 0 | 0 | 2775 | 3600 | 2759.29 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 96008.28 | GGB | 96009.39 | 2759.29 | 2759.29 |  |  |  | 1 | 1 |  |  |  |  | 144841.44 | 2759.29 | 144841.44 | 2759.29 | 10.0924 | [5 empty] | 111.0165 | 2609.2533
18.12.2007 20:00 | 3600 | 2 | 759.96 | GGB | 767.766 | 773.836 | 770.33 | 269.52 | GGB | 11013.3 | GGB | 9.86 | GGB | 1031.15 | GGB | 58.37 | GGB | 172144.54 | GGB | 144363.84 | GGB | 0 | 0 | 2759 | 3600 | 2743.99 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 96049.07 | GGB | 96050.18 | 2743.99 | 2743.99 |  |  |  | 1 | 1 |  |  |  |  | 144363.84 | 2743.99 | 144363.84 | 2743.99 | 9.7115 | [5 empty] | 110.0369 | 2617.8855
18.12.2007 21:00 | 3600 | 2 | 759.93 | GGB | 768.864 | 774.914 | 771.429 | 268.95 | GGB | 11020.2 | GGB | 9.86 | GGB | 1031.07 | GGB | 58.53 | GGB | 171598.77 | GGB | 143826.06 | GGB | 0 | 0 | 2776 | 3600 | 2760.36 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 96088.81 | GGB | 96089.92 | 2760.36 | 2760.36 |  |  |  | 1 | 1 |  |  |  |  | 143826.06 | 2760.36 | 143826.06 | 2760.36 | 9.9902 | [5 empty] | 110.281 | 2627.674
18.12.2007 22:00 | 3600 | 2 | 759.95 | GGB | 767.766 | 773.813 | 768.864 | 267.52 | GGB | 11059.8 | GGB | 9.86 | GGB | 1030.85 | GGB | 59.13 | GGB | 170461.02 | GGB | 142582.86 | GGB | 0 | 0 | 2790 | 3600 | 2774.37 | GGB | 100 | GGB | 37.79 | GGB | 37.79 | GGB | 96126.6 | GGB | 96127.71 | 2774.37 | 2774.37 |  |  |  | 1 | 1 |  |  |  |  | 142582.86 | 2774.37 | 142582.86 | 2774.37 | 10.4678 | [5 empty] | 109.8827 | 2650.5851
18.12.2007 23:00 | 3600 | 2 | 759.31 | GGB | 766.667 | 772.734 | 768.864 | 267.82 | GGB | 11039.1 | GGB | 9.85 | GGB | 1030.91 | GGB | 59.13 | GGB | 170262.96 | GGB | 142423.54 | GGB | 0 | 0 | 2828 | 3600 | 2812.8 | GGB | 100 | GGB | 41.7 | GGB | 41.7 | GGB | 96168.29 | GGB | 96169.41 | 2812.8 | 2812.8 |  |  |  | 1 | 1 |  |  |  |  | 142423.54 | 2812.8 | 142423.54 | 2812.8 | 9.6069 | [5 empty] | 111.2803 | 2653.5501
18.12.2007 24:00 | 3600 | 2 | 759.56 | GGB | 767.766 | 773.789 | 769.963 | 268.21 | GGB | 11053.6 | GGB | 9.86 | GGB | 1030.55 | GGB | 58.77 | GGB | 170551.25 | GGB | 142770.47 | GGB | 0 | 0 | 2821 | 3600 | 2805.45 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 96208.78 | GGB | 96209.9 | 2805.45 | 2805.45 |  |  |  | 1 | 1 |  |  |  |  | 142770.47 | 2805.45 | 142770.47 | 2805.45 | 9.8922 | [5 empty] | 111.2598 | 2647.102
19.12.2007 01:00 | 3600 | 2 | 759.81 | GGB | 767.766 | 773.836 | 769.963 | 268.1 | GGB | 11050.5 | GGB | 9.86 | GGB | 1030.82 | GGB | 58.77 | GGB | 170240.96 | GGB | 142547.95 | GGB | 0 | 0 | 2808 | 3600 | 2792.46 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 96248.94 | GGB | 96250.05 | 2792.46 | 2792.46 |  |  |  | 1 | 1 |  |  |  |  | 142547.95 | 2792.46 | 142547.95 | 2792.46 | 9.9143 | [5 empty] | 110.5721 | 2651.2342
19.12.2007 02:00 | 3600 | 2 | 759.93 | GGB | 768.864 | 773.742 | 769.963 | 267.59 | GGB | 11036.3 | GGB | 9.86 | GGB | 1030.67 | GGB | 59.12 | GGB | 169771.11 | GGB | 141983.92 | GGB | 0 | 0 | 2795 | 3600 | 2779.78 | GGB | 100 | GGB | 41.42 | GGB | 41.42 | GGB | 96290.36 | GGB | 96291.47 | 2779.78 | 2779.78 |  |  |  | 1 | 1 |  |  |  |  | 141983.92 | 2779.78 | 141983.92 | 2779.78 | 9.5288 | [5 empty] | 109.6345 | 2661.7662
19.12.2007 03:00 | 3600 | 2 | 759.51 | GGB | 767.766 | 773.695 | 769.963 | 267.89 | GGB | 11024.1 | GGB | 9.85 | GGB | 1030.65 | GGB | 59.32 | GGB | 170118.82 | GGB | 142185.1 | GGB | 0 | 0 | 2817 | 3600 | 2801.1 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 96329.91 | GGB | 96331.03 | 2801.1 | 2801.1 |  |  |  | 1 | 1 |  |  |  |  | 142185.1 | 2801.1 | 142185.1 | 2801.1 | 10.0676 | [5 empty] | 110.6319 | 2658
19.12.2007 04:00 | 3600 | 2 | 759.7 | GGB | 767.766 | 773.789 | 770.33 | 268.03 | GGB | 11037.8 | GGB | 9.86 | GGB | 1030.36 | GGB | 59.27 | GGB | 170171.63 | GGB | 142214.58 | GGB | 0 | 0 | 2803 | 3600 | 2787.67 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 96371.19 | GGB | 96372.31 | 2787.67 | 2787.67 |  |  |  | 1 | 1 |  |  |  |  | 142214.58 | 2787.67 | 142214.58 | 2787.67 | 9.6039 | [5 empty] | 110.1243 | 2657.449
19.12.2007 05:00 | 3600 | 2 | 759.51 | GGB | 767.766 | 772.734 | 769.963 | 267.67 | GGB | 11028.5 | GGB | 9.85 | GGB | 1029.99 | GGB | 59.2 | GGB | 169981.28 | GGB | 142033.76 | GGB | 0 | 0 | 2810 | 3600 | 2794.96 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 96411.27 | GGB | 96412.39 | 2794.96 | 2794.96 |  |  |  | 1 | 1 |  |  |  |  | 142033.76 | 2794.96 | 142033.76 | 2794.96 | 9.9047 | [5 empty] | 110.2719 | 2660.8322
19.12.2007 06:00 | 3600 | 2 | 759.57 | GGB | 767.766 | 772.711 | 769.963 | 267.68 | GGB | 11038.4 | GGB | 9.85 | GGB | 1029.69 | GGB | 59.06 | GGB | 170216.75 | GGB | 142247.3 | GGB | 0 | 0 | 2815 | 3600 | 2799.02 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 96451.82 | GGB | 96452.94 | 2799.02 | 2799.02 |  |  |  | 1 | 1 |  |  |  |  | 142247.3 | 2799.02 | 142247.3 | 2799.02 | 9.8188 | [5 empty] | 110.5981 | 2656.8378
19.12.2007 07:00 | 3600 | 2 | 759.57 | GGB | 767.766 | 773.719 | 768.864 | 267.6 | GGB | 11048.8 | GGB | 9.86 | GGB | 1029.63 | GGB | 59.02 | GGB | 170389.5 | GGB | 142400.19 | GGB | 0 | 0 | 2809 | 3600 | 2793.89 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 96492.29 | GGB | 96493.41 | 2793.89 | 2793.89 |  |  |  | 1 | 1 |  |  |  |  | 142400.19 | 2793.89 | 142400.19 | 2793.89 | 9.8308 | [5 empty] | 110.514 | 2653.9852
19.12.2007 08:00 | 3600 | 2 | 758.87 | GGB | 768.864 | 774.797 | 771.429 | 269.79 | GGB | 11068.4 | GGB | 9.84 | GGB | 1030.27 | GGB | 58.41 | GGB | 172472.44 | GGB | 144498.47 | GGB | 0 | 0 | 2866 | 3600 | 2850.94 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 96532.41 | GGB | 96533.54 | 2850.94 | 2850.94 |  |  |  | 1 | 1 |  |  |  |  | 144498.47 | 2850.94 | 144498.47 | 2850.94 | 10.2655 | [5 empty] | 114.4324 | 2615.4464
19.12.2007 09:00 | 3600 | 2 | 759.48 | GGB | 766.667 | 772.359 | 768.864 | 269.32 | GGB | 11107.5 | GGB | 9.86 | GGB | 1030.34 | GGB | 58.59 | GGB | 171863.95 | GGB | 143919.82 | GGB | 0 | 0 | 2857 | 3600 | 2841.51 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 96573.15 | GGB | 96574.28 | 2841.51 | 2841.51 |  |  |  | 1 | 1 |  |  |  |  | 143919.82 | 2841.51 | 143919.82 | 2841.51 | 10.038 | [5 empty] | 113.5971 | 2625.9622
19.12.2007 10:00 | 3600 | 2 | 759.41 | GGB | 766.3 | 772.313 | 768.864 | 269.46 | GGB | 11105.1 | GGB | 9.86 | GGB | 1030.52 | GGB | 58.61 | GGB | 171825.44 | GGB | 143903.56 | GGB | 0 | 0 | 2864 | 3600 | 2848.36 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 96613.45 | GGB | 96614.58 | 2848.36 | 2848.36 |  |  |  | 1 | 1 |  |  |  |  | 143903.56 | 2848.36 | 143903.56 | 2848.36 | 10.1709 | [5 empty] | 113.8581 | 2626.2589
19.12.2007 11:00 | 3600 | 2 | 759.36 | GGB | 768.864 | 774.492 | 771.429 | 269.72 | GGB | 11107 | GGB | 9.86 | GGB | 1030.87 | GGB | 58.56 | GGB | 171851.85 | GGB | 143995.91 | GGB | 0 | 0 | 2869 | 3600 | 2853.72 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 96654.27 | GGB | 96655.4 | 2853.72 | 2853.72 |  |  |  | 1 | 1 |  |  |  |  | 143995.91 | 2853.72 | 143995.91 | 2853.72 | 10.0667 | [5 empty] | 114.1456 | 2624.5745
19.12.2007 12:00 | 3600 | 2 | 759.37 | GGB | 766.667 | 772.547 | 768.864 | 269.55 | GGB | 11089.4 | GGB | 9.85 | GGB | 1030.55 | GGB | 58.72 | GGB | 171413.92 | GGB | 143516.29 | GGB | 0 | 0 | 2861 | 3600 | 2844.99 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 96694.64 | GGB | 96695.77 | 2844.99 | 2844.99 |  |  |  | 1 | 1 |  |  |  |  | 143516.29 | 2844.99 | 143516.29 | 2844.99 | 10.114 | [5 empty] | 113.4173 | 2633.3457
19.12.2007 13:00 | 3600 | 2 | 759.09 | GGB | 767.766 | 773.625 | 769.963 | 269.88 | GGB | 11091.7 | GGB | 9.85 | GGB | 1030.49 | GGB | 58.7 | GGB | 171682.4 | GGB | 143739.23 | GGB | 0 | 0 | 2876 | 3600 | 2860.85 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 96734.87 | GGB | 96736 | 2860.85 | 2860.85 |  |  |  | 1 | 1 |  |  |  |  | 143739.23 | 2860.85 | 143739.23 | 2860.85 | 10.2216 | [5 empty] | 114.2268 | 2629.2613
19.12.2007 14:00 | 3600 | 2 | 759.59 | GGB | 767.766 | 773.625 | 769.963 | 269.85 | GGB | 11094.2 | GGB | 9.86 | GGB | 1030.4 | GGB | 58.75 | GGB | 171615.28 | GGB | 143648.21 | GGB | 0 | 0 | 2854 | 3600 | 2838.68 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 96775.7 | GGB | 96776.82 | 2838.68 | 2838.68 |  |  |  | 1 | 1 |  |  |  |  | 143648.21 | 2838.68 | 143648.21 | 2838.68 | 9.9895 | [5 empty] | 113.2698 | 2630.9273
19.12.2007 15:00 | 3600 | 2 | 759.21 | GGB | 766.667 | 772.547 | 768.864 | 270.18 | GGB | 11088.9 | GGB | 9.85 | GGB | 1030.48 | GGB | 58.62 | GGB | 171693.4 | GGB | 143782.58 | GGB | 0 | 0 | 2871 | 3600 | 2855.48 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 96815.82 | GGB | 96816.94 | 2855.48 | 2855.48 |  |  |  | 1 | 1 |  |  |  |  | 143782.58 | 2855.48 | 143782.58 | 2855.48 | 10.2335 | [5 empty] | 114.0467 | 2628.4686
19.12.2007 16:00 | 3600 | 2 | 759.49 | GGB | 767.766 | 773.555 | 769.963 | 270.17 | GGB | 11089.9 | GGB | 9.86 | GGB | 1030.02 | GGB | 58.5 | GGB | 171676.9 | GGB | 143755.78 | GGB | 0 | 0 | 2860 | 3600 | 2844.07 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 96856.67 | GGB | 96857.79 | 2844.07 | 2844.07 |  |  |  | 1 | 1 |  |  |  |  | 143755.78 | 2844.07 | 143755.78 | 2844.07 | 10.0086 | [5 empty] | 113.5699 | 2628.9586
19.12.2007 17:00 | 3600 | 2 | 759.37 | GGB | 767.766 | 773.461 | 768.864 | 270.3 | GGB | 11060.7 | GGB | 9.85 | GGB | 1029.83 | GGB | 58.36 | GGB | 172175.35 | GGB | 144209.44 | GGB | 0 | 0 | 2840 | 3600 | 2824.05 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 96896.74 | GGB | 96897.86 | 2824.05 | 2824.05 |  |  |  | 1 | 1 |  |  |  |  | 144209.44 | 2824.05 | 144209.44 | 2824.05 | 10.1636 | [5 empty] | 113.1263 | 2620.6884
19.12.2007 18:00 | 3600 | 2 | 759.54 | GGB | 766.3 | 771.375 | 767.766 | 269.43 | GGB | 11077.5 | GGB | 9.86 | GGB | 1029.43 | GGB | 58.56 | GGB | 171361.1 | GGB | 143384.43 | GGB | 0 | 0 | 2836 | 3600 | 2820.45 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 96937.53 | GGB | 96938.65 | 2820.45 | 2820.45 |  |  |  | 1 | 1 |  |  |  |  | 143384.43 | 2820.45 | 143384.43 | 2820.45 | 9.9144 | [5 empty] | 112.3357 | 2635.7674
19.12.2007 19:00 | 3600 | 2 | 759.46 | GGB | 766.667 | 772.266 | 768.864 | 269.38 | GGB | 11080.4 | GGB | 9.86 | GGB | 1029.3 | GGB | 58.37 | GGB | 171880.46 | GGB | 143883.44 | GGB | 0 | 0 | 2837 | 3600 | 2821.68 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 96977.98 | GGB | 96979.09 | 2821.68 | 2821.68 |  |  |  | 1 | 1 |  |  |  |  | 143883.44 | 2821.68 | 143883.44 | 2821.68 | 10.0394 | [5 empty] | 112.7758 | 2626.6261
19.12.2007 20:00 | 3600 | 2 | 759.25 | GGB | 766.667 | 773.32 | 768.864 | 269.37 | GGB | 11095.2 | GGB | 9.86 | GGB | 1029.07 | GGB | 57.7 | GGB | 172604.48 | GGB | 144747.42 | GGB | 0 | 0 | 2842 | 3600 | 2825.98 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 97018.46 | GGB | 97019.58 | 2825.98 | 2825.98 |  |  |  | 1 | 1 |  |  |  |  | 144747.42 | 2825.98 | 144747.42 | 2825.98 | 10.1026 | [5 empty] | 113.6259 | 2610.9481
19.12.2007 21:00 | 3600 | 2 | 759.27 | GGB | 766.667 | 772.477 | 768.864 | 269.49 | GGB | 11098.5 | GGB | 9.86 | GGB | 1028.71 | GGB | 58.08 | GGB | 172313.99 | GGB | 144290.38 | GGB | 0 | 0 | 2850 | 3600 | 2834.52 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 97058.53 | GGB | 97059.65 | 2834.52 | 2834.52 |  |  |  | 1 | 1 |  |  |  |  | 144290.38 | 2834.52 | 144290.38 | 2834.52 | 10.207 | [5 empty] | 113.6094 | 2619.2183
19.12.2007 22:00 | 3600 | 2 | 758.86 | GGB | 767.766 | 772.266 | 769.963 | 271.04 | GGB | 11063.4 | GGB | 9.85 | GGB | 1028.26 | GGB | 57.24 | GGB | 174686.32 | GGB | 146585.14 | GGB | 0 | 0 | 2846 | 3600 | 2830.4 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 97099.54 | GGB | 97100.66 | 2830.4 | 2830.4 |  |  |  | 1 | 1 |  |  |  |  | 146585.14 | 2830.4 | 146585.14 | 2830.4 | 10.1169 | [5 empty] | 115.2485 | 2578.215
19.12.2007 23:00 | 3600 | 2 | 759.44 | GGB | 766.667 | 772.477 | 768.864 | 271.26 | GGB | 11094.3 | GGB | 9.86 | GGB | 1027.5 | GGB | 56.83 | GGB | 175201.28 | GGB | 147091.73 | GGB | 0 | 0 | 2824 | 3600 | 2808.21 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 97140 | GGB | 97141.12 | 2808.21 | 2808.21 |  |  |  | 1 | 1 |  |  |  |  | 147091.73 | 2808.21 | 147091.73 | 2808.21 | 10.2092 | [5 empty] | 114.7401 | 2569.3355
19.12.2007 24:00 | 3600 | 2 | 759.44 | GGB | 767.766 | 773.367 | 769.963 | 271.51 | GGB | 11106.3 | GGB | 9.86 | GGB | 1027.62 | GGB | 56.6 | GGB | 175486.27 | GGB | 147451.29 | GGB | 0 | 0 | 2829 | 3600 | 2813.7 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 97180.09 | GGB | 97181.21 | 2813.7 | 2813.7 |  |  |  | 1 | 1 |  |  |  |  | 147451.29 | 2813.7 | 147451.29 | 2813.7 | 10.3488 | [5 empty] | 115.2455 | 2563.0702
20.12.2007 01:00 | 3600 | 2 | 759.3 | GGB | 767.766 | 773.367 | 769.963 | 271.58 | GGB | 11119.8 | GGB | 9.86 | GGB | 1026.86 | GGB | 56.34 | GGB | 175902.19 | GGB | 147805.24 | GGB | 0 | 0 | 2835 | 3600 | 2819.37 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 97221.13 | GGB | 97222.24 | 2819.37 | 2819.37 |  |  |  | 1 | 1 |  |  |  |  | 147805.24 | 2819.37 | 147805.24 | 2819.37 | 10.1564 | [5 empty] | 115.7549 | 2556.9324
20.12.2007 02:00 | 3600 | 2 | 759.39 | GGB | 766.667 | 773.461 | 768.864 | 271.51 | GGB | 11123.3 | GGB | 9.86 | GGB | 1026.59 | GGB | 56.35 | GGB | 176096.95 | GGB | 147928.16 | GGB | 0 | 0 | 2834 | 3600 | 2818.24 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 97261.99 | GGB | 97263.11 | 2818.24 | 2818.24 |  |  |  | 1 | 1 |  |  |  |  | 147928.16 | 2818.24 | 147928.16 | 2818.24 | 10.2006 | [5 empty] | 115.8047 | 2554.8077
20.12.2007 03:00 | 3600 | 2 | 759.66 | GGB | 768.864 | 774.75 | 771.429 | 270.96 | GGB | 11126.9 | GGB | 9.86 | GGB | 1026.14 | GGB | 56.43 | GGB | 175210.08 | GGB | 147081.77 | GGB | 0 | 0 | 2821 | 3600 | 2805.76 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 97302.68 | GGB | 97303.79 | 2805.76 | 2805.76 |  |  |  | 1 | 1 |  |  |  |  | 147081.77 | 2805.76 | 147081.77 | 2805.76 | 10.1444 | [5 empty] | 114.6323 | 2569.5095
20.12.2007 04:00 | 3600 | 2 | 759.85 | GGB | 767.766 | 772.711 | 769.963 | 268.81 | GGB | 11134.3 | GGB | 9.87 | GGB | 1025.38 | GGB | 57.15 | GGB | 172565.97 | GGB | 144436.9 | GGB | 0 | 0 | 2821 | 3600 | 2805.84 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 97343.31 | GGB | 97344.42 | 2805.84 | 2805.84 |  |  |  | 1 | 1 |  |  |  |  | 144436.9 | 2805.84 | 144436.9 | 2805.84 | 9.9746 | [5 empty] | 112.5741 | 2616.5613
20.12.2007 05:00 | 3600 | 2 | 759.38 | GGB | 767.766 | 772.711 | 769.963 | 268.5 | GGB | 11114.1 | GGB | 9.86 | GGB | 1024.52 | GGB | 57.18 | GGB | 172315.09 | GGB | 144093.37 | GGB | 0 | 0 | 2836 | 3600 | 2820.04 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 97384.01 | GGB | 97385.12 | 2820.04 | 2820.04 |  |  |  | 1 | 1 |  |  |  |  | 144093.37 | 2820.04 | 144093.37 | 2820.04 | 9.984 | [5 empty] | 112.8747 | 2622.7994
20.12.2007 06:00 | 3600 | 2 | 759.09 | GGB | 766.667 | 772.688 | 768.864 | 268.84 | GGB | 11081 | GGB | 9.85 | GGB | 1023.48 | GGB | 57.48 | GGB | 171999.3 | GGB | 143554.92 | GGB | 0 | 0 | 2845 | 3600 | 2829.05 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 97424.43 | GGB | 97425.53 | 2829.05 | 2829.05 |  |  |  | 1 | 1 |  |  |  |  | 143554.92 | 2829.05 | 143554.92 | 2829.05 | 10.0501 | [5 empty] | 112.8122 | 2632.637
20.12.2007 07:00 | 3600 | 2 | 759.3 | GGB | 766.667 | 772.688 | 768.864 | 269.01 | GGB | 11068.3 | GGB | 9.86 | GGB | 1023.66 | GGB | 57.91 | GGB | 171494.24 | GGB | 142969.66 | GGB | 0 | 0 | 2834 | 3600 | 2818.51 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 97465.15 | GGB | 97466.26 | 2818.51 | 2818.51 |  |  |  | 1 | 1 |  |  |  |  | 142969.66 | 2818.51 | 142969.66 | 2818.51 | 9.8935 | [5 empty] | 111.9337 | 2643.414
20.12.2007 08:00 | 3600 | 2 | 758.92 | GGB | 767.766 | 773.531 | 768.864 | 268.89 | GGB | 11072.9 | GGB | 9.85 | GGB | 1023.63 | GGB | 57.65 | GGB | 171750.62 | GGB | 143291.95 | GGB | 0 | 0 | 2851 | 3600 | 2834.99 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 97505.34 | GGB | 97506.45 | 2834.99 | 2834.99 |  |  |  | 1 | 1 |  |  |  |  | 143291.95 | 2834.99 | 143291.95 | 2834.99 | 10.1078 | [5 empty] | 112.842 | 2637.4685
20.12.2007 09:00 | 3600 | 2 | 757.75 | GGB | 771.429 | 777.844 | 773.626 | 270.37 | GGB | 11136.6 | GGB | 9.82 | GGB | 1024.05 | GGB | 57.01 | GGB | 174975.71 | GGB | 146328.32 | GGB | 0 | 0 | 2941 | 3600 | 2925.03 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 97546.46 | GGB | 97547.57 | 2925.03 | 2925.03 |  |  |  | 1 | 1 |  |  |  |  | 146328.32 | 2925.03 | 146328.32 | 2925.03 | 10.4089 | [5 empty] | 118.893 | 2582.74
20.12.2007 10:00 | 3600 | 2 | 760.82 | GGB | 767.766 | 773.742 | 769.963 | 270.29 | GGB | 11212.9 | GGB | 9.88 | GGB | 1024.18 | GGB | 62.01 | GGB | 174596.09 | GGB | 143848.84 | GGB | 0 | 0 | 2810 | 3600 | 2794.68 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 97586.67 | GGB | 97587.77 | 2794.68 | 2794.68 |  |  |  | 1 | 1 |  |  |  |  | 143848.84 | 2794.68 | 143848.84 | 2794.68 | 10.0003 | [5 empty] | 111.6699 | 2627.2579
20.12.2007 11:00 | 3600 | 2 | 759.8 | GGB | 767.766 | 773.742 | 768.864 | 270.05 | GGB | 11204 | GGB | 9.86 | GGB | 1024.26 | GGB | 56.94 | GGB | 174982.31 | GGB | 146393.82 | GGB | 0 | 0 | 2849 | 3600 | 2833.58 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 97627.89 | GGB | 97629 | 2833.58 | 2833.58 |  |  |  | 1 | 1 |  |  |  |  | 146393.82 | 2833.58 | 146393.82 | 2833.58 | 10.0611 | [5 empty] | 115.2274 | 2581.5844
20.12.2007 12:00 | 3600 | 2 | 759.64 | GGB | 768.864 | 773.93 | 769.963 | 270.61 | GGB | 11158.5 | GGB | 9.85 | GGB | 1024.28 | GGB | 56.7 | GGB | 175924.2 | GGB | 147291.29 | GGB | 0 | 0 | 2831 | 3600 | 2815.8 | GGB | 100 | GGB | 41.16 | GGB | 41.16 | GGB | 97669.05 | GGB | 97670.16 | 2815.8 | 2815.8 |  |  |  | 1 | 1 |  |  |  |  | 147291.29 | 2815.8 | 147291.29 | 2815.8 | 10.0764 | [5 empty] | 115.2063 | 2565.8544
20.12.2007 13:00 | 3600 | 2 | 760.34 | GGB | 768.864 | 774.023 | 770.33 | 270.25 | GGB | 11129.5 | GGB | 9.87 | GGB | 1024.65 | GGB | 56.65 | GGB | 175706.33 | GGB | 147183.55 | GGB | 0 | 0 | 2769 | 3600 | 2753.1 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 97709.06 | GGB | 97710.17 | 2753.1 | 2753.1 |  |  |  | 1 | 1 |  |  |  |  | 147183.55 | 2753.1 | 147183.55 | 2753.1 | 10.1277 | [5 empty] | 112.5586 | 2567.7326
20.12.2007 14:00 | 3600 | 2 | 760.35 | GGB | 768.864 | 774.07 | 770.33 | 267.42 | GGB | 11123.2 | GGB | 9.87 | GGB | 1023.88 | GGB | 57.46 | GGB | 172056.51 | GGB | 143665.05 | GGB | 0 | 0 | 2772 | 3600 | 2756.88 | GGB | 100 | GGB | 41.5 | GGB | 41.5 | GGB | 97750.55 | GGB | 97751.67 | 2756.88 | 2756.88 |  |  |  | 1 | 1 |  |  |  |  | 143665.05 | 2756.88 | 143665.05 | 2756.88 | 9.5438 | [5 empty] | 110.0187 | 2630.6189
20.12.2007 15:00 | 3600 | 2 | 759.74 | GGB | 767.766 | 774 | 769.963 | 267.26 | GGB | 11085.1 | GGB | 9.86 | GGB | 1023.27 | GGB | 57.58 | GGB | 171834.24 | GGB | 143345.8 | GGB | 0 | 0 | 2794 | 3600 | 2778.02 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 97790.46 | GGB | 97791.58 | 2778.02 | 2778.02 |  |  |  | 1 | 1 |  |  |  |  | 143345.8 | 2778.02 | 143345.8 | 2778.02 | 9.9779 | [5 empty] | 110.616 | 2636.4777
20.12.2007 16:00 | 3600 | 2 | 759.84 | GGB | 767.766 | 773.906 | 769.963 | 267.35 | GGB | 11073.5 | GGB | 9.85 | GGB | 1023.21 | GGB | 57.92 | GGB | 171528.35 | GGB | 142930.85 | GGB | 0 | 0 | 2788 | 3600 | 2772.52 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 97831.43 | GGB | 97832.55 | 2772.52 | 2772.52 |  |  |  | 1 | 1 |  |  |  |  | 142930.85 | 2772.52 | 142930.85 | 2772.52 | 9.6724 | [5 empty] | 110.0774 | 2644.1318
20.12.2007 17:00 | 3600 | 2 | 759.82 | GGB | 766.667 | 771.773 | 768.864 | 268.4 | GGB | 11045.1 | GGB | 9.85 | GGB | 1023.31 | GGB | 57.77 | GGB | 172498.85 | GGB | 143820.15 | GGB | 0 | 0 | 2776 | 3600 | 2760.7 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 97871.84 | GGB | 97872.96 | 2760.7 | 2760.7 |  |  |  | 1 | 1 |  |  |  |  | 143820.15 | 2760.7 | 143820.15 | 2760.7 | 9.8254 | [5 empty] | 110.2901 | 2627.782
20.12.2007 18:00 | 3600 | 2 | 760.24 | GGB | 767.766 | 774.023 | 768.864 | 268.97 | GGB | 11030.8 | GGB | 9.86 | GGB | 1023.6 | GGB | 57.54 | GGB | 173262.48 | GGB | 144597.28 | GGB | 0 | 0 | 2736 | 3600 | 2720.85 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 97912.19 | GGB | 97913.31 | 2720.85 | 2720.85 |  |  |  | 1 | 1 |  |  |  |  | 144597.28 | 2720.85 | 144597.28 | 2720.85 | 9.7504 | [5 empty] | 109.2854 | 2613.6591
20.12.2007 19:00 | 3600 | 2 | 760.04 | GGB | 767.766 | 773.742 | 769.963 | 268.21 | GGB | 11066.1 | GGB | 9.86 | GGB | 1023.5 | GGB | 57.86 | GGB | 172002.6 | GGB | 143392.78 | GGB | 0 | 0 | 2771 | 3600 | 2755.61 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 97952.27 | GGB | 97953.39 | 2755.61 | 2755.61 |  |  |  | 1 | 1 |  |  |  |  | 143392.78 | 2755.61 | 143392.78 | 2755.61 | 9.8586 | [5 empty] | 109.7596 | 2635.6139
20.12.2007 20:00 | 3600 | 2 | 760.13 | GGB | 767.766 | 773.719 | 770.33 | 267.76 | GGB | 11058.1 | GGB | 9.86 | GGB | 1023.6 | GGB | 57.51 | GGB | 172673.8 | GGB | 144120.06 | GGB | 0 | 0 | 2753 | 3600 | 2737.6 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 97992.92 | GGB | 97994.04 | 2737.6 | 2737.6 |  |  |  | 1 | 1 |  |  |  |  | 144120.06 | 2737.6 | 144120.06 | 2737.6 | 9.7059 | [5 empty] | 109.5953 | 2622.3136
20.12.2007 21:00 | 3600 | 2 | 759.92 | GGB | 768.864 | 775.266 | 771.429 | 267.41 | GGB | 11068.7 | GGB | 9.86 | GGB | 1023.46 | GGB | 58.11 | GGB | 171110.22 | GGB | 142537.9 | GGB | 0 | 0 | 2783 | 3600 | 2767.36 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 98033.42 | GGB | 98034.54 | 2767.36 | 2767.36 |  |  |  | 1 | 1 |  |  |  |  | 142537.9 | 2767.36 | 142537.9 | 2767.36 | 9.7396 | [5 empty] | 109.5705 | 2651.4211
20.12.2007 22:00 | 3600 | 2 | 760.21 | GGB | 768.864 | 774.234 | 770.33 | 267.05 | GGB | 11056.5 | GGB | 9.86 | GGB | 1023.93 | GGB | 58.33 | GGB | 170931.97 | GGB | 142361.07 | GGB | 0 | 0 | 2762 | 3600 | 2746.85 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 98074.06 | GGB | 98075.18 | 2746.85 | 2746.85 |  |  |  | 1 | 1 |  |  |  |  | 142361.07 | 2746.85 | 142361.07 | 2746.85 | 9.6222 | [5 empty] | 108.6235 | 2654.7145
20.12.2007 23:00 | 3600 | 2 | 760.11 | GGB | 767.766 | 773.203 | 769.963 | 267.07 | GGB | 11032.4 | GGB | 9.86 | GGB | 1024.28 | GGB | 58.38 | GGB | 170886.85 | GGB | 142346.53 | GGB | 0 | 0 | 2754 | 3600 | 2738.44 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 98114.49 | GGB | 98115.61 | 2738.44 | 2738.44 |  |  |  | 1 | 1 |  |  |  |  | 142346.53 | 2738.44 | 142346.53 | 2738.44 | 9.6415 | [5 empty] | 108.2798 | 2654.9857
20.12.2007 24:00 | 3600 | 2 | 759.96 | GGB | 767.766 | 774.305 | 770.33 | 266.85 | GGB | 11037 | GGB | 9.85 | GGB | 1024.27 | GGB | 58.57 | GGB | 170568.86 | GGB | 142001.5 | GGB | 0 | 0 | 2764 | 3600 | 2748.47 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 98154.07 | GGB | 98155.2 | 2748.47 | 2748.47 |  |  |  | 1 | 1 |  |  |  |  | 142001.5 | 2748.47 | 142001.5 | 2748.47 | 9.8582 | [5 empty] | 108.413 | 2661.4367
21.12.2007 01:00 | 3600 | 2 | 759.97 | GGB | 767.766 | 773.25 | 770.33 | 267.07 | GGB | 11042.8 | GGB | 9.85 | GGB | 1024.03 | GGB | 58.42 | GGB | 170746.01 | GGB | 142178.41 | GGB | 0 | 0 | 2762 | 3600 | 2746.11 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 98194.88 | GGB | 98196.01 | 2746.11 | 2746.11 |  |  |  | 1 | 1 |  |  |  |  | 142178.41 | 2746.11 | 142178.41 | 2746.11 | 9.5672 | [5 empty] | 108.4549 | 2658.1251
21.12.2007 02:00 | 3600 | 2 | 759.84 | GGB | 767.766 | 773.25 | 769.963 | 267.5 | GGB | 11055.3 | GGB | 9.85 | GGB | 1023.73 | GGB | 58.2 | GGB | 171334.69 | GGB | 142721.55 | GGB | 0 | 0 | 2781 | 3600 | 2765.6 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 98235.32 | GGB | 98236.45 | 2765.6 | 2765.6 |  |  |  | 1 | 1 |  |  |  |  | 142721.55 | 2765.6 | 142721.55 | 2765.6 | 9.7604 | [5 empty] | 109.6419 | 2648.0094
21.12.2007 03:00 | 3600 | 2 | 759.62 | GGB | 766.667 | 772.336 | 768.864 | 268.34 | GGB | 11067 | GGB | 9.85 | GGB | 1023.75 | GGB | 58 | GGB | 172080.72 | GGB | 143434.83 | GGB | 0 | 0 | 2791 | 3600 | 2775.98 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 98275.92 | GGB | 98277.06 | 2775.98 | 2775.98 |  |  |  | 1 | 1 |  |  |  |  | 143434.83 | 2775.98 | 143434.83 | 2775.98 | 9.8048 | [5 empty] | 110.6034 | 2634.8412
21.12.2007 04:00 | 3600 | 2 | 760.07 | GGB | 768.864 | 775.5 | 771.429 | 269.87 | GGB | 11066.4 | GGB | 9.86 | GGB | 1024.18 | GGB | 57.3 | GGB | 174501.46 | GGB | 145822.5 | GGB | 0 | 0 | 2764 | 3600 | 2748.58 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 98316.43 | GGB | 98317.56 | 2748.58 | 2748.58 |  |  |  | 1 | 1 |  |  |  |  | 145822.5 | 2748.58 | 145822.5 | 2748.58 | 9.8964 | [5 empty] | 111.3347 | 2591.6988
21.12.2007 05:00 | 3600 | 2 | 759.86 | GGB | 767.766 | 774.492 | 768.864 | 269.09 | GGB | 11095 | GGB | 9.85 | GGB | 1024.02 | GGB | 57.63 | GGB | 173347.21 | GGB | 144689.29 | GGB | 0 | 0 | 2791 | 3600 | 2775.22 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 98356.92 | GGB | 98358.06 | 2775.22 | 2775.22 |  |  |  | 1 | 1 |  |  |  |  | 144689.29 | 2775.22 | 144689.29 | 2775.22 | 9.9147 | [5 empty] | 111.5402 | 2611.9971
21.12.2007 06:00 | 3600 | 2 | 759.48 | GGB | 768.864 | 774.445 | 769.963 | 269.43 | GGB | 11124.4 | GGB | 9.85 | GGB | 1023.74 | GGB | 59.54 | GGB | 173581.58 | GGB | 144013.72 | GGB | 0 | 0 | 2835 | 3600 | 2819.38 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 98397.44 | GGB | 98398.57 | 2819.38 | 2819.38 |  |  |  | 1 | 1 |  |  |  |  | 144013.72 | 2819.38 | 144013.72 | 2819.38 | 10.0229 | [5 empty] | 112.7859 | 2624.25
21.12.2007 07:00 | 3600 | 2 | 759.8 | GGB | 767.766 | 773.273 | 768.864 | 269.37 | GGB | 11138 | GGB | 9.86 | GGB | 1023.75 | GGB | 57.63 | GGB | 173479.25 | GGB | 144762.65 | GGB | 0 | 0 | 2820 | 3600 | 2804.14 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 98438.46 | GGB | 98439.59 | 2804.14 | 2804.14 |  |  |  | 1 | 1 |  |  |  |  | 144762.65 | 2804.14 | 144762.65 | 2804.14 | 9.896 | [5 empty] | 112.7596 | 2610.6734
21.12.2007 08:00 | 3600 | 2 | 759.31 | GGB | 768.864 | 774.352 | 769.963 | 270.88 | GGB | 11121.3 | GGB | 9.84 | GGB | 1024.17 | GGB | 57.15 | GGB | 175182.57 | GGB | 146456.91 | GGB | 0 | 0 | 2848 | 3208 | 2832.27 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 98478.82 | GGB | 98479.95 | 2832.27 | 2832.27 |  |  |  | 1 | 1 |  |  |  |  | 146456.91 | 2832.27 | 146456.91 | 2832.27 | 10.2776 | [5 empty] | 115.2238 | 2580.4723
21.12.2007 09:00 | 3600 | 2 | 760.55 | GGB | 767.766 | 774.352 | 770.33 | 270.83 | GGB | 11123.2 | GGB | 9.87 | GGB | 1024.69 | GGB | 56.7 | GGB | 175540.18 | GGB | 147030.43 | GGB | 0 | 0 | 2777 | 3600 | 2761.87 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 98520.13 | GGB | 98521.27 | 2761.87 | 2761.87 |  |  |  | 1 | 1 |  |  |  |  | 147030.43 | 2761.87 | 147030.43 | 2761.87 | 9.8277 | [5 empty] | 112.7997 | 2570.4067
21.12.2007 10:00 | 3600 | 2 | 760.33 | GGB | 767.766 | 774.141 | 770.33 | 268.77 | GGB | 11134.3 | GGB | 9.87 | GGB | 1024.97 | GGB | 57.62 | GGB | 172984.1 | GGB | 144525.17 | GGB | 0 | 0 | 2794 | 3600 | 2778.3 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 98560.29 | GGB | 98561.43 | 2778.3 | 2778.3 |  |  |  | 1 | 1 |  |  |  |  | 144525.17 | 2778.3 | 144525.17 | 2778.3 | 9.9984 | [5 empty] | 111.5373 | 2614.9632
21.12.2007 11:00 | 3600 | 2 | 759.85 | GGB | 767.766 | 774.422 | 770.33 | 268.59 | GGB | 11111.2 | GGB | 9.85 | GGB | 1024.89 | GGB | 57.81 | GGB | 172488.95 | GGB | 144017.89 | GGB | 0 | 0 | 2815 | 3600 | 2799.74 | GGB | 100 | GGB | 41.49 | GGB | 41.49 | GGB | 98601.77 | GGB | 98602.92 | 2799.74 | 2799.74 |  |  |  | 1 | 1 |  |  |  |  | 144017.89 | 2799.74 | 144017.89 | 2799.74 | 9.7183 | [5 empty] | 112.0035 | 2624.174
21.12.2007 12:00 | 3600 | 2 | 760.26 | GGB | 767.766 | 774.422 | 770.33 | 268.42 | GGB | 11110.5 | GGB | 9.86 | GGB | 1025.06 | GGB | 57.98 | GGB | 172177.55 | GGB | 143708.39 | GGB | 0 | 0 | 2795 | 3600 | 2779.68 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 98641.74 | GGB | 98642.89 | 2779.68 | 2779.68 |  |  |  | 1 | 1 |  |  |  |  | 143708.39 | 2779.68 | 143708.39 | 2779.68 | 9.9941 | [5 empty] | 110.962 | 2629.8256
21.12.2007 13:00 | 3600 | 2 | 760.07 | GGB | 767.766 | 774.328 | 769.963 | 267.91 | GGB | 11090 | GGB | 9.86 | GGB | 1024.81 | GGB | 57.99 | GGB | 171850.75 | GGB | 143396.72 | GGB | 0 | 0 | 2791 | 3600 | 2775.63 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 98682.42 | GGB | 98683.58 | 2775.63 | 2775.63 |  |  |  | 1 | 1 |  |  |  |  | 143396.72 | 2775.63 | 143396.72 | 2775.63 | 9.7817 | [5 empty] | 110.5601 | 2635.5415
21.12.2007 14:00 | 3600 | 2 | 759.67 | GGB | 768.864 | 774.422 | 769.963 | 269.13 | GGB | 11040.6 | GGB | 9.84 | GGB | 1024.39 | GGB | 57.51 | GGB | 173389.02 | GGB | 144831.06 | GGB | 0 | 0 | 2782 | 3600 | 2766.36 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 98722.82 | GGB | 98723.98 | 2766.36 | 2766.36 |  |  |  | 1 | 1 |  |  |  |  | 144831.06 | 2766.36 | 144831.06 | 2766.36 | 9.9172 | [5 empty] | 111.293 | 2609.4403
21.12.2007 15:00 | 3600 | 2 | 760.63 | GGB | 767.766 | 774.422 | 770.33 | 268.33 | GGB | 11108.1 | GGB | 9.87 | GGB | 1024.41 | GGB | 57.47 | GGB | 173040.22 | GGB | 144557.58 | GGB | 0 | 0 | 2749 | 3600 | 2733.4 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 98762.69 | GGB | 98763.85 | 2733.4 | 2733.4 |  |  |  | 1 | 1 |  |  |  |  | 144557.58 | 2733.4 | 144557.58 | 2733.4 | 9.9106 | [5 empty] | 109.7594 | 2614.3769
21.12.2007 16:00 | 3600 | 2 | 759.78 | GGB | 767.766 | 774.422 | 770.33 | 267.48 | GGB | 11124.6 | GGB | 9.85 | GGB | 1024.57 | GGB | 57.57 | GGB | 172650.7 | GGB | 144214.02 | GGB | 0 | 0 | 2812 | 3600 | 2796.34 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 98804.33 | GGB | 98805.49 | 2796.34 | 2796.34 |  |  |  | 1 | 1 |  |  |  |  | 144214.02 | 2796.34 | 144214.02 | 2796.34 | 9.6847 | [5 empty] | 112.0198 | 2620.6051
21.12.2007 17:00 | 3600 | 2 | 759.75 | GGB | 767.766 | 774.492 | 769.963 | 267.52 | GGB | 11138.9 | GGB | 9.85 | GGB | 1024.63 | GGB | 57.3 | GGB | 173025.91 | GGB | 144649.71 | GGB | 0 | 0 | 2817 | 3600 | 2801.23 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 98844.22 | GGB | 98845.38 | 2801.23 | 2801.23 |  |  |  | 1 | 1 |  |  |  |  | 144649.71 | 2801.23 | 144649.71 | 2801.23 | 10.1579 | [5 empty] | 112.5548 | 2612.7118
21.12.2007 18:00 | 3600 | 2 | 759.77 | GGB | 766.667 | 773.367 | 769.963 | 267.55 | GGB | 11146.4 | GGB | 9.85 | GGB | 1024.82 | GGB | 57.26 | GGB | 173273.49 | GGB | 144901.89 | GGB | 0 | 0 | 2823 | 3600 | 2807.26 | GGB | 100 | GGB | 41.85 | GGB | 41.85 | GGB | 98886.08 | GGB | 98887.23 | 2807.26 | 2807.26 |  |  |  | 1 | 1 |  |  |  |  | 144901.89 | 2807.26 | 144901.89 | 2807.26 | 9.7199 | [5 empty] | 112.9937 | 2608.1647
21.12.2007 19:00 | 3600 | 2 | 759.27 | GGB | 766.667 | 772.289 | 768.864 | 268.95 | GGB | 11144.5 | GGB | 9.84 | GGB | 1025.14 | GGB | 56.61 | GGB | 175246.39 | GGB | 146886.3 | GGB | 0 | 0 | 2842 | 3600 | 2826.26 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 98926.47 | GGB | 98927.63 | 2826.26 | 2826.26 |  |  |  | 1 | 1 |  |  |  |  | 146886.3 | 2826.26 | 146886.3 | 2826.26 | 10.2757 | [5 empty] | 115.3164 | 2572.9289
21.12.2007 20:00 | 3600 | 2 | 760.38 | GGB | 767.766 | 773.391 | 770.33 | 269.66 | GGB | 11148.7 | GGB | 9.86 | GGB | 1025.48 | GGB | 56.36 | GGB | 176076.05 | GGB | 147743.51 | GGB | 0 | 0 | 2778 | 3600 | 2762.64 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 98967.05 | GGB | 98968.2 | 2762.64 | 2762.64 |  |  |  | 1 | 1 |  |  |  |  | 147743.51 | 2762.64 | 147743.51 | 2762.64 | 10.0607 | [5 empty] | 113.3784 | 2558.0007
21.12.2007 21:00 | 3600 | 2 | 760.05 | GGB | 767.766 | 772.336 | 768.864 | 268.56 | GGB | 11179.3 | GGB | 9.86 | GGB | 1025.26 | GGB | 56.43 | GGB | 174680.82 | GGB | 146508.82 | GGB | 0 | 0 | 2816 | 3600 | 2800.33 | GGB | 100 | GGB | 41.63 | GGB | 41.63 | GGB | 99008.68 | GGB | 99009.83 | 2800.33 | 2800.33 |  |  |  | 1 | 1 |  |  |  |  | 146508.82 | 2800.33 | 146508.82 | 2800.33 | 9.8552 | [5 empty] | 113.9647 | 2579.558
21.12.2007 22:00 | 3600 | 2 | 759.89 | GGB | 767.766 | 773.508 | 770.33 | 268.81 | GGB | 11194.4 | GGB | 9.85 | GGB | 1025.25 | GGB | 56.71 | GGB | 174571.89 | GGB | 146294.16 | GGB | 0 | 0 | 2844 | 3600 | 2828.33 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 99048.44 | GGB | 99049.59 | 2828.33 | 2828.33 |  |  |  | 1 | 1 |  |  |  |  | 146294.16 | 2828.33 | 146294.16 | 2828.33 | 10.4066 | [5 empty] | 114.9356 | 2583.343
21.12.2007 23:00 | 3600 | 2 | 759.68 | GGB | 767.766 | 773.484 | 769.963 | 269.08 | GGB | 11203.1 | GGB | 9.85 | GGB | 1025.42 | GGB | 56.63 | GGB | 174982.31 | GGB | 146698.09 | GGB | 0 | 0 | 2851 | 3600 | 2835.29 | GGB | 100 | GGB | 42.58 | GGB | 42.58 | GGB | 99091.01 | GGB | 99092.17 | 2835.29 | 2835.29 |  |  |  | 1 | 1 |  |  |  |  | 146698.09 | 2835.29 | 146698.09 | 2835.29 | 9.7682 | [5 empty] | 115.5366 | 2576.2299
21.12.2007 24:00 | 3600 | 2 | 759.44 | GGB | 767.766 | 773.461 | 769.963 | 269.39 | GGB | 11189.9 | GGB | 9.85 | GGB | 1025.26 | GGB | 56.09 | GGB | 176581.1 | GGB | 148255.18 | GGB | 0 | 0 | 2846 | 3600 | 2830.22 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 99130.62 | GGB | 99131.78 | 2830.22 | 2830.22 |  |  |  | 1 | 1 |  |  |  |  | 148255.18 | 2830.22 | 148255.18 | 2830.22 | 10.5932 | [5 empty] | 116.5541 | 2549.1723
22.12.2007 01:00 | 3600 | 2 | 760.03 | GGB | 767.766 | 773.461 | 769.963 | 270.45 | GGB | 11184.8 | GGB | 9.86 | GGB | 1025.25 | GGB | 55.86 | GGB | 177367.84 | GGB | 149019.27 | GGB | 0 | 0 | 2805 | 3600 | 2789.37 | GGB | 100 | GGB | 42.03 | GGB | 42.03 | GGB | 99172.65 | GGB | 99173.81 | 2789.37 | 2789.37 |  |  |  | 1 | 1 |  |  |  |  | 149019.27 | 2789.37 | 149019.27 | 2789.37 | 9.8898 | [5 empty] | 115.4639 | 2536.1015
22.12.2007 02:00 | 3600 | 2 | 760.26 | GGB | 767.766 | 773.625 | 769.963 | 269.11 | GGB | 11207 | GGB | 9.87 | GGB | 1024.7 | GGB | 56.29 | GGB | 175600.7 | GGB | 147262.64 | GGB | 0 | 0 | 2810 | 3600 | 2794.23 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 99213.03 | GGB | 99214.19 | 2794.23 | 2794.23 |  |  |  | 1 | 1 |  |  |  |  | 147262.64 | 2794.23 | 147262.64 | 2794.23 | 10.1903 | [5 empty] | 114.3016 | 2566.3536
22.12.2007 03:00 | 3600 | 2 | 759.68 | GGB | 767.766 | 773.742 | 769.963 | 268.49 | GGB | 11202.4 | GGB | 9.86 | GGB | 1024.41 | GGB | 56.41 | GGB | 174856.87 | GGB | 146545.7 | GGB | 0 | 0 | 2842 | 3600 | 2826.15 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 99253.94 | GGB | 99255.1 | 2826.15 | 2826.15 |  |  |  | 1 | 1 |  |  |  |  | 146545.7 | 2826.15 | 146545.7 | 2826.15 | 10.1237 | [5 empty] | 115.0445 | 2578.9088
22.12.2007 04:00 | 3600 | 2 | 759.62 | GGB | 767.766 | 773.977 | 769.963 | 268.63 | GGB | 11205.9 | GGB | 9.86 | GGB | 1023.94 | GGB | 56.4 | GGB | 175129.76 | GGB | 146711.76 | GGB | 0 | 0 | 2848 | 3600 | 2832.49 | GGB | 100 | GGB | 41.93 | GGB | 41.93 | GGB | 99295.87 | GGB | 99297.03 | 2832.49 | 2832.49 |  |  |  | 1 | 1 |  |  |  |  | 146711.76 | 2832.49 | 146711.76 | 2832.49 | 9.9108 | [5 empty] | 115.4332 | 2575.9898
22.12.2007 05:00 | 3600 | 2 | 759.27 | GGB | 766.667 | 772.828 | 768.864 | 269.27 | GGB | 11180 | GGB | 9.85 | GGB | 1023.56 | GGB | 56.03 | GGB | 176142.07 | GGB | 147669.04 | GGB | 0 | 0 | 2849 | 3600 | 2833.26 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 99336 | GGB | 99337.17 | 2833.26 | 2833.26 |  |  |  | 1 | 1 |  |  |  |  | 147669.04 | 2833.26 | 147669.04 | 2833.26 | 10.4231 | [5 empty] | 116.218 | 2559.2907
22.12.2007 06:00 | 3600 | 2 | 759.86 | GGB | 767.766 | 773.906 | 769.963 | 270.06 | GGB | 11189.8 | GGB | 9.86 | GGB | 1023.42 | GGB | 55.55 | GGB | 177455.87 | GGB | 148969.42 | GGB | 0 | 0 | 2819 | 3600 | 2803.43 | GGB | 100 | GGB | 41.73 | GGB | 41.73 | GGB | 99377.73 | GGB | 99378.9 | 2803.43 | 2803.43 |  |  |  | 1 | 1 |  |  |  |  | 148969.42 | 2803.43 | 148969.42 | 2803.43 | 10.0078 | [5 empty] | 116.007 | 2536.9502
22.12.2007 07:00 | 3600 | 2 | 759.9 | GGB | 767.766 | 773.039 | 768.864 | 268.42 | GGB | 11228.2 | GGB | 9.86 | GGB | 1023.29 | GGB | 56.28 | GGB | 175149.56 | GGB | 146689.91 | GGB | 0 | 0 | 2840 | 3600 | 2824.17 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 99418.1 | GGB | 99419.27 | 2824.17 | 2824.17 |  |  |  | 1 | 1 |  |  |  |  | 146689.91 | 2824.17 | 146689.91 | 2824.17 | 10.262 | [5 empty] | 115.077 | 2576.3735
22.12.2007 08:00 | 3600 | 2 | 759.57 | GGB | 767.766 | 773.039 | 769.963 | 268.68 | GGB | 11217.5 | GGB | 9.86 | GGB | 1023.32 | GGB | 56.29 | GGB | 175333.32 | GGB | 146842.57 | GGB | 0 | 0 | 2858 | 3600 | 2842.94 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 99459.46 | GGB | 99460.63 | 2842.94 | 2842.94 |  |  |  | 1 | 1 |  |  |  |  | 146842.57 | 2842.94 | 146842.57 | 2842.94 | 10.0934 | [5 empty] | 115.9624 | 2573.6951
22.12.2007 09:00 | 3600 | 2 | 759.6 | GGB | 767.766 | 773.297 | 769.963 | 268.99 | GGB | 11225.8 | GGB | 9.86 | GGB | 1023.76 | GGB | 56.24 | GGB | 175605.1 | GGB | 147153.86 | GGB | 0 | 0 | 2862 | 3600 | 2846.77 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 99500.84 | GGB | 99502.01 | 2846.77 | 2846.77 |  |  |  | 1 | 1 |  |  |  |  | 147153.86 | 2846.77 | 147153.86 | 2846.77 | 10.1236 | [5 empty] | 116.3648 | 2568.2507
22.12.2007 10:00 | 3600 | 2 | 759.11 | GGB | 767.766 | 772.242 | 768.864 | 269.88 | GGB | 11226.8 | GGB | 9.85 | GGB | 1024.14 | GGB | 56.17 | GGB | 176010.03 | GGB | 147579.38 | GGB | 0 | 0 | 2893 | 3600 | 2877.33 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 99541.15 | GGB | 99542.33 | 2877.33 | 2877.33 |  |  |  | 1 | 1 |  |  |  |  | 147579.38 | 2877.33 | 147579.38 | 2877.33 | 10.5316 | [5 empty] | 117.954 | 2560.8456
22.12.2007 11:00 | 3600 | 2 | 759.04 | GGB | 767.766 | 773.484 | 770.33 | 271.77 | GGB | 11199.1 | GGB | 9.84 | GGB | 1023.78 | GGB | 55.87 | GGB | 178050.05 | GGB | 149374.51 | GGB | 0 | 0 | 2889 | 3600 | 2873.14 | GGB | 100 | GGB | 41.65 | GGB | 41.65 | GGB | 99582.8 | GGB | 99583.98 | 2873.14 | 2873.14 |  |  |  | 1 | 1 |  |  |  |  | 149374.51 | 2873.14 | 149374.51 | 2873.14 | 10.3043 | [5 empty] | 119.215 | 2530.0702
22.12.2007 12:00 | 3600 | 2 | 759.43 | GGB | 768.864 | 773.883 | 769.963 | 272.47 | GGB | 11202.7 | GGB | 9.85 | GGB | 1023.91 | GGB | 55.94 | GGB | 178757.57 | GGB | 149957.75 | GGB | 0 | 0 | 2866 | 3600 | 2850.46 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 99621.93 | GGB | 99623.11 | 2850.46 | 2850.46 |  |  |  | 1 | 1 |  |  |  |  | 149957.75 | 2850.46 | 149957.75 | 2850.46 | 10.9238 | [5 empty] | 118.7357 | 2520.2299
22.12.2007 13:00 | 3600 | 2 | 759.89 | GGB | 765.201 | 771.773 | 767.766 | 270.77 | GGB | 11255.9 | GGB | 9.87 | GGB | 1023.48 | GGB | 56.65 | GGB | 176398.45 | GGB | 147596.44 | GGB | 0 | 0 | 2870 | 3600 | 2854.4 | GGB | 100 | GGB | 42.27 | GGB | 42.27 | GGB | 99664.2 | GGB | 99665.38 | 2854.4 | 2854.4 |  |  |  | 1 | 1 |  |  |  |  | 147596.44 | 2854.4 | 147596.44 | 2854.4 | 9.9669 | [5 empty] | 117.0276 | 2560.5496
22.12.2007 14:00 | 3600 | 2 | 759.36 | GGB | 767.766 | 773.086 | 769.963 | 270.93 | GGB | 11254.9 | GGB | 9.86 | GGB | 1022.99 | GGB | 56.58 | GGB | 176802.27 | GGB | 147895.87 | GGB | 0 | 0 | 2899 | 3600 | 2883.26 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 99704.71 | GGB | 99705.88 | 2883.26 | 2883.26 |  |  |  | 1 | 1 |  |  |  |  | 147895.87 | 2883.26 | 147895.87 | 2883.26 | 10.5289 | [5 empty] | 118.4506 | 2555.3655
22.12.2007 15:00 | 3600 | 2 | 759.23 | GGB | 767.766 | 773.438 | 769.963 | 271.08 | GGB | 11246 | GGB | 9.85 | GGB | 1022.74 | GGB | 56.55 | GGB | 176836.38 | GGB | 147901.57 | GGB | 0 | 0 | 2908 | 3600 | 2892.26 | GGB | 100 | GGB | 42.05 | GGB | 42.05 | GGB | 99746.76 | GGB | 99747.93 | 2892.26 | 2892.26 |  |  |  | 1 | 1 |  |  |  |  | 147901.57 | 2892.26 | 147901.57 | 2892.26 | 10.1729 | [5 empty] | 118.8249 | 2555.267
22.12.2007 16:00 | 3600 | 2 | 759.1 | GGB | 764.102 | 770.25 | 766.667 | 271.7 | GGB | 11231.9 | GGB | 9.85 | GGB | 1023.44 | GGB | 56.27 | GGB | 177310.63 | GGB | 148523.99 | GGB | 0 | 0 | 2905 | 3600 | 2889.81 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 99787.63 | GGB | 99788.8 | 2889.81 | 2889.81 |  |  |  | 1 | 1 |  |  |  |  | 148523.99 | 2889.81 | 148523.99 | 2889.81 | 10.5017 | [5 empty] | 119.2239 | 2544.5586
22.12.2007 17:00 | 3600 | 2 | 759.66 | GGB | 766.3 | 772.406 | 767.766 | 271.84 | GGB | 11259.5 | GGB | 9.86 | GGB | 1023.39 | GGB | 56.19 | GGB | 177526.29 | GGB | 148735.37 | GGB | 0 | 0 | 2882 | 3600 | 2866.45 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 99827.91 | GGB | 99829.08 | 2866.45 | 2866.45 |  |  |  | 1 | 1 |  |  |  |  | 148735.37 | 2866.45 | 148735.37 | 2866.45 | 10.5845 | [5 empty] | 118.4285 | 2540.9423
22.12.2007 18:00 | 3600 | 2 | 759.43 | GGB | 766.3 | 772.57 | 768.864 | 271.51 | GGB | 11259.6 | GGB | 9.86 | GGB | 1023.43 | GGB | 56.44 | GGB | 176938.71 | GGB | 148133.7 | GGB | 0 | 0 | 2903 | 3600 | 2887.83 | GGB | 100 | GGB | 42.19 | GGB | 42.19 | GGB | 99870.09 | GGB | 99871.27 | 2887.83 | 2887.83 |  |  |  | 1 | 1 |  |  |  |  | 148133.7 | 2887.83 | 148133.7 | 2887.83 | 10.1395 | [5 empty] | 118.8292 | 2551.2628
22.12.2007 19:00 | 3600 | 2 | 759.16 | GGB | 766.3 | 772.617 | 768.864 | 271.83 | GGB | 11261.9 | GGB | 9.85 | GGB | 1023.21 | GGB | 56.26 | GGB | 177462.47 | GGB | 148621.67 | GGB | 0 | 0 | 2921 | 3600 | 2905.8 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 99909.74 | GGB | 99910.92 | 2905.8 | 2905.8 |  |  |  | 1 | 1 |  |  |  |  | 148621.67 | 2905.8 | 148621.67 | 2905.8 | 10.8919 | [5 empty] | 119.9625 | 2542.8862
22.12.2007 20:00 | 3600 | 2 | 759.34 | GGB | 766.667 | 772.594 | 768.864 | 272.05 | GGB | 11280.4 | GGB | 9.86 | GGB | 1023.36 | GGB | 56.41 | GGB | 177603.32 | GGB | 148695.92 | GGB | 0 | 0 | 2913 | 3600 | 2897.61 | GGB | 100 | GGB | 42.26 | GGB | 42.26 | GGB | 99952.01 | GGB | 99953.18 | 2897.61 | 2897.61 |  |  |  | 1 | 1 |  |  |  |  | 148695.92 | 2897.61 | 148695.92 | 2897.61 | 10.1955 | [5 empty] | 119.6841 | 2541.6165
22.12.2007 21:00 | 3600 | 2 | 758.94 | GGB | 766.3 | 772.195 | 768.864 | 272.04 | GGB | 11293.7 | GGB | 9.85 | GGB | 1023.99 | GGB | 56.07 | GGB | 178403.26 | GGB | 149609.39 | GGB | 0 | 0 | 2944 | 3600 | 2928.55 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 99992.21 | GGB | 99993.38 | 2928.55 | 2928.55 |  |  |  | 1 | 1 |  |  |  |  | 149609.39 | 2928.55 | 149609.39 | 2928.55 | 10.899 | [5 empty] | 121.7052 | 2526.0981
22.12.2007 22:00 | 3600 | 2 | 759.66 | GGB | 767.766 | 773.484 | 769.963 | 272.74 | GGB | 11315.1 | GGB | 9.86 | GGB | 1023.97 | GGB | 56.44 | GGB | 178347.14 | GGB | 149390.71 | GGB | 0 | 0 | 2920 | 3600 | 2904.44 | GGB | 100 | GGB | 42.16 | GGB | 42.16 | GGB | 100034.37 | GGB | 100035.54 | 2904.44 | 2904.44 |  |  |  | 1 | 1 |  |  |  |  | 149390.71 | 2904.44 | 149390.71 | 2904.44 | 10.2917 | [5 empty] | 120.5268 | 2529.7959
22.12.2007 23:00 | 3600 | 2 | 759.06 | GGB | 768.864 | 774.305 | 771.429 | 272.48 | GGB | 11301 | GGB | 9.85 | GGB | 1024.01 | GGB | 56.39 | GGB | 178544.1 | GGB | 149584.22 | GGB | 0 | 0 | 2939 | 3600 | 2923.55 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 100075.23 | GGB | 100076.4 | 2923.55 | 2923.55 |  |  |  | 1 | 1 |  |  |  |  | 149584.22 | 2923.55 | 149584.22 | 2923.55 | 10.7028 | [5 empty] | 121.4769 | 2526.5232
22.12.2007 24:00 | 3600 | 2 | 759.06 | GGB | 764.102 | 771.141 | 766.667 | 273 | GGB | 11306.6 | GGB | 9.85 | GGB | 1024.24 | GGB | 56.4 | GGB | 179000.74 | GGB | 149998.55 | GGB | 0 | 0 | 2940 | 3600 | 2924.76 | GGB | 100 | GGB | 41.04 | GGB | 41.04 | GGB | 100116.27 | GGB | 100117.44 | 2924.76 | 2924.76 |  |  |  | 1 | 1 |  |  |  |  | 149998.55 | 2924.76 | 149998.55 | 2924.76 | 10.6898 | [5 empty] | 121.8638 | 2519.5444
23.12.2007 01:00 | 3600 | 2 | 759.25 | GGB | 767.766 | 773.133 | 769.963 | 273.13 | GGB | 11338.7 | GGB | 9.86 | GGB | 1024.6 | GGB | 56.25 | GGB | 179379.26 | GGB | 150438.93 | GGB | 0 | 0 | 2944 | 3600 | 2928.75 | GGB | 100 | GGB | 42.06 | GGB | 42.06 | GGB | 100158.33 | GGB | 100159.5 | 2928.75 | 2928.75 |  |  |  | 1 | 1 |  |  |  |  | 150438.93 | 2928.75 | 150438.93 | 2928.75 | 10.4755 | [5 empty] | 122.3883 | 2512.1689
23.12.2007 02:00 | 3600 | 2 | 759.24 | GGB | 765.201 | 771.07 | 767.766 | 273.84 | GGB | 11353.2 | GGB | 9.85 | GGB | 1024.76 | GGB | 56.09 | GGB | 180119.79 | GGB | 151153.25 | GGB | 0 | 0 | 2956 | 3600 | 2940.83 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 100198.67 | GGB | 100199.84 | 2940.83 | 2940.83 |  |  |  | 1 | 1 |  |  |  |  | 151153.25 | 2940.83 | 151153.25 | 2940.83 | 11.0192 | [5 empty] | 123.4767 | 2500.2969
23.12.2007 03:00 | 3600 | 2 | 759.61 | GGB | 767.766 | 773.109 | 769.963 | 273.73 | GGB | 11372.4 | GGB | 9.86 | GGB | 1024.72 | GGB | 56.13 | GGB | 180020.76 | GGB | 151046.98 | GGB | 0 | 0 | 2944 | 3600 | 2928.16 | GGB | 100 | GGB | 42.33 | GGB | 42.33 | GGB | 100240.99 | GGB | 100242.17 | 2928.16 | 2928.16 |  |  |  | 1 | 1 |  |  |  |  | 151046.98 | 2928.16 | 151046.98 | 2928.16 | 10.4486 | [5 empty] | 122.8583 | 2502.056
23.12.2007 04:00 | 3600 | 2 | 759.15 | GGB | 766.3 | 772.266 | 768.864 | 274.12 | GGB | 11366.5 | GGB | 9.85 | GGB | 1024.91 | GGB | 56.08 | GGB | 180566.53 | GGB | 151556.12 | GGB | 0 | 0 | 2968 | 3600 | 2951.92 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 100281.91 | GGB | 100283.09 | 2951.92 | 2951.92 |  |  |  | 1 | 1 |  |  |  |  | 151556.12 | 2951.92 | 151556.12 | 2951.92 | 10.9331 | [5 empty] | 124.2727 | 2493.6505
23.12.2007 05:00 | 3600 | 2 | 759.51 | GGB | 766.667 | 773.156 | 768.864 | 274.32 | GGB | 11391.8 | GGB | 9.86 | GGB | 1025.01 | GGB | 55.93 | GGB | 180873.52 | GGB | 151899.86 | GGB | 0 | 0 | 2955 | 3600 | 2939.61 | GGB | 100 | GGB | 41.73 | GGB | 41.73 | GGB | 100323.64 | GGB | 100324.82 | 2939.61 | 2939.61 |  |  |  | 1 | 1 |  |  |  |  | 151899.86 | 2939.61 | 151899.86 | 2939.61 | 10.7004 | [5 empty] | 124.0351 | 2488.0076
23.12.2007 06:00 | 3600 | 2 | 759.14 | GGB | 766.667 | 773.25 | 768.864 | 274.42 | GGB | 11389.7 | GGB | 9.85 | GGB | 1024.83 | GGB | 55.94 | GGB | 181104.59 | GGB | 152060.4 | GGB | 0 | 0 | 2975 | 3600 | 2959.61 | GGB | 100 | GGB | 41.54 | GGB | 41.54 | GGB | 100365.18 | GGB | 100366.36 | 2959.61 | 2959.61 |  |  |  | 1 | 1 |  |  |  |  | 152060.4 | 2959.61 | 152060.4 | 2959.61 | 10.8339 | [5 empty] | 125.011 | 2485.3808
23.12.2007 07:00 | 3600 | 2 | 759.5 | GGB | 766.667 | 773.273 | 768.864 | 274.24 | GGB | 11386.1 | GGB | 9.86 | GGB | 1025.29 | GGB | 56.01 | GGB | 180435.59 | GGB | 151534.41 | GGB | 0 | 0 | 2960 | 3600 | 2944.62 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 100405.95 | GGB | 100407.13 | 2944.62 | 2944.62 |  |  |  | 1 | 1 |  |  |  |  | 151534.41 | 2944.62 | 151534.41 | 2944.62 | 10.9446 | [5 empty] | 123.9476 | 2494.0078
23.12.2007 08:00 | 3600 | 2 | 758.59 | GGB | 767.766 | 773.391 | 768.864 | 274.31 | GGB | 11374.9 | GGB | 9.85 | GGB | 1025.48 | GGB | 55.89 | GGB | 180518.11 | GGB | 151690.52 | GGB | 0 | 0 | 3001 | 3600 | 2984.85 | GGB | 100 | GGB | 42.78 | GGB | 42.78 | GGB | 100448.73 | GGB | 100449.91 | 2984.85 | 2984.85 |  |  |  | 1 | 1 |  |  |  |  | 151690.52 | 2984.85 | 151690.52 |  | 10.5838 | [5 empty] | 125.7704 | 2491.4411
23.12.2007 09:00 | 3600 | 2 | 758.96 | GGB | 765.201 | 770.484 | 766.3 | 274.9 | GGB | 11399.5 | GGB | 9.85 | GGB | 1025.79 | GGB | 55.72 | GGB | 181120 | GGB | 152318.1 | GGB | 0 | 0 | 3000 | 3600 | 2983.89 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 100489.28 | GGB | 100490.46 | 2983.89 | 2983.89 |  |  |  | 1 | 1 |  |  |  |  | 152318.1 | 2983.89 | 152318.1 |  | 11.2084 | [5 empty] | 126.2501 | 2481.1759
23.12.2007 10:00 | 3600 | 2 | 759.1 | GGB | 766.667 | 772.664 | 767.766 | 275.42 | GGB | 11427.1 | GGB | 9.86 | GGB | 1026.17 | GGB | 55.74 | GGB | 181687.77 | GGB | 152842.86 | GNB | 0 | 0 | 3002 | 3600 | 2986.65 | GGB | 100 | GGB | 42.84 | GGB | 42.84 | GGB | 100532.12 | GGB | 100533.3 | 2986.65 | 2986.65 |  |  |  | 1 | 1 |  |  |  |  | 152842.86 | 2986.65 |  |  | 10.6557 | [5 empty] | 126.8023 | 2472.6572
23.12.2007 11:00 | 3600 | 2 | 758.09 | GGB | 767.766 | 773.555 | 769.963 | 275.58 | GGB | 11435.2 | GGB | 9.86 | GGB | 1026.54 | GGB | 55.49 | GGB | 181871.53 | GGB | 153170.66 | GNB | 0 | 0 | 3022 | 3600 | 3006.29 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 100572.95 | GGB | 100574.13 | 3006.29 | 3006.29 |  |  |  | 1 | 1 |  |  |  |  | 153170.66 | 3006.29 |  |  | 11.2779 | [5 empty] | 127.9098 | 2467.3655
23.12.2007 12:00 | 3600 | 2 | 757.94 | GGB | 766.3 | 771.773 | 767.766 | 275.78 | GGB | 11442.5 | GGB | 9.85 | GGB | 1026.48 | GGB | 55.35 | GGB | 182362.28 | GGB | 153641.31 | GNB | 0 | 0 | 3028 | 3600 | 3012.05 | GGB | 100 | GGB | 42.14 | GGB | 42.14 | GGB | 100615.09 | GGB | 100616.27 | 3012.05 | 3012.05 |  |  |  | 1 | 1 |  |  |  |  | 153641.31 | 3012.05 |  |  | 10.9819 | [5 empty] | 128.5487 | 2459.8072
23.12.2007 13:00 | 3600 | 2 | 758.19 | GGB | 767.766 | 772.617 | 769.963 | 275.74 | GGB | 11449.5 | GGB | 9.86 | GGB | 1026.37 | GGB | 55.31 | GGB | 182429.4 | GGB | 153698.38 | GNB | 0 | 0 | 3023 | 3600 | 3007.48 | GGB | 100 | GGB | 41.99 | GGB | 41.99 | GGB | 100657.07 | GGB | 100658.26 | 3007.48 | 3007.48 |  |  |  | 1 | 1 |  |  |  |  | 153698.38 | 3007.48 |  |  | 11.0084 | [5 empty] | 128.4013 | 2458.8938
23.12.2007 14:00 | 3600 | 2 | 758.2 | GGB | 765.201 | 771.07 | 767.766 | 275.93 | GGB | 11454 | GGB | 9.86 | GGB | 1026.49 | GGB | 55.13 | GGB | 182651.67 | GGB | 153986.42 | GNB | 0 | 0 | 3024 | 3600 | 3008.67 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 100698.13 | GGB | 100699.32 | 3008.67 | 3008.67 |  |  |  | 1 | 1 |  |  |  |  | 153986.42 | 3008.67 |  |  | 11.2833 | [5 empty] | 128.6929 | 2454.2943
23.12.2007 15:00 | 3600 | 2 | 757.84 | GGB | 766.3 | 772.125 | 767.766 | 276.74 | GGB | 11451.1 | GGB | 9.85 | GGB | 1026.37 | GGB | 55.29 | GGB | 182713.28 | GGB | 153947.85 | GNB | 0 | 0 | 3049 | 3600 | 3033.53 | GGB | 100 | GGB | 42.82 | GGB | 42.82 | GGB | 100740.95 | GGB | 100742.14 | 3033.53 | 3033.53 |  |  |  | 1 | 1 |  |  |  |  | 153947.85 | 3033.53 |  |  | 10.9062 | [5 empty] | 129.7237 | 2454.9092
23.12.2007 16:00 | 3600 | 2 | 758.06 | GGB | 766.3 | 771.82 | 768.864 | 277.21 | GGB | 11454.1 | GGB | 9.85 | GGB | 1026.8 | GGB | 55.43 | GGB | 182868.43 | GGB | 154078.02 | GNB | 0 | 0 | 3045 | 3600 | 3029.72 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 100781.21 | GGB | 100782.4 | 3029.72 | 3029.72 |  |  |  | 1 | 1 |  |  |  |  | 154078.02 | 3029.72 |  |  | 11.595 | [5 empty] | 129.6703 | 2452.8353
23.12.2007 17:00 | 3600 | 2 | 758.35 | GGB | 765.201 | 771.656 | 767.766 | 277.59 | GGB | 11466.6 | GGB | 9.85 | GGB | 1026.65 | GGB | 55.5 | GGB | 183067.59 | GGB | 154190.16 | GNB | 0 | 0 | 3041 | 3600 | 3025.14 | GGB | 100 | GGB | 42.73 | GGB | 42.73 | GGB | 100823.94 | GGB | 100825.13 | 3025.14 | 3025.14 |  |  |  | 1 | 1 |  |  |  |  | 154190.16 | 3025.14 |  |  | 10.9161 | [5 empty] | 129.5686 | 2451.0514
23.12.2007 18:00 | 3600 | 2 | 758.14 | GGB | 766.667 | 772.242 | 768.864 | 277.65 | GGB | 11470.5 | GGB | 9.86 | GGB | 1026.7 | GGB | 55.6 | GGB | 183274.46 | GGB | 154321.94 | GNB | 0 | 0 | 3052 | 3600 | 3036.7 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 100864.78 | GGB | 100865.97 | 3036.7 | 3036.7 |  |  |  | 1 | 1 |  |  |  |  | 154321.94 | 3036.7 |  |  | 11.4748 | [5 empty] | 130.1748 | 2448.9583
23.12.2007 19:00 | 3600 | 2 | 758.34 | GGB | 767.766 | 773.297 | 769.963 | 276.82 | GGB | 11446.3 | GGB | 9.86 | GGB | 1026.82 | GGB | 55.65 | GGB | 182660.47 | GGB | 153801.88 | GNB | 0 | 0 | 3033 | 3600 | 3017.76 | GGB | 100 | GGB | 41.96 | GGB | 41.96 | GGB | 100906.74 | GGB | 100907.93 | 3017.76 | 3017.76 |  |  |  | 1 | 1 |  |  |  |  | 153801.88 | 3017.76 |  |  | 11.0614 | [5 empty] | 128.927 | 2457.2391
23.12.2007 20:00 | 3600 | 2 | 758.6 | GGB | 767.766 | 773.227 | 769.963 | 274.62 | GGB | 11353.7 | GGB | 9.85 | GGB | 1026.97 | GGB | 56.1 | GGB | 180207.82 | GGB | 151549.98 | GGB | 0 | 0 | 2967 | 3600 | 2951.26 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 100948.14 | GGB | 100949.33 | 2951.26 | 2951.26 |  |  |  | 1 | 1 |  |  |  |  | 151549.98 | 2951.26 | 151549.98 | 2951.26 | 10.8035 | [5 empty] | 124.2398 | 2493.7516
23.12.2007 21:00 | 3600 | 2 | 758.92 | GGB | 766.3 | 772.266 | 768.864 | 275.11 | GGB | 11351.4 | GGB | 9.85 | GGB | 1027.29 | GGB | 56.26 | GGB | 179845.8 | GGB | 151220.83 | GGB | 0 | 0 | 2955 | 3600 | 2939.33 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 100989.09 | GGB | 100990.28 | 2939.33 | 2939.33 |  |  |  | 1 | 1 |  |  |  |  | 151220.83 | 2939.33 | 151220.83 | 2939.33 | 10.8544 | [5 empty] | 123.4689 | 2499.1795
23.12.2007 22:00 | 3600 | 2 | 759.25 | GGB | 766.667 | 773.461 | 768.864 | 274.98 | GGB | 11349 | GGB | 9.86 | GGB | 1027.4 | GGB | 56.37 | GGB | 179536.61 | GGB | 150924.51 | GGB | 0 | 0 | 2937 | 3600 | 2921.77 | GGB | 100 | GGB | 42.36 | GGB | 42.36 | GGB | 101031.45 | GGB | 101032.64 | 2921.77 | 2921.77 |  |  |  | 1 | 1 |  |  |  |  | 150924.51 | 2921.77 | 150924.51 | 2921.77 | 10.41 | [5 empty] | 122.4908 | 2504.0863
23.12.2007 23:00 | 3600 | 2 | 758.71 | GGB | 767.766 | 774.68 | 770.33 | 274.94 | GGB | 11357.5 | GGB | 9.85 | GGB | 1027.81 | GGB | 56.15 | GGB | 179897.52 | GGB | 151388.32 | GGB | 0 | 0 | 2953 | 3600 | 2937.34 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 101071.47 | GGB | 101072.67 | 2937.34 | 2937.34 |  |  |  | 1 | 1 |  |  |  |  | 151388.32 | 2937.34 | 151388.32 | 2937.34 | 11.1086 | [5 empty] | 123.5219 | 2496.4145
23.12.2007 24:00 | 3600 | 2 | 758.91 | GGB | 767.766 | 773.156 | 769.963 | 275.72 | GGB | 11363 | GGB | 9.85 | GGB | 1027.65 | GGB | 56.21 | GGB | 180294.74 | GGB | 151676.03 | GGB | 0 | 0 | 2961 | 3600 | 2945.41 | GGB | 100 | GGB | 43.51 | GGB | 43.51 | GGB | 101114.98 | GGB | 101116.18 | 2945.41 | 2945.41 |  |  |  | 1 | 1 |  |  |  |  | 151676.03 | 2945.41 | 151676.03 | 2945.41 | 10.2677 | [5 empty] | 124.0967 | 2491.6791
24.12.2007 01:00 | 3600 | 2 | 758.78 | GGB | 766.667 | 773.039 | 769.963 | 275.93 | GGB | 11367.6 | GGB | 9.85 | GGB | 1027.64 | GGB | 56.27 | GGB | 180387.17 | GGB | 151721.23 | GGB | 0 | 0 | 2962 | 3600 | 2946.08 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 101154.12 | GGB | 101155.32 | 2946.08 | 2946.08 |  |  |  | 1 | 1 |  |  |  |  | 151721.23 | 2946.08 | 151721.23 | 2946.08 | 11.4201 | [5 empty] | 124.1619 | 2490.9368
24.12.2007 02:00 | 3600 | 2 | 758.83 | GGB | 766.3 | 772.992 | 768.864 | 275.86 | GGB | 11366.8 | GGB | 9.85 | GGB | 1027.87 | GGB | 56.32 | GGB | 180246.33 | GGB | 151612.35 | GGB | 0 | 0 | 2964 | 3600 | 2948.3 | GGB | 100 | GGB | 43.85 | GGB | 43.85 | GGB | 101197.97 | GGB | 101199.17 | 2948.3 | 2948.3 |  |  |  | 1 | 1 |  |  |  |  | 151612.35 | 2948.3 | 151612.35 | 2948.3 | 10.1938 | [5 empty] | 124.1663 | 2492.7257
24.12.2007 03:00 | 3600 | 2 | 759.22 | GGB | 767.766 | 773.016 | 770.696 | 275.93 | GGB | 11379 | GGB | 9.86 | GGB | 1027.7 | GGB | 56.32 | GGB | 180475.2 | GGB | 151781.24 | GGB | 0 | 0 | 2952 | 3600 | 2935.93 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 101237.1 | GGB | 101238.3 | 2935.93 | 2935.93 |  |  |  | 1 | 1 |  |  |  |  | 151781.24 | 2935.93 | 151781.24 | 2935.93 | 11.3882 | [5 empty] | 123.7831 | 2489.952
24.12.2007 04:00 | 3600 | 2 | 758.91 | GGB | 766.3 | 771.75 | 769.597 | 276.08 | GGB | 11373 | GGB | 9.85 | GGB | 1028 | GGB | 56.22 | GGB | 180748.08 | GGB | 152101.33 | GGB | 0 | 0 | 2968 | 3600 | 2952.2 | GGB | 100 | GGB | 43.74 | GGB | 43.74 | GGB | 101280.84 | GGB | 101282.04 | 2952.2 | 2952.2 |  |  |  | 1 | 1 |  |  |  |  | 152101.33 | 2952.2 | 152101.33 | 2952.2 | 10.266 | [5 empty] | 124.7315 | 2484.712
24.12.2007 05:00 | 3600 | 2 | 759.15 | GGB | 766.667 | 772.594 | 770.33 | 276.17 | GGB | 11387.6 | GGB | 9.86 | GGB | 1028.07 | GGB | 56.18 | GGB | 180759.08 | GGB | 152138.48 | GGB | 0 | 0 | 2952 | 3600 | 2936.58 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 101320.6 | GGB | 101321.8 | 2936.58 | 2936.58 |  |  |  | 1 | 1 |  |  |  |  | 152138.48 | 2936.58 | 152138.48 | 2936.58 | 11.2366 | [5 empty] | 124.1019 | 2484.1053
24.12.2007 06:00 | 3600 | 2 | 758.79 | GGB | 767.766 | 772.852 | 769.963 | 276.26 | GGB | 11377.2 | GGB | 9.85 | GGB | 1027.74 | GGB | 56.21 | GGB | 180996.76 | GGB | 152277.62 | GGB | 0 | 0 | 2979 | 3600 | 2963.02 | GGB | 100 | GGB | 42.83 | GGB | 42.83 | GGB | 101363.43 | GGB | 101364.63 | 2963.02 | 2963.02 |  |  |  | 1 | 1 |  |  |  |  | 152277.62 | 2963.02 | 152277.62 | 2963.02 | 10.5347 | [5 empty] | 125.3338 | 2481.8355
24.12.2007 07:00 | 3600 | 2 | 759.18 | GGB | 767.766 | 773.719 | 769.963 | 276.12 | GGB | 11380.3 | GGB | 9.86 | GGB | 1027.43 | GGB | 56.21 | GGB | 180871.32 | GGB | 152125.85 | GGB | 0 | 0 | 2959 | 3600 | 2942.92 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 101404.33 | GGB | 101405.53 | 2942.92 | 2942.92 |  |  |  | 1 | 1 |  |  |  |  | 152125.85 | 2942.92 | 152125.85 | 2942.92 | 10.9461 | [5 empty] | 124.3595 | 2484.3115
24.12.2007 08:00 | 3600 | 2 | 758.95 | GGB | 766.667 | 772.43 | 768.864 | 276.52 | GGB | 11392.5 | GGB | 9.85 | GGB | 1027.63 | GGB | 55.99 | GGB | 181337.86 | GGB | 152648.1 | GGB | 0 | 0 | 2976 | 3600 | 2960.39 | GGB | 100 | GGB | 41.94 | GGB | 41.94 | GGB | 101446.27 | GGB | 101447.47 | 2960.39 | 2960.39 |  |  |  | 1 | 1 |  |  |  |  | 152648.1 | 2960.39 | 152648.1 | 2960.39 | 10.7749 | [5 empty] | 125.5272 | 2475.812
24.12.2007 09:00 | 3600 | 2 | 758.98 | GGB | 766.667 | 772.664 | 768.864 | 276.67 | GGB | 11406.2 | GGB | 9.85 | GGB | 1028.02 | GGB | 55.99 | GGB | 181757.09 | GGB | 153060.04 | GNB | 0 | 0 | 2981 | 3600 | 2965.03 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 101487.2 | GGB | 101488.41 | 2965.03 | 2965.03 |  |  |  | 1 | 1 |  |  |  |  | 153060.04 | 2965.03 |  |  | 11.0852 | [5 empty] | 126.0632 | 2469.1487
24.12.2007 10:00 | 3600 | 2 | 759.28 | GGB | 766.667 | 772.688 | 768.864 | 276.59 | GGB | 11424.8 | GGB | 9.86 | GGB | 1028.89 | GGB | 56.05 | GGB | 181534.82 | GGB | 152973.01 | GNB | 0 | 0 | 2973 | 3600 | 2957.51 | GGB | 100 | GGB | 42.4 | GGB | 42.4 | GGB | 101529.6 | GGB | 101530.81 | 2957.51 | 2957.51 |  |  |  | 1 | 1 |  |  |  |  | 152973.01 | 2957.51 |  | 2957.51 | 10.6703 | [5 empty] | 125.672 | 2470.5535
24.12.2007 11:00 | 3600 | 2 | 759 | GGB | 766.667 | 772.922 | 768.864 | 276.52 | GGB | 11407.7 | GGB | 9.86 | GGB | 1028.87 | GGB | 56.01 | GGB | 181468.8 | GGB | 152936.25 | GNB | 0 | 0 | 2976 | 3600 | 2960.5 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 101570.59 | GGB | 101571.8 | 2960.5 | 2960.5 |  |  |  | 1 | 1 |  |  |  |  | 152936.25 | 2960.5 |  | 2960.5 | 11.0458 | [5 empty] | 125.7688 | 2471.1473
24.12.2007 12:00 | 3600 | 2 | 758.64 | GGB | 767.766 | 773.227 | 769.963 | 276.52 | GGB | 11404.4 | GGB | 9.86 | GGB | 1028.35 | GGB | 56.14 | GGB | 181392.88 | GGB | 152735.13 | GNB | 0 | 0 | 2980 | 3600 | 2964.03 | GGB | 100 | GGB | 41.91 | GGB | 41.91 | GGB | 101612.5 | GGB | 101613.71 | 2964.03 | 2964.03 |  |  |  | 1 | 1 |  |  |  |  | 152735.13 | 2964.03 |  |  | 10.802 | [5 empty] | 125.7532 | 2474.4013
24.12.2007 13:00 | 3600 | 2 | 758.76 | GGB | 766.667 | 772.219 | 767.766 | 276.53 | GGB | 11392.1 | GGB | 9.86 | GGB | 1028.12 | GGB | 56.07 | GGB | 181209.12 | GGB | 152577.59 | GGB | 0 | 0 | 2970 | 3600 | 2954.31 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 101653.96 | GGB | 101655.18 | 2954.31 | 2954.31 |  |  |  | 1 | 1 |  |  |  |  | 152577.59 | 2954.31 | 152577.59 | 2954.31 | 10.8696 | [5 empty] | 125.2115 | 2476.9562
24.12.2007 14:00 | 3600 | 2 | 758.64 | GGB | 767.766 | 773.672 | 769.963 | 276.56 | GGB | 11393.5 | GGB | 9.86 | GGB | 1028.34 | GGB | 56.05 | GGB | 181064.98 | GGB | 152499.42 | GGB | 0 | 0 | 2983 | 3600 | 2967.64 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 101695.27 | GGB | 101696.49 | 2967.64 | 2967.64 |  |  |  | 1 | 1 |  |  |  |  | 152499.42 | 2967.64 | 152499.42 |  | 10.9553 | [5 empty] | 125.712 | 2478.2258
24.12.2007 15:00 | 3600 | 2 | 758.92 | GGB | 766.667 | 772.617 | 768.864 | 276.48 | GGB | 11391.5 | GGB | 9.86 | GGB | 1028.51 | GGB | 56.07 | GGB | 180951.64 | GGB | 152419.69 | GGB | 0 | 0 | 2968 | 3600 | 2952.85 | GGB | 100 | GGB | 42.23 | GGB | 42.23 | GGB | 101737.5 | GGB | 101738.72 | 2952.85 | 2952.85 |  |  |  | 1 | 1 |  |  |  |  | 152419.69 | 2952.85 | 152419.69 | 2952.85 | 10.6576 | [5 empty] | 125.0201 | 2479.5222
24.12.2007 16:00 | 3600 | 2 | 758.54 | GGB | 767.766 | 772.617 | 768.864 | 276.56 | GGB | 11374.6 | GGB | 9.85 | GGB | 1028.21 | GGB | 56.09 | GGB | 180680.96 | GGB | 152137.79 | GGB | 0 | 0 | 2987 | 3600 | 2971.02 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 101778.27 | GGB | 101779.49 | 2971.02 | 2971.02 |  |  |  | 1 | 1 |  |  |  |  | 152137.79 | 2971.02 | 152137.79 |  | 11.0867 | [5 empty] | 125.5568 | 2484.1165
24.12.2007 17:00 | 3600 | 2 | 758.88 | GGB | 767.766 | 773.391 | 769.963 | 276.45 | GGB | 11377.3 | GGB | 9.86 | GGB | 1028.16 | GGB | 56.21 | GGB | 180553.32 | GGB | 151966.05 | GGB | 0 | 0 | 2976 | 3600 | 2960.84 | GGB | 100 | GGB | 42.29 | GGB | 42.29 | GGB | 101820.56 | GGB | 101821.78 | 2960.84 | 2960.84 |  |  |  | 1 | 1 |  |  |  |  | 151966.05 | 2960.84 | 151966.05 | 2960.84 | 10.6396 | [5 empty] | 124.9853 | 2486.9239
24.12.2007 18:00 | 3600 | 2 | 759.22 | GGB | 766.667 | 773.391 | 769.963 | 276.25 | GGB | 11375 | GGB | 9.86 | GGB | 1028.36 | GGB | 56.21 | GGB | 180320.05 | GGB | 151797.61 | GGB | 0 | 0 | 2964 | 3600 | 2948.18 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 101861.31 | GGB | 101862.54 | 2948.18 | 2948.18 |  |  |  | 1 | 1 |  |  |  |  | 151797.61 | 2948.18 | 151797.61 | 2948.18 | 10.9796 | [5 empty] | 124.313 | 2489.6835
24.12.2007 19:00 | 3600 | 2 | 759.08 | GGB | 767.766 | 773.484 | 769.963 | 275.8 | GGB | 11367.7 | GGB | 9.86 | GGB | 1028.39 | GGB | 56.23 | GGB | 180194.61 | GGB | 151688.52 | GGB | 0 | 0 | 2969 | 3600 | 2952.93 | GGB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 101903.19 | GGB | 101904.42 | 2952.93 | 2952.93 |  |  |  | 1 | 1 |  |  |  |  | 151688.52 | 2952.93 | 151688.52 | 2952.93 | 10.6955 | [5 empty] | 124.4238 | 2491.474
24.12.2007 20:00 | 3600 | 2 | 758.95 | GGB | 766.667 | 772.523 | 767.766 | 275.73 | GGB | 11353.3 | GGB | 9.85 | GGB | 1028.47 | GGB | 55.97 | GGB | 179889.82 | GGB | 151564.09 | GGB | 0 | 0 | 2964 | 3600 | 2947.96 | GGB | 100 | GGB | 34.81 | GGB | 34.81 | GGB | 101937.99 | GGB | 101939.23 | 2947.96 | 2947.96 |  |  |  | 1 | 1 |  |  |  |  | 151564.09 | 2947.96 | 151564.09 | 2947.96 | 12.8355 | [5 empty] | 124.1125 | 2493.5194
24.12.2007 21:00 | 3600 | 2 | 758.89 | GGB | 766.3 | 772.5 | 768.864 | 276.29 | GGB | 11362.4 | GGB | 9.85 | GGB | 1028.43 | GGB | 56.44 | GGB | 180345.36 | GGB | 151723.09 | GGB | 0 | 0 | 2987 | 3600 | 2970.91 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 101977.32 | GGB | 101978.55 | 2970.91 | 2970.91 |  |  |  | 1 | 1 |  |  |  |  | 151723.09 | 2970.91 | 151723.09 |  | 11.4638 | [5 empty] | 125.2099 | 2490.9063
24.12.2007 22:00 | 3600 | 2 | 759.13 | GGB | 767.766 | 772.336 | 768.864 | 276.41 | GGB | 11372.8 | GGB | 9.86 | GGB | 1028.63 | GGB | 56.32 | GGB | 180589.63 | GGB | 152015.86 | GGB | 0 | 0 | 2970 | 3600 | 2954.7 | GGB | 100 | GGB | 35.21 | GGB | 35.21 | GGB | 102012.52 | GGB | 102013.76 | 2954.7 | 2954.7 |  |  |  | 1 | 1 |  |  |  |  | 152015.86 | 2954.7 | 152015.86 | 2954.7 | 12.7566 | [5 empty] | 124.767 | 2486.109
24.12.2007 23:00 | 3600 | 2 | 759.05 | GGB | 767.766 | 773.836 | 769.963 | 276.81 | GGB | 11379.5 | GGB | 9.86 | GGB | 1028.66 | GGB | 56.47 | GGB | 180792.09 | GGB | 152122.83 | GGB | 0 | 0 | 2978 | 3600 | 2962.86 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 102052.86 | GGB | 102054.09 | 2962.86 | 2962.86 |  |  |  | 1 | 1 |  |  |  |  | 152122.83 | 2962.86 | 152122.83 | 2962.86 | 11.1758 | [5 empty] | 125.1996 | 2484.3608
24.12.2007 24:00 | 3600 | 2 | 758.88 | GGB | 768.864 | 774.914 | 771.429 | 276.8 | GGB | 11382.3 | GGB | 9.86 | GGB | 1028.86 | GGB | 56.43 | GGB | 180858.11 | GGB | 152223.96 | GGB | 0 | 0 | 2988 | 3600 | 2972.51 | GGB | 100 | GGB | 37.89 | GGB | 37.89 | GGB | 102090.75 | GGB | 102091.98 | 2972.51 | 2972.51 |  |  |  | 1 | 1 |  |  |  |  | 152223.96 | 2972.51 | 152223.96 |  | 11.9421 | [5 empty] | 125.6909 | 2482.7103
25.12.2007 01:00 | 3600 | 2 | 759.03 | GGB | 766.667 | 773.461 | 768.864 | 277.04 | GGB | 11375.3 | GGB | 9.85 | GGB | 1028.94 | GGB | 56.64 | GGB | 180942.84 | GGB | 152209.08 | GGB | 0 | 0 | 2987 | 3600 | 2971.41 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 102129.11 | GGB | 102130.34 | 2971.41 | 2971.41 |  |  |  | 1 | 1 |  |  |  |  | 152209.08 | 2971.41 | 152209.08 |  | 11.7903 | [5 empty] | 125.6321 | 2482.9531
25.12.2007 02:00 | 3600 | 2 | 759.2 | GGB | 766.667 | 772.336 | 768.864 | 276.88 | GGB | 11374.2 | GGB | 9.86 | GGB | 1028.93 | GGB | 56.63 | GGB | 180629.24 | GGB | 151952.03 | GGB | 0 | 0 | 2980 | 3600 | 2964.79 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 102169.34 | GGB | 102170.57 | 2964.79 | 2964.79 |  |  |  | 1 | 1 |  |  |  |  | 151952.03 | 2964.79 | 151952.03 |  | 11.1983 | [5 empty] | 125.1405 | 2487.1533
25.12.2007 03:00 | 3600 | 2 | 759.07 | GGB | 766.667 | 772.148 | 768.864 | 276.82 | GGB | 11367.3 | GGB | 9.86 | GGB | 1028.93 | GGB | 56.66 | GGB | 180752.48 | GGB | 152039.09 | GGB | 0 | 0 | 2977 | 3600 | 2961.27 | GGB | 100 | GGB | 36.45 | GGB | 36.45 | GGB | 102205.79 | GGB | 102207.02 | 2961.27 | 2961.27 |  |  |  | 1 | 1 |  |  |  |  | 152039.09 | 2961.27 | 152039.09 | 2961.27 | 12.352 | [5 empty] | 125.0636 | 2485.7292
25.12.2007 04:00 | 3600 | 2 | 759.35 | GGB | 766.667 | 771.563 | 767.766 | 276.42 | GGB | 11375 | GGB | 9.86 | GGB | 1028.58 | GGB | 56.59 | GGB | 180419.08 | GGB | 151739.92 | GGB | 0 | 0 | 2966 | 3600 | 2950.38 | GGB | 100 | GGB | 46.36 | GGB | 46.36 | GGB | 102252.15 | GGB | 102253.38 | 2950.38 | 2950.38 |  |  |  | 1 | 1 |  |  |  |  | 151739.92 | 2950.38 | 151739.92 | 2950.38 | 9.6568 | [5 empty] | 124.3585 | 2490.63
25.12.2007 05:00 | 3600 | 2 | 759.43 | GGB | 766.667 | 772.852 | 768.864 | 276.8 | GGB | 11384.8 | GGB | 9.86 | GGB | 1028.54 | GGB | 56.25 | GGB | 180869.12 | GGB | 152268.5 | GGB | 0 | 0 | 2984 | 3600 | 2968.2 | GGB | 100 | GGB | 42.99 | GGB | 42.99 | GGB | 102295.14 | GGB | 102296.37 | 2968.2 | 2968.2 |  |  |  | 1 | 1 |  |  |  |  | 152268.5 | 2968.2 | 152268.5 |  | 10.5132 | [5 empty] | 125.5454 | 2481.9841
25.12.2007 06:00 | 3600 | 2 | 759.18 | GGB | 765.201 | 770.25 | 767.766 | 276.85 | GGB | 11383 | GGB | 9.85 | GGB | 1028.4 | GGB | 56.14 | GGB | 181060.58 | GGB | 152459.06 | GGB | 0 | 0 | 2992 | 3600 | 2976.38 | GGB | 100 | GGB | 43.29 | GGB | 43.29 | GGB | 102338.42 | GGB | 102339.66 | 2976.38 | 2976.38 |  |  |  | 1 | 1 |  |  |  |  | 152459.06 | 2976.38 | 152459.06 |  | 10.4822 | [5 empty] | 126.0489 | 2478.8819
25.12.2007 07:00 | 3600 | 2 | 759.2 | GGB | 769.963 | 776.25 | 772.527 | 277.14 | GGB | 11400.6 | GGB | 9.86 | GGB | 1028.82 | GGB | 56.12 | GGB | 181155.21 | GGB | 152612.71 | GGB | 0 | 0 | 2993 | 3600 | 2977.11 | GGB | 100 | GGB | 41.95 | GGB | 41.95 | GGB | 102380.37 | GGB | 102381.61 | 2977.11 | 2977.11 |  |  |  | 1 | 1 |  |  |  |  | 152612.71 | 2977.11 | 152612.71 |  | 10.8306 | [5 empty] | 126.2069 | 2476.3861
25.12.2007 08:00 | 3600 | 2 | 759.59 | GGB | 767.766 | 773.156 | 769.597 | 276.75 | GGB | 11382.8 | GGB | 9.86 | GGB | 1028.68 | GGB | 56.29 | GGB | 180536.82 | GGB | 151992.21 | GGB | 0 | 0 | 2967 | 3600 | 2951.3 | GGB | 100 | GGB | 42.81 | GGB | 42.81 | GGB | 102423.18 | GGB | 102424.42 | 2951.3 | 2951.3 |  |  |  | 1 | 1 |  |  |  |  | 151992.21 | 2951.3 | 151992.21 | 2951.3 | 10.4783 | [5 empty] | 124.6041 | 2486.4959
25.12.2007 09:00 | 3600 | 2 | 759.23 | GGB | 766.3 | 772.055 | 768.498 | 276.69 | GGB | 11370.8 | GGB | 9.85 | GGB | 1028.93 | GGB | 56.41 | GGB | 180426.78 | GGB | 151880.34 | GGB | 0 | 0 | 2978 | 3600 | 2961.88 | GGB | 100 | GGB | 42.98 | GGB | 42.98 | GGB | 102466.16 | GGB | 102467.4 | 2961.88 | 2961.88 |  |  |  | 1 | 1 |  |  |  |  | 151880.34 | 2961.88 | 151880.34 | 2961.88 | 10.4665 | [5 empty] | 124.9587 | 2488.3273
25.12.2007 10:00 | 3600 | 2 | 759.33 | GGB | 767.766 | 773.438 | 769.597 | 277.09 | GGB | 11392.4 | GGB | 9.85 | GGB | 1029.26 | GGB | 56.29 | GGB | 181143.1 | GGB | 152589.23 | GGB | 0 | 0 | 2984 | 3600 | 2968.22 | GGB | 100 | GGB | 43.3 | GGB | 43.3 | GGB | 102509.46 | GGB | 102510.7 | 2968.22 | 2968.22 |  |  |  | 1 | 1 |  |  |  |  | 152589.23 | 2968.22 | 152589.23 |  | 10.46 | [5 empty] | 125.8107 | 2476.7672
25.12.2007 11:00 | 3600 | 2 | 759.63 | GGB | 766.667 | 772.148 | 768.498 | 276.91 | GGB | 11378 | GGB | 9.86 | GGB | 1029.19 | GGB | 56.44 | GGB | 180307.95 | GGB | 151804.27 | GGB | 0 | 0 | 2964 | 3600 | 2948.62 | GGB | 100 | GGB | 42.79 | GGB | 42.79 | GGB | 102552.25 | GGB | 102553.49 | 2948.62 | 2948.62 |  |  |  | 1 | 1 |  |  |  |  | 151804.27 | 2948.62 | 151804.27 | 2948.62 | 10.4607 | [5 empty] | 124.337 | 2489.5742
25.12.2007 12:00 | 3600 | 2 | 759.24 | GGB | 766.3 | 772.125 | 768.498 | 276.53 | GGB | 11370.5 | GGB | 9.86 | GGB | 1029.01 | GGB | 56.6 | GGB | 179888.72 | GGB | 151351.36 | GGB | 0 | 0 | 2948 | 3600 | 2932.06 | GGB | 100 | GGB | 43.2 | GGB | 43.2 | GGB | 102595.46 | GGB | 102596.69 | 2932.06 | 2932.06 |  |  |  | 1 | 1 |  |  |  |  | 151351.36 | 2932.06 | 151351.36 | 2932.06 | 10.2725 | [5 empty] | 123.2698 | 2497.0241
25.12.2007 13:00 | 3600 | 2 | 759.17 | GGB | 767.766 | 773.25 | 770.696 | 276.5 | GGB | 11359.5 | GGB | 9.86 | GGB | 1028.88 | GGB | 56.48 | GGB | 179853.51 | GGB | 151359.94 | GGB | 0 | 0 | 2960 | 3600 | 2944.35 | GGB | 100 | GGB | 42.66 | GGB | 42.66 | GGB | 102638.12 | GGB | 102639.35 | 2944.35 | 2944.35 |  |  |  | 1 | 1 |  |  |  |  | 151359.94 | 2944.35 | 151359.94 | 2944.35 | 10.4467 | [5 empty] | 123.7935 | 2496.8826
25.12.2007 14:00 | 3600 | 2 | 759.67 | GGB | 767.766 | 773.063 | 769.597 | 276.15 | GGB | 11347.2 | GGB | 9.86 | GGB | 1028.77 | GGB | 61.96 | GGB | 179429.88 | GGB | 148518.74 | GGB | 0 | 0 | 2928 | 3600 | 2912.71 | GGB | 100 | GGB | 42.98 | GGB | 42.98 | GGB | 102681.1 | GGB | 102682.33 | 2912.71 | 2912.71 |  |  |  | 1 | 1 |  |  |  |  | 148518.74 | 2912.71 | 148518.74 | 2912.71 | 10.065 | [5 empty] | 120.1644 | 2544.6486
25.12.2007 15:00 | 3600 | 2 | 759.21 | GGB | 766.667 | 773.203 | 769.597 | 276.02 | GGB | 11325.1 | GGB | 9.85 | GGB | 1028.84 | GGB | 64.62 | GGB | 179228.51 | GGB | 147190.38 | GGB | 0 | 0 | 2944 | 3600 | 2928.01 | GGB | 100 | GGB | 41.66 | GGB | 41.66 | GGB | 102722.77 | GGB | 102723.99 | 2928.01 | 2928.01 |  |  |  | 1 | 1 |  |  |  |  | 147190.38 | 2928.01 | 147190.38 | 2928.01 | 10.3451 | [5 empty] | 119.7153 | 2567.6135
25.12.2007 16:00 | 3600 | 2 | 759.09 | GGB | 767.766 | 773.32 | 769.597 | 276.3 | GGB | 11332 | GGB | 9.85 | GGB | 1028.57 | GGB | 59.99 | GGB | 179362.76 | GGB | 149309.4 | GGB | 0 | 0 | 2949 | 3600 | 2933.09 | GGB | 100 | GGB | 42.77 | GGB | 42.77 | GGB | 102765.53 | GGB | 102766.76 | 2933.09 | 2933.09 |  |  |  | 1 | 1 |  |  |  |  | 149309.4 | 2933.09 | 149309.4 | 2933.09 | 10.2394 | [5 empty] | 121.6494 | 2531.1735
25.12.2007 17:00 | 3600 | 2 | 759.26 | GGB | 766.667 | 772.266 | 769.597 | 276.54 | GGB | 11341.7 | GGB | 9.85 | GGB | 1028.71 | GGB | 56.67 | GGB | 179792.99 | GGB | 151197.24 | GGB | 0 | 0 | 2954 | 3600 | 2938.19 | GGB | 100 | GGB | 42.46 | GGB | 42.46 | GGB | 102807.99 | GGB | 102809.22 | 2938.19 | 2938.19 |  |  |  | 1 | 1 |  |  |  |  | 151197.24 | 2938.19 | 151197.24 | 2938.19 | 10.4627 | [5 empty] | 123.4017 | 2499.5694
25.12.2007 18:00 | 3600 | 2 | 759.44 | GGB | 767.766 | 773.133 | 770.696 | 276.35 | GGB | 11349.1 | GGB | 9.86 | GGB | 1028.27 | GGB | 56.62 | GGB | 179715.96 | GGB | 151086.91 | GGB | 0 | 0 | 2942 | 3600 | 2926.88 | GGB | 100 | GGB | 43.03 | GGB | 43.03 | GGB | 102851.02 | GGB | 102852.25 | 2926.88 | 2926.88 |  |  |  | 1 | 1 |  |  |  |  | 151086.91 | 2926.88 | 151086.91 | 2926.88 | 10.2769 | [5 empty] | 122.837 | 2501.3947
25.12.2007 19:00 | 3600 | 2 | 759.13 | GGB | 765.201 | 770.93 | 768.132 | 276.49 | GGB | 11341.4 | GGB | 9.85 | GGB | 1028.7 | GGB | 56.5 | GGB | 179993.25 | GGB | 151442.92 | GGB | 0 | 0 | 2955 | 3600 | 2939.62 | GGB | 100 | GGB | 42.84 | GGB | 42.84 | GGB | 102893.86 | GGB | 102895.09 | 2939.62 | 2939.62 |  |  |  | 1 | 1 |  |  |  |  | 151442.92 | 2939.62 | 151442.92 | 2939.62 | 10.3918 | [5 empty] | 123.6624 | 2495.5145
25.12.2007 20:00 | 3600 | 2 | 759.28 | GGB | 767.766 | 773.133 | 769.597 | 276.67 | GGB | 11375.4 | GGB | 9.86 | GGB | 1028.3 | GGB | 56.43 | GGB | 180417.98 | GGB | 151769.74 | GGB | 0 | 0 | 2955 | 3600 | 2939.15 | GGB | 100 | GGB | 42.87 | GGB | 42.87 | GGB | 102936.73 | GGB | 102937.96 | 2939.15 | 2939.15 |  |  |  | 1 | 1 |  |  |  |  | 151769.74 | 2939.15 | 151769.74 | 2939.15 | 10.4053 | [5 empty] | 123.9095 | 2490.1407
25.12.2007 21:00 | 3600 | 2 | 759.05 | GGB | 767.766 | 773.109 | 769.597 | 277.94 | GGB | 11338.4 | GGB | 9.85 | GGB | 1028.09 | GGB | 55.69 | GGB | 182616.45 | GGB | 153934.15 | GNB | 0 | 0 | 2947 | 3600 | 2931.66 | GGB | 100 | GGB | 42.01 | GGB | 42.01 | GGB | 102978.74 | GGB | 102979.97 | 2931.66 | 2931.66 |  |  |  | 1 | 1 |  |  |  |  | 153934.15 | 2931.66 |  | 2931.66 | 10.7423 | [5 empty] | 125.3563 | 2455.1277
25.12.2007 22:00 | 3600 | 2 | 759.73 | GGB | 767.766 | 774.023 | 769.597 | 276.37 | GGB | 11397.2 | GGB | 9.87 | GGB | 1028.23 | GGB | 56.09 | GGB | 180608.34 | GGB | 152077.7 | GGB | 0 | 0 | 2937 | 3600 | 2921.44 | GGB | 100 | GGB | 42.02 | GGB | 42.02 | GGB | 103020.75 | GGB | 103021.99 | 2921.44 | 2921.44 |  |  |  | 1 | 1 |  |  |  |  | 152077.7 | 2921.44 | 152077.7 | 2921.44 | 10.5732 | [5 empty] | 123.4127 | 2485.0981
25.12.2007 23:00 | 3600 | 2 | 759.22 | GGB | 769.963 | 775.758 | 771.795 | 277.12 | GGB | 11379.4 | GGB | 9.85 | GGB | 1028.38 | GGB | 55.84 | GGB | 182406.29 | GGB | 153729.94 | GNB | 0 | 0 | 2955 | 3600 | 2939.75 | GGB | 100 | GGB | 43.46 | GGB | 43.46 | GGB | 103064.22 | GGB | 103065.45 | 2939.75 | 2939.75 |  |  |  | 1 | 1 |  |  |  |  | 153729.94 | 2939.75 |  | 2939.75 | 10.3987 | [5 empty] | 125.5354 | 2458.389
25.12.2007 24:00 | 3600 | 2 | 759.21 | GGB | 766.667 | 772.547 | 768.864 | 278.53 | GGB | 11334.6 | GGB | 9.85 | GGB | 1028.36 | GGB | 56.48 | GGB | 183155.62 | GGB | 154060.91 | GNB | 0 | 0 | 2940 | 3600 | 2924.63 | GGB | 100 | GGB | 42.67 | GGB | 42.67 | GGB | 103106.89 | GGB | 103108.12 | 2924.63 | 2924.63 |  |  |  | 1 | 1 |  |  |  |  | 154060.91 | 2924.63 |  | 2924.63 | 10.5594 | [5 empty] | 125.1587 | 2453.1077
26.12.2007 01:00 | 3600 | 2 | 760.05 | GGB | 768.864 | 775.523 | 771.429 | 277.56 | GGB | 11379.8 | GGB | 9.87 | GGB | 1028.2 | GGB | 55.75 | GGB | 181987.06 | GGB | 153394.05 | GNB | 0 | 0 | 2913 | 3600 | 2897.62 | GGB | 100 | GGB | 42.51 | GGB | 42.51 | GGB | 103149.4 | GGB | 103150.63 | 2897.62 | 2897.62 |  |  |  | 1 | 1 |  |  |  |  | 153394.05 | 2897.62 |  | 2897.62 | 10.4558 | [5 empty] | 123.466 | 2463.7722
26.12.2007 02:00 | 3600 | 2 | 759.21 | GGB | 767.766 | 772.664 | 769.963 | 276.63 | GGB | 11383.3 | GGB | 9.85 | GGB | 1027.83 | GGB | 56.03 | GGB | 180964.85 | GGB | 152347.74 | GGB | 0 | 0 | 2969 | 3600 | 2953.85 | GGB | 100 | GGB | 42.34 | GGB | 42.34 | GGB | 103191.74 | GGB | 103192.97 | 2953.85 | 2953.85 |  |  |  | 1 | 1 |  |  |  |  | 152347.74 | 2953.85 | 152347.74 | 2953.85 | 10.6285 | [5 empty] | 125.0034 | 2480.6932
26.12.2007 03:00 | 3600 | 2 | 759.26 | GGB | 766.3 | 772.359 | 768.864 | 277.14 | GGB | 11405.1 | GGB | 9.85 | GGB | 1028.02 | GGB | 55.86 | GGB | 181615.15 | GGB | 153000.02 | GNB | 0 | 0 | 2983 | 3600 | 2967.07 | GGB | 100 | GGB | 42.13 | GGB | 42.13 | GGB | 103233.87 | GGB | 103235.1 | 2967.07 | 2967.07 |  |  |  | 1 | 1 |  |  |  |  | 153000.02 | 2967.07 |  |  | 10.7753 | [5 empty] | 126.1005 | 2470.1173
26.12.2007 04:00 | 3600 | 2 | 759.51 | GGB | 767.766 | 773.625 | 770.33 | 277.22 | GGB | 11428.1 | GGB | 9.86 | GGB | 1028.57 | GGB | 61.2 | GGB | 181859.42 | GGB | 150841.83 | GGB | 0 | 0 | 2978 | 3600 | 2961.86 | GGB | 100 | GGB | 44.01 | GGB | 44.01 | GGB | 103277.87 | GGB | 103279.11 | 2961.86 | 2961.86 |  |  |  | 1 | 1 |  |  |  |  | 150841.83 | 2961.86 | 150841.83 | 2961.86 | 10.1516 | [5 empty] | 124.1034 | 2505.4589
26.12.2007 05:00 | 3600 | 2 | 759.36 | GGB | 767.766 | 773.555 | 769.963 | 277.34 | GGB | 11431.8 | GGB | 9.86 | GGB | 1028.12 | GGB | 69.42 | GEB | 182287.45 | GGB | 147500.89 | GGB | 0 | 0 | 2989 | 3600 | 2973.25 | GGB | 100 | GGB | 41.42 | GGB | 41.42 | GGB | 103319.29 | GGB | 103320.53 | 2973.25 | 2973.25 |  |  |  | 1 | 1 |  |  |  |  | 147500.89 | 2973.25 | 147500.89 |  | 10.588 | [5 empty] | 121.8214 | 2562.2083
26.12.2007 06:00 | 3600 | 2 | 759.41 | GGB | 766.3 | 772.781 | 768.864 | 277.74 | GGB | 11437.9 | GGB | 9.86 | GGB | 1028.3 | GGB | 70.87 | GEB | 182345.77 | GGB | 146950.34 | GGB | 0 | 0 | 2993 | 3600 | 2977.47 | GGB | 100 | GGB | 43.43 | GGB | 43.43 | GGB | 103362.73 | GGB | 103363.96 | 2977.47 | 2977.47 |  |  |  | 1 | 1 |  |  |  |  | 146950.34 | 2977.47 | 146950.34 |  | 10.0746 | [5 empty] | 121.539 | 2571.8076
26.12.2007 07:00 | 3600 | 2 | 759.48 | GGB | 766.667 | 773.555 | 768.864 | 277.68 | GGB | 11437.9 | GGB | 9.86 | GGB | 1027.95 | GGB | 70.87 | GEB | 182272.05 | GGB | 146841.4 | GGB | 0 | 0 | 2985 | 3600 | 2969.63 | GGB | 100 | GGB | 42.14 | GGB | 42.14 | GGB | 103404.87 | GGB | 103406.1 | 2969.63 | 2969.63 |  |  |  | 1 | 1 |  |  |  |  | 146841.4 | 2969.63 | 146841.4 |  | 10.348 | [5 empty] | 121.1291 | 2573.7156
26.12.2007 08:00 | 3600 | 2 | 759.3 | GGB | 766.667 | 773.461 | 769.963 | 277.78 | GGB | 11443.5 | GGB | 9.85 | GGB | 1027.87 | GGB | 70.87 | GEB | 182669.27 | GGB | 147150.06 | GGB | 0 | 0 | 2993 | 3600 | 2977.57 | GGB | 100 | GGB | 43.64 | GGB | 43.64 | GGB | 103448.51 | GGB | 103449.74 | 2977.57 | 2977.57 |  |  |  | 1 | 1 |  |  |  |  | 147150.06 | 2977.57 | 147150.06 |  | 10.0401 | [5 empty] | 121.7082 | 2568.317
26.12.2007 09:00 | 3600 | 2 | 759.41 | GGB | 767.766 | 773.531 | 769.963 | 277.91 | GGB | 11459.8 | GGB | 9.86 | GGB | 1028.05 | GGB | 70.87 | GEB | 182938.85 | GGB | 147392.79 | GGB | 0 | 0 | 2988 | 3600 | 2972.67 | GGB | 100 | GGB | 41.5 | GGB | 41.5 | GGB | 103490.01 | GGB | 103491.24 | 2972.67 | 2972.67 |  |  |  | 1 | 1 |  |  |  |  | 147392.79 | 2972.67 | 147392.79 |  | 10.5578 | [5 empty] | 121.7084 | 2564.0874
26.12.2007 10:00 | 3600 | 2 | 759.43 | GGB | 767.766 | 774.258 | 769.963 | 278.18 | GGB | 11464.5 | GGB | 9.86 | GGB | 1028.67 | GGB | 70.87 | GEB | 183161.12 | GGB | 147661.46 | GGB | 0 | 0 | 2993 | 3600 | 2976.91 | GGB | 100 | GGB | 43.28 | GGB | 43.28 | GGB | 103533.29 | GGB | 103534.52 | 2976.91 | 2976.91 |  |  |  | 1 | 1 |  |  |  |  | 147661.46 | 2976.91 | 147661.46 |  | 10.1565 | [5 empty] | 122.1041 | 2559.4221
26.12.2007 11:00 | 3600 | 2 | 759.57 | GGB | 767.766 | 773.461 | 769.963 | 278.05 | GGB | 11459.4 | GGB | 9.86 | GGB | 1029.01 | GGB | 70.87 | GEB | 182837.62 | GGB | 147448.93 | GGB | 0 | 0 | 2983 | 3600 | 2967.78 | GGB | 100 | GGB | 43.1 | GGB | 43.1 | GGB | 103576.39 | GGB | 103577.62 | 2967.78 | 2967.78 |  |  |  | 1 | 1 |  |  |  |  | 147448.93 | 2967.78 | 147448.93 |  | 10.153 | [5 empty] | 121.5544 | 2563.1112
26.12.2007 12:00 | 3600 | 2 | 759.66 | GGB | 768.864 | 774.305 | 771.429 | 277.8 | GGB | 11467 | GGB | 9.86 | GGB | 1029.12 | GGB | 70.87 | GEB | 182869.53 | GGB | 147490.28 | GGB | 0 | 0 | 2974 | 3600 | 2958.26 | GGB | 100 | GGB | 41.75 | GGB | 41.75 | GGB | 103618.14 | GGB | 103619.37 | 2958.26 | 2958.26 |  |  |  | 1 | 1 |  |  |  |  | 147490.28 | 2958.26 | 147490.28 | 2958.26 | 10.4506 | [5 empty] | 121.1985 | 2562.3926
26.12.2007 13:00 | 3600 | 2 | 759.42 | GGB | 767.766 | 773.25 | 769.963 | 277.76 | GGB | 11454.7 | GGB | 9.86 | GGB | 1028.52 | GGB | 70.87 | GEB | 182886.04 | GGB | 147416.98 | GGB | 0 | 0 | 2981 | 3600 | 2965.63 | GGB | 100 | GGB | 43.19 | GGB | 43.19 | GGB | 103661.33 | GGB | 103662.56 | 2965.63 | 2965.63 |  |  |  | 1 | 1 |  |  |  |  | 147416.98 | 2965.63 | 147416.98 |  | 10.1223 | [5 empty] | 121.4401 | 2563.6667
26.12.2007 14:00 | 3600 | 2 | 759.63 | GGB | 767.766 | 774.398 | 770.33 | 277.79 | GGB | 11454.6 | GGB | 9.86 | GGB | 1028.22 | GGB | 70.87 | GEB | 182858.53 | GGB | 147352.21 | GGB | 0 | 0 | 2977 | 3600 | 2961.11 | GGB | 100 | GGB | 43.21 | GGB | 43.21 | GGB | 103704.54 | GGB | 103705.77 | 2961.11 | 2961.11 |  |  |  | 1 | 1 |  |  |  |  | 147352.21 | 2961.11 | 147352.21 | 2961.11 | 10.0978 | [5 empty] | 121.2017 | 2564.7936
26.12.2007 15:00 | 3600 | 2 | 759.71 | GGB | 768.864 | 773.977 | 771.429 | 277.58 | GGB | 11459 | GGB | 9.86 | GGB | 1028.04 | GGB | 70.87 | GEB | 182788.11 | GGB | 147269.92 | GGB | 0 | 0 | 2974 | 3600 | 2958.08 | GGB | 100 | GGB | 41.66 | GGB | 41.66 | GGB | 103746.19 | GGB | 103747.43 | 2958.08 | 2958.08 |  |  |  | 1 | 1 |  |  |  |  | 147269.92 | 2958.08 | 147269.92 | 2958.08 | 10.4569 | [5 empty] | 121.0101 | 2566.2267
26.12.2007 16:00 | 3600 | 2 | 759.56 | GGB | 765.201 | 771.211 | 767.766 | 277.48 | GGB | 11456.5 | GGB | 9.86 | GGB | 1028.21 | GGB | 70.87 | GEB | 182840.92 | GGB | 147336.6 | GGB | 0 | 0 | 2974 | 3600 | 2958.41 | GGB | 100 | GGB | 43 | GGB | 43 | GGB | 103789.19 | GGB | 103790.43 | 2958.41 | 2958.41 |  |  |  | 1 | 1 |  |  |  |  | 147336.6 | 2958.41 | 147336.6 | 2958.41 | 10.1368 | [5 empty] | 121.0784 | 2565.0653
26.12.2007 17:00 | 3600 | 2 | 759.52 | GGB | 767.766 | 774.023 | 769.963 | 277.44 | GGB | 11448.3 | GGB | 9.86 | GGB | 1028.39 | GGB | 70.87 | GEB | 182428.3 | GGB | 147029.6 | GGB | 0 | 0 | 2983 | 3600 | 2967.1 | GGB | 100 | GGB | 43.49 | GGB | 43.49 | GGB | 103832.68 | GGB | 103833.92 | 2967.1 | 2967.1 |  |  |  | 1 | 1 |  |  |  |  | 147029.6 | 2967.1 | 147029.6 |  | 10.0311 | [5 empty] | 121.181 | 2570.4212
26.12.2007 18:00 | 3600 | 2 | 759.54 | GGB | 767.766 | 772.688 | 769.963 | 277.74 | GGB | 11449.4 | GGB | 9.86 | GGB | 1028.83 | GGB | 70.87 | GEB | 182521.83 | GGB | 147168.75 | GGB | 0 | 0 | 2983 | 3600 | 2967.22 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 103874.24 | GGB | 103875.48 | 2967.22 | 2967.22 |  |  |  | 1 | 1 |  |  |  |  | 147168.75 | 2967.22 | 147168.75 |  | 10.5073 | [5 empty] | 121.3006 | 2567.9908
26.12.2007 19:00 | 3600 | 2 | 759.89 | GGB | 767.766 | 774 | 770.33 | 277.22 | GGB | 11430.7 | GGB | 9.86 | GGB | 1029.37 | GGB | 70.87 | GEB | 181709.78 | GGB | 146590.17 | GGB | 0 | 0 | 2955 | 3600 | 2939.24 | GGB | 100 | GGB | 42.92 | GGB | 42.92 | GGB | 103917.16 | GGB | 103918.4 | 2939.24 | 2939.24 |  |  |  | 1 | 1 |  |  |  |  | 146590.17 | 2939.24 | 146590.17 | 2939.24 | 10.0388 | [5 empty] | 119.6844 | 2578.1265
26.12.2007 20:00 | 3600 | 2 | 759.81 | GGB | 767.766 | 772.734 | 769.963 | 276.61 | GGB | 11404.2 | GGB | 9.86 | GGB | 1029.02 | GGB | 70.87 | GEB | 181175.01 | GGB | 146109.53 | GGB | 0 | 0 | 2941 | 3600 | 2925.29 | GGB | 100 | GGB | 42.65 | GGB | 42.65 | GGB | 103959.81 | GGB | 103961.05 | 2925.29 | 2925.29 |  |  |  | 1 | 1 |  |  |  |  | 146109.53 | 2925.29 | 146109.53 | 2925.29 | 10.0214 | [5 empty] | 118.7258 | 2586.6075
26.12.2007 21:00 | 3600 | 2 | 759.81 | GGB | 767.766 | 773.203 | 769.963 | 276.59 | GGB | 11413.5 | GGB | 9.86 | GGB | 1029.03 | GGB | 70.87 | GEB | 181395.08 | GGB | 146288.41 | GGB | 0 | 0 | 2943 | 3600 | 2927.6 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 104000.87 | GGB | 104002.11 | 2927.6 | 2927.6 |  |  |  | 1 | 1 |  |  |  |  | 146288.41 | 2927.6 | 146288.41 | 2927.6 | 10.4304 | [5 empty] | 118.965 | 2583.4446
26.12.2007 22:00 | 3600 | 2 | 759.81 | GGB | 767.766 | 774.211 | 770.33 | 276.87 | GGB | 11423.2 | GGB | 9.86 | GGB | 1030.01 | GGB | 70.87 | GEB | 181393.98 | GGB | 146426.95 | GGB | 0 | 0 | 2947 | 3600 | 2931.3 | GGB | 100 | GGB | 42.72 | GGB | 42.72 | GGB | 104043.59 | GGB | 104044.83 | 2931.3 | 2931.3 |  |  |  | 1 | 1 |  |  |  |  | 146426.95 | 2931.3 | 146426.95 | 2931.3 | 10.0473 | [5 empty] | 119.2281 | 2581.0003
26.12.2007 23:00 | 3600 | 2 | 759.94 | GGB | 766.667 | 773.156 | 769.963 | 276.38 | GGB | 11421.5 | GGB | 9.86 | GGB | 1030.64 | GGB | 70.87 | GEB | 181437.99 | GGB | 146551.23 | GGB | 0 | 0 | 2941 | 3600 | 2925.03 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 104084.66 | GGB | 104085.9 | 2925.03 | 2925.03 |  |  |  | 1 | 1 |  |  |  |  | 146551.23 | 2925.03 | 146551.23 | 2925.03 | 10.4375 | [5 empty] | 119.0741 | 2578.8115
26.12.2007 24:00 | 3600 | 2 | 759.62 | GGB | 767.766 | 773.063 | 769.597 | 277.12 | GGB | 11402 | GGB | 9.85 | GGB | 1031.12 | GGB | 70.87 | GEB | 181220.13 | GGB | 146444.2 | GGB | 0 | 0 | 2958 | 3600 | 2942.83 | GGB | 100 | GGB | 42.27 | GGB | 42.27 | GGB | 104126.92 | GGB | 104128.17 | 2942.83 | 2942.83 |  |  |  | 1 | 1 |  |  |  |  | 146444.2 | 2942.83 | 146444.2 | 2942.83 | 10.1954 | [5 empty] | 119.7112 | 2580.6963
27.12.2007 01:00 | 3600 | 2 | 759.83 | GGB | 768.864 | 774.094 | 769.597 | 277.21 | GGB | 11412.2 | GGB | 9.86 | GGB | 1031.4 | GGB | 70.87 | GEB | 181192.62 | GGB | 146461.36 | GGB | 0 | 0 | 2947 | 3600 | 2931.1 | GGB | 100 | GGB | 42.44 | GGB | 42.44 | GGB | 104169.36 | GGB | 104170.61 | 2931.1 | 2931.1 |  |  |  | 1 | 1 |  |  |  |  | 146461.36 | 2931.1 | 146461.36 | 2931.1 | 10.1153 | [5 empty] | 119.248 | 2580.3939
27.12.2007 02:00 | 3600 | 2 | 759.67 | GGB | 766.3 | 772.641 | 768.498 | 277.06 | GGB | 11391.6 | GGB | 9.86 | GGB | 1031.91 | GGB | 70.87 | GEB | 180709.57 | GGB | 146143.87 | GGB | 0 | 0 | 2953 | 3600 | 2937.38 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 104210.65 | GGB | 104211.9 | 2937.38 | 2937.38 |  |  |  | 1 | 1 |  |  |  |  | 146143.87 | 2937.38 | 146143.87 | 2937.38 | 10.3967 | [5 empty] | 119.2445 | 2585.9997
27.12.2007 03:00 | 3600 | 2 | 759.85 | GGB | 767.766 | 773.648 | 769.597 | 277.01 | GGB | 11395.8 | GGB | 9.86 | GGB | 1032.06 | GGB | 70.87 | GEB | 180611.64 | GGB | 146085.7 | GGB | 0 | 0 | 2938 | 3600 | 2922.33 | GGB | 100 | GGB | 42.36 | GGB | 42.36 | GGB | 104253.01 | GGB | 104254.26 | 2922.33 | 2922.33 |  |  |  | 1 | 1 |  |  |  |  | 146085.7 | 2922.33 | 146085.7 | 2922.33 | 10.0782 | [5 empty] | 118.5863 | 2587.0294
27.12.2007 04:00 | 3600 | 2 | 759.57 | GGB | 766.3 | 772.57 | 768.132 | 277.08 | GGB | 11385.6 | GGB | 9.85 | GGB | 1032.15 | GGB | 70.87 | GEB | 180531.31 | GGB | 146033.35 | GGB | 0 | 0 | 2958 | 3600 | 2942.52 | GGB | 100 | GGB | 42.38 | GGB | 42.38 | GGB | 104295.39 | GGB | 104296.64 | 2942.52 | 2942.52 |  |  |  | 1 | 1 |  |  |  |  | 146033.35 | 2942.52 | 146033.35 | 2942.52 | 10.1394 | [5 empty] | 119.3628 | 2587.9568
27.12.2007 05:00 | 3600 | 2 | 759.82 | GGB | 767.766 | 773.906 | 769.597 | 277.13 | GGB | 11390.6 | GGB | 9.86 | GGB | 1032.1 | GGB | 70.87 | GEB | 180471.9 | GGB | 145978.28 | GGB | 0 | 0 | 2951 | 3600 | 2934.89 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 104335.95 | GGB | 104337.21 | 2934.89 | 2934.89 |  |  |  | 1 | 1 |  |  |  |  | 145978.28 | 2934.89 | 145978.28 | 2934.89 | 10.5603 | [5 empty] | 119.0084 | 2588.9331
27.12.2007 06:00 | 3600 | 2 | 759.49 | GGB | 767.766 | 774.047 | 770.33 | 277.18 | GGB | 11388.2 | GGB | 9.85 | GGB | 1032.31 | GGB | 70.87 | GEB | 180542.32 | GGB | 146064.68 | GGB | 0 | 0 | 2966 | 3600 | 2949.88 | GGB | 100 | GGB | 42.74 | GGB | 42.74 | GGB | 104378.69 | GGB | 104379.95 | 2949.88 | 2949.88 |  |  |  | 1 | 1 |  |  |  |  | 146064.68 | 2949.88 | 146064.68 | 2949.88 | 10.0813 | [5 empty] | 119.687 | 2587.4017
27.12.2007 07:00 | 3600 | 2 | 759.99 | GGB | 768.864 | 775.266 | 771.429 | 277.43 | GGB | 11421.8 | GGB | 9.86 | GGB | 1032.66 | GGB | 70.87 | GEB | 181272.94 | GGB | 146705.04 | GGB | 0 | 0 | 2950 | 3600 | 2934.41 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 104419.11 | GGB | 104420.37 | 2934.41 | 2934.41 |  |  |  | 1 | 1 |  |  |  |  | 146705.04 | 2934.41 | 146705.04 | 2934.41 | 10.6505 | [5 empty] | 119.5813 | 2576.1078
27.12.2007 08:00 | 3600 | 2 | 759.71 | GGB | 768.864 | 774.82 | 769.963 | 277.87 | GGB | 11431.7 | GGB | 9.85 | GGB | 1033.35 | GGB | 70.87 | GEB | 181667.96 | GGB | 147123.47 | GGB | 0 | 0 | 2969 | 3600 | 2953.38 | GGB | 100 | GGB | 42.85 | GGB | 42.85 | GGB | 104461.96 | GGB | 104463.22 | 2953.38 | 2953.38 |  |  |  | 1 | 1 |  |  |  |  | 147123.47 | 2953.38 | 147123.47 | 2953.38 | 10.1403 | [5 empty] | 120.6976 | 2568.7812
27.12.2007 09:00 | 3600 | 2 | 760.01 | GGB | 768.864 | 774.68 | 771.429 | 278.49 | GGB | 11461.9 | GGB | 9.85 | GGB | 1033.94 | GGB | 70.87 | GEB | 182653.87 | GGB | 148006.99 | GGB | 0 | 0 | 2968 | 3600 | 2952.86 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 104502.86 | GGB | 104504.13 | 2952.86 | 2952.86 |  |  |  | 1 | 1 |  |  |  |  | 148006.99 | 2952.86 | 148006.99 | 2952.86 | 10.6831 | [5 empty] | 121.4011 | 2553.447
27.12.2007 10:00 | 3600 | 2 | 761.56 | GGB | 771.429 | 777.188 | 773.26 | 276.93 | GGB | 11442.2 | GGB | 9.9 | GGB | 1033.84 | GGB | 70.87 | GEB | 180204.51 | GGB | 146006.85 | GGB | 0 | 0 | 2887 | 3600 | 2871.16 | GGB | 100 | GGB | 43.07 | GGB | 43.07 | GGB | 104545.94 | GGB | 104547.2 | 2871.16 | 2871.16 |  |  |  | 1 | 1 |  |  |  |  | 146006.85 | 2871.16 | 146006.85 | 2871.16 | 9.7332 | [5 empty] | 116.447 | 2588.4265
27.12.2007 11:00 | 3600 | 2 | 759.04 | GGB | 768.864 | 773.977 | 770.696 | 275.44 | GGB | 11294.4 | GGB | 9.85 | GGB | 1033.31 | GGB | 70.87 | GEB | 177620.92 | GGB | 143840.46 | GGB | 0 | 0 | 2966 | 3600 | 2950.6 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 104586.31 | GGB | 104587.58 | 2950.6 | 2950.6 |  |  |  | 1 | 1 |  |  |  |  | 143840.46 | 2950.6 | 143840.46 | 2950.6 | 10.5105 | [5 empty] | 117.8932 | 2627.411
27.12.2007 12:00 | 3600 | 2 | 759.2 | GGB | 767.766 | 772.711 | 769.597 | 275.46 | GGB | 11287.7 | GGB | 9.85 | GGB | 1033.6 | GGB | 70.87 | GEB | 177543.9 | GGB | 143818.06 | GGB | 0 | 0 | 2965 | 3600 | 2949.53 | GGB | 100 | GGB | 43.15 | GGB | 43.15 | GGB | 104629.46 | GGB | 104630.73 | 2949.53 | 2949.53 |  |  |  | 1 | 1 |  |  |  |  | 143818.06 | 2949.53 | 143818.06 | 2949.53 | 9.8307 | [5 empty] | 117.8321 | 2627.8202
27.12.2007 13:00 | 3600 | 2 | 759.62 | GGB | 767.766 | 773.859 | 769.597 | 275.22 | GGB | 11288.9 | GGB | 9.86 | GGB | 1033.37 | GGB | 70.87 | GEB | 177265.51 | GGB | 143560.9 | GGB | 0 | 0 | 2937 | 3600 | 2921.66 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 104670.29 | GGB | 104671.56 | 2921.66 | 2921.66 |  |  |  | 1 | 1 |  |  |  |  | 143560.9 | 2921.66 | 143560.9 | 2921.66 | 10.2727 | [5 empty] | 116.51 | 2632.5274
27.12.2007 14:00 | 3600 | 2 | 759.46 | GGB | 766.667 | 772.852 | 769.597 | 274.66 | GGB | 11277.7 | GGB | 9.86 | GGB | 1033.11 | GGB | 70.87 | GEB | 177047.65 | GGB | 143348.72 | GGB | 0 | 0 | 2935 | 3600 | 2919.43 | GGB | 100 | GGB | 41.54 | GGB | 41.54 | GGB | 104711.83 | GGB | 104713.1 | 2919.43 | 2919.43 |  |  |  | 1 | 1 |  |  |  |  | 143348.72 | 2919.43 | 143348.72 | 2919.43 | 10.0745 | [5 empty] | 116.249 | 2636.424
27.12.2007 15:00 | 3600 | 2 | 759.28 | GGB | 767.766 | 773.93 | 769.597 | 274.5 | GGB | 11267.9 | GGB | 9.85 | GGB | 1031.61 | GGB | 70.87 | GEB | 166752.89 | GGB | 134816.65 | GGB | 0 | 0 | 2943 | 3055 | 2927.19 | GGB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 104752.81 | GGB | 104754.08 | 2927.19 | 2927.19 |  |  |  | 1 | 1 |  |  |  |  | 134816.65 | 2927.19 | 134816.65 | 2927.19 | 9.6299 | [5 empty] | 109.6205 | 2803.2739
27.12.2007 16:00 | 3600 | 2 | 759.24 | GGB | 766.667 | 772.758 | 768.498 | 274.56 | GGB | 11267.6 | GGB | 9.85 | GGB | 1032.73 | GGB | 70.87 | GEB | 177155.48 | GGB | 143382.38 | GGB | 0 | 0 | 2940 | 3600 | 2924.05 | GGB | 100 | GGB | 41.35 | GGB | 41.35 | GGB | 104794.17 | GGB | 104795.43 | 2924.05 | 2924.05 |  |  |  | 1 | 1 |  |  |  |  | 143382.38 | 2924.05 | 143382.38 | 2924.05 | 10.1392 | [5 empty] | 116.4603 | 2635.805
27.12.2007 17:00 | 3600 | 2 | 759.38 | GGB | 766.667 | 772.781 | 768.498 | 274.52 | GGB | 11274.3 | GGB | 9.86 | GGB | 1032.65 | GGB | 65.83 | GEB | 177234.7 | GGB | 145570.17 | GGB | 0 | 0 | 2934 | 3600 | 2918.54 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 104835.53 | GGB | 104836.79 | 2918.54 | 2918.54 |  |  |  | 1 | 1 |  |  |  |  | 145570.17 | 2918.54 | 145570.17 | 2918.54 | 10.2721 | [5 empty] | 118.0145 | 2596.1912
27.12.2007 18:00 | 3600 | 2 | 759.31 | GGB | 767.766 | 772.805 | 769.597 | 274.54 | GGB | 11273.6 | GGB | 9.86 | GGB | 1032.87 | GGB | 57.07 | GGB | 177334.83 | GGB | 149549.51 | GGB | 0 | 0 | 2941 | 3600 | 2925.01 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 104876.35 | GGB | 104877.61 | 2925.01 | 2925.01 |  |  |  | 1 | 1 |  |  |  |  | 149549.51 | 2925.01 | 149549.51 | 2925.01 | 10.7162 | [5 empty] | 121.5094 | 2527.1096
27.12.2007 19:00 | 3600 | 2 | 759.54 | GGB | 767.766 | 773.953 | 770.696 | 274.38 | GGB | 11281.3 | GGB | 9.86 | GGB | 1032.65 | GGB | 57.05 | GGB | 177061.95 | GGB | 149295.46 | GGB | 0 | 0 | 2925 | 3600 | 2909.4 | GGB | 100 | GGB | 41.79 | GGB | 41.79 | GGB | 104918.15 | GGB | 104919.4 | 2909.4 | 2909.4 |  |  |  | 1 | 1 |  |  |  |  | 149295.46 | 2909.4 | 149295.46 | 2909.4 | 10.3939 | [5 empty] | 120.6556 | 2531.4099
27.12.2007 20:00 | 3600 | 2 | 759.38 | GGB | 767.766 | 772.898 | 769.597 | 274.06 | GGB | 11257.4 | GGB | 9.86 | GGB | 1032.04 | GGB | 57 | GGB | 176835.28 | GGB | 149040.19 | GGB | 0 | 0 | 2929 | 3600 | 2913.47 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 104958.79 | GGB | 104960.05 | 2913.47 | 2913.47 |  |  |  | 1 | 1 |  |  |  |  | 149040.19 | 2913.47 | 149040.19 | 2913.47 | 10.682 | [5 empty] | 120.6178 | 2535.7456
27.12.2007 21:00 | 3600 | 2 | 759.51 | GGB | 767.766 | 774 | 769.597 | 274.06 | GGB | 11257.7 | GGB | 9.86 | GGB | 1031.94 | GGB | 57.15 | GGB | 176792.37 | GGB | 148921.56 | GGB | 0 | 0 | 2924 | 3600 | 2908.02 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 105000.01 | GGB | 105001.27 | 2908.02 | 2908.02 |  |  |  | 1 | 1 |  |  |  |  | 148921.56 | 2908.02 | 148921.56 | 2908.02 | 10.5062 | [5 empty] | 120.2964 | 2537.7655
27.12.2007 22:00 | 3600 | 2 | 759.52 | GGB | 766.667 | 772.992 | 769.597 | 273.57 | GGB | 11247.4 | GGB | 9.86 | GGB | 1031.47 | GGB | 57.08 | GGB | 176341.23 | GGB | 148504.95 | GGB | 0 | 0 | 2915 | 3600 | 2899.08 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 105041.33 | GGB | 105042.59 | 2899.08 | 2899.08 |  |  |  | 1 | 1 |  |  |  |  | 148504.95 | 2899.08 | 148504.95 | 2899.08 | 10.4194 | [5 empty] | 119.591 | 2544.8849
27.12.2007 23:00 | 3600 | 2 | 759.55 | GGB | 768.864 | 775.148 | 770.696 | 273.3 | GGB | 11238 | GGB | 9.86 | GGB | 1030.89 | GGB | 57.18 | GGB | 176004.53 | GGB | 148095.2 | GGB | 0 | 0 | 2911 | 3600 | 2895.32 | GGB | 100 | GGB | 42.44 | GGB | 42.44 | GGB | 105083.76 | GGB | 105085.03 | 2895.32 | 2895.32 |  |  |  | 1 | 1 |  |  |  |  | 148095.2 | 2895.32 | 148095.2 | 2895.32 | 10.1033 | [5 empty] | 119.1064 | 2551.9261
27.12.2007 24:00 | 3600 | 2 | 759.56 | GGB | 767.766 | 774 | 769.597 | 273.09 | GGB | 11225.1 | GGB | 9.86 | GGB | 1030.48 | GGB | 57.26 | GGB | 175852.68 | GGB | 147870.56 | GGB | 0 | 0 | 2907 | 3600 | 2891.69 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 105124.72 | GGB | 105125.98 | 2891.69 | 2891.69 |  |  |  | 1 | 1 |  |  |  |  | 147870.56 | 2891.69 | 147870.56 | 2891.69 | 10.4419 | [5 empty] | 118.7766 | 2555.8029
28.12.2007 01:00 | 3600 | 2 | 759.5 | GGB | 767.766 | 772.734 | 769.597 | 272.94 | GGB | 11216.8 | GGB | 9.86 | GGB | 1030.21 | GGB | 57.26 | GGB | 175634.81 | GGB | 147650.61 | GGB | 0 | 0 | 2907 | 3600 | 2891.91 | GGB | 100 | GGB | 41.35 | GGB | 41.35 | GGB | 105166.07 | GGB | 105167.33 | 2891.91 | 2891.91 |  |  |  | 1 | 1 |  |  |  |  | 147650.61 | 2891.91 | 147650.61 | 2891.91 | 10.3263 | [5 empty] | 118.609 | 2559.6101
28.12.2007 02:00 | 3600 | 2 | 759.65 | GGB | 767.766 | 774 | 769.597 | 272.75 | GGB | 11205.4 | GGB | 9.86 | GGB | 1029.85 | GGB | 57.51 | GGB | 175469.76 | GGB | 147347.14 | GGB | 0 | 0 | 2895 | 3600 | 2879.08 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 105206.08 | GGB | 105207.35 | 2879.08 | 2879.08 |  |  |  | 1 | 1 |  |  |  |  | 147347.14 | 2879.08 | 147347.14 | 2879.08 | 10.6003 | [5 empty] | 117.8401 | 2564.8818
28.12.2007 03:00 | 3600 | 2 | 759.67 | GGB | 767.766 | 773.953 | 769.597 | 272.32 | GGB | 11197.8 | GGB | 9.86 | GGB | 1029.06 | GGB | 57.44 | GGB | 175002.12 | GGB | 146874.26 | GGB | 0 | 0 | 2888 | 3600 | 2872.53 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 105247.36 | GGB | 105248.63 | 2872.53 | 2872.53 |  |  |  | 1 | 1 |  |  |  |  | 146874.26 | 2872.53 | 146874.26 | 2872.53 | 10.2205 | [5 empty] | 117.1946 | 2573.1398
28.12.2007 04:00 | 3600 | 2 | 759.71 | GGB | 766.667 | 772.758 | 769.597 | 272.19 | GGB | 11176.4 | GGB | 9.86 | GGB | 1028.64 | GGB | 57.56 | GGB | 174601.59 | GGB | 146425.48 | GGB | 0 | 0 | 2882 | 3600 | 2866.32 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 105288.39 | GGB | 105289.66 | 2866.32 | 2866.32 |  |  |  | 1 | 1 |  |  |  |  | 146425.48 | 2866.32 | 146425.48 | 2866.32 | 10.2292 | [5 empty] | 116.584 | 2581.0262
28.12.2007 05:00 | 3600 | 2 | 759.67 | GGB | 767.766 | 773.672 | 769.597 | 271.98 | GGB | 11157.2 | GGB | 9.86 | GGB | 1027.84 | GGB | 57.72 | GGB | 174074.53 | GGB | 145796.94 | GGB | 0 | 0 | 2873 | 3600 | 2857.15 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 105329.26 | GGB | 105330.54 | 2857.15 | 2857.15 |  |  |  | 1 | 1 |  |  |  |  | 145796.94 | 2857.15 | 145796.94 | 2857.15 | 10.1899 | [5 empty] | 115.7121 | 2592.1532
28.12.2007 06:00 | 3600 | 2 | 759.88 | GGB | 766.667 | 772.688 | 769.597 | 271.87 | GGB | 11154.2 | GGB | 9.86 | GGB | 1027.31 | GGB | 57.71 | GGB | 173851.16 | GGB | 145538.57 | GGB | 0 | 0 | 2860 | 3600 | 2844.08 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 105370.1 | GGB | 105371.38 | 2844.08 | 2844.08 |  |  |  | 1 | 1 |  |  |  |  | 145538.57 | 2844.08 | 145538.57 | 2844.08 | 10.1352 | [5 empty] | 114.9787 | 2596.7549
28.12.2007 07:00 | 3600 | 2 | 759.4 | GGB | 767.766 | 773.906 | 769.597 | 272.07 | GGB | 11139.7 | GGB | 9.85 | GGB | 1027.2 | GGB | 57.85 | GGB | 173757.64 | GGB | 145386.32 | GGB | 0 | 0 | 2884 | 3600 | 2868.84 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 105410.74 | GGB | 105412.02 | 2868.84 | 2868.84 |  |  |  | 1 | 1 |  |  |  |  | 145386.32 | 2868.84 | 145386.32 | 2868.84 | 10.263 | [5 empty] | 115.8584 | 2599.4743
28.12.2007 08:00 | 3600 | 2 | 759.94 | GGB | 767.766 | 773.906 | 769.597 | 271.72 | GGB | 11138.2 | GGB | 9.86 | GGB | 1026.55 | GGB | 57.99 | GGB | 173477.05 | GGB | 144998.79 | GGB | 0 | 0 | 2865 | 3208 | 2849.7 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 105451.53 | GGB | 105452.82 | 2849.7 | 2849.7 |  |  |  | 1 | 1 |  |  |  |  | 144998.79 | 2849.7 | 144998.79 | 2849.7 | 10.1275 | [5 empty] | 114.7786 | 2606.4218
28.12.2007 09:00 | 3600 | 2 | 759.63 | GGB | 767.766 | 773.859 | 769.597 | 271.55 | GGB | 11123.6 | GGB | 9.86 | GGB | 1025.99 | GGB | 58.06 | GGB | 173291.09 | GGB | 144730.46 | GGB | 0 | 0 | 2873 | 3600 | 2857.08 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 105492.18 | GGB | 105493.47 | 2857.08 | 2857.08 |  |  |  | 1 | 1 |  |  |  |  | 144730.46 | 2857.08 | 144730.46 | 2857.08 | 10.1724 | [5 empty] | 114.8629 | 2611.2541
28.12.2007 10:00 | 3600 | 2 | 759.8 | GGB | 767.766 | 773.93 | 769.597 | 271.3 | GGB | 11112.6 | GGB | 9.86 | GGB | 1025.72 | GGB | 58.06 | GGB | 173265.78 | GGB | 144672.57 | GGB | 0 | 0 | 2861 | 3600 | 2845.47 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 105532.8 | GGB | 105534.09 | 2845.47 | 2845.47 |  |  |  | 1 | 1 |  |  |  |  | 144672.57 | 2845.47 | 144672.57 | 2845.47 | 10.1345 | [5 empty] | 114.3504 | 2612.2989
28.12.2007 11:00 | 3600 | 2 | 759.84 | GGB | 766.667 | 772.805 | 769.597 | 271.33 | GGB | 11093.5 | GGB | 9.86 | GGB | 1025.72 | GGB | 58.08 | GGB | 173181.06 | GGB | 144595.6 | GGB | 0 | 0 | 2847 | 3600 | 2831.38 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 105573.43 | GGB | 105574.72 | 2831.38 | 2831.38 |  |  |  | 1 | 1 |  |  |  |  | 144595.6 | 2831.38 | 144595.6 | 2831.38 | 10.0764 | [5 empty] | 113.7236 | 2613.6895
28.12.2007 12:00 | 3600 | 2 | 759.91 | GGB | 768.864 | 774.961 | 770.696 | 271.61 | GGB | 11060.1 | GGB | 9.86 | GGB | 1025.02 | GGB | 57.08 | GGB | 174525.67 | GGB | 146056.22 | GGB | 0 | 0 | 2817 | 3600 | 2801.19 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 105613.75 | GGB | 105615.04 | 2801.19 | 2801.19 |  |  |  | 1 | 1 |  |  |  |  | 146056.22 | 2801.19 | 146056.22 | 2801.19 | 10.1471 | [5 empty] | 113.6476 | 2587.5516
28.12.2007 13:00 | 3600 | 2 | 760.16 | GGB | 766.667 | 772.922 | 769.597 | 269.57 | GGB | 11096.9 | GGB | 9.87 | GGB | 1024.7 | GGB | 57.88 | GGB | 172272.18 | GGB | 143778.13 | GGB | 0 | 0 | 2811 | 3600 | 2795.06 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 105654.29 | GGB | 105655.58 | 2795.06 | 2795.06 |  |  |  | 1 | 1 |  |  |  |  | 143778.13 | 2795.06 | 143778.13 | 2795.06 | 9.9129 | [5 empty] | 111.6301 | 2628.55
28.12.2007 14:00 | 3600 | 2 | 760.15 | GGB | 767.766 | 774.047 | 769.597 | 268.65 | GGB | 11085.6 | GGB | 9.86 | GGB | 1024.16 | GGB | 57.74 | GGB | 171391.91 | GGB | 143027.56 | GGB | 0 | 0 | 2815 | 3600 | 2799.85 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 105695.32 | GGB | 105696.61 | 2799.85 | 2799.85 |  |  |  | 1 | 1 |  |  |  |  | 143027.56 | 2799.85 | 143027.56 | 2799.85 | 9.7601 | [5 empty] | 111.2377 | 2642.3439
28.12.2007 15:00 | 3600 | 2 | 759.87 | GGB | 766.667 | 773.016 | 768.498 | 269.17 | GGB | 11029.3 | GGB | 9.85 | GGB | 1023.11 | GGB | 57.78 | GGB | 171232.36 | GGB | 142731.74 | GGB | 0 | 0 | 2815 | 3600 | 2799.85 | GGB | 100 | GGB | 41.83 | GGB | 41.83 | GGB | 105737.15 | GGB | 105738.44 | 2799.85 | 2799.85 |  |  |  | 1 | 1 |  |  |  |  | 142731.74 | 2799.85 | 142731.74 | 2799.85 | 9.5536 | [5 empty] | 111.0076 | 2647.8203
28.12.2007 16:00 | 3600 | 2 | 759.91 | GGB | 767.766 | 774.117 | 769.597 | 269.91 | GGB | 10998.3 | GGB | 9.85 | GGB | 1022.93 | GGB | 57.31 | GGB | 172508.75 | GGB | 143974.18 | GGB | 0 | 0 | 2787 | 3600 | 2771.49 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 105776.74 | GGB | 105778.03 | 2771.49 | 2771.49 |  |  |  | 1 | 1 |  |  |  |  | 143974.18 | 2771.49 | 143974.18 | 2771.49 | 10.0789 | [5 empty] | 110.8397 | 2624.9707
28.12.2007 17:00 | 3600 | 2 | 760.24 | GGB | 767.766 | 773.273 | 769.597 | 268.15 | GGB | 11022.7 | GGB | 9.86 | GGB | 1022.48 | GGB | 58.28 | GGB | 169873.44 | GGB | 141297.91 | GGB | 0 | 0 | 2788 | 3600 | 2772.63 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 105817.37 | GGB | 105818.66 | 2772.63 | 2772.63 |  |  |  | 1 | 1 |  |  |  |  | 141297.91 | 2772.63 | 141297.91 | 2772.63 | 9.6423 | [5 empty] | 108.8241 | 2674.6892
28.12.2007 18:00 | 3600 | 2 | 760.02 | GGB | 766.667 | 773.273 | 769.597 | 267.79 | GGB | 11013.8 | GGB | 9.86 | GGB | 1022.33 | GGB | 58.57 | GGB | 169445.41 | GGB | 140798.34 | GGB | 0 | 0 | 2800 | 3600 | 2784.6 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 105856.82 | GGB | 105858.12 | 2784.6 | 2784.6 |  |  |  | 1 | 1 |  |  |  |  | 140798.34 | 2784.6 | 140798.34 | 2784.6 | 9.9358 | [5 empty] | 108.9075 | 2684.1794
28.12.2007 19:00 | 3600 | 2 | 759.95 | GGB | 768.864 | 774.375 | 770.696 | 267.75 | GGB | 11003 | GGB | 9.86 | GGB | 1022.04 | GGB | 58.54 | GGB | 169413.5 | GGB | 140743.66 | GGB | 0 | 0 | 2802 | 3600 | 2786.38 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 105897.63 | GGB | 105898.93 | 2786.38 | 2786.38 |  |  |  | 1 | 1 |  |  |  |  | 140743.66 | 2786.38 | 140743.66 | 2786.38 | 9.6095 | [5 empty] | 108.9348 | 2685.2222
28.12.2007 20:00 | 3600 | 2 | 759.88 | GGB | 767.766 | 774.586 | 770.696 | 267.42 | GGB | 10989.5 | GGB | 9.86 | GGB | 1021.63 | GGB | 58.51 | GGB | 169184.63 | GGB | 140513.22 | GGB | 0 | 0 | 2796 | 3600 | 2780.64 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 105937.5 | GGB | 105938.8 | 2780.64 | 2780.64 |  |  |  | 1 | 1 |  |  |  |  | 140513.22 | 2780.64 | 140513.22 | 2780.64 | 9.7998 | [5 empty] | 108.5324 | 2689.6259
28.12.2007 21:00 | 3600 | 2 | 759.42 | GGB | 768.864 | 774.539 | 770.696 | 268.57 | GGB | 10948.1 | GGB | 9.85 | GGB | 1021.42 | GGB | 58.16 | GGB | 170391.7 | GGB | 141636.54 | GGB | 0 | 0 | 2791 | 3600 | 2775.24 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 105977.92 | GGB | 105979.22 | 2775.24 | 2775.24 |  |  |  | 1 | 1 |  |  |  |  | 141636.54 | 2775.24 | 141636.54 | 2775.24 | 9.7248 | [5 empty] | 109.1876 | 2668.2945
28.12.2007 22:00 | 3600 | 2 | 760.26 | GGB | 767.766 | 774.539 | 770.696 | 269.11 | GGB | 10943.5 | GGB | 9.86 | GGB | 1020.97 | GGB | 58.04 | GGB | 171252.17 | GGB | 142336.94 | GGB | 0 | 0 | 2749 | 3600 | 2733.75 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 106017.31 | GGB | 106018.62 | 2733.75 | 2733.75 |  |  |  | 1 | 1 |  |  |  |  | 142336.94 | 2733.75 | 142336.94 | 2733.75 | 9.876 | [5 empty] | 108.0871 | 2655.1646
28.12.2007 23:00 | 3600 | 2 | 760.03 | GGB | 766.667 | 773.461 | 769.597 | 268.58 | GGB | 10932.4 | GGB | 9.86 | GGB | 1020.74 | GGB | 57.96 | GGB | 170848.34 | GGB | 142004.93 | GGB | 0 | 0 | 2741 | 3600 | 2726.03 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 106057.32 | GGB | 106058.63 | 2726.03 | 2726.03 |  |  |  | 1 | 1 |  |  |  |  | 142004.93 | 2726.03 | 142004.93 | 2726.03 | 9.6753 | [5 empty] | 107.5305 | 2661.3724
28.12.2007 24:00 | 3600 | 2 | 760.29 | GGB | 767.766 | 774.492 | 770.696 | 268.33 | GGB | 10920.2 | GGB | 9.86 | GGB | 1020.15 | GGB | 58.04 | GGB | 170583.16 | GGB | 141669.2 | GGB | 0 | 0 | 2729 | 3600 | 2713.81 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 106096.57 | GGB | 106097.88 | 2713.81 | 2713.81 |  |  |  | 1 | 1 |  |  |  |  | 141669.2 | 2713.81 | 141669.2 | 2713.81 | 9.7952 | [5 empty] | 106.7954 | 2667.6794
29.12.2007 01:00 | 3600 | 2 | 760 | GGB | 766.667 | 773.438 | 768.498 | 268.16 | GGB | 10899.2 | GGB | 9.85 | GGB | 1019.85 | GGB | 58.05 | GGB | 170396.1 | GGB | 141466.02 | GGB | 0 | 0 | 2733 | 3600 | 2718.03 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 106135.68 | GGB | 106136.98 | 2718.03 | 2718.03 |  |  |  | 1 | 1 |  |  |  |  | 141466.02 | 2718.03 | 141466.02 | 2718.03 | 9.834 | [5 empty] | 106.808 | 2671.5108
29.12.2007 02:00 | 3600 | 2 | 760.23 | GGB | 767.766 | 774.492 | 770.696 | 267.83 | GGB | 10931.6 | GGB | 9.86 | GGB | 1019.77 | GGB | 57.89 | GGB | 170709.7 | GGB | 141786.02 | GGB | 0 | 0 | 2731 | 3600 | 2715.6 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 106176.04 | GGB | 106177.35 | 2715.6 | 2715.6 |  |  |  | 1 | 1 |  |  |  |  | 141786.02 | 2715.6 | 141786.02 | 2715.6 | 9.5376 | [5 empty] | 106.9539 | 2665.4814
29.12.2007 03:00 | 3600 | 2 | 760.25 | GGB | 768.864 | 774.492 | 770.696 | 267.42 | GGB | 10935.8 | GGB | 9.86 | GGB | 1019.34 | GGB | 57.75 | GGB | 170896.76 | GGB | 141940.42 | GGB | 0 | 0 | 2728 | 3600 | 2712.41 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 106216.34 | GGB | 106217.65 | 2712.41 | 2712.41 |  |  |  | 1 | 1 |  |  |  |  | 141940.42 | 2712.41 | 141940.42 | 2712.41 | 9.5534 | [5 empty] | 106.9446 | 2662.5819
29.12.2007 04:00 | 3600 | 2 | 759.96 | GGB | 767.766 | 773.25 | 769.597 | 267.2 | GGB | 10925.5 | GGB | 9.85 | GGB | 1019.05 | GGB | 57.71 | GGB | 170971.58 | GGB | 141982.21 | GGB | 0 | 0 | 2736 | 3600 | 2720.11 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 106256.83 | GGB | 106258.14 | 2720.11 | 2720.11 |  |  |  | 1 | 1 |  |  |  |  | 141982.21 | 2720.11 | 141982.21 | 2720.11 | 9.5383 | [5 empty] | 107.2798 | 2661.7983
29.12.2007 05:00 | 3600 | 2 | 760.12 | GGB | 767.766 | 774.422 | 769.597 | 267.01 | GGB | 10933 | GGB | 9.86 | GGB | 1018.61 | GGB | 57.73 | GGB | 170739.41 | GGB | 141715.67 | GGB | 0 | 0 | 2734 | 3600 | 2718.98 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 106296.43 | GGB | 106297.74 | 2718.98 | 2718.98 |  |  |  | 1 | 1 |  |  |  |  | 141715.67 | 2718.98 | 141715.67 | 2718.98 | 9.7304 | [5 empty] | 107.0339 | 2666.8046
29.12.2007 06:00 | 3600 | 2 | 760.24 | GGB | 767.766 | 774.281 | 770.696 | 265.4 | GGB | 10962.9 | GGB | 9.87 | GGB | 1018.31 | GGB | 58.42 | GGB | 168784.11 | GGB | 139760.54 | GGB | 0 | 0 | 2748 | 3600 | 2732.69 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 106336.26 | GGB | 106337.57 | 2732.69 | 2732.69 |  |  |  | 1 | 1 |  |  |  |  | 139760.54 | 2732.69 | 139760.54 | 2732.69 | 9.5888 | [5 empty] | 106.0895 | 2704.1109
29.12.2007 07:00 | 0 | 1 | 573.61 | XNN | 367.766 | 348.094 | 349.451 | 121 | XNN | 5387.41 | XNN | 14.71 | XNN | 1009.02 | XNN | 66.15 | XNN | 168445.2 | XNN | 135058.94 | XNN | 0 | 0 | 2756 | 1363 | 2740.05 | UUU | 100 | XNN | 17.13 | XNN | 17.13 | XNN | 0 | UUU | 106337.57 | 2740.05 | 2740.05 |  |  |  | 0 | 0 | [14 empty] | 102.7967
29.12.2007 08:00 | 0 | 1 | 234.34 | XNN | 182.784 | 154.031 | 164.103 | 3 | XNN | 1549.92 | XNN | 19.98 | XNN | 1004.21 | XNN | 49.55 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 0 | 0 | 0 | UUU | 100 | XNN | 0.14 | XNN | 0.14 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 09:00 | 0 | 1 | 154.24 | XNN | 151.282 | 122.813 | 135.897 | 2.95 | XNN | 1554.66 | XNN | 19.98 | XNN | 1004.45 | XNN | 39.81 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 0 | 0 | 0 | UUU | 100 | XNN | 1.87 | XNN | 1.87 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 10:00 | 0 | 1 | 137.44 | XNN | 140.293 | 112.477 | 123.81 | 2.93 | XNN | 1695.93 | XNN | 19.98 | XNN | 1004.44 | XNN | 39.28 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 0 | 0 | 0 | UUU | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 11:00 | 0 | 1 | 119.81 | XNN | 131.502 | 105.023 | 109.157 | 2.92 | XNN | 1753.75 | XNN | 19.99 | XNN | 1003.88 | XNN | 38.74 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 0 | 0 | 0 | UUU | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 12:00 | 0 | 1 | 111.58 | XNN | 117.949 | 112.711 | 115.018 | 2.91 | XNN | 1750.79 | XNN | 19.99 | XNN | 1003.08 | XNN | 38.26 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -11 | 2670 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 13:00 | 0 | 1 | 134.23 | XNN | 146.154 | 142.383 | 144.322 | 2.92 | XNN | 1752.49 | XNN | 19.99 | XNN | 1003.67 | XNN | 37.86 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -11 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 14:00 | 0 | 1 | 157.79 | XNN | 161.905 | 157.383 | 161.905 | 2.94 | XNN | 1748.66 | XNN | 19.98 | XNN | 1003.05 | XNN | 38.61 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -11 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 15:00 | 0 | 1 | 167.27 | XNN | 183.883 | 175.852 | 178.022 | 2.96 | XNN | 1752.86 | XNN | 19.98 | XNN | 1002.85 | XNN | 38.82 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -11 | 3600 | 0 | GGB | 100 | XNN | 1.85 | XNN | 1.85 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 16:00 | 0 | 1 | 190.93 | XNN | 200 | 191.039 | 190.11 | 2.93 | XNN | 1747.18 | XNN | 19.98 | XNN | 1002.41 | XNN | 40.15 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -11 | 3600 | 0 | GGB | 100 | XNN | 3.61 | XNN | 3.61 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 17:00 | 0 | 1 | 202.45 | XNN | 215.751 | 206.156 | 208.425 | 2.91 | XNN | 1731.66 | XNN | 19.98 | XNN | 1002.24 | XNN | 40.95 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -11 | 3600 | 0 | GGB | 100 | XNN | 1.65 | XNN | 1.65 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 18:00 | 0 | 1 | 204.06 | XNN | 154.945 | 150.422 | 143.956 | 10.34 | XNN | 1723.07 | XNN | 18.13 | XNN | 1001.48 | XNN | 51.63 | XNN | 23.78 | XNN | 19.77 | XNN | 0 | 0 | 39 | 3600 | 25.87 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 25.87 | 25.87 |  |  |  | 0 | 0 | [14 empty] | 0.00014207
29.12.2007 19:00 | 0 | 1 | 116.06 | XNN | 91.2088 | 92.6953 | 90.1099 | 57.68 | XNN | 1733.44 | XNN | 6.68 | XNN | 1002.61 | XNN | 42.59 | XNN | 14373.16 | XNN | 12305.75 | XNN | 0 | 0 | -12 | 3600 | 0 | GGB | 100 | XNN | 0.03 | XNN | 0.03 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 20:00 | 0 | 1 | 115.54 | XNN | 110.623 | 110.484 | 109.157 | 138.43 | XNN | 1776.78 | XNN | 3.72 | XNN | 1007.15 | XNN | 25.74 | XNN | 59409.55 | XNN | 53976.61 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 21:00 | 0 | 1 | 120.23 | XNN | 121.978 | 122.602 | 121.245 | 167.48 | XNN | 1815.74 | XNN | 2.59 | XNN | 1008.95 | XNN | 17.05 | XNN | 76410.97 | XNN | 71630.96 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 22:00 | 0 | 1 | 122.63 | XNN | 121.978 | 122.578 | 121.978 | 151.26 | XNN | 1831.49 | XNN | 3.22 | XNN | 1008.8 | XNN | 20.06 | XNN | 70911.05 | XNN | 65782.78 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 23:00 | 0 | 1 | 122.96 | XNN | 126.74 | 127.055 | 126.74 | 177.67 | XNN | 1826.85 | XNN | 2.42 | XNN | 1010.49 | XNN | 15.18 | XNN | 85882.35 | XNN | 81158.63 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
29.12.2007 24:00 | 0 | 1 | 128.46 | XNN | 124.176 | 124.875 | 124.176 | 197.17 | XNN | 1833.43 | XNN | 2.27 | XNN | 1011.62 | XNN | 10.58 | XNN | 95530.22 | XNN | 91842.5 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 01:00 | 0 | 1 | 163.94 | XNN | 215.751 | 212.906 | 213.919 | 90.47 | XNN | 1841.05 | XNN | 11.77 | XNN | 1006.37 | XNN | 43.53 | XNN | 44883.55 | XNN | 38457.96 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 02:00 | 0 | 1 | 201.69 | XNN | 180.586 | 190.195 | 193.407 | 2.83 | XNN | 1621.09 | XNN | 19.98 | XNN | 1002.17 | XNN | 40.51 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 03:00 | 0 | 1 | 171.56 | XNN | 171.795 | 178.383 | 179.853 | 2.81 | XNN | 1564.49 | XNN | 19.98 | XNN | 1002.09 | XNN | 39.55 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 04:00 | 0 | 1 | 162.18 | XNN | 165.934 | 167.531 | 168.864 | 2.82 | XNN | 1596.24 | XNN | 19.98 | XNN | 1002.23 | XNN | 37.73 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 05:00 | 0 | 1 | 156.87 | XNN | 164.469 | 164.086 | 161.538 | 2.81 | XNN | 1604.7 | XNN | 19.99 | XNN | 1002.15 | XNN | 37.16 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 06:00 | 0 | 1 | 156.15 | XNN | 164.469 | 163.125 | 157.875 | 2.81 | XNN | 1609.01 | XNN | 19.98 | XNN | 1002.19 | XNN | 37.03 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 07:00 | 0 | 1 | 156.72 | XNN | 165.568 | 164.086 | 161.538 | 2.81 | XNN | 1611.76 | XNN | 19.99 | XNN | 1002.36 | XNN | 38.08 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2.25 | XNN | 2.25 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 08:00 | 0 | 1 | 160.99 | XNN | 165.934 | 167.227 | 164.103 | 2.8 | XNN | 1605.78 | XNN | 19.99 | XNN | 1002.46 | XNN | 39.31 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 09:00 | 0 | 1 | 161.88 | XNN | 168.132 | 165.164 | 158.974 | 2.81 | XNN | 1600.66 | XNN | 19.99 | XNN | 1002.79 | XNN | 39.58 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 10:00 | 0 | 1 | 172.91 | XNN | 189.011 | 182.203 | 157.875 | 2.81 | XNN | 1596.91 | XNN | 19.99 | XNN | 1003.32 | XNN | 39.67 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 11:00 | 0 | 1 | 185.66 | XNN | 196.337 | 188.484 | 156.777 | 2.84 | XNN | 1599.18 | XNN | 19.98 | XNN | 1003.88 | XNN | 39.73 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 12:00 | 0 | 1 | 191.05 | XNN | 198.535 | 190.57 | 160.073 | 2.83 | XNN | 1589.84 | XNN | 19.98 | XNN | 1004.1 | XNN | 39.83 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.74 | XNN | 1.74 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 13:00 | 0 | 1 | 197.39 | XNN | 216.85 | 211.125 | 195.604 | 2.85 | XNN | 1585.51 | XNN | 19.98 | XNN | 1003.69 | XNN | 40.16 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 14:00 | 0 | 1 | 173.38 | XNN | 102.198 | 123 | 113.187 | 12.66 | XNN | 1577.18 | XNN | 13.47 | XNN | 1002.23 | XNN | 48.44 | XNN | 3.01 | XNN | 2.53 | XNN | 0 | 0 | -11 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 15:00 | 0 | 1 | 99.57 | XNN | 106.96 | 107.648 | 105.861 | 79.8 | XNN | 1568.39 | XNN | 3.68 | XNN | 1005.84 | XNN | 55.12 | XNN | 31405.51 | XNN | 25944.92 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.2 | XNN | 1.2 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 16:00 | 0 | 1 | 150 | XNN | 209.524 | 206.531 | 205.861 | 127.71 | XNN | 1599.32 | XNN | 8.79 | XNN | 1010.1 | XNN | 37.96 | XNN | 67961.48 | XNN | 59494.97 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0.3 | XNN | 0.3 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 17:00 | 0 | 1 | 219.79 | XNN | 215.751 | 218.578 | 219.414 | 2.93 | XNN | 1594.45 | XNN | 19.98 | XNN | 1004.26 | XNN | 40.94 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 18:00 | 0 | 1 | 204.2 | XNN | 114.652 | 117.211 | 116.483 | 15.9 | XNN | 1579.6 | XNN | 13.62 | XNN | 1004.48 | XNN | 68.15 | XNN | 869.52 | XNN | 689.98 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 19:00 | 0 | 1 | 107.87 | XNN | 117.949 | 118.078 | 116.483 | 105.14 | XNN | 1594.27 | XNN | 2.92 | XNN | 1009.13 | XNN | 47.73 | XNN | 47039.44 | XNN | 39886.64 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 20:00 | 0 | 1 | 123.48 | XNN | 136.264 | 136.734 | 135.897 | 178.78 | XNN | 1628.27 | XNN | 2.48 | XNN | 1013.56 | XNN | 21 | XNN | 85522.43 | XNN | 79456.47 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 21:00 | 0 | 1 | 131.61 | XNN | 126.74 | 128.18 | 122.344 | 182.07 | XNN | 1637.95 | XNN | 2.71 | XNN | 1014.69 | XNN | 15.17 | XNN | 89527.66 | XNN | 84957.07 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 22:00 | 0 | 1 | 124.24 | XNN | 126.74 | 127.031 | 123.077 | 181.59 | XNN | 1641.14 | XNN | 2.75 | XNN | 1015.55 | XNN | 14.66 | XNN | 85671.75 | XNN | 81510.85 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 23:00 | 0 | 1 | 139.56 | XNN | 146.154 | 146.367 | 145.055 | 222.86 | XNN | 1654.9 | XNN | 2.58 | XNN | 1019.14 | XNN | 6.76 | XNN | 120902.91 | XNN | 118697.17 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
30.12.2007 24:00 | 0 | 1 | 157.64 | XNN | 208.425 | 207.984 | 205.494 | 77.89 | XNN | 1648.42 | XNN | 10.12 | XNN | 1010.22 | XNN | 52.43 | XNN | 41399 | XNN | 34633.48 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 01:00 | 0 | 1 | 168.08 | XNN | 141.392 | 144.469 | 155.311 | 2.84 | XNN | 1686.53 | XNN | 19.98 | XNN | 1006.76 | XNN | 41.78 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.39 | XNN | 1.39 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 02:00 | 0 | 1 | 124.68 | XNN | 119.414 | 130.477 | 132.234 | 2.86 | XNN | 1676.26 | XNN | 19.98 | XNN | 1006.51 | XNN | 38.72 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 03:00 | 0 | 1 | 120.02 | XNN | 121.978 | 126.352 | 127.473 | 2.87 | XNN | 1592.33 | XNN | 19.98 | XNN | 1006.49 | XNN | 38.57 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 04:00 | 0 | 1 | 117.46 | XNN | 120.513 | 123.117 | 121.245 | 2.86 | XNN | 1532.13 | XNN | 19.98 | XNN | 1006.64 | XNN | 38.18 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 05:00 | 0 | 1 | 115.97 | XNN | 119.414 | 119.578 | 117.582 | 2.83 | XNN | 1547.98 | XNN | 19.98 | XNN | 1006.48 | XNN | 38.35 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 06:00 | 0 | 1 | 116 | XNN | 115.751 | 120.469 | 118.681 | 2.82 | XNN | 658.19 | XNN | 19.98 | XNN | 1006.54 | XNN | 38.59 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 07:00 | 0 | 1 | 115.83 | XNN | 116.85 | 119.414 | 115.018 | 2.85 | XNN | 50.08 | XNN | 14.36 | XNN | 1006.71 | XNN | 38.28 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 08:00 | 0 | 1 | 115.43 | XNN | 116.85 | 118.125 | 106.593 | 2.83 | XNN | 8.93 | XNN | 0 | XNN | 1006.62 | XNN | 38.2 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 09:00 | 0 | 1 | 114.78 | XNN | 110.989 | 113.977 | 96.7033 | 2.84 | XNN | 8.93 | XNN | 0 | XNN | 1006.84 | XNN | 37.51 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 10:00 | 0 | 1 | 111.21 | XNN | 112.088 | 112.57 | 90.8425 | 2.84 | XNN | 328.05 | XNN | 4.79 | XNN | 1007.07 | XNN | 37.17 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.51 | XNN | 1.51 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 11:00 | 0 | 1 | 111.7 | XNN | 112.088 | 112.57 | 95.9707 | 2.84 | XNN | 209.53 | XNN | 9.49 | XNN | 1007 | XNN | 37.85 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 4.05 | XNN | 4.05 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 12:00 | 0 | 1 | 114.18 | XNN | 114.652 | 114.727 | 101.099 | 2.84 | XNN | 8.91 | XNN | 0 | XNN | 1006.93 | XNN | 38.6 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 4.45 | XNN | 4.45 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 13:00 | 0 | 1 | 115.19 | XNN | 115.751 | 114.727 | 102.93 | 2.86 | XNN | 8.92 | XNN | 0 | XNN | 1006.93 | XNN | 38.51 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 5.31 | XNN | 5.31 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 14:00 | 0 | 1 | 115.61 | XNN | 114.652 | 113.719 | 106.96 | 2.86 | XNN | 8.92 | XNN | 0 | XNN | 1006.88 | XNN | 38.35 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 5.07 | XNN | 5.07 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 15:00 | 0 | 1 | 131.22 | XNN | 152.381 | 151.336 | 147.253 | 2.86 | XNN | 8.92 | XNN | 0 | XNN | 1008.14 | XNN | 25.08 | XNN | 72.37 | XNN | 65.96 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 4.45 | XNN | 4.45 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 16:00 | 0 | 1 | 166.74 | XNN | 167.033 | 163.922 | 156.044 | 2.85 | XNN | 8.93 | XNN | 0 | XNN | 1009.05 | XNN | 13.82 | XNN | 50.56 | XNN | 47.94 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 3.32 | XNN | 3.32 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 17:00 | 0 | 1 | 173.32 | XNN | 162.271 | 156.469 | 145.055 | 2.84 | XNN | 8.93 | XNN | 0 | XNN | 1009.88 | XNN | 3.66 | XNN | 13.97 | XNN | 13.75 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 18:00 | 0 | 1 | 170.76 | XNN | 160.806 | 154.242 | 146.154 | 2.82 | XNN | 8.93 | XNN | 0 | XNN | 1010.48 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 19:00 | 0 | 1 | 169.56 | XNN | 161.905 | 154.242 | 145.421 | 2.81 | XNN | 8.92 | XNN | 0 | XNN | 1011.02 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.75 | XNN | 1.75 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 20:00 | 0 | 1 | 169.16 | XNN | 161.905 | 156.258 | 147.985 | 2.8 | XNN | 8.93 | XNN | 0 | XNN | 1011.08 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0.09 | XNN | 0.09 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 21:00 | 0 | 1 | 169.5 | XNN | 163.37 | 156.258 | 149.084 | 2.8 | XNN | 8.93 | XNN | 0 | XNN | 1011.22 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 22:00 | 0 | 1 | 169.85 | XNN | 164.469 | 157.313 | 150.549 | 2.8 | XNN | 8.93 | XNN | 0 | XNN | 1011.58 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 23:00 | 0 | 1 | 169.93 | XNN | 164.469 | 158.367 | 154.212 | 2.81 | XNN | 8.93 | XNN | 0 | XNN | 1011.93 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
31.12.2007 24:00 | 0 | 1 | 169.93 | XNN | 165.568 | 159.398 | 155.311 | 2.81 | XNN | 8.93 | XNN | 0 | XNN | 1012.03 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 01:00 | 0 | 1 | 169.9 | XNN | 165.568 | 160.477 | 155.311 | 2.82 | XNN | 8.93 | XNN | 0 | XNN | 1012.37 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.81 | XNN | 1.81 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 02:00 | 0 | 1 | 169.84 | XNN | 165.934 | 160.477 | 156.41 | 2.83 | XNN | 8.93 | XNN | 0 | XNN | 1012.52 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 03:00 | 0 | 1 | 169.91 | XNN | 167.033 | 160.477 | 157.875 | 2.84 | XNN | 8.93 | XNN | 0 | XNN | 1013.2 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 04:00 | 0 | 1 | 169.77 | XNN | 167.033 | 160.477 | 157.875 | 2.84 | XNN | 8.93 | XNN | 0 | XNN | 1013.48 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 05:00 | 0 | 1 | 169.17 | XNN | 167.033 | 161.508 | 157.143 | 2.84 | XNN | 8.93 | XNN | 0 | XNN | 1013.81 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 06:00 | 0 | 1 | 169.17 | XNN | 167.033 | 161.508 | 157.143 | 2.85 | XNN | 8.92 | XNN | 0 | XNN | 1014.16 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 07:00 | 0 | 1 | 169.16 | XNN | 167.033 | 161.508 | 156.777 | 2.85 | XNN | 8.93 | XNN | 0 | XNN | 1014.57 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 08:00 | 0 | 1 | 169.33 | XNN | 167.033 | 161.508 | 157.875 | 2.85 | XNN | 8.93 | XNN | 0 | XNN | 1015 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 09:00 | 0 | 1 | 169.16 | XNN | 168.132 | 161.508 | 157.143 | 2.86 | XNN | 8.93 | XNN | 0 | XNN | 1015.67 | XNN | 0.07 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 10:00 | 0 | 1 | 168.58 | XNN | 167.033 | 161.508 | 157.875 | 2.88 | XNN | 8.92 | XNN | 0 | XNN | 1016 | XNN | 1.71 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 11:00 | 0 | 1 | 169.01 | XNN | 167.033 | 161.508 | 157.875 | 2.89 | XNN | 8.92 | XNN | 0 | XNN | 1016.52 | XNN | 2.53 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 12:00 | 0 | 1 | 169.17 | XNN | 167.033 | 161.508 | 158.242 | 2.89 | XNN | 8.93 | XNN | 0 | XNN | 1016.95 | XNN | 2.89 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 13:00 | 0 | 1 | 171.07 | XNN | 168.132 | 164.719 | 164.469 | 2.88 | XNN | 8.92 | XNN | 0 | XNN | 1017.39 | XNN | 3.49 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 14:00 | 0 | 1 | 178.96 | XNN | 178.022 | 175.477 | 172.894 | 2.88 | XNN | 8.93 | XNN | 0 | XNN | 1018.05 | XNN | 4.33 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 15:00 | 0 | 1 | 203.29 | XNN | 215.751 | 218.602 | 214.652 | 2.9 | XNN | 8.92 | XNN | 0 | XNN | 1018.63 | XNN | 3.85 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 16:00 | 0 | 1 | 251.36 | XNN | 253.846 | 248.813 | 247.619 | 2.92 | XNN | 8.93 | XNN | 0 | XNN | 1019.19 | XNN | 3.13 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 17:00 | 0 | 1 | 267.85 | XNN | 262.271 | 253.289 | 252.381 | 2.92 | XNN | 8.93 | XNN | 0 | XNN | 1019.94 | XNN | 2.33 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 18:00 | 0 | 1 | 267.46 | XNN | 160.806 | 152.156 | 153.114 | 5.34 | XNN | 8.93 | XNN | 0 | XNN | 1020.53 | XNN | 4.22 | XNN | 21.34 | XNN | 21.17 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 19:00 | 0 | 1 | 154.15 | XNN | 84.9817 | 84.75 | 83.1502 | 43.14 | XNN | 8.93 | XNN | 0 | XNN | 1020.45 | XNN | 39.31 | XNN | 4599.68 | XNN | 4050.28 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 20:00 | 0 | 1 | 107.48 | XNN | 120.513 | 121.008 | 121.245 | 157.53 | XNN | 8.93 | XNN | 0 | XNN | 1026.65 | XNN | 15.69 | XNN | 63317.18 | XNN | 60683.09 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 21:00 | 0 | 1 | 125.76 | XNN | 126.74 | 126.352 | 127.106 | 189.79 | XNN | 8.93 | XNN | 0 | XNN | 1029.62 | XNN | 7.7 | XNN | 90476.81 | XNN | 89440.36 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 22:00 | 0 | 1 | 137.63 | XNN | 140.293 | 141.82 | 140.659 | 235.53 | XNN | 8.94 | XNN | 0 | XNN | 1033.56 | XNN | 2.87 | XNN | 130622.19 | XNN | 131885.68 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 23:00 | 0 | 1 | 142.09 | XNN | 167.033 | 164.766 | 159.707 | 164.47 | XNN | 8.94 | XNN | 0 | XNN | 1029.91 | XNN | 23.11 | XNN | 86735.77 | XNN | 81301.35 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
01.01.2008 24:00 | 0 | 1 | 163.18 | XNN | 153.48 | 138.023 | 138.828 | 2.99 | XNN | 8.93 | XNN | 0 | XNN | 1022.62 | XNN | 26.75 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 01:00 | 0 | 1 | 137.26 | XNN | 129.304 | 122.836 | 128.571 | 2.97 | XNN | 8.93 | XNN | 0 | XNN | 1023.46 | XNN | 8.46 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 02:00 | 0 | 1 | 124.85 | XNN | 119.414 | 115.242 | 127.473 | 2.95 | XNN | 8.93 | XNN | 0 | XNN | 1023.97 | XNN | 6.04 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 03:00 | 0 | 1 | 115.82 | XNN | 115.751 | 113.18 | 124.908 | 2.94 | XNN | 8.93 | XNN | 0 | XNN | 1024.93 | XNN | 4.91 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 04:00 | 0 | 1 | 117.27 | XNN | 112.088 | 112.172 | 122.344 | 2.91 | XNN | 8.93 | XNN | 0 | XNN | 1025.25 | XNN | 4.23 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 05:00 | 0 | 1 | 117.82 | XNN | 110.989 | 112.172 | 120.146 | 2.91 | XNN | 8.93 | XNN | 0 | XNN | 1025.99 | XNN | 3.71 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 06:00 | 0 | 1 | 117.99 | XNN | 110.623 | 112.383 | 120.146 | 2.91 | XNN | 8.92 | XNN | 0 | XNN | 1026.15 | XNN | 3.45 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 07:00 | 0 | 1 | 117.78 | XNN | 109.524 | 112.641 | 119.78 | 2.87 | XNN | 8.93 | XNN | 0 | XNN | 1026.49 | XNN | 3.39 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 08:00 | 0 | 1 | 118.63 | XNN | 114.286 | 112.594 | 119.78 | 2.79 | XNN | 8.92 | XNN | 0 | XNN | 1026.64 | XNN | 3.18 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 09:00 | 0 | 1 | 119.14 | XNN | 113.187 | 114.727 | 116.483 | 2.78 | XNN | 8.93 | XNN | 0 | XNN | 1026.87 | XNN | 2.72 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 10:00 | 0 | 1 | 116.64 | XNN | 114.652 | 112.641 | 114.652 | 2.77 | XNN | 8.93 | XNN | 0 | XNN | 1027.14 | XNN | 2.55 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2.05 | XNN | 2.05 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 11:00 | 0 | 1 | 114.87 | XNN | 119.414 | 113.625 | 114.652 | 2.76 | XNN | 8.93 | XNN | 0 | XNN | 1027.03 | XNN | 3.17 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 12:00 | 0 | 1 | 115.12 | XNN | 121.978 | 115.523 | 113.919 | 2.78 | XNN | 8.91 | XNN | 0 | XNN | 1026.92 | XNN | 3.47 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 13:00 | 0 | 1 | 123.39 | XNN | 139.927 | 137.227 | 136.996 | 2.76 | XNN | 8.92 | XNN | 0 | XNN | 1026.59 | XNN | 3.88 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 14:00 | 0 | 1 | 159.49 | XNN | 149.817 | 146.813 | 149.084 | 2.73 | XNN | 8.92 | XNN | 0 | XNN | 1026.05 | XNN | 6.42 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 15:00 | 0 | 1 | 177.82 | XNN | 159.707 | 153.469 | 157.875 | 2.69 | XNN | 8.6 | XNN | 0 | XNN | 1025.61 | XNN | 4.98 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 16:00 | 0 | 1 | 181.35 | XNN | 164.469 | 157.852 | 161.538 | 2.69 | XNN | 8.82 | XNN | 0 | XNN | 1025.58 | XNN | 2.55 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 17:00 | 0 | 1 | 181.41 | XNN | 169.231 | 164.227 | 167.399 | 2.68 | XNN | 8.91 | XNN | 0 | XNN | 1025.62 | XNN | 1.17 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 18:00 | 0 | 1 | 181.29 | XNN | 172.894 | 167.461 | 169.963 | 2.61 | XNN | 8.92 | XNN | 0 | XNN | 1025.21 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 19:00 | 0 | 1 | 180.92 | XNN | 175.458 | 168.539 | 171.062 | 2.66 | XNN | 8.93 | XNN | 0 | XNN | 1025.26 | XNN | 0.31 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 20:00 | 0 | 1 | 180.84 | XNN | 176.557 | 170.695 | 172.527 | 2.72 | XNN | 8.92 | XNN | 0 | XNN | 1024.79 | XNN | 0.12 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 21:00 | 0 | 1 | 180.71 | XNN | 176.923 | 170.695 | 172.527 | 2.7 | XNN | 8.92 | XNN | 0 | XNN | 1024.43 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 22:00 | 0 | 1 | 180.6 | XNN | 178.022 | 171.727 | 173.626 | 2.68 | XNN | 8.93 | XNN | 0 | XNN | 1024.36 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 23:00 | 0 | 1 | 180.15 | XNN | 178.022 | 171.727 | 173.26 | 2.69 | XNN | 8.93 | XNN | 0 | XNN | 1024.42 | XNN | 0.1 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
02.01.2008 24:00 | 0 | 1 | 180.15 | XNN | 178.022 | 172.805 | 173.626 | 2.76 | XNN | 8.93 | XNN | 0 | XNN | 1024.44 | XNN | 0.25 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 01:00 | 0 | 1 | 180.89 | XNN | 175.458 | 168.633 | 168.864 | 2.79 | XNN | 8.93 | XNN | 0 | XNN | 1024.7 | XNN | 0.28 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 02:00 | 0 | 1 | 180.92 | XNN | 176.557 | 170.648 | 169.963 | 2.8 | XNN | 8.93 | XNN | 0 | XNN | 1025.09 | XNN | 0.24 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 03:00 | 0 | 1 | 180.9 | XNN | 176.557 | 170.648 | 168.132 | 2.81 | XNN | 8.92 | XNN | 0 | XNN | 1025.67 | XNN | 0.37 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 04:00 | 0 | 1 | 180.86 | XNN | 176.557 | 170.648 | 170.696 | 2.8 | XNN | 8.93 | XNN | 0 | XNN | 1026.03 | XNN | 0.08 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 05:00 | 0 | 1 | 184.86 | XNN | 186.447 | 183.773 | 181.685 | 2.79 | XNN | 8.93 | XNN | 0 | XNN | 1026.57 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 06:00 | 0 | 1 | 214.16 | XNN | 227.839 | 225.773 | 221.978 | 2.76 | XNN | 8.93 | XNN | 0 | XNN | 1027.07 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 07:00 | 0 | 1 | 228.96 | XNN | 236.63 | 230.063 | 226.74 | 2.72 | XNN | 8.92 | XNN | 0 | XNN | 1027.96 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 08:00 | 0 | 1 | 227.99 | XNN | 237.729 | 230.063 | 227.839 | 2.7 | XNN | 8.92 | XNN | 0 | XNN | 1028.73 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 09:00 | 0 | 1 | 230.51 | XNN | 232.967 | 224.813 | 220.879 | 2.62 | XNN | 8.92 | XNN | 0 | XNN | 1029.46 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 10:00 | 0 | 1 | 233.06 | XNN | 225.641 | 216.422 | 209.89 | 2.69 | XNN | 8.92 | XNN | 0 | XNN | 1030.1 | XNN | 0.17 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 3.32 | XNN | 3.32 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 11:00 | 0 | 1 | 232.85 | XNN | 220.879 | 212.719 | 203.663 | 2.77 | XNN | 8.91 | XNN | 0 | XNN | 1030.64 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 12:00 | 0 | 1 | 231.51 | XNN | 218.315 | 209.555 | 201.099 | 2.81 | XNN | 8.92 | XNN | 0 | XNN | 1030.84 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 13:00 | 0 | 1 | 230.81 | XNN | 217.216 | 209.555 | 203.663 | 2.83 | XNN | 8.93 | XNN | 0 | XNN | 1030.77 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 14:00 | 0 | 1 | 232.12 | XNN | 213.553 | 205.383 | 198.168 | 2.88 | XNN | 8.92 | XNN | 0 | XNN | 1030.54 | XNN | 2.75 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 15:00 | 0 | 1 | 232.94 | XNN | 208.425 | 201.094 | 195.604 | 2.9 | XNN | 8.93 | XNN | 0 | XNN | 1030.68 | XNN | 1.26 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 16:00 | 0 | 1 | 229.69 | XNN | 206.227 | 197.859 | 191.941 | 2.93 | XNN | 8.93 | XNN | 0 | XNN | 1030.79 | XNN | 2.02 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2.87 | XNN | 2.87 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 17:00 | 0 | 1 | 235.57 | XNN | 220.513 | 215.133 | 207.692 | 2.98 | XNN | 8.92 | XNN | 0 | XNN | 1030.89 | XNN | 2.86 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.78 | XNN | 1.78 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 18:00 | 0 | 1 | 252.46 | XNN | 231.502 | 223.805 | 217.582 | 3.02 | XNN | 8.92 | XNN | 0 | XNN | 1031.05 | XNN | 3.33 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 19:00 | 0 | 1 | 257.33 | XNN | 231.868 | 224.953 | 217.582 | 3 | XNN | 8.91 | XNN | 0 | XNN | 1031.13 | XNN | 3.12 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0.99 | XNN | 0.99 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 20:00 | 0 | 1 | 264.47 | XNN | 187.912 | 182.789 | 179.853 | 2.93 | XNN | 8.92 | XNN | 0 | XNN | 1031.39 | XNN | 1.52 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.03 | XNN | 1.03 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 21:00 | 0 | 1 | 274.25 | XNN | 186.447 | 180.586 | 178.388 | 2.92 | XNN | 8.91 | XNN | 0 | XNN | 1031.26 | XNN | 1.88 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2.19 | XNN | 2.19 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 22:00 | 0 | 1 | 277.37 | XNN | 218.315 | 212.977 | 213.187 | 5.14 | XNN | 8.93 | XNN | 0 | XNN | 1031.56 | XNN | 1.53 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.56 | XNN | 1.56 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 23:00 | 0 | 1 | 208.63 | XNN | 93.7729 | 94.6406 | 91.9414 | 51.48 | XNN | 8.93 | XNN | 0 | XNN | 1032.8 | XNN | 28.99 | XNN | 13119.11 | XNN | 12091.38 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0.13 | XNN | 0.13 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
03.01.2008 24:00 | 0 | 1 | 116.91 | XNN | 121.978 | 122.813 | 122.344 | 195.35 | XNN | 8.92 | XNN | 0 | XNN | 1043.81 | XNN | 4.63 | XNN | 112429.21 | XNN | 113916.68 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 01:00 | 0 | 1 | 125.1 | XNN | 121.978 | 122.813 | 122.344 | 207.59 | XNN | 8.91 | XNN | 0 | XNN | 1044.21 | XNN | 4.48 | XNN | 122295.94 | XNN | 124027.24 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2 | XNN | 2 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 02:00 | 0 | 1 | 124.96 | XNN | 123.077 | 122.813 | 123.443 | 209.12 | XNN | 8.92 | XNN | 0 | XNN | 1043.93 | XNN | 4.25 | XNN | 122788.89 | XNN | 124596.93 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2.1 | XNN | 2.1 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 03:00 | 0 | 1 | 125.21 | XNN | 123.077 | 122.813 | 123.077 | 211.98 | XNN | 1502.26 | XNN | 1.59 | XNN | 1044.05 | XNN | 4.57 | XNN | 122440.08 | XNN | 124115.57 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 7.64 | XNN | 7.64 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 04:00 | 0 | 1 | 124.87 | XNN | 121.978 | 122.813 | 122.344 | 211.96 | XNN | 2240.52 | XNN | 2.36 | XNN | 1044.28 | XNN | 4.49 | XNN | 122759.18 | XNN | 124500.91 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 2.57 | XNN | 2.57 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 05:00 | 0 | 1 | 124.38 | XNN | 121.978 | 122.813 | 121.978 | 212.38 | XNN | 3796.58 | XNN | 3.96 | XNN | 1044.51 | XNN | 3.47 | XNN | 122042.86 | XNN | 124260.32 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 0.68 | XNN | 0.68 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 06:00 | 0 | 1 | 124.82 | XNN | 123.077 | 122.813 | 122.344 | 213.84 | XNN | 3822.46 | XNN | 4 | XNN | 1044.4 | XNN | 4.44 | XNN | 121586.22 | XNN | 123346.95 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.16 | XNN | 1.16 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 07:00 | 0 | 1 | 126.22 | XNN | 126.74 | 127.289 | 127.106 | 212.75 | XNN | 3828.3 | XNN | 4.29 | XNN | 1044.64 | XNN | 4.78 | XNN | 121907.52 | XNN | 123552.79 | XNN | 0 | 0 | -13 | 3600 | 0 | GGB | 100 | XNN | 1.8 | XNN | 1.8 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 08:00 | 0 | 1 | 131.96 | XNN | 130.403 | 130.5 | 130.769 | 222.73 | XNN | 4182.15 | XNN | 4.94 | XNN | 1045.6 | XNN | 1.9 | XNN | 130028.01 | XNN | 133286.14 | XNN | 0 | 0 | -6 | 3206 | 0 | GGB | 100 | XNN | 1.83 | XNN | 1.83 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 09:00 | 0 | 1 | 132.89 | XNN | 132.601 | 132.656 | 131.135 | 220.85 | XNN | 7125.31 | XNN | 8.18 | XNN | 1045.33 | XNN | 2.04 | XNN | 129285.28 | XNN | 132419.4 | XNN | 0 | 0 | -1 | 3600 | 0 | GGB | 100 | XNN | 1.71 | XNN | 1.71 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 10:00 | 0 | 1 | 133.85 | XNN | 136.264 | 138.023 | 133.333 | 229.55 | XNN | 7471.44 | XNN | 8.56 | XNN | 1045.45 | XNN | 2.39 | XNN | 132110.95 | XNN | 135159.63 | XNN | 0 | 0 | -1 | 3600 | 0 | GGB | 100 | XNN | 2.12 | XNN | 2.12 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 11:00 | 0 | 1 | 135.61 | XNN | 137.729 | 138.023 | 134.799 | 229.67 | XNN | 7541.91 | XNN | 8.69 | XNN | 1045.45 | XNN | 3.43 | XNN | 131457.35 | XNN | 133985.54 | XNN | 0 | 0 | -1 | 3600 | 0 | GGB | 100 | XNN | 1.8 | XNN | 1.8 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 12:00 | 0 | 1 | 349.11 | XNN | 417.216 | 413.414 | 398.901 | 143.26 | XNN | 5369.88 | XNN | 12.9 | XNN | 1040.24 | XNN | 36.63 | XNN | 84855.74 | XNN | 76829.06 | XNN | 0 | 0 | 1494 | 3600 | 1479.27 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 1479.27 | 1479.27 |  |  |  | 0 | 0 | [14 empty] | 31.5697
04.01.2008 13:00 | 0 | 1 | 297.88 | XNN | 250.183 | 229.875 | 237.729 | 2.92 | XNN | 1017.11 | XNN | 12.04 | XNN | 1033.07 | XNN | 17.2 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 506 | 3600 | 492.8 | GGB | 100 | XNN | 0.22 | XNN | 0.22 | XNN | 0 | UUU | 106337.57 | 492.8 | 492.8 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 14:00 | 0 | 1 | 243.69 | XNN | 193.773 | 217.875 | 184.249 | 2.92 | XNN | 1924.02 | XNN | 19.99 | XNN | 1032.95 | XNN | 6.39 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 65 | 3600 | 51.85 | GGB | 100 | XNN | 4.34 | XNN | 4.34 | XNN | 0 | UUU | 106337.57 | 51.85 | 51.85 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 15:00 | 0 | 1 | 216.1 | XNN | 107.326 | 114.82 | 109.157 | 41.53 | XNN | 1946.69 | XNN | 13.04 | XNN | 1032.81 | XNN | 29.62 | XNN | 11475.09 | XNN | 10554.33 | XNN | 0 | 0 | 154 | 3600 | 140.78 | GGB | 100 | XNN | 4.1 | XNN | 4.1 | XNN | 0 | UUU | 106337.57 | 140.78 | 140.78 |  |  |  | 0 | 0 | [14 empty] | 0.41273
04.01.2008 16:00 | 0 | 1 | 134.07 | XNN | 142.491 | 143.625 | 143.223 | 226.43 | XNN | 2046.44 | XNN | 2.12 | XNN | 1043.87 | XNN | 1.07 | XNN | 130982.01 | XNN | 134445.28 | XNN | 0 | 0 | 0 | 3600 | 0 | GGB | 100 | XNN | 6.85 | XNN | 6.85 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 17:00 | 0 | 1 | 145.59 | XNN | 143.59 | 144.703 | 144.322 | 231.89 | XNN | 2083.15 | XNN | 2.47 | XNN | 1044.11 | XNN | 0.46 | XNN | 142131.73 | XNN | 146251.45 | XNN | 0 | 0 | 0 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 18:00 | 0 | 1 | 146.14 | XNN | 143.956 | 144.703 | 144.322 | 233.51 | XNN | 2954.44 | XNN | 3.44 | XNN | 1044.24 | XNN | 1.97 | XNN | 142066.81 | XNN | 145400.31 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 19:00 | 0 | 1 | 145.2 | XNN | 142.491 | 143.695 | 143.223 | 229.72 | XNN | 7244.65 | XNN | 8.22 | XNN | 1043.88 | XNN | 3.6 | XNN | 137973.55 | XNN | 140331.57 | XNN | 0 | 0 | 0 | 3600 | 0 | GGB | 100 | XNN | 0.03 | XNN | 0.03 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 20:00 | 0 | 1 | 144.11 | XNN | 141.392 | 143.695 | 142.125 | 228.81 | XNN | 7287.16 | XNN | 8.24 | XNN | 1043.7 | XNN | 1.82 | XNN | 138461 | XNN | 141713.96 | XNN | 0 | 0 | 0 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0
04.01.2008 21:00 | 0 | 1 | 301.67 | XNN | 727.472 | 743.227 | 746.154 | 223.25 | XNN | 7607.86 | XNN | 8.54 | XNN | 1043.46 | XNN | 7.38 | XNN | 140617.66 | XNN | 141032.29 | XNN | 0 | 0 | 1008 | 3600 | 994.54 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106337.57 | 994.54 | 994.54 |  |  |  | 0 | 0 | [14 empty] | 38.9617
04.01.2008 22:00 | 3600 | 2 | 751.65 | GNB | 746.886 | 757.266 | 765.934 | 235.83 | GNB | 9247.71 | GGB | 9.68 | GGB | 1041.87 | GGB | 51.15 | GGB | 147073.34 | GGB | 127395.03 | GGB | 0 | 0 | 3774 | 3600 | 3498 | GKB | 100 | GGB | 19.73 | GGB | 19.73 | GGB | 106355.99 | GGB | 106357.3 | 3498 | 2966.5835 |  |  |  | 0 | 1 | [14 empty] | 123.7855 | 2966.5835 |  | 104.98
04.01.2008 23:00 | 3600 | 2 | 758.91 | GGB | 752.015 | 760.875 | 769.597 | 263.27 | GGB | 9912.66 | GGB | 9.77 | GGB | 1042.86 | GGB | 56.35 | GGB | 164542.31 | GGB | 140409.78 | GGB | 0 | 0 | 3444 | 3600 | 3427.57 | GNB | 100 | GGB | 43.82 | GGB | 43.82 | GGB | 106399.8 | GGB | 106401.12 | 3427.57 | 2691.6074 |  |  |  | 0 | 1 | [14 empty] | 133.6845 | 2691.6074 |  | 104.98
04.01.2008 24:00 | 3600 | 2 | 761.41 | GGB | 758.974 | 766.406 | 774.359 | 270.23 | GGB | 10202.8 | GGB | 9.82 | GGB | 1043.17 | GGB | 55.63 | GGB | 174646.71 | GGB | 149405.46 | GGB | 0 | 0 | 3186 | 3600 | 3170.67 | GGB | 100 | GGB | 28.41 | GGB | 28.41 | GGB | 106428.21 | GGB | 106429.53 | 3170.67 | 2529.5461 |  |  |  | 0 | 1 | [14 empty] | 131.5876 | 2529.5461 |  | 104.98
05.01.2008 01:00 | 3600 | 2 | 760.36 | GGB | 760.44 | 767.438 | 773.26 | 271.11 | GGB | 10263.4 | GGB | 9.83 | GGB | 1042.92 | GGB | 55.95 | GGB | 175740.44 | GGB | 150159.09 | GGB | 0 | 0 | 3080 | 3600 | 3063.92 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 106469.35 | GGB | 106470.67 | 3063.92 | 2516.8506 |  |  |  | 0 | 1 | [14 empty] | 127.7987 | 2516.8506 |  | 104.98
05.01.2008 02:00 | 3600 | 2 | 759.18 | GGB | 757.875 | 764.016 | 769.597 | 271.48 | GGB | 10260 | GGB | 9.83 | GGB | 1042.42 | GGB | 55.92 | GGB | 176000.12 | GGB | 150321.33 | GGB | 0 | 0 | 3020 | 3600 | 3004.54 | GGB | 100 | GGB | 42.23 | GGB | 42.23 | GGB | 106511.58 | GGB | 106512.9 | 3004.54 | 2514.1342 |  |  |  | 0 | 1 | [14 empty] | 125.4573 | 2514.1342 |  | 104.98
05.01.2008 03:00 | 0 | 1 | 423.89 | XNN | 252.015 | 241.102 | 246.886 | 55.95 | XNN | 3274.75 | XNN | 17.42 | XNN | 1031.03 | XNN | 86.65 | XNN | 37074.01 | XNN | 28642.78 | XNN | 0 | 0 | 869 | 3600 | 855.28 | GGB | 100 | XNN | 7.19 | XNN | 7.19 | XNN | 0 | UUU | 106512.9 | 855.28 | 855.28 |  |  |  | 0 | 0 | [14 empty] | 6.8049 |  |  | #VALUE!
05.01.2008 04:00 | 0 | 1 | 186.81 | XNN | 175.092 | 137.109 | 153.114 | 2.7 | XNN | 1907.69 | XNN | 19.99 | XNN | 1029.53 | XNN | 12.53 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 40 | 3600 | 26.47 | GGB | 100 | XNN | 27.28 | XNN | 27.28 | XNN | 0 | UUU | 106512.9 | 26.47 | 26.47 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 05:00 | 0 | 1 | 169.48 | XNN | 117.582 | 148.242 | 124.908 | 2.78 | XNN | 2381.18 | XNN | 19.99 | XNN | 1029.15 | XNN | 6.44 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 22 | 3600 | 9.14 | GGB | 100 | XNN | 6.96 | XNN | 6.96 | XNN | 0 | UUU | 106512.9 | 9.14 | 9.14 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 06:00 | 0 | 1 | 159.68 | XNN | 116.483 | 125.484 | 116.483 | 2.77 | XNN | 2744.94 | XNN | 19.99 | XNN | 1029.14 | XNN | 4.08 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 15 | 3600 | 1.68 | GGB | 100 | XNN | 6.95 | XNN | 6.95 | XNN | 0 | UUU | 106512.9 | 1.68 | 1.68 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 07:00 | 0 | 1 | 152.81 | XNN | 109.157 | 124.336 | 113.919 | 2.73 | XNN | 2718.77 | XNN | 19.99 | XNN | 1028.52 | XNN | 2.5 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 12 | 3600 | 0 | GGB | 100 | XNN | 4.87 | XNN | 4.87 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 08:00 | 0 | 1 | 143.08 | XNN | 100.366 | 112.359 | 115.018 | 2.71 | XNN | 2692.99 | XNN | 19.99 | XNN | 1028.24 | XNN | 2.03 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 10 | 3600 | 0 | GGB | 100 | XNN | 1.23 | XNN | 1.23 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 09:00 | 0 | 1 | 133.73 | XNN | 98.1685 | 106.852 | 112.82 | 2.73 | XNN | 2684.94 | XNN | 19.99 | XNN | 1027.96 | XNN | 1.57 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 8 | 3600 | 0 | GGB | 100 | XNN | 0.6 | XNN | 0.6 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 10:00 | 0 | 1 | 131.26 | XNN | 93.0403 | 102.516 | 111.355 | 2.76 | XNN | 2668.6 | XNN | 19.99 | XNN | 1027.76 | XNN | 1.65 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 7 | 3600 | 0 | GGB | 100 | XNN | 1.68 | XNN | 1.68 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 11:00 | 0 | 1 | 129.74 | XNN | 105.128 | 108.117 | 115.018 | 2.81 | XNN | 2678.91 | XNN | 19.99 | XNN | 1027.14 | XNN | 2.16 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 6 | 3600 | 0 | GGB | 100 | XNN | 1.55 | XNN | 1.55 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 12:00 | 0 | 1 | 130.3 | XNN | 134.432 | 111.117 | 135.897 | 2.89 | XNN | 2715.11 | XNN | 19.99 | XNN | 1025.91 | XNN | 1.9 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 7 | 3600 | 0 | GGB | 100 | XNN | 0.54 | XNN | 0.54 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 13:00 | 0 | 1 | 137.13 | XNN | 138.095 | 125.297 | 138.462 | 3.13 | XNN | 2758.11 | XNN | 19.99 | XNN | 1024.58 | XNN | 3.33 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 6 | 3600 | 0 | GGB | 100 | XNN | 0.9 | XNN | 0.9 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 14:00 | 0 | 1 | 146.05 | XNN | 138.095 | 129.516 | 136.996 | 2.94 | XNN | 2789.15 | XNN | 19.99 | XNN | 1023.52 | XNN | 3.68 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 6 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 15:00 | 0 | 1 | 146.42 | XNN | 152.747 | 133.734 | 149.084 | 2.93 | XNN | 2826.53 | XNN | 19.99 | XNN | 1022.6 | XNN | 2.62 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 16:00 | 0 | 1 | 148.84 | XNN | 162.637 | 146.391 | 160.806 | 2.93 | XNN | 2868.04 | XNN | 19.99 | XNN | 1021.61 | XNN | 2.99 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 17:00 | 0 | 1 | 149.8 | XNN | 168.864 | 157.992 | 167.033 | 2.92 | XNN | 2890.71 | XNN | 19.99 | XNN | 1020.82 | XNN | 1.47 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 18:00 | 0 | 1 | 149.81 | XNN | 168.864 | 165.211 | 167.033 | 2.92 | XNN | 2912.86 | XNN | 19.99 | XNN | 1020.06 | XNN | 0.14 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 5 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 19:00 | 0 | 1 | 149.17 | XNN | 162.637 | 161.039 | 158.608 | 2.86 | XNN | 2923.19 | XNN | 19.99 | XNN | 1019.54 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 20:00 | 0 | 1 | 151.94 | XNN | 165.201 | 163.031 | 136.63 | 2.73 | XNN | 2916.64 | XNN | 19.99 | XNN | 1019.17 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 21:00 | 0 | 1 | 157.31 | XNN | 173.626 | 171.727 | 130.403 | 2.71 | XNN | 2905.76 | XNN | 19.99 | XNN | 1018.78 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 4 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 22:00 | 0 | 1 | 186.38 | XNN | 215.018 | 213.961 | 167.033 | 2.81 | XNN | 2892.21 | XNN | 19.99 | XNN | 1017.9 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 3 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 23:00 | 0 | 1 | 224.75 | XNN | 242.125 | 238.711 | 181.685 | 2.89 | XNN | 2906.43 | XNN | 19.99 | XNN | 1016.75 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
05.01.2008 24:00 | 0 | 1 | 245.95 | XNN | 256.777 | 253.477 | 196.703 | 2.92 | XNN | 2885.64 | XNN | 19.99 | XNN | 1016.05 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 01:00 | 0 | 1 | 259.17 | XNN | 255.678 | 249.305 | 176.19 | 2.93 | XNN | 2870.12 | XNN | 19.99 | XNN | 1015.22 | XNN | 0.06 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 02:00 | 0 | 1 | 270.39 | XNN | 232.234 | 213.773 | 172.527 | 2.94 | XNN | 2874.27 | XNN | 19.99 | XNN | 1014.14 | XNN | 0.12 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 03:00 | 0 | 1 | 272.2 | XNN | 199.267 | 192.398 | 175.092 | 2.96 | XNN | 2880.39 | XNN | 19.99 | XNN | 1013.12 | XNN | 0.82 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 04:00 | 0 | 1 | 271.83 | XNN | 195.604 | 181.664 | 179.853 | 2.98 | XNN | 2872.11 | XNN | 19.99 | XNN | 1012.31 | XNN | 1.82 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 4.01 | XNN | 4.01 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 05:00 | 0 | 1 | 271.83 | XNN | 202.93 | 196.078 | 202.564 | 3.48 | XNN | 2873.62 | XNN | 19.98 | XNN | 1011.45 | XNN | 2.08 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0 | XNN | 0 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 06:00 | 0 | 1 | 258.7 | XNN | 113.919 | 133.102 | 136.264 | 14.37 | XNN | 2878.17 | XNN | 18.51 | XNN | 1010.21 | XNN | 31.12 | XNN | 0 | XNN | 0 | XNN | 0 | 0 | 2 | 3600 | 0 | GGB | 100 | XNN | 0.44 | XNN | 0.44 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 07:00 | 0 | 1 | 139.61 | XNN | 106.593 | 107.484 | 104.762 | 92.84 | XNN | 2990.27 | XNN | 7.36 | XNN | 1013.09 | XNN | 39.41 | XNN | 38896.94 | XNN | 33992.97 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 5.52 | XNN | 5.52 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 08:00 | 0 | 1 | 136.45 | XNN | 141.758 | 143.578 | 142.491 | 209.18 | XNN | 5811.12 | XNN | 6.76 | XNN | 1021.48 | XNN | 0.08 | XNN | 128535.95 | XNN | 129574.73 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 6.9 | XNN | 6.9 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 09:00 | 0 | 1 | 146.2 | XNN | 145.421 | 146.836 | 145.055 | 217.46 | XNN | 7373.83 | XNN | 8.59 | XNN | 1021.02 | XNN | 0.3 | XNN | 131582.79 | XNN | 132476.76 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 5.29 | XNN | 5.29 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 10:00 | 0 | 1 | 148.78 | XNN | 147.985 | 148.992 | 148.718 | 225.32 | XNN | 7445.97 | XNN | 8.51 | XNN | 1020.94 | XNN | 0.69 | XNN | 139461.21 | XNN | 140198.27 | XNN | 0 | 0 | 1 | 3600 | 0 | GGB | 100 | XNN | 5.38 | XNN | 5.38 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 11:00 | 0 | 1 | 150.26 | XNN | 147.985 | 148.992 | 148.718 | 226.67 | XNN | 7596.34 | XNN | 8.65 | XNN | 1020.45 | XNN | 1.74 | XNN | 142220.86 | XNN | 142361.31 | XNN | 0 | 0 | 0 | 3600 | 0 | GGB | 100 | XNN | 5.39 | XNN | 5.39 | XNN | 0 | UUU | 106512.9 | 0 | 0 |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | #VALUE!
06.01.2008 12:00 | 0 | 1 | 171.39 | XNN | 465.568 | 534.352 | 400 | 226.38 | XNN | 7701.66 | XNN | 8.79 | XNN | 1020.05 | XNN | 2.5 | XNN | 142365 | XNN | 142058.13 | XNN | 0 | 0 | 21 | 3600 | 8.33 | GGB | 100 | XNN | 6.04 | XNN | 6.04 | XNN | 0 | UUU | 106512.9 | 8.33 | 8.33 |  |  |  | 0 | 0 | [14 empty] | 0.32871 |  |  | #VALUE!
06.01.2008 13:00 | 3600 | 2 | 725.16 | GNB | 753.113 | 756.539 | 755.311 | 231.58 | GNB | 8840.43 | GGB | 9.68 | GGB | 1016.64 | GGB | 49.12 | GGB | 129705.61 | GGB | 110322.7 | GGB | 0 | 0 | 2855 | 3600 | 2839.27 | GGB | 100 | GGB | 5.92 | GGB | 5.92 | GGB | 106517.5 | GGB | 106518.82 | 2839.27 | 2839.27 |  |  |  | 0 | 1 | [14 empty] | 87.01 |  |  | #VALUE!
06.01.2008 14:00 | 3600 | 2 | 752.94 | GNB | 766.3 | 769.523 | 767.766 | 263.13 | GGB | 9872.4 | GGB | 9.78 | GGB | 1017.83 | GGB | 57.02 | GGB | 158025.01 | GGB | 131343.04 | GGB | 0 | 0 | 2708 | 3600 | 2692.65 | GGB | 100 | GGB | 3.03 | GGB | 3.03 | GGB | 106520.53 | GGB | 106521.85 | 2692.65 | 2692.65 |  |  |  | 0 | 1 | [14 empty] | 98.2391 |  |  | #VALUE!
06.01.2008 15:00 | 3600 | 2 | 759.72 | GGB | 766.667 | 770.953 | 768.864 | 263.22 | GGB | 10288.5 | GGB | 9.86 | GGB | 1017.27 | GGB | 59.72 | GGB | 158466.24 | GGB | 130572 | GGB | 0 | 0 | 2646 | 3600 | 2630.69 | GGB | 100 | GGB | 20.24 | GGB | 20.24 | GGB | 106540.77 | GGB | 106542.09 | 2630.69 | 2630.69 |  |  |  | 1 | 1 |  |  |  |  | 130572 | 2630.69 | 130572 | 2630.69 | 16.9711 | [5 empty] | 95.4151 |  |  | #VALUE!
06.01.2008 16:00 | 3600 | 2 | 759.52 | GGB | 764.102 | 767.648 | 766.3 | 262.71 | GGB | 10345.4 | GGB | 9.83 | GGB | 1017.18 | GGB | 60.85 | GGB | 158952.59 | GGB | 130515.95 | GGB | 0 | 0 | 2709 | 3600 | 2693.97 | GGB | 100 | GGB | 37.31 | GGB | 37.31 | GGB | 106578.08 | GGB | 106579.4 | 2693.97 | 2693.97 |  |  |  | 1 | 1 |  |  |  |  | 130515.95 | 2693.97 | 130515.95 | 2693.97 | 9.4239 | [5 empty] | 97.6683 |  |  | #VALUE!
06.01.2008 17:00 | 3600 | 2 | 759.92 | GGB | 765.201 | 768.797 | 766.667 | 261.38 | GGB | 10367.4 | GGB | 9.83 | GGB | 1016.86 | GGB | 61.39 | GGB | 157704.81 | GGB | 129241.52 | GGB | 0 | 0 | 2739 | 3600 | 2723.62 | GGB | 100 | GGB | 43.73 | GGB | 43.73 | GGB | 106621.81 | GGB | 106623.13 | 2723.62 | 2723.62 |  |  |  | 1 | 1 |  |  |  |  | 129241.52 | 2723.62 | 129241.52 | 2723.62 | 8.0495 | [5 empty] | 97.7791 |  |  | #VALUE!
06.01.2008 18:00 | 3600 | 2 | 759.44 | GGB | 766.3 | 769.898 | 767.766 | 259.34 | GGB | 10355.3 | GGB | 9.83 | GGB | 1016.06 | GGB | 61.76 | GGB | 155962.97 | GGB | 127572.33 | GGB | 0 | 0 | 2764 | 3600 | 2748.75 | GGB | 100 | GGB | 46.68 | GGB | 46.68 | GGB | 106668.48 | GGB | 106669.81 | 2748.75 | 2748.75 |  |  |  | 1 | 1 |  |  |  |  | 127572.33 | 2748.75 | 127572.33 | 2748.75 | 7.5121 | [5 empty] | 97.4068 |  |  | #VALUE!
06.01.2008 19:00 | 3600 | 2 | 760.23 | GGB | 764.102 | 768.82 | 767.033 | 259.73 | GGB | 10315.7 | GGB | 9.83 | GGB | 1015.56 | GGB | 60.64 | GGB | 157314.19 | GGB | 129047.03 | GGB | 0 | 0 | 2695 | 3600 | 2679.42 | GGB | 100 | GGB | 42.26 | GGB | 42.26 | GGB | 106710.75 | GGB | 106712.07 | 2679.42 | 2679.42 |  |  |  | 1 | 1 |  |  |  |  | 129047.03 | 2679.42 | 129047.03 | 2679.42 | 8.182 | [5 empty] | 96.0476 |  |  | #VALUE!
06.01.2008 20:00 | 3600 | 2 | 760.17 | GGB | 763.004 | 766.688 | 764.835 | 259.34 | GGB | 10311.9 | GGB | 9.82 | GGB | 1015.27 | GGB | 60.35 | GGB | 157154.64 | GGB | 128993.38 | GGB | 0 | 0 | 2683 | 3600 | 2667.96 | GGB | 100 | GGB | 43.18 | GGB | 43.18 | GGB | 106753.93 | GGB | 106755.25 | 2667.96 | 2667.96 |  |  |  | 0 | 1 | [14 empty] | 95.597 |  |  | #VALUE!
06.01.2008 21:00 | 3600 | 2 | 760.34 | GGB | 765.201 | 768.867 | 767.033 | 257.86 | GGB | 10359.3 | GGB | 9.84 | GGB | 1014.63 | GGB | 60.55 | GGB | 156316.18 | GGB | 128145.35 | GGB | 0 | 0 | 2663 | 3600 | 2647.2 | GGB | 100 | GGB | 36.85 | GGB | 36.85 | GGB | 106790.78 | GGB | 106792.1 | 2647.2 | 2647.2 |  |  |  | 1 | 1 |  |  |  |  | 128145.35 | 2647.2 | 128145.35 | 2647.2 | 9.2056 | [5 empty] | 94.2295 |  |  | #VALUE!
06.01.2008 22:00 | 3600 | 2 | 760.15 | GGB | 764.102 | 768.867 | 767.033 | 256.43 | GGB | 10332.9 | GGB | 9.82 | GGB | 1014.4 | GGB | 61.02 | GGB | 155622.97 | GGB | 127369.33 | GGB | 0 | 0 | 2660 | 3600 | 2644.2 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 106827.74 | GGB | 106829.06 | 2644.2 | 2644.2 |  |  |  | 1 | 1 |  |  |  |  | 127369.33 | 2644.2 | 127369.33 | 2644.2 | 9.1123 | [5 empty] | 93.5528 |  |  | #VALUE!
06.01.2008 23:00 | 3600 | 2 | 760.63 | GGB | 764.102 | 767.859 | 765.934 | 257.09 | GGB | 10331 | GGB | 9.83 | GGB | 1014.73 | GGB | 60.32 | GGB | 157544.16 | GGB | 129254.25 | GGB | 0 | 0 | 2631 | 3600 | 2615.33 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 106865.87 | GGB | 106867.19 | 2615.33 | 2615.33 |  |  |  | 1 | 1 |  |  |  |  | 129254.25 | 2615.33 | 129254.25 | 2615.33 | 8.8655 | [5 empty] | 93.9007 |  |  | #VALUE!
06.01.2008 24:00 | 3600 | 2 | 760.38 | GGB | 765.201 | 768.867 | 767.033 | 257.24 | GGB | 10312.8 | GGB | 9.82 | GGB | 1014.39 | GGB | 60.63 | GGB | 157291.08 | GGB | 128883.03 | GGB | 0 | 0 | 2627 | 3600 | 2612.09 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 106905.42 | GGB | 106906.74 | 2612.09 | 2612.09 |  |  |  | 1 | 1 |  |  |  |  | 128883.03 | 2612.09 | 128883.03 | 2612.09 | 8.5121 | [5 empty] | 93.515 |  |  | #VALUE!
07.01.2008 01:00 | 3600 | 2 | 760.57 | GGB | 763.004 | 767.602 | 765.934 | 256.16 | GGB | 10334.4 | GGB | 9.83 | GGB | 1014.14 | GGB | 61.35 | GGB | 155490.93 | GGB | 127101.53 | GGB | 0 | 0 | 2626 | 3600 | 2611.06 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 106944.7 | GGB | 106946.02 | 2611.06 | 2611.06 |  |  |  | 0 | 1 | [14 empty] | 92.186 |  |  | #VALUE!
07.01.2008 02:00 | 3600 | 2 | 760.2 | GGB | 764.102 | 767.578 | 765.934 | 255.39 | GGB | 10318 | GGB | 9.82 | GGB | 1014.05 | GGB | 61.8 | GGB | 154770.21 | GGB | 126332.26 | GGB | 0 | 0 | 2646 | 3600 | 2630.82 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 106983.89 | GGB | 106985.22 | 2630.82 | 2630.82 |  |  |  | 1 | 1 |  |  |  |  | 126332.26 | 2630.82 | 126332.26 | 2630.82 | 8.4785 | [5 empty] | 92.3215 |  |  | #VALUE!
07.01.2008 03:00 | 3600 | 2 | 760.2 | GGB | 765.201 | 768.609 | 767.033 | 256.83 | GGB | 10293.7 | GGB | 9.82 | GGB | 1014.43 | GGB | 61.44 | GGB | 155907.96 | GGB | 127444.98 | GGB | 0 | 0 | 2643 | 3600 | 2627.93 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 107023.58 | GGB | 107024.9 | 2627.93 | 2627.93 |  |  |  | 1 | 1 |  |  |  |  | 127444.98 | 2627.93 | 127444.98 | 2627.93 | 8.4404 | [5 empty] | 93.0324 |  |  | #VALUE!
07.01.2008 04:00 | 3600 | 2 | 760.74 | GGB | 764.102 | 768.68 | 767.033 | 257.84 | GGB | 10297.9 | GGB | 9.83 | GGB | 1014.57 | GGB | 61.05 | GGB | 156772.82 | GGB | 128320.26 | GGB | 0 | 0 | 2623 | 3600 | 2607.42 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 107063.56 | GGB | 107064.88 | 2607.42 | 2607.42 |  |  |  | 1 | 1 |  |  |  |  | 128320.26 | 2607.42 | 128320.26 | 2607.42 | 8.3688 | [5 empty] | 92.9402 |  |  | #VALUE!
07.01.2008 05:00 | 3600 | 2 | 760.67 | GGB | 764.102 | 767.625 | 765.934 | 257.2 | GGB | 10306.4 | GGB | 9.83 | GGB | 1014.62 | GGB | 61.2 | GGB | 156328.29 | GGB | 127903.82 | GGB | 0 | 0 | 2614 | 3600 | 2598.96 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 107103.6 | GGB | 107104.92 | 2598.96 | 2598.96 |  |  |  | 1 | 1 |  |  |  |  | 127903.82 | 2598.96 | 127903.82 | 2598.96 | 8.3021 | [5 empty] | 92.338 |  |  | #VALUE!
07.01.2008 06:00 | 3600 | 2 | 760.02 | GGB | 764.102 | 767.648 | 765.934 | 256.53 | GGB | 10347.4 | GGB | 9.83 | GGB | 1014.85 | GGB | 61.79 | GGB | 155234.55 | GGB | 126814.96 | GGB | 0 | 0 | 2646 | 3600 | 2630.6 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 107142.61 | GGB | 107143.93 | 2630.6 | 2630.6 |  |  |  | 1 | 1 |  |  |  |  | 126814.96 | 2630.6 | 126814.96 | 2630.6 | 8.5516 | [5 empty] | 92.6665 |  |  | #VALUE!
07.01.2008 07:00 | 3600 | 2 | 759.86 | GGB | 763.004 | 767.625 | 765.934 | 257.8 | GGB | 10325.3 | GGB | 9.82 | GGB | 1014.89 | GGB | 61.41 | GGB | 156791.53 | GGB | 128236.86 | GGB | 0 | 0 | 2648 | 3600 | 2632.56 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 107183.56 | GGB | 107184.89 | 2632.56 | 2632.56 |  |  |  | 0 | 1 | [14 empty] | 93.7753 |  |  | #VALUE!
07.01.2008 08:00 | 3600 | 2 | 760.3 | GGB | 765.201 | 768.914 | 767.033 | 258.12 | GGB | 10358.7 | GGB | 9.83 | GGB | 1015.2 | GGB | 61.24 | GGB | 157168.94 | GGB | 128651.45 | GGB | 0 | 0 | 2649 | 3600 | 2633.85 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 107222.15 | GGB | 107223.47 | 2633.85 | 2633.85 |  |  |  | 1 | 1 |  |  |  |  | 128651.45 | 2633.85 | 128651.45 | 2633.85 | 8.783 | [5 empty] | 94.1246 |  |  | #VALUE!
07.01.2008 09:00 | 3600 | 2 | 760.27 | GGB | 765.201 | 768.914 | 767.033 | 257.47 | GGB | 10364.3 | GGB | 9.83 | GGB | 1015.36 | GGB | 61.03 | GGB | 156806.93 | GGB | 128455.76 | GGB | 0 | 0 | 2635 | 3600 | 2619.98 | GGB | 100 | GGB | 37.8 | GGB | 37.8 | GGB | 107259.95 | GGB | 107261.27 | 2619.98 | 2619.98 |  |  |  | 1 | 1 |  |  |  |  | 128455.76 | 2619.98 | 128455.76 | 2619.98 | 8.9035 | [5 empty] | 93.4865 |  |  | #VALUE!
07.01.2008 10:00 | 3600 | 2 | 760.16 | GGB | 765.201 | 768.891 | 767.033 | 256.21 | GGB | 10385.7 | GGB | 9.83 | GGB | 1015.5 | GGB | 61.9 | GGB | 154990.27 | GGB | 126654.38 | GGB | 0 | 0 | 2651 | 3600 | 2635.22 | GGB | 100 | GGB | 38.15 | GGB | 38.15 | GGB | 107298.1 | GGB | 107299.42 | 2635.22 | 2635.22 |  |  |  | 1 | 1 |  |  |  |  | 126654.38 | 2635.22 | 126654.38 | 2635.22 | 8.7487 | [5 empty] | 92.7117 |  |  | #VALUE!
07.01.2008 11:00 | 3600 | 2 | 760.16 | GGB | 764.102 | 768.867 | 767.033 | 255.93 | GGB | 10377.4 | GGB | 9.83 | GGB | 1015.3 | GGB | 62.08 | GGB | 154762.5 | GGB | 126377.35 | GGB | 0 | 0 | 2657 | 3600 | 2641.88 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 107336.92 | GGB | 107338.24 | 2641.88 | 2641.88 |  |  |  | 1 | 1 |  |  |  |  | 126377.35 | 2641.88 | 126377.35 | 2641.88 | 8.6006 | [5 empty] | 92.7427 |  |  | #VALUE!
07.01.2008 12:00 | 3600 | 2 | 759.83 | GGB | 765.201 | 768.938 | 768.132 | 255.85 | GGB | 10375.3 | GGB | 9.82 | GGB | 1015.13 | GGB | 62 | GGB | 154769.11 | GGB | 126390.93 | GGB | 0 | 0 | 2673 | 3600 | 2657.46 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 107375.54 | GGB | 107376.87 | 2657.46 | 2657.46 |  |  |  | 1 | 1 |  |  |  |  | 126390.93 | 2657.46 | 126390.93 | 2657.46 | 8.6948 | [5 empty] | 93.2997 |  |  | #VALUE!
07.01.2008 13:00 | 3600 | 2 | 760.32 | GGB | 765.201 | 768.914 | 767.033 | 256.61 | GGB | 10366.3 | GGB | 9.83 | GGB | 1015.21 | GGB | 61.73 | GGB | 155589.96 | GGB | 127175.15 | GGB | 0 | 0 | 2644 | 3600 | 2628.48 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 107413.7 | GGB | 107415.03 | 2628.48 | 2628.48 |  |  |  | 1 | 1 |  |  |  |  | 127175.15 | 2628.48 | 127175.15 | 2628.48 | 8.7599 | [5 empty] | 92.8548 |  |  | #VALUE!
07.01.2008 14:00 | 3600 | 2 | 757.13 | GGB | 765.201 | 768.891 | 767.766 | 262.21 | GGB | 10418.7 | GGB | 9.77 | GGB | 1015.52 | GGB | 60.3 | GGB | 160669.12 | GGB | 131929.47 | GGB | 0 | 0 | 2809 | 3600 | 2793.62 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 107452.78 | GGB | 107454.1 | 2793.62 | 2793.62 |  |  |  | 1 | 1 |  |  |  |  | 131929.47 | 2793.62 | 131929.47 | 2793.62 | 9.4333 | [5 empty] | 102.378 |  |  | #VALUE!
07.01.2008 15:00 | 3600 | 2 | 758.58 | GGB | 766.3 | 770.203 | 768.864 | 269.16 | GGB | 10770.9 | GGB | 9.8 | GGB | 1015.97 | GGB | 58.73 | GGB | 169739.2 | GGB | 140098.99 | GGB | 0 | 0 | 2825 | 3600 | 2809.78 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 107491.5 | GGB | 107492.83 | 2809.78 | 2697.5783 |  |  |  | 1 | 1 |  |  |  |  | 140098.99 | 2697.5783 | 140098.99 | 2697.5783 | 9.758 | [5 empty] | 109.3465 | 2697.5783 |  | 104.98
07.01.2008 16:00 | 3600 | 2 | 760.09 | GGB | 765.201 | 769.148 | 767.766 | 269.68 | GGB | 10821.2 | GGB | 9.82 | GGB | 1015.79 | GGB | 58.74 | GGB | 170578.76 | GGB | 140761.74 | GGB | 0 | 0 | 2755 | 3600 | 2739.8 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 107532.45 | GGB | 107533.78 | 2739.8 | 2684.8773 |  |  |  | 1 | 1 |  |  |  |  | 140761.74 | 2684.8773 | 140761.74 | 2684.8773 | 9.229 | [5 empty] | 107.1275 | 2684.8773 |  | 104.98
07.01.2008 17:00 | 3600 | 2 | 760.13 | GGB | 766.3 | 770.18 | 768.864 | 269.77 | GGB | 10823.3 | GGB | 9.83 | GGB | 1015.99 | GGB | 58.79 | GGB | 170608.47 | GGB | 140791.18 | GGB | 0 | 0 | 2752 | 3600 | 2736.95 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 107571.24 | GGB | 107572.57 | 2736.95 | 2684.3159 |  |  |  | 1 | 1 |  |  |  |  | 140791.18 | 2684.3159 | 140791.18 | 2684.3159 | 9.7429 | [5 empty] | 107.0385 | 2684.3159 |  | 104.98
07.01.2008 18:00 | 3600 | 2 | 760.16 | GGB | 766.3 | 769.875 | 769.597 | 269.61 | GGB | 10839 | GGB | 9.83 | GGB | 1016.33 | GGB | 59.02 | GGB | 170165.03 | GGB | 140377.13 | GGB | 0 | 0 | 2754 | 3600 | 2738.58 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 107611.53 | GGB | 107612.86 | 2738.58 | 2692.2334 |  |  |  | 1 | 1 |  |  |  |  | 140377.13 | 2692.2334 | 140377.13 | 2692.2334 | 9.3802 | [5 empty] | 106.7872 | 2692.2334 |  | 104.98
07.01.2008 19:00 | 3600 | 2 | 760.02 | GGB | 765.201 | 768.867 | 768.132 | 268.58 | GGB | 10870.3 | GGB | 9.82 | GGB | 1016.29 | GGB | 59.55 | GGB | 168729.09 | GGB | 138963.02 | GGB | 0 | 0 | 2782 | 3600 | 2766.61 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 107651.3 | GGB | 107652.63 | 2766.61 | 2719.63 |  |  |  | 1 | 1 |  |  |  |  | 138963.02 | 2719.63 | 138963.02 | 2719.63 | 9.5028 | [5 empty] | 106.7935 | 2719.63 |  | 104.98
07.01.2008 20:00 | 3600 | 2 | 759.75 | GGB | 765.201 | 769.969 | 768.498 | 269.61 | GGB | 10847.1 | GGB | 9.82 | GGB | 1016.35 | GGB | 58.82 | GGB | 170608.47 | GGB | 140830.98 | GGB | 0 | 0 | 2779 | 3600 | 2763.44 | GGB | 100 | GGB | 42.65 | GGB | 42.65 | GGB | 107693.95 | GGB | 107695.28 | 2763.44 | 2683.5573 |  |  |  | 1 | 1 |  |  |  |  | 140830.98 | 2683.5573 | 140830.98 | 2683.5573 | 8.8611 | [5 empty] | 108.105 | 2683.5573 |  | 104.98
07.01.2008 21:00 | 3600 | 2 | 759.91 | GGB | 765.201 | 768.938 | 768.132 | 269.87 | GGB | 10829.1 | GGB | 9.82 | GGB | 1016.06 | GGB | 58.7 | GGB | 170591.96 | GGB | 140826.75 | GGB | 0 | 0 | 2772 | 3600 | 2756.36 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 107733.39 | GGB | 107734.72 | 2756.36 | 2683.6379 |  |  |  | 1 | 1 |  |  |  |  | 140826.75 | 2683.6379 | 140826.75 | 2683.6379 | 9.5824 | [5 empty] | 107.8248 | 2683.6379 |  | 104.98
07.01.2008 22:00 | 3600 | 2 | 760.22 | GGB | 765.201 | 768.938 | 767.033 | 268.75 | GGB | 10861.5 | GGB | 9.84 | GGB | 1015.69 | GGB | 58.99 | GGB | 169318.87 | GGB | 139602.11 | GGB | 0 | 0 | 2755 | 3600 | 2739.74 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 107774.54 | GGB | 107775.87 | 2739.74 | 2707.1797 |  |  |  | 1 | 1 |  |  |  |  | 139602.11 | 2707.1797 | 139602.11 | 2707.1797 | 9.1842 | [5 empty] | 106.2426 | 2707.1797 |  | 104.98
07.01.2008 23:00 | 3600 | 2 | 759.56 | GGB | 764.102 | 768.938 | 767.033 | 268.42 | GGB | 10839.2 | GGB | 9.82 | GGB | 1015.81 | GGB | 59.18 | GGB | 168847.93 | GGB | 139151.59 | GGB | 0 | 0 | 2787 | 3600 | 2771.44 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 107814.09 | GGB | 107815.41 | 2771.44 | 2715.9445 |  |  |  | 1 | 1 |  |  |  |  | 139151.59 | 2715.9445 | 139151.59 | 2715.9445 | 9.5581 | [5 empty] | 107.1251 | 2715.9445 |  | 104.98
07.01.2008 24:00 | 3600 | 2 | 760.14 | GGB | 766.3 | 768.867 | 768.132 | 269.27 | GGB | 10826.4 | GGB | 9.82 | GGB | 1016.07 | GGB | 58.63 | GGB | 170226.65 | GGB | 140556.47 | GGB | 0 | 0 | 2754 | 3600 | 2738.66 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 107854.7 | GGB | 107856.03 | 2738.66 | 2688.7983 |  |  |  | 1 | 1 |  |  |  |  | 140556.47 | 2688.7983 | 140556.47 | 2688.7983 | 9.304 | [5 empty] | 106.9268 | 2688.7983 |  | 104.98
08.01.2008 01:00 | 3600 | 2 | 760.12 | GGB | 767.766 | 771.094 | 769.597 | 268.57 | GGB | 10847.2 | GGB | 9.83 | GGB | 1015.45 | GGB | 58.61 | GGB | 169647.87 | GGB | 140002.86 | GGB | 0 | 0 | 2738 | 3600 | 2722.49 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 107895.3 | GGB | 107896.63 | 2722.49 | 2699.4306 |  |  |  | 1 | 1 |  |  |  |  | 140002.86 | 2699.4306 | 140002.86 | 2699.4306 | 9.3086 | [5 empty] | 105.8768 | 2699.4306 |  | 104.98
08.01.2008 02:00 | 3600 | 2 | 760.08 | GGB | 763.004 | 767.648 | 767.033 | 267.56 | GGB | 10844.6 | GGB | 9.82 | GGB | 1015.24 | GGB | 59.18 | GGB | 168010.57 | GGB | 138385.12 | GGB | 0 | 0 | 2766 | 3600 | 2750.82 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 107935.78 | GGB | 107937.1 | 2750.82 | 2730.9873 |  |  |  | 0 | 1 | [14 empty] | 105.7424 | 2730.9873 |  | 104.98
08.01.2008 03:00 | 3600 | 2 | 760.32 | GGB | 765.201 | 768.727 | 767.033 | 268.84 | GGB | 10806.3 | GGB | 9.82 | GGB | 1015.24 | GGB | 58.56 | GGB | 169535.64 | GGB | 139902.7 | GGB | 0 | 0 | 2744 | 3600 | 2729.01 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 107975.05 | GGB | 107976.37 | 2729.01 | 2701.3632 |  |  |  | 1 | 1 |  |  |  |  | 139902.7 | 2701.3632 | 139902.7 | 2701.3632 | 9.6238 | [5 empty] | 106.0544 | 2701.3632 |  | 104.98
08.01.2008 04:00 | 3600 | 2 | 760.42 | GGB | 764.102 | 767.859 | 767.033 | 268.69 | GGB | 10803.2 | GGB | 9.82 | GGB | 1014.86 | GGB | 58.59 | GGB | 169192.33 | GGB | 139554.6 | GGB | 0 | 0 | 2733 | 3600 | 2717.73 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 108015.43 | GGB | 108016.75 | 2717.73 | 2708.1013 |  |  |  | 1 | 1 |  |  |  |  | 139554.6 | 2708.1013 | 139554.6 | 2708.1013 | 9.3593 | [5 empty] | 105.3533 | 2708.1013 |  | 104.98
08.01.2008 05:00 | 3600 | 2 | 760.64 | GGB | 764.102 | 767.836 | 767.033 | 267.01 | GGB | 10852.2 | GGB | 9.83 | GGB | 1014.09 | GGB | 59.13 | GGB | 167459.3 | GGB | 137795.57 | GGB | 0 | 0 | 2741 | 3600 | 2725.49 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 108054.85 | GGB | 108056.17 | 2725.49 | 2725.49 |  |  |  | 1 | 1 |  |  |  |  | 137795.57 | 2725.49 | 137795.57 | 2725.49 | 9.5272 | [5 empty] | 104.3223 |  |  | #VALUE!
08.01.2008 06:00 | 3600 | 2 | 760.39 | GGB | 765.201 | 768.938 | 768.132 | 268.23 | GGB | 10810.1 | GGB | 9.82 | GGB | 1014.35 | GGB | 58.57 | GGB | 169414.6 | GGB | 139673.61 | GGB | 0 | 0 | 2738 | 3600 | 2722.2 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 108095.21 | GGB | 108096.53 | 2722.2 | 2705.7939 |  |  |  | 1 | 1 |  |  |  |  | 139673.61 | 2705.7939 | 139673.61 | 2705.7939 | 9.3639 | [5 empty] | 105.6165 | 2705.7939 |  | 104.98
08.01.2008 07:00 | 3600 | 2 | 760.57 | GGB | 765.201 | 768.891 | 768.132 | 267.88 | GGB | 10801.1 | GGB | 9.83 | GGB | 1014.07 | GGB | 58.49 | GGB | 169226.44 | GGB | 139515.99 | GGB | 0 | 0 | 2722 | 3600 | 2706.77 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 108136 | GGB | 108137.31 | 2706.77 | 2706.77 |  |  |  | 1 | 1 |  |  |  |  | 139515.99 | 2706.77 | 139515.99 | 2706.77 | 9.2604 | [5 empty] | 104.8994 |  |  | #VALUE!
08.01.2008 08:00 | 3600 | 2 | 760.74 | GGB | 764.102 | 767.883 | 767.033 | 266.39 | GGB | 10825.7 | GGB | 9.83 | GGB | 1013.71 | GGB | 59.05 | GGB | 167362.47 | GGB | 137698.66 | GGB | 0 | 0 | 2723 | 3600 | 2707.95 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 108175.58 | GGB | 108176.89 | 2707.95 | 2707.95 |  |  |  | 1 | 1 |  |  |  |  | 137698.66 | 2707.95 | 137698.66 | 2707.95 | 9.4209 | [5 empty] | 103.5781 |  |  | #VALUE!
08.01.2008 09:00 | 3600 | 2 | 759.9 | GGB | 764.102 | 767.883 | 768.132 | 267.21 | GGB | 10793.4 | GGB | 9.81 | GGB | 1013.82 | GGB | 58.73 | GGB | 168173.42 | GGB | 138511.99 | GGB | 0 | 0 | 2761 | 3600 | 2745.97 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 108215.76 | GGB | 108217.07 | 2745.97 | 2728.4858 |  |  |  | 1 | 1 |  |  |  |  | 138511.99 | 2728.4858 | 138511.99 | 2728.4858 | 9.4059 | [5 empty] | 105.6527 | 2728.4858 |  | 104.98
08.01.2008 10:00 | 3600 | 2 | 760.57 | GGB | 764.102 | 767.813 | 766.667 | 267.77 | GGB | 10805.6 | GGB | 9.83 | GGB | 1014.2 | GGB | 58.29 | GGB | 169143.92 | GGB | 139548.12 | GGB | 0 | 0 | 2722 | 3600 | 2706.43 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 108254.79 | GGB | 108256.1 | 2706.43 | 2706.43 |  |  |  | 1 | 1 |  |  |  |  | 139548.12 | 2706.43 | 139548.12 | 2706.43 | 9.6766 | [5 empty] | 104.9103 |  |  | #VALUE!
08.01.2008 11:00 | 3600 | 2 | 760.99 | GGB | 764.102 | 768.844 | 768.864 | 266.41 | GGB | 10821 | GGB | 9.84 | GGB | 1014.41 | GGB | 58.74 | GGB | 167749.79 | GGB | 138240.79 | GGB | 0 | 0 | 2703 | 3600 | 2687.35 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 108295.01 | GGB | 108296.32 | 2687.35 | 2687.35 |  |  |  | 1 | 1 |  |  |  |  | 138240.79 | 2687.35 | 138240.79 | 2687.35 | 9.2367 | [5 empty] | 103.1948 |  |  | #VALUE!
08.01.2008 12:00 | 3600 | 2 | 760.51 | GGB | 763.004 | 766.734 | 767.766 | 265.6 | GGB | 10787.3 | GGB | 9.82 | GGB | 1014.36 | GGB | 59.03 | GGB | 167184.22 | GGB | 137647.01 | GGB | 0 | 0 | 2717 | 3600 | 2701.46 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 108334.67 | GGB | 108335.98 | 2701.46 | 2701.46 |  |  |  | 0 | 1 | [14 empty] | 103.2911 |  |  | #VALUE!
08.01.2008 13:00 | 3600 | 2 | 761.1 | GGB | 765.201 | 768.961 | 769.597 | 265.79 | GGB | 10765 | GGB | 9.83 | GGB | 1014.1 | GGB | 58.61 | GGB | 167617.75 | GGB | 138144.04 | GGB | 0 | 0 | 2676 | 3600 | 2660.76 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 108374.31 | GGB | 108375.62 | 2660.76 | 2660.76 |  |  |  | 1 | 1 |  |  |  |  | 138144.04 | 2660.76 | 138144.04 | 2660.76 | 9.2727 | [5 empty] | 102.1023 |  |  | #VALUE!
08.01.2008 14:00 | 3600 | 2 | 761.37 | GGB | 765.201 | 770.109 | 769.597 | 264.73 | GGB | 10755.9 | GGB | 9.84 | GGB | 1014.06 | GGB | 58.93 | GGB | 166517.41 | GGB | 137098.4 | GGB | 0 | 0 | 2666 | 3600 | 2650.74 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 108415.61 | GGB | 108416.92 | 2650.74 | 2650.74 |  |  |  | 1 | 1 |  |  |  |  | 137098.4 | 2650.74 | 137098.4 | 2650.74 | 8.7993 | [5 empty] | 100.9478 |  |  | #VALUE!
08.01.2008 15:00 | 3600 | 2 | 760.49 | GGB | 763.004 | 766.828 | 767.033 | 264.25 | GGB | 10722.9 | GGB | 9.82 | GGB | 1013.81 | GGB | 59.42 | GGB | 165667.95 | GGB | 136162.49 | GGB | 0 | 0 | 2695 | 3600 | 2680.07 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 108454.46 | GGB | 108455.77 | 2680.07 | 2680.07 |  |  |  | 0 | 1 | [14 empty] | 101.3681 |  |  | #VALUE!
08.01.2008 16:00 | 3600 | 2 | 760.96 | GGB | 764.102 | 767.883 | 768.132 | 264.89 | GGB | 10713.5 | GGB | 9.83 | GGB | 1014.05 | GGB | 59.06 | GGB | 166378.77 | GGB | 136930.17 | GGB | 0 | 0 | 2665 | 3600 | 2649.43 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 108494.52 | GGB | 108495.83 | 2649.43 | 2649.43 |  |  |  | 1 | 1 |  |  |  |  | 136930.17 | 2649.43 | 136930.17 | 2649.43 | 9.0561 | [5 empty] | 100.7741 |  |  | #VALUE!
08.01.2008 17:00 | 3600 | 2 | 761.02 | GGB | 765.201 | 769.008 | 769.597 | 264.49 | GGB | 10725.5 | GGB | 9.83 | GGB | 1014.22 | GGB | 59.14 | GGB | 165869.31 | GGB | 136500.5 | GGB | 0 | 0 | 2668 | 3600 | 2652.61 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 108533.29 | GGB | 108534.6 | 2652.61 | 2652.61 |  |  |  | 1 | 1 |  |  |  |  | 136500.5 | 2652.61 | 136500.5 | 2652.61 | 9.3392 | [5 empty] | 100.5785 |  |  | #VALUE!
08.01.2008 18:00 | 3600 | 2 | 760.93 | GGB | 763.004 | 766.922 | 767.033 | 263.18 | GGB | 10741.3 | GGB | 9.83 | GGB | 1014.17 | GGB | 59.78 | GGB | 164022.95 | GGB | 134712.6 | GGB | 0 | 0 | 2687 | 3600 | 2671.75 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 108573.1 | GGB | 108574.42 | 2671.75 | 2671.75 |  |  |  | 0 | 1 | [14 empty] | 99.9773 |  |  | #VALUE!
08.01.2008 19:00 | 3600 | 2 | 760.71 | GGB | 764.102 | 768.141 | 768.132 | 264.06 | GGB | 10709.9 | GGB | 9.82 | GGB | 1013.9 | GGB | 59.41 | GGB | 165444.58 | GGB | 135998.68 | GGB | 0 | 0 | 2682 | 3600 | 2666.63 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 108612.56 | GGB | 108613.88 | 2666.63 | 2666.63 |  |  |  | 1 | 1 |  |  |  |  | 135998.68 | 2666.63 | 135998.68 | 2666.63 | 9.1905 | [5 empty] | 100.7384 |  |  | #VALUE!
08.01.2008 20:00 | 3600 | 2 | 761.33 | GGB | 764.102 | 768.141 | 768.498 | 264.08 | GGB | 10693.2 | GGB | 9.83 | GGB | 1013.94 | GGB | 59.29 | GGB | 165562.32 | GGB | 136149.47 | GGB | 0 | 0 | 2643 | 3600 | 2627.7 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 108651.04 | GGB | 108652.36 | 2627.7 | 2627.7 |  |  |  | 1 | 1 |  |  |  |  | 136149.47 | 2627.7 | 136149.47 | 2627.7 | 9.2973 | [5 empty] | 99.3778 |  |  | #VALUE!
08.01.2008 21:00 | 3600 | 2 | 761.48 | GGB | 764.102 | 767.133 | 767.033 | 262.5 | GGB | 10681 | GGB | 9.83 | GGB | 1013.85 | GGB | 59.11 | GGB | 164519.2 | GGB | 135349.73 | GGB | 0 | 0 | 2636 | 3600 | 2620.95 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 108690.41 | GGB | 108691.73 | 2620.95 | 2620.95 |  |  |  | 1 | 1 |  |  |  |  | 135349.73 | 2620.95 | 135349.73 | 2620.95 | 9.0105 | [5 empty] | 98.5402 |  |  | #VALUE!
08.01.2008 22:00 | 3600 | 2 | 761.19 | GGB | 764.102 | 768.141 | 768.498 | 261.46 | GGB | 10680.5 | GGB | 9.83 | GGB | 1013.74 | GGB | 60.26 | GGB | 162219.49 | GGB | 132983.52 | GGB | 0 | 0 | 2652 | 3600 | 2636.5 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 108728.94 | GGB | 108730.27 | 2636.5 | 2636.5 |  |  |  | 1 | 1 |  |  |  |  | 132983.52 | 2636.5 | 132983.52 | 2636.5 | 9.0973 | [5 empty] | 97.392 |  |  | #VALUE!
08.01.2008 23:00 | 3600 | 2 | 761.1 | GGB | 764.102 | 768.141 | 768.132 | 262.55 | GGB | 10611.1 | GGB | 9.82 | GGB | 1013.88 | GGB | 59.77 | GGB | 163260.41 | GGB | 134054.91 | GGB | 0 | 0 | 2630 | 3600 | 2614.86 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 108769.43 | GGB | 108770.76 | 2614.86 | 2614.86 |  |  |  | 1 | 1 |  |  |  |  | 134054.91 | 2614.86 | 134054.91 | 2614.86 | 8.6573 | [5 empty] | 97.3708 |  |  | #VALUE!
08.01.2008 24:00 | 3600 | 2 | 761.9 | GGB | 765.201 | 768.328 | 769.597 | 261.97 | GGB | 10606.1 | GGB | 9.83 | GGB | 1013.94 | GGB | 59.82 | GGB | 163081.06 | GGB | 133895.09 | GGB | 0 | 0 | 2599 | 3600 | 2583.87 | GGB | 100 | GGB | 37.7 | GGB | 37.7 | GGB | 108807.13 | GGB | 108808.46 | 2583.87 | 2583.87 |  |  |  | 1 | 1 |  |  |  |  | 133895.09 | 2583.87 | 133895.09 | 2583.87 | 9.1769 | [5 empty] | 96.1021 |  |  | #VALUE!
09.01.2008 01:00 | 3600 | 2 | 761.98 | GGB | 765.201 | 769.242 | 769.597 | 260.49 | GGB | 10599.5 | GGB | 9.83 | GGB | 1014.17 | GGB | 60.26 | GGB | 161438.25 | GGB | 132398.61 | GGB | 0 | 0 | 2597 | 3600 | 2581.86 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 108846.26 | GGB | 108847.59 | 2581.86 | 2581.86 |  |  |  | 1 | 1 |  |  |  |  | 132398.61 | 2581.86 | 132398.61 | 2581.86 | 8.7359 | [5 empty] | 94.9541 |  |  | #VALUE!
09.01.2008 02:00 | 3600 | 2 | 761.82 | GGB | 764.102 | 766.875 | 768.132 | 259.89 | GGB | 10571.9 | GGB | 9.82 | GGB | 1014.3 | GGB | 60.57 | GGB | 161090.55 | GGB | 132007.37 | GGB | 0 | 0 | 2604 | 3600 | 2588.8 | GGB | 100 | GGB | 35.73 | GGB | 35.73 | GGB | 108881.99 | GGB | 108883.32 | 2588.8 | 2588.8 |  |  |  | 1 | 1 |  |  |  |  | 132007.37 | 2588.8 | 132007.37 | 2588.8 | 9.5645 | [5 empty] | 94.928 |  |  | #VALUE!
09.01.2008 03:00 | 3600 | 2 | 762.19 | GGB | 765.201 | 768.07 | 769.597 | 260.29 | GGB | 10551.5 | GGB | 9.83 | GGB | 1014.36 | GGB | 60.32 | GGB | 161505.37 | GGB | 132453.96 | GGB | 0 | 0 | 2575 | 3600 | 2559.34 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 108921.48 | GGB | 108922.81 | 2559.34 | 2559.34 |  |  |  | 1 | 1 |  |  |  |  | 132453.96 | 2559.34 | 132453.96 | 2559.34 | 8.5843 | [5 empty] | 94.1652 |  |  | #VALUE!
09.01.2008 04:00 | 3600 | 2 | 761.95 | GGB | 765.201 | 768.234 | 769.597 | 260.5 | GGB | 10545.9 | GGB | 9.82 | GGB | 1014.62 | GGB | 60.34 | GGB | 161622.01 | GGB | 132576.88 | GGB | 0 | 0 | 2577 | 3600 | 2562.04 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 108958.8 | GGB | 108960.13 | 2562.04 | 2562.04 |  |  |  | 1 | 1 |  |  |  |  | 132576.88 | 2562.04 | 132576.88 | 2562.04 | 9.1015 | [5 empty] | 94.352 |  |  | #VALUE!
09.01.2008 05:00 | 3600 | 2 | 762.32 | GGB | 766.3 | 769.242 | 770.696 | 260.71 | GGB | 10557.5 | GGB | 9.83 | GGB | 1015.31 | GGB | 60.5 | GGB | 161739.75 | GGB | 132698.66 | GGB | 0 | 0 | 2570 | 3600 | 2554.82 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 108997.86 | GGB | 108999.2 | 2554.82 | 2554.82 |  |  |  | 1 | 1 |  |  |  |  | 132698.66 | 2554.82 | 132698.66 | 2554.82 | 8.6773 | [5 empty] | 94.1726 |  |  | #VALUE!
09.01.2008 06:00 | 3600 | 2 | 762.17 | GGB | 766.3 | 770.109 | 769.597 | 260.72 | GGB | 10548.9 | GGB | 9.82 | GGB | 1015.1 | GGB | 60.44 | GGB | 161858.58 | GGB | 132796.54 | GGB | 0 | 0 | 2578 | 3600 | 2562.63 | GGB | 100 | GGB | 36.57 | GGB | 36.57 | GGB | 109034.43 | GGB | 109035.77 | 2562.63 | 2562.63 |  |  |  | 1 | 1 |  |  |  |  | 132796.54 | 2562.63 | 132796.54 | 2562.63 | 9.3057 | [5 empty] | 94.5301 |  |  | #VALUE!
09.01.2008 07:00 | 3600 | 2 | 762.19 | GGB | 765.201 | 769.172 | 768.498 | 260.18 | GGB | 10545.3 | GGB | 9.82 | GGB | 1015.2 | GGB | 60.54 | GGB | 161563.69 | GGB | 132527.4 | GGB | 0 | 0 | 2563 | 3600 | 2547.46 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 109073.16 | GGB | 109074.49 | 2547.46 | 2547.46 |  |  |  | 1 | 1 |  |  |  |  | 132527.4 | 2547.46 | 132527.4 | 2547.46 | 8.7192 | [5 empty] | 93.7801 |  |  | #VALUE!
09.01.2008 08:00 | 3600 | 2 | 761.69 | GGB | 766.3 | 770.391 | 771.795 | 260.71 | GGB | 10556.8 | GGB | 9.82 | GGB | 1015.66 | GGB | 60.46 | GGB | 162132.57 | GGB | 133082.32 | GGB | 0 | 0 | 2593 | 3600 | 2577.63 | GGB | 100 | GGB | 37.5 | GGB | 37.5 | GGB | 109110.65 | GGB | 109111.99 | 2577.63 | 2577.63 |  |  |  | 1 | 1 |  |  |  |  | 133082.32 | 2577.63 | 133082.32 | 2577.63 | 9.1477 | [5 empty] | 95.2881 |  |  | #VALUE!
09.01.2008 09:00 | 3600 | 2 | 761.8 | GGB | 765.201 | 769.242 | 768.864 | 260.52 | GGB | 10605 | GGB | 9.83 | GGB | 1015.85 | GGB | 60.15 | GGB | 162766.36 | GGB | 133756.88 | GGB | 0 | 0 | 2576 | 3600 | 2561.04 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 109149.43 | GGB | 109150.76 | 2561.04 | 2561.04 |  |  |  | 1 | 1 |  |  |  |  | 133756.88 | 2561.04 | 133756.88 | 2561.04 | 8.8356 | [5 empty] | 95.1546 |  |  | #VALUE!
09.01.2008 10:00 | 3600 | 2 | 761.41 | GGB | 765.201 | 769.313 | 769.963 | 260.2 | GGB | 10615 | GGB | 9.83 | GGB | 1016.53 | GGB | 59.67 | GGB | 163010.64 | GGB | 134236.89 | GGB | 0 | 0 | 2586 | 3600 | 2570.5 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 109188.54 | GGB | 109189.87 | 2570.5 | 2570.5 |  |  |  | 1 | 1 |  |  |  |  | 134236.89 | 2570.5 | 134236.89 | 2570.5 | 8.8227 | [5 empty] | 95.8489 |  |  | #VALUE!
09.01.2008 11:00 | 3600 | 2 | 761.21 | GGB | 765.201 | 768.117 | 768.864 | 260.24 | GGB | 10615.1 | GGB | 9.82 | GGB | 1016.91 | GGB | 59.7 | GGB | 163096.46 | GGB | 134348.89 | GGB | 0 | 0 | 2592 | 3600 | 2576.64 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 109226.68 | GGB | 109228.01 | 2576.64 | 2576.64 |  |  |  | 1 | 1 |  |  |  |  | 134348.89 | 2576.64 | 134348.89 | 2576.64 | 9.0763 | [5 empty] | 96.158 |  |  | #VALUE!
09.01.2008 12:00 | 3600 | 2 | 761.7 | GGB | 765.201 | 768.234 | 768.864 | 260.11 | GGB | 10616.7 | GGB | 9.83 | GGB | 1017.3 | GGB | 59.75 | GGB | 162956.72 | GGB | 134261.68 | GGB | 0 | 0 | 2580 | 3600 | 2564.55 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 109264.81 | GGB | 109266.14 | 2564.55 | 2564.55 |  |  |  | 1 | 1 |  |  |  |  | 134261.68 | 2564.55 | 134261.68 | 2564.55 | 9.0302 | [5 empty] | 95.6447 |  |  | #VALUE!
09.01.2008 13:00 | 3600 | 2 | 761.55 | GGB | 765.201 | 769.359 | 768.864 | 259.78 | GGB | 10603.8 | GGB | 9.82 | GGB | 1017.19 | GGB | 59.77 | GGB | 162655.23 | GGB | 133990.81 | GGB | 0 | 0 | 2583 | 3600 | 2568.18 | GGB | 100 | GGB | 37.8 | GGB | 37.8 | GGB | 109302.61 | GGB | 109303.94 | 2568.18 | 2568.18 |  |  |  | 1 | 1 |  |  |  |  | 133990.81 | 2568.18 | 133990.81 | 2568.18 | 9.1035 | [5 empty] | 95.5868 |  |  | #VALUE!
09.01.2008 14:00 | 3600 | 2 | 761.65 | GGB | 764.102 | 768.609 | 768.864 | 258.72 | GGB | 10627.1 | GGB | 9.83 | GGB | 1015.65 | GGB | 59.05 | GGB | 162853.29 | GGB | 134241.3 | GGB | 0 | 0 | 2589 | 2956 | 2573.85 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 109340.67 | GGB | 109342 | 2573.85 | 2573.85 |  |  |  | 1 | 1 |  |  |  |  | 134241.3 | 2573.85 | 134241.3 | 2573.85 | 9.0782 | [5 empty] | 95.9769 |  |  | #VALUE!
09.01.2008 15:00 | 3600 | 2 | 761.25 | GGB | 765.201 | 768.609 | 768.864 | 258.3 | GGB | 10633.1 | GGB | 9.83 | GGB | 1015.7 | GGB | 60.39 | GGB | 162353.73 | GGB | 133298.7 | GGB | 0 | 0 | 2608 | 3600 | 2593.17 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 109379.08 | GGB | 109380.42 | 2593.17 | 2593.17 |  |  |  | 1 | 1 |  |  |  |  | 133298.7 | 2593.17 | 133298.7 | 2593.17 | 8.997 | [5 empty] | 96.0184 |  |  | #VALUE!
09.01.2008 16:00 | 3600 | 2 | 760.05 | GGB | 765.201 | 769.547 | 769.963 | 262.7 | GGB | 10670.1 | GGB | 9.8 | GGB | 1016.34 | GGB | 59.36 | GGB | 166472.3 | GGB | 137189.04 | GGB | 0 | 0 | 2670 | 3600 | 2654.18 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 109419.21 | GGB | 109420.55 | 2654.18 | 2654.18 |  |  |  | 1 | 1 |  |  |  |  | 137189.04 | 2654.18 | 137189.04 | 2654.18 | 9.0736 | [5 empty] | 101.1457 |  |  | #VALUE!
09.01.2008 17:00 | 3600 | 2 | 761.1 | GGB | 765.201 | 768.188 | 768.864 | 263.88 | GGB | 10743.7 | GGB | 9.83 | GGB | 1016.24 | GGB | 59.17 | GGB | 167425.19 | GGB | 138040.86 | GGB | 0 | 0 | 2652 | 3600 | 2636.75 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 109457.93 | GGB | 109459.27 | 2636.75 | 2636.75 |  |  |  | 1 | 1 |  |  |  |  | 138040.86 | 2636.75 | 138040.86 | 2636.75 | 9.4003 | [5 empty] | 101.1053 |  |  | #VALUE!
09.01.2008 18:00 | 3600 | 2 | 761.35 | GGB | 765.201 | 769.195 | 769.963 | 263.13 | GGB | 10768.5 | GGB | 9.84 | GGB | 1015.88 | GGB | 59.32 | GGB | 166996.06 | GGB | 137577 | GGB | 0 | 0 | 2650 | 3600 | 2635.11 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 109498.3 | GGB | 109499.64 | 2635.11 | 2635.11 |  |  |  | 1 | 1 |  |  |  |  | 137577 | 2635.11 | 137577 | 2635.11 | 8.9802 | [5 empty] | 100.7029 |  |  | #VALUE!
09.01.2008 19:00 | 3600 | 2 | 760.71 | GGB | 763.004 | 767.906 | 767.766 | 261.71 | GGB | 10769.7 | GGB | 9.83 | GGB | 1015.13 | GGB | 59.61 | GGB | 166898.13 | GGB | 137276.2 | GGB | 0 | 0 | 2682 | 3600 | 2666.83 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 109536.95 | GGB | 109538.29 | 2666.83 | 2666.83 |  |  |  | 0 | 1 | [14 empty] | 101.6923 |  |  | #VALUE!
09.01.2008 20:00 | 3600 | 2 | 760.55 | GGB | 765.201 | 769.055 | 768.864 | 263.76 | GGB | 10771.8 | GGB | 9.83 | GGB | 1014.66 | GGB | 58.8 | GGB | 169787.62 | GGB | 139927.72 | GGB | 0 | 0 | 2680 | 3600 | 2664.71 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 109577.12 | GGB | 109578.46 | 2664.71 | 2664.71 |  |  |  | 1 | 1 |  |  |  |  | 139927.72 | 2664.71 | 139927.72 | 2664.71 | 9.2822 | [5 empty] | 103.5741 |  |  | #VALUE!
09.01.2008 21:00 | 3600 | 2 | 760.65 | GGB | 764.102 | 768.211 | 768.864 | 263.98 | GGB | 10787.6 | GGB | 9.83 | GGB | 1013.94 | GGB | 58.52 | GGB | 170228.85 | GGB | 140310.29 | GGB | 0 | 0 | 2681 | 3600 | 2666 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 109615.43 | GGB | 109616.77 | 2666 | 2666 |  |  |  | 1 | 1 |  |  |  |  | 140310.29 | 2666 | 140310.29 | 2666 | 9.7642 | [5 empty] | 103.9076 |  |  | #VALUE!
09.01.2008 22:00 | 3600 | 2 | 761.01 | GGB | 764.102 | 768.188 | 768.864 | 263.54 | GGB | 10833.5 | GGB | 9.84 | GGB | 1013.52 | GGB | 58.66 | GGB | 169861.34 | GGB | 139888.23 | GGB | 0 | 0 | 2682 | 3600 | 2666.17 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 109655.68 | GGB | 109657.02 | 2666.17 | 2666.17 |  |  |  | 1 | 1 |  |  |  |  | 139888.23 | 2666.17 | 139888.23 | 2666.17 | 9.2662 | [5 empty] | 103.6016 |  |  | #VALUE!
09.01.2008 23:00 | 3600 | 2 | 760.23 | GGB | 763.004 | 767.109 | 767.766 | 262.22 | GGB | 10840.7 | GGB | 9.83 | GGB | 1013.64 | GGB | 58.52 | GGB | 168967.87 | GGB | 139227.81 | GGB | 0 | 0 | 2713 | 3600 | 2697.95 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 109694.32 | GGB | 109695.66 | 2697.95 | 2697.95 |  |  |  | 0 | 1 | [14 empty] | 104.3416 |  |  | #VALUE!
09.01.2008 24:00 | 3600 | 2 | 760.47 | GGB | 764.102 | 767.391 | 768.132 | 263.18 | GGB | 10810.8 | GGB | 9.83 | GGB | 1013.23 | GGB | 58.59 | GGB | 169465.22 | GGB | 139552.75 | GGB | 0 | 0 | 2704 | 3600 | 2688.13 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 109735.02 | GGB | 109736.36 | 2688.13 | 2688.13 |  |  |  | 1 | 1 |  |  |  |  | 139552.75 | 2688.13 | 139552.75 | 2688.13 | 9.2171 | [5 empty] | 104.2044 |  |  | #VALUE!
10.01.2008 01:00 | 3600 | 2 | 760.65 | GGB | 764.102 | 768.633 | 768.498 | 263.55 | GGB | 10797.4 | GGB | 9.84 | GGB | 1012.87 | GGB | 58.29 | GGB | 170301.47 | GGB | 140320.16 | GGB | 0 | 0 | 2677 | 3600 | 2661.36 | GGB | 100 | GGB | 38.09 | GGB | 38.09 | GGB | 109773.11 | GGB | 109774.45 | 2661.36 | 2661.36 |  |  |  | 1 | 1 |  |  |  |  | 140320.16 | 2661.36 | 140320.16 | 2661.36 | 9.8042 | [5 empty] | 103.734 |  |  | #VALUE!
10.01.2008 02:00 | 3600 | 2 | 760.62 | GGB | 763.004 | 767.32 | 768.132 | 261.94 | GGB | 10829.8 | GGB | 9.84 | GGB | 1012.33 | GGB | 58.92 | GGB | 168294.46 | GGB | 138327.59 | GGB | 0 | 0 | 2697 | 3600 | 2681.39 | GGB | 100 | GGB | 41.42 | GGB | 41.42 | GGB | 109814.53 | GGB | 109815.87 | 2681.39 | 2681.39 |  |  |  | 0 | 1 | [14 empty] | 103.0306 |  |  | #VALUE!
10.01.2008 03:00 | 3600 | 2 | 760.44 | GGB | 763.004 | 767.32 | 768.132 | 261.67 | GGB | 10821 | GGB | 9.84 | GGB | 1011.91 | GGB | 58.86 | GGB | 168393.49 | GGB | 138377.74 | GGB | 0 | 0 | 2707 | 3600 | 2691.68 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 109853.23 | GGB | 109854.58 | 2691.68 | 2691.68 |  |  |  | 0 | 1 | [14 empty] | 103.4635 |  |  | #VALUE!
10.01.2008 04:00 | 3600 | 2 | 760.19 | GGB | 764.102 | 767.32 | 768.132 | 262.87 | GGB | 10790.5 | GGB | 9.83 | GGB | 1011.74 | GGB | 58.44 | GGB | 169881.15 | GGB | 139753.23 | GGB | 0 | 0 | 2699 | 3600 | 2684.05 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 109893.48 | GGB | 109894.83 | 2684.05 | 2684.05 |  |  |  | 1 | 1 |  |  |  |  | 139753.23 | 2684.05 | 139753.23 | 2684.05 | 9.3194 | [5 empty] | 104.1957 |  |  | #VALUE!
10.01.2008 05:00 | 3600 | 2 | 760.7 | GGB | 763.004 | 767.531 | 768.132 | 262.33 | GGB | 10814.4 | GGB | 9.84 | GGB | 1010.85 | GGB | 58.4 | GGB | 168643.27 | GGB | 138630.94 | GGB | 0 | 0 | 2679 | 3600 | 2663.49 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 109931.93 | GGB | 109933.28 | 2663.49 | 2663.49 |  |  |  | 0 | 1 | [14 empty] | 102.5673 |  |  | #VALUE!
10.01.2008 06:00 | 3600 | 2 | 760.17 | GGB | 764.102 | 767.578 | 768.132 | 261.97 | GGB | 10823.1 | GGB | 9.83 | GGB | 1010.52 | GGB | 58.65 | GGB | 167528.62 | GGB | 137564.05 | GGB | 0 | 0 | 2712 | 3600 | 2696.77 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 109972.22 | GGB | 109973.57 | 2696.77 | 2696.77 |  |  |  | 1 | 1 |  |  |  |  | 137564.05 | 2696.77 | 137564.05 | 2696.77 | 9.2077 | [5 empty] | 103.0496 |  |  | #VALUE!
10.01.2008 07:00 | 3600 | 2 | 760.37 | GGB | 763.004 | 767.578 | 767.033 | 262.06 | GGB | 10817.3 | GGB | 9.83 | GGB | 1010.81 | GGB | 58.79 | GGB | 166998.26 | GGB | 137111.75 | GGB | 0 | 0 | 2706 | 3600 | 2690.54 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 110010.39 | GGB | 110011.74 | 2690.54 | 2690.54 |  |  |  | 0 | 1 | [14 empty] | 102.4735 |  |  | #VALUE!
10.01.2008 08:00 | 3600 | 2 | 759.95 | GGB | 763.004 | 766.57 | 768.132 | 262.71 | GGB | 10831.4 | GGB | 9.83 | GGB | 1010.85 | GGB | 58.48 | GGB | 166208.22 | GGB | 136594.97 | GGB | 0 | 0 | 2740 | 3600 | 2724.62 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 110051.14 | GGB | 110052.48 | 2724.62 | 2724.62 |  |  |  | 0 | 1 | [14 empty] | 103.3804 |  |  | #VALUE!
10.01.2008 09:00 | 3600 | 2 | 759.49 | GGB | 763.004 | 766.594 | 768.132 | 264.32 | GGB | 10925.4 | GGB | 9.81 | GGB | 1011.56 | GGB | 57.85 | GGB | 169263.86 | GGB | 139469.17 | GGB | 0 | 0 | 2776 | 3600 | 2760.73 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 110090.24 | GGB | 110091.58 | 2760.73 | 2709.7602 |  |  |  | 0 | 1 | [14 empty] | 106.9546 | 2709.7602 |  | 104.98
10.01.2008 10:00 | 3600 | 2 | 761.4 | GGB | 765.201 | 768.984 | 769.597 | 265.94 | GGB | 11067.5 | GGB | 9.84 | GGB | 1011.93 | GGB | 57.59 | GGB | 172539.56 | GGB | 142331.89 | GGB | 0 | 0 | 2721 | 3600 | 2705.56 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 110130.46 | GGB | 110131.8 | 2705.56 | 2655.2588 |  |  |  | 1 | 1 |  |  |  |  | 142331.89 | 2655.2588 | 142331.89 | 2655.2588 | 9.3965 | [5 empty] | 106.9687 | 2655.2588 |  | 104.98
10.01.2008 11:00 | 3600 | 2 | 761.37 | GGB | 764.102 | 767.93 | 769.597 | 265.38 | GGB | 11047.2 | GGB | 9.84 | GGB | 1012.67 | GGB | 57.94 | GGB | 171926.67 | GGB | 141781.11 | GGB | 0 | 0 | 2706 | 3600 | 2690.54 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 110170.16 | GGB | 110171.5 | 2690.54 | 2665.5737 |  |  |  | 1 | 1 |  |  |  |  | 141781.11 | 2665.5737 | 141781.11 | 2665.5737 | 9.5196 | [5 empty] | 105.9633 | 2665.5737 |  | 104.98
10.01.2008 12:00 | 3600 | 2 | 761.19 | GGB | 765.201 | 767.977 | 769.597 | 265.07 | GGB | 11026 | GGB | 9.83 | GGB | 1013.05 | GGB | 58.13 | GGB | 171358.9 | GGB | 141284.45 | GGB | 0 | 0 | 2707 | 3600 | 2691.99 | GGB | 100 | GGB | 41.08 | GGB | 41.08 | GGB | 110211.24 | GGB | 110212.58 | 2691.99 | 2674.9441 |  |  |  | 1 | 1 |  |  |  |  | 141284.45 | 2674.9441 | 141284.45 | 2674.9441 | 9.1998 | [5 empty] | 105.649 | 2674.9441 |  | 104.98
10.01.2008 13:00 | 3600 | 2 | 761.88 | GGB | 766.3 | 769.969 | 770.696 | 264.95 | GGB | 11031.2 | GGB | 9.84 | GGB | 1012.98 | GGB | 58.1 | GGB | 171319.29 | GGB | 141256.36 | GGB | 0 | 0 | 2685 | 3600 | 2669.99 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 110250.2 | GGB | 110251.53 | 2669.99 | 2669.99 |  |  |  | 1 | 1 |  |  |  |  | 141256.36 | 2669.99 | 141256.36 | 2669.99 | 9.683 | [5 empty] | 104.7647 |  |  | #VALUE!
10.01.2008 14:00 | 3600 | 2 | 761.7 | GGB | 765.201 | 769.078 | 769.597 | 264.78 | GGB | 11003.3 | GGB | 9.83 | GGB | 1013.09 | GGB | 58.31 | GGB | 170950.67 | GGB | 140876.73 | GGB | 0 | 0 | 2685 | 3600 | 2669.5 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 110290.68 | GGB | 110292.02 | 2669.5 | 2669.5 |  |  |  | 1 | 1 |  |  |  |  | 140876.73 | 2669.5 | 140876.73 | 2669.5 | 9.288 | [5 empty] | 104.464 |  |  | #VALUE!
10.01.2008 15:00 | 3600 | 2 | 761.58 | GGB | 765.201 | 769.195 | 769.597 | 264.76 | GGB | 10999.2 | GGB | 9.83 | GGB | 1013.19 | GGB | 58.36 | GGB | 170820.83 | GGB | 140763.6 | GGB | 0 | 0 | 2680 | 3600 | 2664.79 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 110330.08 | GGB | 110331.41 | 2664.79 | 2664.79 |  |  |  | 1 | 1 |  |  |  |  | 140763.6 | 2664.79 | 140763.6 | 2664.79 | 9.5229 | [5 empty] | 104.196 |  |  | #VALUE!
10.01.2008 16:00 | 3600 | 2 | 761.67 | GGB | 763.004 | 767.133 | 768.498 | 265.16 | GGB | 11000.5 | GGB | 9.83 | GGB | 1013.67 | GGB | 58.46 | GGB | 171285.18 | GGB | 141171.58 | GGB | 0 | 0 | 2684 | 3600 | 2668.58 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 110370.16 | GGB | 110371.49 | 2668.58 | 2668.58 |  |  |  | 0 | 1 | [14 empty] | 104.6466 |  |  | #VALUE!
10.01.2008 17:00 | 3600 | 2 | 762.18 | GGB | 764.102 | 768.164 | 768.498 | 265.5 | GGB | 11011.9 | GGB | 9.84 | GGB | 1014.33 | GGB | 58.61 | GGB | 171413.92 | GGB | 141304.82 | GGB | 0 | 0 | 2679 | 3600 | 2663.15 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 110409.51 | GGB | 110410.85 | 2663.15 | 2663.15 |  |  |  | 1 | 1 |  |  |  |  | 141304.82 | 2663.15 | 141304.82 | 2663.15 | 9.5609 | [5 empty] | 104.5322 |  |  | #VALUE!
10.01.2008 18:00 | 3600 | 2 | 761.9 | GGB | 765.201 | 769.242 | 770.696 | 266.19 | GGB | 11017.7 | GGB | 9.83 | GGB | 1014.74 | GGB | 58.74 | GGB | 171665.89 | GGB | 141511.06 | GGB | 0 | 0 | 2692 | 3600 | 2676.5 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 110448.94 | GGB | 110450.28 | 2676.5 | 2670.6605 |  |  |  | 1 | 1 |  |  |  |  | 141511.06 | 2670.6605 | 141511.06 | 2670.6605 | 9.5848 | [5 empty] | 105.2095 | 2670.6605 |  | 104.98
10.01.2008 19:00 | 3600 | 2 | 762 | GGB | 766.3 | 770.25 | 770.696 | 265.96 | GGB | 11019.8 | GGB | 9.84 | GGB | 1014.38 | GGB | 58.95 | GGB | 171629.58 | GGB | 141343.73 | GGB | 0 | 0 | 2675 | 3600 | 2659.67 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 110488.32 | GGB | 110489.66 | 2659.67 | 2659.67 |  |  |  | 1 | 1 |  |  |  |  | 141343.73 | 2659.67 | 141343.73 | 2659.67 | 9.5462 | [5 empty] | 104.4244 |  |  | #VALUE!
10.01.2008 20:00 | 3600 | 2 | 762.32 | GGB | 765.201 | 769.195 | 770.696 | 265.77 | GGB | 11021.9 | GGB | 9.84 | GGB | 1013.9 | GGB | 58.82 | GGB | 171693.4 | GGB | 141385.41 | GGB | 0 | 0 | 2670 | 3600 | 2655.07 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 110528.85 | GGB | 110530.19 | 2655.07 | 2655.07 |  |  |  | 1 | 1 |  |  |  |  | 141385.41 | 2655.07 | 141385.41 | 2655.07 | 9.262 | [5 empty] | 104.2745 |  |  | #VALUE!
10.01.2008 21:00 | 3600 | 2 | 762.04 | GGB | 765.201 | 769.078 | 769.597 | 265.47 | GGB | 11009.6 | GGB | 9.83 | GGB | 1013.73 | GGB | 58.77 | GGB | 171593.27 | GGB | 141301.28 | GGB | 0 | 0 | 2669 | 3600 | 2653.47 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 110568.1 | GGB | 110569.44 | 2653.47 | 2653.47 |  |  |  | 1 | 1 |  |  |  |  | 141301.28 | 2653.47 | 141301.28 | 2653.47 | 9.5526 | [5 empty] | 104.1496 |  |  | #VALUE!
10.01.2008 22:00 | 3600 | 2 | 762.25 | GGB | 766.3 | 770.227 | 771.795 | 265.92 | GGB | 10991.4 | GGB | 9.84 | GGB | 1013.35 | GGB | 58.34 | GGB | 173240.48 | GGB | 142786.06 | GGB | 0 | 0 | 2653 | 3600 | 2638.09 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 110607.34 | GGB | 110608.67 | 2638.09 | 2638.09 |  |  |  | 1 | 1 |  |  |  |  | 142786.06 | 2638.09 | 142786.06 | 2638.09 | 9.6019 | [5 empty] | 104.634 |  |  | #VALUE!
10.01.2008 23:00 | 3600 | 2 | 762.7 | GGB | 765.201 | 769.008 | 770.696 | 265.48 | GGB | 10984.5 | GGB | 9.84 | GGB | 1013.05 | GGB | 58.11 | GGB | 172286.48 | GGB | 142057.61 | GGB | 0 | 0 | 2632 | 3600 | 2616.37 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 110646.32 | GGB | 110647.65 | 2616.37 | 2616.37 |  |  |  | 1 | 1 |  |  |  |  | 142057.61 | 2616.37 | 142057.61 | 2616.37 | 9.535 | [5 empty] | 103.2431 |  |  | #VALUE!
10.01.2008 24:00 | 3600 | 2 | 762.24 | GGB | 767.766 | 771.164 | 772.161 | 264.62 | GGB | 10998.6 | GGB | 9.84 | GGB | 1012.72 | GGB | 58.64 | GGB | 171243.36 | GGB | 140925.22 | GGB | 0 | 0 | 2658 | 3600 | 2642.83 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 110686.35 | GGB | 110687.69 | 2642.83 | 2642.83 |  |  |  | 1 | 1 |  |  |  |  | 140925.22 | 2642.83 | 140925.22 | 2642.83 | 9.3017 | [5 empty] | 103.4559 |  |  | #VALUE!
11.01.2008 01:00 | 3600 | 2 | 762.4 | GGB | 766.3 | 770.039 | 770.696 | 265.18 | GGB | 10956.3 | GGB | 9.83 | GGB | 1012.64 | GGB | 58.08 | GGB | 173024.81 | GGB | 142620.56 | GGB | 0 | 0 | 2631 | 3600 | 2615.67 | GGB | 100 | GGB | 37.59 | GGB | 37.59 | GGB | 110723.95 | GGB | 110725.28 | 2615.67 | 2615.67 |  |  |  | 1 | 1 |  |  |  |  | 142620.56 | 2615.67 | 142620.56 | 2615.67 | 9.9241 | [5 empty] | 103.6245 |  |  | #VALUE!
11.01.2008 02:00 | 3600 | 2 | 763.34 | GGB | 765.201 | 768.984 | 769.597 | 263.77 | GGB | 10971.8 | GGB | 9.85 | GGB | 1011.96 | GGB | 58.4 | GGB | 171234.56 | GGB | 140915.55 | GGB | 0 | 0 | 2611 | 3600 | 2595.68 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 110765.32 | GGB | 110766.66 | 2595.68 | 2595.68 |  |  |  | 1 | 1 |  |  |  |  | 140915.55 | 2595.68 | 140915.55 | 2595.68 | 8.8393 | [5 empty] | 101.6032 |  |  | #VALUE!
11.01.2008 03:00 | 3600 | 2 | 761.89 | GGB | 764.102 | 767.93 | 769.597 | 263.27 | GGB | 10961.3 | GGB | 9.83 | GGB | 1011.53 | GGB | 58.61 | GGB | 170652.48 | GGB | 140288.42 | GGB | 0 | 0 | 2651 | 3600 | 2635.59 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 110804.57 | GGB | 110805.9 | 2635.59 | 2635.59 |  |  |  | 1 | 1 |  |  |  |  | 140288.42 | 2635.59 | 140288.42 | 2635.59 | 9.4226 | [5 empty] | 102.7063 |  |  | #VALUE!
11.01.2008 04:00 | 3600 | 2 | 761.68 | GGB | 765.201 | 768.961 | 769.597 | 265 | GGB | 10949 | GGB | 9.82 | GGB | 1011.33 | GGB | 58.09 | GGB | 172857.56 | GGB | 142294.18 | GGB | 0 | 0 | 2652 | 3600 | 2636.88 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 110846.04 | GGB | 110847.37 | 2636.88 | 2636.88 |  |  |  | 1 | 1 |  |  |  |  | 142294.18 | 2636.88 | 142294.18 | 2636.88 | 9.0478 | [5 empty] | 104.2257 |  |  | #VALUE!
11.01.2008 05:00 | 3600 | 2 | 762.83 | GGB | 764.102 | 767.953 | 769.597 | 264.44 | GGB | 10986.8 | GGB | 9.84 | GGB | 1011.28 | GGB | 58.33 | GGB | 172079.62 | GGB | 141543.58 | GGB | 0 | 0 | 2631 | 3600 | 2615.37 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 110884.54 | GGB | 110885.87 | 2615.37 | 2615.37 |  |  |  | 1 | 1 |  |  |  |  | 141543.58 | 2615.37 | 141543.58 | 2615.37 | 9.6153 | [5 empty] | 102.8302 |  |  | #VALUE!
11.01.2008 06:00 | 3600 | 2 | 761.9 | GGB | 765.201 | 768.891 | 769.597 | 264.23 | GGB | 10962.9 | GGB | 9.83 | GGB | 1010.35 | GGB | 58.42 | GGB | 171804.54 | GGB | 141147.95 | GGB | 0 | 0 | 2656 | 3600 | 2640.36 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 110925.67 | GGB | 110927 | 2640.36 | 2640.36 |  |  |  | 1 | 1 |  |  |  |  | 141147.95 | 2640.36 | 141147.95 | 2640.36 | 9.0611 | [5 empty] | 103.5226 |  |  | #VALUE!
11.01.2008 07:00 | 3600 | 2 | 762.57 | GGB | 765.201 | 768.703 | 770.696 | 265.14 | GGB | 10948.2 | GGB | 9.84 | GGB | 1010.1 | GGB | 58.01 | GGB | 173266.88 | GGB | 142492.53 | GGB | 0 | 0 | 2623 | 3600 | 2607.89 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 110964.7 | GGB | 110966.03 | 2607.89 | 2607.89 |  |  |  | 1 | 1 |  |  |  |  | 142492.53 | 2607.89 | 142492.53 | 2607.89 | 9.521 | [5 empty] | 103.2236 |  |  | #VALUE!
11.01.2008 08:00 | 3600 | 2 | 762.44 | GGB | 764.102 | 768.844 | 768.498 | 263.58 | GGB | 10971.6 | GGB | 9.84 | GGB | 1009.9 | GGB | 58.62 | GGB | 170970.48 | GGB | 140318.17 | GGB | 0 | 0 | 2628 | 3208 | 2612.38 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 111004.95 | GGB | 111006.28 | 2612.38 | 2612.38 |  |  |  | 1 | 1 |  |  |  |  | 140318.17 | 2612.38 | 140318.17 | 2612.38 | 9.1072 | [5 empty] | 101.8234 |  |  | #VALUE!
11.01.2008 09:00 | 3600 | 2 | 762.14 | GGB | 765.201 | 769.898 | 770.696 | 263.22 | GGB | 10962.8 | GGB | 9.84 | GGB | 1009.36 | GGB | 58.82 | GGB | 170869.25 | GGB | 140073.88 | GGB | 0 | 0 | 2637 | 3600 | 2621.74 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 111044.89 | GGB | 111046.23 | 2621.74 | 2621.74 |  |  |  | 1 | 1 |  |  |  |  | 140073.88 | 2621.74 | 140073.88 | 2621.74 | 9.1924 | [5 empty] | 102.0104 |  |  | #VALUE!
11.01.2008 10:00 | 3600 | 2 | 762.01 | GGB | 765.201 | 769.875 | 770.696 | 264.37 | GGB | 10925.4 | GGB | 9.83 | GGB | 1009.72 | GGB | 58.36 | GGB | 172131.34 | GGB | 141357.3 | GGB | 0 | 0 | 2623 | 3600 | 2607.85 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 111084.67 | GGB | 111086.01 | 2607.85 | 2607.85 |  |  |  | 1 | 1 |  |  |  |  | 141357.3 | 2607.85 | 141357.3 | 2607.85 | 9.2669 | [5 empty] | 102.3996 |  |  | #VALUE!
11.01.2008 11:00 | 3600 | 2 | 762.47 | GGB | 765.201 | 769.898 | 769.597 | 264.6 | GGB | 10918.5 | GGB | 9.84 | GGB | 1009.3 | GGB | 58.17 | GGB | 172563.77 | GGB | 141733.55 | GGB | 0 | 0 | 2593 | 3600 | 2577.34 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 111125.84 | GGB | 111127.18 | 2577.34 | 2577.34 |  |  |  | 1 | 1 |  |  |  |  | 141733.55 | 2577.34 | 141733.55 | 2577.34 | 8.8729 | [5 empty] | 101.471 |  |  | #VALUE!
11.01.2008 12:00 | 3600 | 2 | 761.66 | GGB | 766.3 | 769.922 | 771.795 | 264.13 | GGB | 10916.1 | GGB | 9.84 | GGB | 1008.5 | GGB | 58.28 | GGB | 171889.26 | GGB | 141020.18 | GGB | 0 | 0 | 2593 | 3600 | 2577.95 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 111164.84 | GGB | 111166.18 | 2577.95 | 2577.95 |  |  |  | 1 | 1 |  |  |  |  | 141020.18 | 2577.95 | 141020.18 | 2577.95 | 9.3216 | [5 empty] | 100.9842 |  |  | #VALUE!
11.01.2008 13:00 | 3600 | 2 | 761.35 | GGB | 764.102 | 768.797 | 769.597 | 262.81 | GGB | 10930.7 | GGB | 9.84 | GGB | 1008.17 | GGB | 58.91 | GGB | 169949.37 | GGB | 139118.54 | GGB | 0 | 0 | 2619 | 3600 | 2603.77 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 111205.35 | GGB | 111206.69 | 2603.77 | 2603.77 |  |  |  | 1 | 1 |  |  |  |  | 139118.54 | 2603.77 | 139118.54 | 2603.77 | 8.9418 | [5 empty] | 100.6202 |  |  | #VALUE!
11.01.2008 14:00 | 3600 | 2 | 761.32 | GGB | 765.201 | 769.945 | 770.696 | 262.66 | GGB | 10917.2 | GGB | 9.84 | GGB | 1007.79 | GGB | 59.15 | GGB | 169778.81 | GGB | 138828.11 | GGB | 0 | 0 | 2612 | 3600 | 2597.06 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 111244.12 | GGB | 111245.46 | 2597.06 | 2597.06 |  |  |  | 1 | 1 |  |  |  |  | 138828.11 | 2597.06 | 138828.11 | 2597.06 | 9.2996 | [5 empty] | 100.1514 |  |  | #VALUE!
11.01.2008 15:00 | 3600 | 2 | 761.29 | GGB | 765.201 | 768.656 | 770.696 | 262.38 | GGB | 10899.5 | GGB | 9.84 | GGB | 1007.51 | GGB | 59.32 | GGB | 169355.18 | GGB | 138372.28 | GGB | 0 | 0 | 2610 | 3600 | 2594.43 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 111284.81 | GGB | 111286.14 | 2594.43 | 2594.43 |  |  |  | 1 | 1 |  |  |  |  | 138372.28 | 2594.43 | 138372.28 | 2594.43 | 8.8249 | [5 empty] | 99.7214 |  |  | #VALUE!
11.01.2008 16:00 | 3600 | 2 | 761.27 | GGB | 765.201 | 768.656 | 769.597 | 262.17 | GGB | 10894.5 | GGB | 9.83 | GGB | 1007.49 | GGB | 59.29 | GGB | 169366.19 | GGB | 138388.91 | GGB | 0 | 0 | 2609 | 3600 | 2593.55 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 111324.02 | GGB | 111325.36 | 2593.55 | 2593.55 |  |  |  | 1 | 1 |  |  |  |  | 138388.91 | 2593.55 | 138388.91 | 2593.55 | 9.1514 | [5 empty] | 99.6996 |  |  | #VALUE!
11.01.2008 17:00 | 3600 | 2 | 761.28 | GGB | 765.201 | 768.633 | 770.696 | 263.45 | GGB | 10869.1 | GGB | 9.83 | GGB | 1007.83 | GGB | 58.85 | GGB | 170890.16 | GGB | 139867.59 | GGB | 0 | 0 | 2603 | 3600 | 2587.65 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 111364.51 | GGB | 111365.85 | 2587.65 | 2587.65 |  |  |  | 1 | 1 |  |  |  |  | 139867.59 | 2587.65 | 139867.59 | 2587.65 | 8.9387 | [5 empty] | 100.5357 |  |  | #VALUE!
11.01.2008 18:00 | 3600 | 2 | 762.13 | GGB | 765.201 | 769.641 | 770.696 | 263.35 | GGB | 10896.2 | GGB | 9.84 | GGB | 1008.12 | GGB | 58.84 | GGB | 171242.26 | GGB | 140200.69 | GGB | 0 | 0 | 2587 | 3600 | 2571.61 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 111404.41 | GGB | 111405.75 | 2571.61 | 2571.61 |  |  |  | 1 | 1 |  |  |  |  | 140200.69 | 2571.61 | 140200.69 | 2571.61 | 9.0361 | [5 empty] | 100.1504 |  |  | #VALUE!
11.01.2008 19:00 | 3600 | 2 | 761.66 | GGB | 764.102 | 768.492 | 769.597 | 261.94 | GGB | 10902.2 | GGB | 9.84 | GGB | 1007.88 | GGB | 59.29 | GGB | 169466.32 | GGB | 138526.79 | GGB | 0 | 0 | 2602 | 3600 | 2586.87 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 111443.89 | GGB | 111445.23 | 2586.87 | 2586.87 |  |  |  | 1 | 1 |  |  |  |  | 138526.79 | 2586.87 | 138526.79 | 2586.87 | 9.0768 | [5 empty] | 99.5419 |  |  | #VALUE!
11.01.2008 20:00 | 3600 | 2 | 761.41 | GGB | 764.102 | 768.539 | 769.597 | 262.1 | GGB | 10892.5 | GGB | 9.83 | GGB | 1008.11 | GGB | 59.43 | GGB | 169383.79 | GGB | 138430.32 | GGB | 0 | 0 | 2611 | 3600 | 2595.88 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 111483.64 | GGB | 111484.98 | 2595.88 | 2595.88 |  |  |  | 1 | 1 |  |  |  |  | 138430.32 | 2595.88 | 138430.32 | 2595.88 | 9.0402 | [5 empty] | 99.819 |  |  | #VALUE!
11.01.2008 21:00 | 3600 | 2 | 761.62 | GGB | 765.201 | 768.539 | 769.597 | 262.18 | GGB | 10890 | GGB | 9.84 | GGB | 1007.85 | GGB | 59.57 | GGB | 169444.31 | GGB | 138386.2 | GGB | 0 | 0 | 2610 | 3600 | 2594.44 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 111522.56 | GGB | 111523.9 | 2594.44 | 2594.44 |  |  |  | 1 | 1 |  |  |  |  | 138386.2 | 2594.44 | 138386.2 | 2594.44 | 9.2249 | [5 empty] | 99.7319 |  |  | #VALUE!
11.01.2008 22:00 | 3600 | 2 | 762.06 | GGB | 764.102 | 768.633 | 769.597 | 260.87 | GGB | 10904.7 | GGB | 9.84 | GGB | 1007.34 | GGB | 59.49 | GGB | 169376.09 | GGB | 138292.56 | GGB | 0 | 0 | 2586 | 3600 | 2570.84 | GGB | 100 | GGB | 41.69 | GGB | 41.69 | GGB | 111564.25 | GGB | 111565.59 | 2570.84 | 2570.84 |  |  |  | 1 | 1 |  |  |  |  | 138292.56 | 2570.84 | 138292.56 | 2570.84 | 8.5279 | [5 empty] | 98.7578 |  |  | #VALUE!
11.01.2008 23:00 | 3600 | 2 | 760.74 | GGB | 764.102 | 768.563 | 769.597 | 263.27 | GGB | 10843.4 | GGB | 9.81 | GGB | 1008.2 | GGB | 58.93 | GGB | 171308.28 | GGB | 140228.36 | GGB | 0 | 0 | 2626 | 3600 | 2610.18 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 111603.19 | GGB | 111604.53 | 2610.18 | 2610.18 |  |  |  | 1 | 1 |  |  |  |  | 140228.36 | 2610.18 | 140228.36 | 2610.18 | 9.3996 | [5 empty] | 101.6726 |  |  | #VALUE!
11.01.2008 24:00 | 3600 | 2 | 762.86 | GGB | 764.102 | 767.227 | 768.498 | 262.3 | GGB | 10886.3 | GGB | 9.85 | GGB | 1007.85 | GGB | 59.21 | GGB | 170051.7 | GGB | 139032.68 | GGB | 0 | 0 | 2567 | 3600 | 2551.64 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 111642.98 | GGB | 111644.32 | 2551.64 | 2551.64 |  |  |  | 1 | 1 |  |  |  |  | 139032.68 | 2551.64 | 139032.68 | 2551.64 | 8.9158 | [5 empty] | 98.5448 |  |  | #VALUE!
12.01.2008 01:00 | 3600 | 2 | 761.65 | GGB | 764.102 | 768.281 | 769.597 | 261.7 | GGB | 10876.1 | GGB | 9.83 | GGB | 1007.79 | GGB | 59.69 | GGB | 169087.8 | GGB | 138035.75 | GGB | 0 | 0 | 2605 | 3600 | 2589.9 | GGB | 100 | GGB | 38.14 | GGB | 38.14 | GGB | 111681.11 | GGB | 111682.46 | 2589.9 | 2589.9 |  |  |  | 1 | 1 |  |  |  |  | 138035.75 | 2589.9 | 138035.75 | 2589.9 | 9.3733 | [5 empty] | 99.3052 |  |  | #VALUE!
12.01.2008 02:00 | 3600 | 2 | 761.58 | GGB | 764.102 | 768.258 | 769.597 | 262.23 | GGB | 10882.9 | GGB | 9.83 | GGB | 1007.8 | GGB | 59.83 | GGB | 169257.25 | GGB | 138116.98 | GGB | 0 | 0 | 2607 | 3600 | 2591.63 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 111722.21 | GGB | 111723.55 | 2591.63 | 2591.63 |  |  |  | 1 | 1 |  |  |  |  | 138116.98 | 2591.63 | 138116.98 | 2591.63 | 8.7113 | [5 empty] | 99.43 |  |  | #VALUE!
12.01.2008 03:00 | 3600 | 2 | 761.5 | GGB | 764.102 | 768.188 | 769.597 | 262.41 | GGB | 10889.9 | GGB | 9.83 | GGB | 1007.71 | GGB | 59.69 | GGB | 169587.36 | GGB | 138432.68 | GGB | 0 | 0 | 2614 | 3600 | 2598.7 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 111761.35 | GGB | 111762.7 | 2598.7 | 2598.7 |  |  |  | 1 | 1 |  |  |  |  | 138432.68 | 2598.7 | 138432.68 | 2598.7 | 9.1889 | [5 empty] | 99.9292 |  |  | #VALUE!
12.01.2008 04:00 | 3600 | 2 | 761.31 | GGB | 764.102 | 768.188 | 769.597 | 263.49 | GGB | 10878.3 | GGB | 9.82 | GGB | 1007.51 | GGB | 59.28 | GGB | 171027.7 | GGB | 139756.64 | GGB | 0 | 0 | 2619 | 3600 | 2603.75 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 111802.57 | GGB | 111803.92 | 2603.75 | 2603.75 |  |  |  | 1 | 1 |  |  |  |  | 139756.64 | 2603.75 | 139756.64 | 2603.75 | 8.828 | [5 empty] | 101.0809 |  |  | #VALUE!
12.01.2008 05:00 | 3600 | 2 | 761.88 | GGB | 764.102 | 769.219 | 769.597 | 263.81 | GGB | 10919.3 | GGB | 9.84 | GGB | 1007.59 | GGB | 58.85 | GGB | 171807.84 | GGB | 140585.54 | GGB | 0 | 0 | 2598 | 3600 | 2582.72 | GGB | 100 | GGB | 37.87 | GGB | 37.87 | GGB | 111840.44 | GGB | 111841.79 | 2582.72 | 2582.72 |  |  |  | 1 | 1 |  |  |  |  | 140585.54 | 2582.72 | 140585.54 | 2582.72 | 9.5879 | [5 empty] | 100.8592 |  |  | #VALUE!
12.01.2008 06:00 | 3600 | 2 | 760.97 | GGB | 764.102 | 768.164 | 769.597 | 263.25 | GGB | 10943.1 | GGB | 9.83 | GGB | 1007.74 | GGB | 59.1 | GGB | 171047.5 | GGB | 139878.45 | GGB | 0 | 0 | 2647 | 3600 | 2631.39 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 111881.74 | GGB | 111883.09 | 2631.39 | 2631.39 |  |  |  | 1 | 1 |  |  |  |  | 139878.45 | 2631.39 | 139878.45 | 2631.39 | 8.9122 | [5 empty] | 102.243 |  |  | #VALUE!
12.01.2008 07:00 | 3600 | 2 | 761.24 | GGB | 764.102 | 768.094 | 768.498 | 263.3 | GGB | 10955.9 | GGB | 9.83 | GGB | 1007.73 | GGB | 58.96 | GGB | 171269.77 | GGB | 140115.69 | GGB | 0 | 0 | 2642 | 3600 | 2627.14 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 111921.67 | GGB | 111923.02 | 2627.14 | 2627.14 |  |  |  | 1 | 1 |  |  |  |  | 140115.69 | 2627.14 | 140115.69 | 2627.14 | 9.2187 | [5 empty] | 102.251 |  |  | #VALUE!
12.01.2008 08:00 | 3600 | 2 | 761.09 | GGB | 765.201 | 768.117 | 768.498 | 263.7 | GGB | 10955.1 | GGB | 9.83 | GGB | 1007.7 | GGB | 58.86 | GGB | 171520.65 | GGB | 140362.17 | GGB | 0 | 0 | 2652 | 3600 | 2636.45 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 111962.37 | GGB | 111963.72 | 2636.45 | 2636.45 |  |  |  | 1 | 1 |  |  |  |  | 140362.17 | 2636.45 | 140362.17 | 2636.45 | 9.0923 | [5 empty] | 102.7938 |  |  | #VALUE!
12.01.2008 09:00 | 3600 | 2 | 761.07 | GGB | 765.201 | 768.188 | 769.597 | 265.05 | GGB | 10935.1 | GGB | 9.83 | GGB | 1007.81 | GGB | 58.15 | GGB | 173798.35 | GGB | 142543.52 | GGB | 0 | 0 | 2632 | 3600 | 2616.32 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 112001.84 | GGB | 112003.18 | 2616.32 | 2616.32 |  |  |  | 1 | 1 |  |  |  |  | 142543.52 | 2616.32 | 142543.52 | 2616.32 | 9.4511 | [5 empty] | 103.5943 |  |  | #VALUE!
12.01.2008 10:00 | 3600 | 2 | 761.8 | GGB | 764.102 | 768.141 | 769.597 | 263.44 | GGB | 10969.2 | GGB | 9.85 | GGB | 1008.2 | GGB | 58.71 | GGB | 171642.79 | GGB | 140595.16 | GGB | 0 | 0 | 2623 | 3600 | 2607.21 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 112041.62 | GGB | 112042.96 | 2607.21 | 2607.21 |  |  |  | 1 | 1 |  |  |  |  | 140595.16 | 2607.21 | 140595.16 | 2607.21 | 9.2147 | [5 empty] | 101.8225 |  |  | #VALUE!
12.01.2008 11:00 | 3600 | 2 | 761.26 | GGB | 765.201 | 769.266 | 769.597 | 263.02 | GGB | 10958 | GGB | 9.84 | GGB | 1008.32 | GGB | 58.98 | GGB | 170784.52 | GGB | 139796.39 | GGB | 0 | 0 | 2633 | 3600 | 2617.73 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 112083.08 | GGB | 112084.43 | 2617.73 | 2617.73 |  |  |  | 1 | 1 |  |  |  |  | 139796.39 | 2617.73 | 139796.39 | 2617.73 | 8.8244 | [5 empty] | 101.6526 |  |  | #VALUE!
12.01.2008 12:00 | 3600 | 2 | 762.03 | GGB | 765.201 | 769.031 | 769.597 | 261.3 | GGB | 10905.7 | GGB | 9.85 | GGB | 1008.3 | GGB | 59.35 | GGB | 169211.04 | GGB | 138346.66 | GGB | 0 | 0 | 2587 | 3600 | 2571.75 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 112121.9 | GGB | 112123.25 | 2571.75 | 2571.75 |  |  |  | 1 | 1 |  |  |  |  | 138346.66 | 2571.75 | 138346.66 | 2571.75 | 9.1652 | [5 empty] | 98.8314 |  |  | #VALUE!
12.01.2008 13:00 | 3600 | 2 | 761.26 | GGB | 764.102 | 767.93 | 768.498 | 261.51 | GGB | 10859.8 | GGB | 9.83 | GGB | 1007.76 | GGB | 59.26 | GGB | 169686.39 | GGB | 138700.53 | GGB | 0 | 0 | 2598 | 3600 | 2582.31 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 112162.33 | GGB | 112163.68 | 2582.31 | 2582.31 |  |  |  | 1 | 1 |  |  |  |  | 138700.53 | 2582.31 | 138700.53 | 2582.31 | 8.859 | [5 empty] | 99.491 |  |  | #VALUE!
12.01.2008 14:00 | 3600 | 2 | 761.77 | GGB | 764.102 | 768.047 | 769.597 | 263.01 | GGB | 10862.6 | GGB | 9.83 | GGB | 1007.25 | GGB | 58.65 | GGB | 171321.49 | GGB | 140226.29 | GGB | 0 | 0 | 2580 | 3600 | 2565.19 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 112201.08 | GGB | 112202.43 | 2565.19 | 2565.19 |  |  |  | 1 | 1 |  |  |  |  | 140226.29 | 2565.19 | 140226.29 | 2565.19 | 9.2828 | [5 empty] | 99.9186 |  |  | #VALUE!
12.01.2008 15:00 | 3600 | 2 | 761.41 | GGB | 764.102 | 767.977 | 769.597 | 262 | GGB | 10910.3 | GGB | 9.83 | GGB | 1006.54 | GGB | 59.14 | GGB | 169926.26 | GGB | 138780.92 | GGB | 0 | 0 | 2623 | 3600 | 2607.42 | GGB | 100 | GGB | 41.39 | GGB | 41.39 | GGB | 112242.47 | GGB | 112243.82 | 2607.42 | 2607.42 |  |  |  | 1 | 1 |  |  |  |  | 138780.92 | 2607.42 | 138780.92 | 2607.42 | 8.7427 | [5 empty] | 100.5167 |  |  | #VALUE!
12.01.2008 16:00 | 3600 | 2 | 761.19 | GGB | 765.201 | 768.984 | 769.597 | 262.54 | GGB | 10923.8 | GGB | 9.84 | GGB | 1006.69 | GGB | 59.1 | GGB | 170375.2 | GGB | 139185.12 | GGB | 0 | 0 | 2628 | 3600 | 2612.83 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 112281.68 | GGB | 112283.03 | 2612.83 | 2612.83 |  |  |  | 1 | 1 |  |  |  |  | 139185.12 | 2612.83 | 139185.12 | 2612.83 | 9.2749 | [5 empty] | 101.0186 |  |  | #VALUE!
12.01.2008 17:00 | 3600 | 2 | 761.31 | GGB | 765.201 | 768.984 | 769.597 | 262.37 | GGB | 10922.4 | GGB | 9.83 | GGB | 1006.48 | GGB | 59.08 | GGB | 170255.26 | GGB | 139064.32 | GGB | 0 | 0 | 2625 | 3600 | 2609.37 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 112321.99 | GGB | 112323.34 | 2609.37 | 2609.37 |  |  |  | 1 | 1 |  |  |  |  | 139064.32 | 2609.37 | 139064.32 | 2609.37 | 9.002 | [5 empty] | 100.7973 |  |  | #VALUE!
12.01.2008 18:00 | 3600 | 2 | 761.36 | GGB | 765.201 | 768.938 | 769.597 | 262.21 | GGB | 10918.2 | GGB | 9.84 | GGB | 1006.3 | GGB | 59.05 | GGB | 170335.58 | GGB | 139119.22 | GGB | 0 | 0 | 2622 | 3600 | 2606.32 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 112361.18 | GGB | 112362.53 | 2606.32 | 2606.32 |  |  |  | 1 | 1 |  |  |  |  | 139119.22 | 2606.32 | 139119.22 | 2606.32 | 9.2521 | [5 empty] | 100.7192 |  |  | #VALUE!
12.01.2008 19:00 | 3600 | 2 | 761.64 | GGB | 764.102 | 767.93 | 768.498 | 261.86 | GGB | 10891.7 | GGB | 9.83 | GGB | 1006.37 | GGB | 59.03 | GGB | 170210.15 | GGB | 139033.94 | GGB | 0 | 0 | 2604 | 3600 | 2589.05 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 112401.51 | GGB | 112402.86 | 2589.05 | 2589.05 |  |  |  | 1 | 1 |  |  |  |  | 139033.94 | 2589.05 | 139033.94 | 2589.05 | 8.9255 | [5 empty] | 99.9905 |  |  | #VALUE!
12.01.2008 20:00 | 3600 | 2 | 762.11 | GGB | 765.201 | 770.063 | 770.696 | 262.93 | GGB | 10866.1 | GGB | 9.84 | GGB | 1006.61 | GGB | 58.54 | GGB | 171669.19 | GGB | 140468.1 | GGB | 0 | 0 | 2571 | 3600 | 2555.98 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 112441.62 | GGB | 112442.97 | 2555.98 | 2555.98 |  |  |  | 1 | 1 |  |  |  |  | 140468.1 | 2555.98 | 140468.1 | 2555.98 | 8.9512 | [5 empty] | 99.7316 |  |  | #VALUE!
12.01.2008 21:00 | 3600 | 2 | 762.16 | GGB | 764.102 | 769.055 | 769.597 | 261.38 | GGB | 10887.5 | GGB | 9.84 | GGB | 1006.55 | GGB | 59.16 | GGB | 169395.9 | GGB | 138340.53 | GGB | 0 | 0 | 2585 | 3600 | 2570.14 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 112480.59 | GGB | 112481.93 | 2570.14 | 2570.14 |  |  |  | 1 | 1 |  |  |  |  | 138340.53 | 2570.14 | 138340.53 | 2570.14 | 9.1261 | [5 empty] | 98.7651 |  |  | #VALUE!
12.01.2008 22:00 | 3600 | 2 | 761.53 | GGB | 764.102 | 769.055 | 769.597 | 261.3 | GGB | 10880.4 | GGB | 9.83 | GGB | 1005.74 | GGB | 59.19 | GGB | 169297.97 | GGB | 138133.4 | GGB | 0 | 0 | 2600 | 3600 | 2584.4 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 112520.88 | GGB | 112522.22 | 2584.4 | 2584.4 |  |  |  | 1 | 1 |  |  |  |  | 138133.4 | 2584.4 | 138133.4 | 2584.4 | 8.8606 | [5 empty] | 99.1644 |  |  | #VALUE!
12.01.2008 23:00 | 3600 | 2 | 761.76 | GGB | 765.201 | 769.031 | 770.696 | 262.38 | GGB | 10858.1 | GGB | 9.83 | GGB | 1005.41 | GGB | 58.66 | GGB | 170799.93 | GGB | 139537.51 | GGB | 0 | 0 | 2586 | 3600 | 2570.46 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 112559.52 | GGB | 112560.86 | 2570.46 | 2570.46 |  |  |  | 1 | 1 |  |  |  |  | 139537.51 | 2570.46 | 139537.51 | 2570.46 | 9.2825 | [5 empty] | 99.6321 |  |  | #VALUE!
12.01.2008 24:00 | 3600 | 2 | 761.67 | GGB | 764.102 | 767.953 | 769.597 | 261.61 | GGB | 10880 | GGB | 9.83 | GGB | 1005.67 | GGB | 59.07 | GGB | 169531.24 | GGB | 138365.05 | GGB | 0 | 0 | 2603 | 3600 | 2587.59 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 112601 | GGB | 112602.33 | 2587.59 | 2587.59 |  |  |  | 1 | 1 |  |  |  |  | 138365.05 | 2587.59 | 138365.05 | 2587.59 | 8.6335 | [5 empty] | 99.4533 |  |  | #VALUE!
13.01.2008 01:00 | 3600 | 2 | 762.49 | GGB | 765.201 | 770.18 | 770.696 | 261.26 | GGB | 10892.7 | GGB | 9.84 | GGB | 1005.29 | GGB | 59.22 | GGB | 169102.11 | GGB | 137901.73 | GGB | 0 | 0 | 2582 | 3600 | 2566.83 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 112640.02 | GGB | 112641.36 | 2566.83 | 2566.83 |  |  |  | 1 | 1 |  |  |  |  | 137901.73 | 2566.83 | 137901.73 | 2566.83 | 9.0692 | [5 empty] | 98.3251 |  |  | #VALUE!
13.01.2008 02:00 | 3600 | 2 | 761.87 | GGB | 764.102 | 768.914 | 769.597 | 262.09 | GGB | 10823.1 | GGB | 9.82 | GGB | 1005.27 | GGB | 58.82 | GGB | 170185.94 | GGB | 138951.29 | GGB | 0 | 0 | 2579 | 3600 | 2563.27 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 112680.07 | GGB | 112681.41 | 2563.27 | 2563.27 |  |  |  | 1 | 1 |  |  |  |  | 138951.29 | 2563.27 | 138951.29 | 2563.27 | 8.8931 | [5 empty] | 98.936 |  |  | #VALUE!
13.01.2008 03:00 | 3600 | 2 | 762.44 | GGB | 764.102 | 768.914 | 768.498 | 262.36 | GGB | 10875.9 | GGB | 9.84 | GGB | 1005.62 | GGB | 58.94 | GGB | 169730.4 | GGB | 138575.19 | GGB | 0 | 0 | 2587 | 3600 | 2571.85 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 112718.95 | GGB | 112720.29 | 2571.85 | 2571.85 |  |  |  | 1 | 1 |  |  |  |  | 138575.19 | 2571.85 | 138575.19 | 2571.85 | 9.1665 | [5 empty] | 98.9985 |  |  | #VALUE!
13.01.2008 04:00 | 3600 | 2 | 761.74 | GGB | 765.201 | 768.914 | 769.597 | 262.21 | GGB | 10885.8 | GGB | 9.83 | GGB | 1005.73 | GGB | 59.19 | GGB | 169172.53 | GGB | 138032.55 | GGB | 0 | 0 | 2612 | 3600 | 2596.78 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 112758.73 | GGB | 112760.07 | 2596.78 | 2596.78 |  |  |  | 1 | 1 |  |  |  |  | 138032.55 | 2596.78 | 138032.55 | 2596.78 | 9.0106 | [5 empty] | 99.5667 |  |  | #VALUE!
13.01.2008 05:00 | 3600 | 2 | 761.56 | GGB | 764.102 | 768.914 | 768.498 | 262.5 | GGB | 10892.4 | GGB | 9.83 | GGB | 1006.24 | GGB | 59.2 | GGB | 169384.89 | GGB | 138270.01 | GGB | 0 | 0 | 2620 | 3600 | 2604.84 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 112799.32 | GGB | 112800.67 | 2604.84 | 2604.84 |  |  |  | 1 | 1 |  |  |  |  | 138270.01 | 2604.84 | 138270.01 | 2604.84 | 8.8712 | [5 empty] | 100.0476 |  |  | #VALUE!
13.01.2008 06:00 | 3600 | 2 | 761.4 | GGB | 764.102 | 767.906 | 768.498 | 262.7 | GGB | 10901.2 | GGB | 9.83 | GGB | 1006.66 | GGB | 59.14 | GGB | 169433.31 | GGB | 138393.15 | GGB | 0 | 0 | 2629 | 3600 | 2613.26 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 112838.55 | GGB | 112839.9 | 2613.26 | 2613.26 |  |  |  | 1 | 1 |  |  |  |  | 138393.15 | 2613.26 | 138393.15 | 2613.26 | 9.2189 | [5 empty] | 100.4604 |  |  | #VALUE!
13.01.2008 07:00 | 3600 | 2 | 761.56 | GGB | 764.835 | 769.172 | 769.597 | 263.56 | GGB | 10927.7 | GGB | 9.83 | GGB | 1007.86 | GGB | 59.05 | GGB | 170192.54 | GGB | 139216.18 | GGB | 0 | 0 | 2641 | 3600 | 2625.51 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 112878.46 | GGB | 112879.81 | 2625.51 | 2625.51 |  |  |  | 1 | 1 |  |  |  |  | 139216.18 | 2625.51 | 139216.18 | 2625.51 | 9.1584 | [5 empty] | 101.5315 |  |  | #VALUE!
13.01.2008 08:00 | 3600 | 2 | 761.84 | GGB | 765.934 | 770.297 | 770.696 | 264.25 | GGB | 10930.5 | GGB | 9.84 | GGB | 1008.81 | GGB | 58.78 | GGB | 171053.01 | GGB | 140164.59 | GGB | 0 | 0 | 2629 | 3600 | 2614.14 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 112917.61 | GGB | 112918.96 | 2614.14 | 2614.14 |  |  |  | 1 | 1 |  |  |  |  | 140164.59 | 2614.14 | 140164.59 | 2614.14 | 9.3591 | [5 empty] | 101.7805 |  |  | #VALUE!
13.01.2008 09:00 | 3600 | 2 | 761.88 | GGB | 765.934 | 769.195 | 769.597 | 263.24 | GGB | 10921.4 | GGB | 9.84 | GGB | 1009.44 | GGB | 59.11 | GGB | 169840.43 | GGB | 139120.17 | GGB | 0 | 0 | 2620 | 3600 | 2605.12 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 112958.66 | GGB | 112960.01 | 2605.12 | 2605.12 |  |  |  | 1 | 1 |  |  |  |  | 139120.17 | 2605.12 | 139120.17 | 2605.12 | 8.8289 | [5 empty] | 100.6735 |  |  | #VALUE!
13.01.2008 10:00 | 3600 | 2 | 762.24 | GGB | 764.469 | 768.141 | 769.597 | 262.51 | GGB | 10907.7 | GGB | 9.84 | GGB | 1009.85 | GGB | 59.17 | GGB | 169075.7 | GGB | 138526.79 | GGB | 0 | 0 | 2602 | 3600 | 2586.79 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 112997.7 | GGB | 112999.04 | 2586.79 | 2586.79 |  |  |  | 1 | 1 |  |  |  |  | 138526.79 | 2586.79 | 138526.79 | 2586.79 | 9.1811 | [5 empty] | 99.5388 |  |  | #VALUE!
13.01.2008 11:00 | 3600 | 2 | 762.1 | GGB | 764.469 | 768.234 | 769.597 | 262.29 | GGB | 10889 | GGB | 9.83 | GGB | 1010.53 | GGB | 59.35 | GGB | 168547.54 | GGB | 138112.08 | GGB | 0 | 0 | 2599 | 3600 | 2583.88 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 113037.57 | GGB | 113038.91 | 2583.88 | 2583.88 |  |  |  | 1 | 1 |  |  |  |  | 138112.08 | 2583.88 | 138112.08 | 2583.88 | 8.9507 | [5 empty] | 99.1292 |  |  | #VALUE!
13.01.2008 12:00 | 3600 | 2 | 762.44 | GGB | 764.835 | 768.211 | 769.597 | 261.98 | GGB | 10878.3 | GGB | 9.84 | GGB | 1011.28 | GGB | 59.44 | GGB | 168172.32 | GGB | 137869.72 | GGB | 0 | 0 | 2587 | 3600 | 2571.76 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 113076.3 | GGB | 113077.64 | 2571.76 | 2571.76 |  |  |  | 1 | 1 |  |  |  |  | 137869.72 | 2571.76 | 137869.72 | 2571.76 | 9.1549 | [5 empty] | 98.4911 |  |  | #VALUE!
13.01.2008 13:00 | 3600 | 2 | 762.58 | GGB | 764.835 | 769.266 | 769.597 | 261.72 | GGB | 10870.9 | GGB | 9.84 | GGB | 1011.76 | GGB | 59.49 | GGB | 167865.33 | GGB | 137662.53 | GGB | 0 | 0 | 2579 | 3600 | 2563.95 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 113117.49 | GGB | 113118.83 | 2563.95 | 2563.95 |  |  |  | 1 | 1 |  |  |  |  | 137662.53 | 2563.95 | 137662.53 | 2563.95 | 8.5691 | [5 empty] | 98.0444 |  |  | #VALUE!
13.01.2008 14:00 | 3600 | 2 | 762.19 | GGB | 764.469 | 768.211 | 769.597 | 261.86 | GGB | 10872.1 | GGB | 9.83 | GGB | 1012.2 | GGB | 59.51 | GGB | 167901.64 | GGB | 137740.95 | GGB | 0 | 0 | 2584 | 3600 | 2569.07 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 113156.19 | GGB | 113157.53 | 2569.07 | 2569.07 |  |  |  | 1 | 1 |  |  |  |  | 137740.95 | 2569.07 | 137740.95 | 2569.07 | 9.1438 | [5 empty] | 98.2962 |  |  | #VALUE!
13.01.2008 15:00 | 3600 | 2 | 761.33 | GGB | 763.37 | 768.211 | 768.498 | 262.13 | GGB | 10873.5 | GGB | 9.83 | GGB | 1012.79 | GGB | 59.51 | GGB | 167917.04 | GGB | 137835.99 | GGB | 0 | 0 | 2590 | 3600 | 2575.02 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 113196.01 | GGB | 113197.35 | 2575.02 | 2575.02 |  |  |  | 0 | 1 | [14 empty] | 98.5918 |  |  | #VALUE!
13.01.2008 16:00 | 3600 | 2 | 761.71 | GGB | 763.37 | 767.156 | 768.498 | 262.18 | GGB | 10880.7 | GGB | 9.83 | GGB | 1013.62 | GGB | 59.49 | GGB | 168339.57 | GGB | 138303.1 | GGB | 0 | 0 | 2585 | 3600 | 2569.61 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 113236.42 | GGB | 113237.76 | 2569.61 | 2569.61 |  |  |  | 0 | 1 | [14 empty] | 98.7181 |  |  | #VALUE!
13.01.2008 17:00 | 3600 | 2 | 761.42 | GGB | 763.37 | 767.156 | 768.498 | 262.81 | GGB | 10888.9 | GGB | 9.83 | GGB | 1014.34 | GGB | 59.3 | GGB | 169068 | GGB | 139082.54 | GGB | 0 | 0 | 2592 | 3600 | 2576.78 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 113277.36 | GGB | 113278.71 | 2576.78 | 2576.78 |  |  |  | 0 | 1 | [14 empty] | 99.5514 |  |  | #VALUE!
13.01.2008 18:00 | 3600 | 2 | 762.1 | GGB | 764.469 | 768.234 | 769.597 | 262.64 | GGB | 10907.1 | GGB | 9.84 | GGB | 1015.11 | GGB | 59.26 | GGB | 168863.33 | GGB | 139036.76 | GGB | 0 | 0 | 2588 | 3600 | 2573.03 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 113316.44 | GGB | 113317.79 | 2573.03 | 2573.03 |  |  |  | 1 | 1 |  |  |  |  | 139036.76 | 2573.03 | 139036.76 | 2573.03 | 9.1542 | [5 empty] | 99.3738 |  |  | #VALUE!
13.01.2008 19:00 | 3600 | 2 | 761.84 | GGB | 764.835 | 769.289 | 770.696 | 262.65 | GGB | 10917.8 | GGB | 9.84 | GGB | 1015.8 | GGB | 59.38 | GGB | 168776.41 | GGB | 139009.25 | GGB | 0 | 0 | 2593 | 3600 | 2577.73 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 113356 | GGB | 113357.35 | 2577.73 | 2577.73 |  |  |  | 1 | 1 |  |  |  |  | 139009.25 | 2577.73 | 139009.25 | 2577.73 | 9.0578 | [5 empty] | 99.5356 |  |  | #VALUE!
13.01.2008 20:00 | 3600 | 2 | 761.53 | GGB | 763.37 | 767.109 | 768.132 | 263.52 | GGB | 10898.9 | GGB | 9.82 | GGB | 1016.69 | GGB | 59.23 | GGB | 169728.2 | GGB | 139978.17 | GGB | 0 | 0 | 2598 | 3600 | 2582.95 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 113395.75 | GGB | 113397.1 | 2582.95 | 2582.95 |  |  |  | 0 | 1 | [14 empty] | 100.4324 |  |  | #VALUE!
13.01.2008 21:00 | 3600 | 2 | 762.81 | GGB | 763.37 | 768.422 | 769.597 | 263.93 | GGB | 10925.8 | GGB | 9.84 | GGB | 1017.7 | GGB | 58.99 | GGB | 170100.11 | GGB | 140524.54 | GGB | 0 | 0 | 2573 | 3600 | 2557.31 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 113435.31 | GGB | 113436.66 | 2557.31 | 2557.31 |  |  |  | 0 | 1 | [14 empty] | 99.8236 |  |  | #VALUE!
13.01.2008 22:00 | 3600 | 2 | 762.1 | GGB | 764.469 | 768.422 | 769.597 | 263.43 | GGB | 10939.9 | GGB | 9.83 | GGB | 1018.01 | GGB | 59.4 | GGB | 169327.68 | GGB | 139758.1 | GGB | 0 | 0 | 2604 | 3600 | 2588.87 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 113475.47 | GGB | 113476.82 | 2588.87 | 2588.87 |  |  |  | 1 | 1 |  |  |  |  | 139758.1 | 2588.87 | 139758.1 | 2588.87 | 9.0094 | [5 empty] | 100.5043 |  |  | #VALUE!
13.01.2008 23:00 | 3600 | 2 | 761.88 | GGB | 764.835 | 768.398 | 769.597 | 264.83 | GGB | 10919.5 | GGB | 9.82 | GGB | 1018.31 | GGB | 58.78 | GGB | 171379.81 | GGB | 141756.55 | GGB | 0 | 0 | 2600 | 3600 | 2585.06 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 113514.81 | GGB | 113516.17 | 2585.06 | 2585.06 |  |  |  | 1 | 1 |  |  |  |  | 141756.55 | 2585.06 | 141756.55 | 2585.06 | 9.3126 | [5 empty] | 101.7914 |  |  | #VALUE!
13.01.2008 24:00 | 3600 | 2 | 762.4 | GGB | 763.37 | 767.555 | 768.498 | 264.33 | GGB | 10957.7 | GGB | 9.84 | GGB | 1018.67 | GGB | 59.2 | GGB | 170355.39 | GGB | 140782.48 | GGB | 0 | 0 | 2596 | 3600 | 2580.65 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 113554.22 | GGB | 113555.58 | 2580.65 | 2580.65 |  |  |  | 0 | 1 | [14 empty] | 100.9195 |  |  | #VALUE!
14.01.2008 01:00 | 3600 | 2 | 761.47 | GGB | 764.469 | 767.977 | 768.864 | 263.87 | GGB | 10971 | GGB | 9.83 | GGB | 1018.77 | GGB | 59.28 | GGB | 170374.1 | GGB | 140774.42 | GGB | 0 | 0 | 2639 | 3600 | 2623.16 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 113592.96 | GGB | 113594.32 | 2623.16 | 2623.16 |  |  |  | 1 | 1 |  |  |  |  | 140774.42 | 2623.16 | 140774.42 | 2623.16 | 9.5321 | [5 empty] | 102.5761 |  |  | #VALUE!
14.01.2008 02:00 | 3600 | 2 | 761.14 | GGB | 763.37 | 767.953 | 768.864 | 267.36 | GGB | 10971.7 | GGB | 9.82 | GGB | 1018.85 | GGB | 58.65 | GGB | 173549.67 | GGB | 143684.73 | GGB | 0 | 0 | 2653 | 3600 | 2637.48 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 113632.13 | GGB | 113633.48 | 2637.48 | 2630.2586 |  |  |  | 0 | 1 | [14 empty] | 105.2682 | 2630.2586 |  | 104.98
14.01.2008 03:00 | 3600 | 2 | 761.74 | GGB | 763.37 | 767.906 | 768.864 | 267.87 | GGB | 11051.5 | GGB | 9.84 | GGB | 1019.28 | GGB | 58.52 | GGB | 173689.41 | GGB | 143918.75 | GGB | 0 | 0 | 2657 | 3600 | 2641.23 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 113670.44 | GGB | 113671.79 | 2641.23 | 2625.9817 |  |  |  | 0 | 1 | [14 empty] | 105.5896 | 2625.9817 |  | 104.98
14.01.2008 04:00 | 3600 | 2 | 760.52 | GGB | 763.37 | 766.898 | 767.766 | 268.14 | GGB | 11093.8 | GGB | 9.82 | GGB | 1019.68 | GGB | 58.57 | GGB | 173944.69 | GGB | 144162.91 | GGB | 0 | 0 | 2732 | 3600 | 2716.18 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 113709.16 | GGB | 113710.52 | 2716.18 | 2621.5342 |  |  |  | 0 | 1 | [14 empty] | 108.7701 | 2621.5342 |  | 104.98
14.01.2008 05:00 | 3600 | 2 | 760.53 | GGB | 762.271 | 766.875 | 766.667 | 269.21 | GGB | 11105.4 | GGB | 9.82 | GGB | 1019.88 | GGB | 58.17 | GGB | 175464.26 | GGB | 145626.06 | GGB | 0 | 0 | 2732 | 3600 | 2716.46 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 113747.77 | GGB | 113749.12 | 2716.46 | 2595.1948 |  |  |  | 0 | 1 | [14 empty] | 109.8854 | 2595.1948 |  | 104.98
14.01.2008 06:00 | 3600 | 2 | 761.08 | GGB | 764.469 | 768.961 | 768.864 | 270.19 | GGB | 11145.6 | GGB | 9.84 | GGB | 1020.04 | GGB | 57.71 | GGB | 176581.1 | GGB | 146779.25 | GGB | 0 | 0 | 2715 | 3600 | 2699.81 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 113786.19 | GGB | 113787.54 | 2699.81 | 2574.8054 |  |  |  | 1 | 1 |  |  |  |  | 146779.25 | 2574.8054 | 146779.25 | 2574.8054 | 9.8368 | [5 empty] | 110.0767 | 2574.8054 |  | 104.98
14.01.2008 07:00 | 3600 | 2 | 760.57 | GGB | 763.37 | 767.906 | 768.864 | 269.76 | GGB | 11174.8 | GGB | 9.83 | GGB | 1020.42 | GGB | 58.07 | GGB | 175952.81 | GGB | 146154.95 | GGB | 0 | 0 | 2765 | 3600 | 2749.7 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 113825.46 | GGB | 113826.81 | 2749.7 | 2585.8036 |  |  |  | 0 | 1 | [14 empty] | 111.634 | 2585.8036 |  | 104.98
14.01.2008 08:00 | 3600 | 2 | 760.32 | GGB | 764.469 | 767.953 | 768.864 | 271.11 | GGB | 11179.4 | GGB | 9.82 | GGB | 1020.52 | GGB | 57.39 | GGB | 177866.3 | GGB | 148061.94 | GGB | 0 | 0 | 2774 | 3600 | 2758.41 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 113865.15 | GGB | 113866.5 | 2758.41 | 2552.4993 |  |  |  | 1 | 1 |  |  |  |  | 148061.94 | 2552.4993 | 148061.94 | 2552.4993 | 9.522 | [5 empty] | 113.4488 | 2552.4993 |  | 104.98
14.01.2008 09:00 | 3600 | 2 | 761.21 | GGB | 763.37 | 766.664 | 767.766 | 269.87 | GGB | 11224.6 | GGB | 9.85 | GGB | 1020.6 | GGB | 57.5 | GGB | 176482.07 | GGB | 146870.62 | GGB | 0 | 0 | 2748 | 3600 | 2732.79 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 113903.28 | GGB | 113904.63 | 2732.79 | 2573.2035 |  |  |  | 0 | 1 | [14 empty] | 111.4907 | 2573.2035 |  | 104.98
14.01.2008 10:00 | 3600 | 2 | 760.08 | GGB | 763.37 | 766.641 | 767.766 | 270.89 | GGB | 11186.2 | GGB | 9.82 | GGB | 1020.99 | GGB | 57.05 | GGB | 178002.74 | GGB | 148396.29 | GGB | 0 | 0 | 2775 | 3600 | 2759.38 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 113944.45 | GGB | 113945.81 | 2759.38 | 2546.7483 |  |  |  | 0 | 1 | [14 empty] | 113.7449 | 2546.7483 |  | 104.98
14.01.2008 11:00 | 3600 | 2 | 760.85 | GGB | 763.37 | 767.531 | 767.766 | 270.98 | GGB | 11188.7 | GGB | 9.84 | GGB | 1021.31 | GGB | 56.81 | GGB | 178596.92 | GGB | 149045.76 | GGB | 0 | 0 | 2729 | 3600 | 2713.15 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 113982.95 | GGB | 113984.31 | 2713.15 | 2535.6508 |  |  |  | 0 | 1 | [14 empty] | 112.3288 | 2535.6508 |  | 104.98
14.01.2008 12:00 | 3600 | 2 | 761.54 | GGB | 762.271 | 766.5 | 767.766 | 268.86 | GGB | 11199.7 | GGB | 9.85 | GGB | 1021.29 | GGB | 57.54 | GGB | 176094.75 | GGB | 146632.92 | GGB | 0 | 0 | 2710 | 3600 | 2694.33 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 114023.82 | GGB | 114025.18 | 2694.33 | 2577.3748 |  |  |  | 0 | 1 | [14 empty] | 109.7437 | 2577.3748 |  | 104.98
14.01.2008 13:00 | 3600 | 2 | 761.08 | GGB | 763.37 | 767.578 | 767.766 | 267.36 | GGB | 11157.3 | GGB | 9.84 | GGB | 1020.35 | GGB | 58 | GGB | 174681.92 | GGB | 145116.61 | GGB | 0 | 0 | 2715 | 3600 | 2699.18 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 114062.77 | GGB | 114064.13 | 2699.18 | 2604.3056 |  |  |  | 0 | 1 | [14 empty] | 108.8044 | 2604.3056 |  | 104.98
14.01.2008 14:00 | 3600 | 2 | 762.04 | GGB | 764.835 | 769.781 | 769.963 | 267.44 | GGB | 11079.6 | GGB | 9.85 | GGB | 1019.43 | GGB | 57.81 | GGB | 175195.78 | GGB | 145499.76 | GGB | 0 | 0 | 2652 | 3600 | 2636.44 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 114103.13 | GGB | 114104.49 | 2636.44 | 2597.4476 |  |  |  | 1 | 1 |  |  |  |  | 145499.76 | 2597.4476 | 145499.76 | 2597.4476 | 9.3639 | [5 empty] | 106.5559 | 2597.4476 |  | 104.98
14.01.2008 15:00 | 3600 | 2 | 762.14 | GGB | 764.835 | 769.852 | 770.33 | 265.61 | GGB | 11028.2 | GGB | 9.84 | GGB | 1018.46 | GGB | 58.26 | GGB | 173144.75 | GGB | 143461.67 | GGB | 0 | 0 | 2619 | 3600 | 2603.68 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 114144.01 | GGB | 114145.37 | 2603.68 | 2603.68 |  |  |  | 1 | 1 |  |  |  |  | 143461.67 | 2603.68 | 143461.67 | 2603.68 | 9.1372 | [5 empty] | 103.7579 |  |  | #VALUE!
14.01.2008 16:00 | 3600 | 2 | 760.97 | GGB | 762.271 | 767.695 | 767.766 | 265.14 | GGB | 11016.7 | GGB | 9.82 | GGB | 1017.49 | GGB | 58.63 | GGB | 172139.04 | GGB | 142336.14 | GGB | 0 | 0 | 2671 | 3600 | 2655.8 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 114184.1 | GGB | 114185.45 | 2655.8 | 2655.1795 |  |  |  | 0 | 1 | [14 empty] | 105.0045 | 2655.1795 |  | 104.98
14.01.2008 17:00 | 3600 | 2 | 761.08 | GGB | 764.469 | 768.563 | 769.963 | 267.43 | GGB | 11019.2 | GGB | 9.83 | GGB | 1017.09 | GGB | 57.91 | GGB | 174717.13 | GGB | 144724.8 | GGB | 0 | 0 | 2663 | 3600 | 2647.98 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 114225.57 | GGB | 114226.92 | 2647.98 | 2611.3562 |  |  |  | 1 | 1 |  |  |  |  | 144724.8 | 2611.3562 | 144724.8 | 2611.3562 | 9.1133 | [5 empty] | 106.4523 | 2611.3562 |  | 104.98
14.01.2008 18:00 | 3600 | 2 | 761.43 | GGB | 763.37 | 767.695 | 768.864 | 266.27 | GGB | 11068 | GGB | 9.84 | GGB | 1016.8 | GGB | 58.19 | GGB | 173387.92 | GGB | 143458.26 | GGB | 0 | 0 | 2672 | 3600 | 2657.04 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 114264.67 | GGB | 114266.02 | 2657.04 | 2634.4109 |  |  |  | 0 | 1 | [14 empty] | 105.8818 | 2634.4109 |  | 104.98
14.01.2008 19:00 | 3600 | 2 | 761.12 | GGB | 764.469 | 768.773 | 769.963 | 267.11 | GGB | 11033.8 | GGB | 9.83 | GGB | 1016.31 | GGB | 57.86 | GGB | 174506.97 | GGB | 144459.75 | GGB | 0 | 0 | 2664 | 3600 | 2649.1 | GGB | 100 | GGB | 42.23 | GGB | 42.23 | GGB | 114306.9 | GGB | 114308.25 | 2649.1 | 2616.1474 |  |  |  | 1 | 1 |  |  |  |  | 144459.75 | 2616.1474 | 144459.75 | 2616.1474 | 8.9493 | [5 empty] | 106.3023 | 2616.1474 |  | 104.98
14.01.2008 20:00 | 3600 | 2 | 761.2 | GGB | 764.102 | 768.914 | 768.864 | 267.27 | GGB | 11029.9 | GGB | 9.83 | GGB | 1016.05 | GGB | 57.82 | GGB | 174629.1 | GGB | 144542.65 | GGB | 0 | 0 | 2658 | 3600 | 2642.57 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 114346.21 | GGB | 114347.56 | 2642.57 | 2614.647 |  |  |  | 1 | 1 |  |  |  |  | 144542.65 | 2614.647 | 144542.65 | 2614.647 | 9.614 | [5 empty] | 106.1011 | 2614.647 |  | 104.98
14.01.2008 21:00 | 3600 | 2 | 761.74 | GGB | 766.3 | 770.086 | 769.963 | 265.34 | GGB | 11089.2 | GGB | 9.85 | GGB | 1015.7 | GGB | 58.34 | GGB | 172889.47 | GGB | 142826.35 | GGB | 0 | 0 | 2667 | 3600 | 2651.45 | GGB | 100 | GGB | 42.21 | GGB | 42.21 | GGB | 114388.42 | GGB | 114389.77 | 2651.45 | 2646.0664 |  |  |  | 1 | 1 |  |  |  |  | 142826.35 | 2646.0664 | 142826.35 | 2646.0664 | 8.9535 | [5 empty] | 105.1936 | 2646.0664 |  | 104.98
14.01.2008 22:00 | 3600 | 2 | 760.38 | GGB | 765.201 | 768.914 | 768.864 | 267.78 | GGB | 11028.2 | GGB | 9.82 | GGB | 1015.24 | GGB | 57.53 | GGB | 175082.44 | GGB | 144929.69 | GGB | 0 | 0 | 2701 | 3600 | 2685.8 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 114428.35 | GGB | 114429.7 | 2685.8 | 2607.6644 |  |  |  | 1 | 1 |  |  |  |  | 144929.69 | 2607.6644 | 144929.69 | 2607.6644 | 9.4648 | [5 empty] | 108.1256 | 2607.6644 |  | 104.98
14.01.2008 23:00 | 3600 | 2 | 761.88 | GGB | 765.201 | 769.148 | 768.864 | 267.57 | GGB | 11081.7 | GGB | 9.84 | GGB | 1015.57 | GGB | 57.84 | GGB | 174362.82 | GGB | 144243.06 | GGB | 0 | 0 | 2667 | 3600 | 2651.89 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 114469.13 | GGB | 114470.48 | 2651.89 | 2620.0775 |  |  |  | 1 | 1 |  |  |  |  | 144243.06 | 2620.0775 | 144243.06 | 2620.0775 | 9.2675 | [5 empty] | 106.2546 | 2620.0775 |  | 104.98
14.01.2008 24:00 | 3600 | 2 | 760.97 | GGB | 763.004 | 766.922 | 768.132 | 266.79 | GGB | 11099.3 | GGB | 9.84 | GGB | 1015.25 | GGB | 58.12 | GGB | 173645.4 | GGB | 143483.9 | GGB | 0 | 0 | 2706 | 3600 | 2690.78 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 114509.51 | GGB | 114510.86 | 2690.78 | 2633.9401 |  |  |  | 0 | 1 | [14 empty] | 107.2454 | 2633.9401 |  | 104.98
15.01.2008 01:00 | 3600 | 2 | 760.92 | GGB | 764.102 | 768.047 | 768.132 | 265.85 | GGB | 11084.5 | GGB | 9.83 | GGB | 1014.65 | GGB | 58.11 | GGB | 173126.04 | GGB | 142973.57 | GGB | 0 | 0 | 2696 | 3600 | 2680.79 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 114550.25 | GGB | 114551.61 | 2680.79 | 2643.3417 |  |  |  | 1 | 1 |  |  |  |  | 142973.57 | 2643.3417 | 142973.57 | 2643.3417 | 9.2743 | [5 empty] | 106.4673 | 2643.3417 |  | 104.98
15.01.2008 02:00 | 3600 | 2 | 760.69 | GGB | 765.201 | 769.266 | 769.597 | 267.72 | GGB | 11062.3 | GGB | 9.82 | GGB | 1014.84 | GGB | 57.53 | GGB | 175312.41 | GGB | 145061.02 | GGB | 0 | 0 | 2705 | 3600 | 2689.13 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 114591 | GGB | 114592.36 | 2689.13 | 2605.3036 |  |  |  | 1 | 1 |  |  |  |  | 145061.02 | 2605.3036 | 145061.02 | 2605.3036 | 9.2743 | [5 empty] | 108.3578 | 2605.3036 |  | 104.98
15.01.2008 03:00 | 3600 | 2 | 761.35 | GGB | 765.201 | 769.195 | 770.696 | 268.06 | GGB | 11090.5 | GGB | 9.84 | GGB | 1014.33 | GGB | 57.22 | GGB | 175726.14 | GGB | 145468.05 | GGB | 0 | 0 | 2673 | 3600 | 2657.41 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 114631.05 | GGB | 114632.41 | 2657.41 | 2598.0138 |  |  |  | 1 | 1 |  |  |  |  | 145468.05 | 2598.0138 | 145468.05 | 2598.0138 | 9.4364 | [5 empty] | 107.3801 | 2598.0138 |  | 104.98
15.01.2008 04:00 | 3600 | 2 | 760.73 | GGB | 762.637 | 767.063 | 767.033 | 267.68 | GGB | 11098.4 | GGB | 9.82 | GGB | 1013.99 | GGB | 57.49 | GGB | 175190.28 | GGB | 144857.76 | GGB | 0 | 0 | 2716 | 3600 | 2700.32 | GGB | 100 | GGB | 41.25 | GGB | 41.25 | GGB | 114672.3 | GGB | 114673.66 | 2700.32 | 2608.9593 |  |  |  | 0 | 1 | [14 empty] | 108.6562 | 2608.9593 |  | 104.98
15.01.2008 05:00 | 3600 | 2 | 761.23 | GGB | 763.004 | 767.977 | 767.033 | 267.75 | GGB | 11138.9 | GGB | 9.84 | GGB | 1013.93 | GGB | 57.12 | GGB | 175513.77 | GGB | 145278.43 | GGB | 0 | 0 | 2691 | 3600 | 2675.89 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 114712.3 | GGB | 114713.66 | 2675.89 | 2601.4048 |  |  |  | 0 | 1 | [14 empty] | 107.9859 | 2601.4048 |  | 104.98
15.01.2008 06:00 | 3600 | 2 | 760.32 | GGB | 764.102 | 768.023 | 768.498 | 269.13 | GGB | 11110.4 | GGB | 9.82 | GGB | 1013.45 | GGB | 56.57 | GGB | 177417.36 | GGB | 147030.01 | GGB | 0 | 0 | 2734 | 3600 | 2718.46 | GGB | 100 | GGB | 41.49 | GGB | 41.49 | GGB | 114753.79 | GGB | 114755.15 | 2718.46 | 2570.414 |  |  |  | 1 | 1 |  |  |  |  | 147030.01 | 2570.414 | 147030.01 | 2570.414 | 9.1089 | [5 empty] | 111.0264 | 2570.414 |  | 104.98
15.01.2008 07:00 | 3600 | 2 | 761.42 | GGB | 765.201 | 769.313 | 769.597 | 268.47 | GGB | 11162 | GGB | 9.85 | GGB | 1013.61 | GGB | 56.47 | GGB | 176781.36 | GGB | 146569.72 | GGB | 0 | 0 | 2690 | 3600 | 2675.04 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 114793.75 | GGB | 114795.12 | 2675.04 | 2578.4862 |  |  |  | 1 | 1 |  |  |  |  | 146569.72 | 2578.4862 | 146569.72 | 2578.4862 | 9.4553 | [5 empty] | 108.9111 | 2578.4862 |  | 104.98
15.01.2008 08:00 | 3600 | 2 | 760.63 | GGB | 765.201 | 769.406 | 768.498 | 267.06 | GGB | 11165.8 | GGB | 9.83 | GGB | 1013.59 | GGB | 56.92 | GGB | 175199.08 | GGB | 145057.74 | GGB | 0 | 0 | 2732 | 3600 | 2717 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 114835.12 | GGB | 114836.48 | 2717 | 2605.3625 |  |  |  | 1 | 1 |  |  |  |  | 145057.74 | 2605.3625 | 145057.74 | 2605.3625 | 9.1375 | [5 empty] | 109.4783 | 2605.3625 |  | 104.98
15.01.2008 09:00 | 3600 | 2 | 760.63 | GGB | 763.004 | 767.32 | 767.033 | 267.06 | GGB | 11153.5 | GGB | 9.83 | GGB | 1013.59 | GGB | 56.87 | GGB | 175375.13 | GGB | 145225.91 | GGB | 0 | 0 | 2730 | 3600 | 2714.62 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 114875.94 | GGB | 114877.31 | 2714.62 | 2602.3455 |  |  |  | 0 | 1 | [14 empty] | 109.5092 | 2602.3455 |  | 104.98
15.01.2008 10:00 | 3600 | 2 | 761.15 | GGB | 764.102 | 768.258 | 768.498 | 268.34 | GGB | 11108.6 | GGB | 9.84 | GGB | 1013.9 | GGB | 56.44 | GGB | 176839.68 | GGB | 146673.63 | GGB | 0 | 0 | 2696 | 3600 | 2680.28 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 114916.69 | GGB | 114918.05 | 2680.28 | 2576.6595 |  |  |  | 1 | 1 |  |  |  |  | 146673.63 | 2576.6595 | 146673.63 | 2576.6595 | 9.2766 | [5 empty] | 109.2018 | 2576.6595 |  | 104.98
15.01.2008 11:00 | 3600 | 2 | 761.47 | GGB | 765.201 | 769.383 | 769.597 | 267.54 | GGB | 11089.5 | GGB | 9.84 | GGB | 1013.75 | GGB | 56.98 | GGB | 175210.08 | GGB | 145062.27 | GGB | 0 | 0 | 2671 | 3600 | 2656.11 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 114957.26 | GGB | 114958.62 | 2656.11 | 2605.2812 |  |  |  | 1 | 1 |  |  |  |  | 145062.27 | 2605.2812 | 145062.27 | 2605.2812 | 9.3155 | [5 empty] | 107.0282 | 2605.2812 |  | 104.98
15.01.2008 12:00 | 3600 | 2 | 761.03 | GGB | 764.102 | 767.18 | 768.132 | 266.2 | GGB | 11056.1 | GGB | 9.83 | GGB | 1013.31 | GGB | 57.83 | GGB | 173339.51 | GGB | 143083.87 | GGB | 0 | 0 | 2680 | 3600 | 2665.09 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 114997.78 | GGB | 114999.14 | 2665.09 | 2641.304 |  |  |  | 1 | 1 |  |  |  |  | 143083.87 | 2641.304 | 143083.87 | 2641.304 | 9.3269 | [5 empty] | 105.9254 | 2641.304 |  | 104.98
15.01.2008 13:00 | 3600 | 2 | 761.39 | GGB | 764.102 | 769.359 | 768.498 | 266.82 | GGB | 11013.6 | GGB | 9.84 | GGB | 1012.56 | GGB | 57.5 | GGB | 174221.98 | GGB | 143846.6 | GGB | 0 | 0 | 2644 | 3600 | 2628.19 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 115038.82 | GGB | 115040.19 | 2628.19 | 2627.2988 |  |  |  | 1 | 1 |  |  |  |  | 143846.6 | 2627.2988 | 143846.6 | 2627.2988 | 9.2065 | [5 empty] | 105.0156 | 2627.2988 |  | 104.98
15.01.2008 14:00 | 3600 | 2 | 761.74 | GGB | 764.102 | 768.305 | 769.597 | 265.07 | GGB | 11015.4 | GGB | 9.84 | GGB | 1011.8 | GGB | 58.19 | GGB | 171872.76 | GGB | 141506.27 | GGB | 0 | 0 | 2642 | 3600 | 2626.5 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 115078.76 | GGB | 115080.13 | 2626.5 | 2626.5 |  |  |  | 1 | 1 |  |  |  |  | 141506.27 | 2626.5 | 141506.27 | 2626.5 | 9.3056 | [5 empty] | 103.2406 |  |  | #VALUE!
15.01.2008 15:00 | 3600 | 2 | 761.46 | GGB | 764.102 | 768.094 | 769.597 | 264.5 | GGB | 10996 | GGB | 9.84 | GGB | 1011.69 | GGB | 58.58 | GGB | 170602.97 | GGB | 140281.04 | GGB | 0 | 0 | 2654 | 3600 | 2638.15 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 115119.51 | GGB | 115120.88 | 2638.15 | 2638.15 |  |  |  | 1 | 1 |  |  |  |  | 140281.04 | 2638.15 | 140281.04 | 2638.15 | 9.0818 | [5 empty] | 102.8007 |  |  | #VALUE!
15.01.2008 16:00 | 3600 | 2 | 761.35 | GGB | 765.201 | 769.453 | 769.597 | 264.66 | GGB | 10982.7 | GGB | 9.83 | GGB | 1011.72 | GGB | 58.77 | GGB | 170450.02 | GGB | 140079.73 | GGB | 0 | 0 | 2656 | 3600 | 2640.88 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 115158.94 | GGB | 115160.31 | 2640.88 | 2640.88 |  |  |  | 1 | 1 |  |  |  |  | 140079.73 | 2640.88 | 140079.73 | 2640.88 | 9.382 | [5 empty] | 102.7594 |  |  | #VALUE!
15.01.2008 17:00 | 3600 | 2 | 761.33 | GGB | 764.102 | 769.266 | 768.498 | 264.79 | GGB | 10978 | GGB | 9.83 | GGB | 1011.56 | GGB | 58.93 | GGB | 170306.98 | GGB | 139872.48 | GGB | 0 | 0 | 2653 | 3600 | 2637.76 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 115199.66 | GGB | 115201.02 | 2637.76 | 2637.76 |  |  |  | 1 | 1 |  |  |  |  | 139872.48 | 2637.76 | 139872.48 | 2637.76 | 9.0629 | [5 empty] | 102.4861 |  |  | #VALUE!
15.01.2008 18:00 | 3600 | 2 | 761.43 | GGB | 764.102 | 768.094 | 768.498 | 264.83 | GGB | 10975.1 | GGB | 9.83 | GGB | 1011.27 | GGB | 59 | GGB | 170388.4 | GGB | 139868.44 | GGB | 0 | 0 | 2656 | 3600 | 2640.86 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 115239.05 | GGB | 115240.42 | 2640.86 | 2640.86 |  |  |  | 1 | 1 |  |  |  |  | 139868.44 | 2640.86 | 139868.44 | 2640.86 | 9.3749 | [5 empty] | 102.6036 |  |  | #VALUE!
15.01.2008 19:00 | 3600 | 2 | 761.53 | GGB | 765.201 | 769.289 | 769.597 | 264.86 | GGB | 10977.6 | GGB | 9.84 | GGB | 1011.24 | GGB | 59.09 | GGB | 170155.13 | GGB | 139637.19 | GGB | 0 | 0 | 2651 | 3600 | 2635.91 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 115279.93 | GGB | 115281.3 | 2635.91 | 2635.91 |  |  |  | 1 | 1 |  |  |  |  | 139637.19 | 2635.91 | 139637.19 | 2635.91 | 9.0037 | [5 empty] | 102.242 |  |  | #VALUE!
15.01.2008 20:00 | 3600 | 2 | 761.47 | GGB | 764.102 | 769.266 | 768.498 | 264.84 | GGB | 10968.4 | GGB | 9.83 | GGB | 1010.98 | GGB | 59.06 | GGB | 170287.17 | GGB | 139718.93 | GGB | 0 | 0 | 2653 | 3600 | 2637.33 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 115319.43 | GGB | 115320.8 | 2637.33 | 2637.33 |  |  |  | 1 | 1 |  |  |  |  | 139718.93 | 2637.33 | 139718.93 | 2637.33 | 9.3287 | [5 empty] | 102.3569 |  |  | #VALUE!
15.01.2008 21:00 | 3600 | 2 | 761.67 | GGB | 765.201 | 769.406 | 769.597 | 264.27 | GGB | 10977.9 | GGB | 9.84 | GGB | 1010.64 | GGB | 59.12 | GGB | 170214.55 | GGB | 139590.36 | GGB | 0 | 0 | 2642 | 3600 | 2626.3 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 115360.04 | GGB | 115361.41 | 2626.3 | 2626.3 |  |  |  | 1 | 1 |  |  |  |  | 139590.36 | 2626.3 | 139590.36 | 2626.3 | 9.0275 | [5 empty] | 101.835 |  |  | #VALUE!
15.01.2008 22:00 | 3600 | 2 | 761.5 | GGB | 764.102 | 769.43 | 768.498 | 263.94 | GGB | 10952.3 | GGB | 9.83 | GGB | 1010.33 | GGB | 59.06 | GGB | 169757.91 | GGB | 139196.67 | GGB | 0 | 0 | 2645 | 3600 | 2629.99 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 115399.82 | GGB | 115401.18 | 2629.99 | 2629.99 |  |  |  | 1 | 1 |  |  |  |  | 139196.67 | 2629.99 | 139196.67 | 2629.99 | 9.2051 | [5 empty] | 101.6905 |  |  | #VALUE!
15.01.2008 23:00 | 3600 | 2 | 761.41 | GGB | 764.102 | 769.43 | 768.498 | 263.91 | GGB | 10943.4 | GGB | 9.83 | GGB | 1010.05 | GGB | 59.18 | GGB | 169651.17 | GGB | 139020.27 | GGB | 0 | 0 | 2645 | 3600 | 2629.19 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 115440.42 | GGB | 115441.78 | 2629.19 | 2629.19 |  |  |  | 1 | 1 |  |  |  |  | 139020.27 | 2629.19 | 139020.27 | 2629.19 | 9.0027 | [5 empty] | 101.5308 |  |  | #VALUE!
15.01.2008 24:00 | 3600 | 2 | 761.6 | GGB | 764.102 | 768.352 | 768.498 | 263.98 | GGB | 10935.5 | GGB | 9.83 | GGB | 1009.69 | GGB | 59.16 | GGB | 169871.24 | GGB | 139161.2 | GGB | 0 | 0 | 2635 | 3600 | 2619.72 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 115480.38 | GGB | 115481.74 | 2619.72 | 2619.72 |  |  |  | 1 | 1 |  |  |  |  | 139161.2 | 2619.72 | 139161.2 | 2619.72 | 9.1232 | [5 empty] | 101.2676 |  |  | #VALUE!
16.01.2008 01:00 | 3600 | 2 | 761.58 | GGB | 765.201 | 769.43 | 769.597 | 265.39 | GGB | 10911.7 | GGB | 9.83 | GGB | 1009.36 | GGB | 58.42 | GGB | 172021.3 | GGB | 141189.75 | GGB | 0 | 0 | 2622 | 3600 | 2606.46 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 115521.47 | GGB | 115522.83 | 2606.46 | 2606.46 |  |  |  | 1 | 1 |  |  |  |  | 141189.75 | 2606.46 | 141189.75 | 2606.46 | 8.9561 | [5 empty] | 102.2237 |  |  | #VALUE!
16.01.2008 02:00 | 3600 | 2 | 762.49 | GGB | 764.102 | 769.43 | 768.498 | 264.27 | GGB | 10938.6 | GGB | 9.85 | GGB | 1009.14 | GGB | 58.7 | GGB | 170770.22 | GGB | 140014.42 | GGB | 0 | 0 | 2602 | 3600 | 2586.28 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 115561.11 | GGB | 115562.47 | 2586.28 | 2586.28 |  |  |  | 1 | 1 |  |  |  |  | 140014.42 | 2586.28 | 140014.42 | 2586.28 | 9.1351 | [5 empty] | 100.5879 |  |  | #VALUE!
16.01.2008 03:00 | 3600 | 2 | 761.21 | GGB | 765.201 | 769.43 | 768.498 | 264.72 | GGB | 10904.5 | GGB | 9.83 | GGB | 1008.71 | GGB | 58.53 | GGB | 171426.02 | GGB | 140564.45 | GGB | 0 | 0 | 2630 | 3600 | 2614.35 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 115601.6 | GGB | 115602.96 | 2614.35 | 2614.35 |  |  |  | 1 | 1 |  |  |  |  | 140564.45 | 2614.35 | 140564.45 | 2614.35 | 9.0759 | [5 empty] | 102.0791 |  |  | #VALUE!
16.01.2008 04:00 | 3600 | 2 | 761.94 | GGB | 764.102 | 768.492 | 768.132 | 264.18 | GGB | 10922.9 | GGB | 9.83 | GGB | 1008.64 | GGB | 58.78 | GGB | 170619.47 | GGB | 139789.37 | GGB | 0 | 0 | 2621 | 3600 | 2606 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 115641.11 | GGB | 115642.47 | 2606 | 2606 |  |  |  | 1 | 1 |  |  |  |  | 139789.37 | 2606 | 139789.37 | 2606 | 9.2202 | [5 empty] | 101.192 |  |  | #VALUE!
16.01.2008 05:00 | 3600 | 2 | 762.08 | GGB | 765.201 | 769.383 | 769.597 | 265.03 | GGB | 10908.8 | GGB | 9.84 | GGB | 1008.36 | GGB | 58.36 | GGB | 171935.48 | GGB | 141007.61 | GGB | 0 | 0 | 2602 | 3600 | 2586.57 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 115681.5 | GGB | 115682.86 | 2586.57 | 2586.57 |  |  |  | 1 | 1 |  |  |  |  | 141007.61 | 2586.57 | 141007.61 | 2586.57 | 9.0301 | [5 empty] | 101.3128 |  |  | #VALUE!
16.01.2008 06:00 | 3600 | 2 | 762.19 | GGB | 764.102 | 768.445 | 768.498 | 263.92 | GGB | 10931.3 | GGB | 9.84 | GGB | 1007.79 | GGB | 58.75 | GGB | 170536.95 | GGB | 139616.8 | GGB | 0 | 0 | 2610 | 3600 | 2594.98 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 115720.96 | GGB | 115722.31 | 2594.98 | 2594.98 |  |  |  | 1 | 1 |  |  |  |  | 139616.8 | 2594.98 | 139616.8 | 2594.98 | 9.1838 | [5 empty] | 100.6397 |  |  | #VALUE!
16.01.2008 07:00 | 3600 | 2 | 761.62 | GGB | 764.102 | 768.609 | 768.498 | 265 | GGB | 10905.2 | GGB | 9.83 | GGB | 1007.58 | GGB | 58.26 | GGB | 172123.63 | GGB | 141094.35 | GGB | 0 | 0 | 2618 | 3600 | 2602.81 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 115761.47 | GGB | 115762.83 | 2602.81 | 2602.81 |  |  |  | 1 | 1 |  |  |  |  | 141094.35 | 2602.81 | 141094.35 | 2602.81 | 9.0632 | [5 empty] | 102.0116 |  |  | #VALUE!
16.01.2008 08:00 | 3600 | 2 | 762.24 | GGB | 763.004 | 768.586 | 768.498 | 264.07 | GGB | 10935.8 | GGB | 9.84 | GGB | 1007.36 | GGB | 58.56 | GGB | 170769.12 | GGB | 139826.79 | GGB | 0 | 0 | 2615 | 3600 | 2599.76 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 115801.01 | GGB | 115802.37 | 2599.76 | 2599.76 |  |  |  | 0 | 1 | [14 empty] | 100.9767 |  |  | #VALUE!
16.01.2008 09:00 | 3600 | 2 | 761.72 | GGB | 765.201 | 769.617 | 768.498 | 264.95 | GGB | 10908.8 | GGB | 9.83 | GGB | 1007.74 | GGB | 58.17 | GGB | 172279.88 | GGB | 141281.24 | GGB | 0 | 0 | 2624 | 3600 | 2608.83 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 115841.51 | GGB | 115842.87 | 2608.83 | 2608.83 |  |  |  | 1 | 1 |  |  |  |  | 141281.24 | 2608.83 | 141281.24 | 2608.83 | 9.1007 | [5 empty] | 102.383 |  |  | #VALUE!
16.01.2008 10:00 | 3600 | 2 | 762.29 | GGB | 765.201 | 769.781 | 769.597 | 264.76 | GGB | 10910 | GGB | 9.84 | GGB | 1008.06 | GGB | 58.24 | GGB | 171823.24 | GGB | 140922.25 | GGB | 0 | 0 | 2598 | 3600 | 2583.14 | GGB | 100 | GGB | 41.16 | GGB | 41.16 | GGB | 115882.67 | GGB | 115884.03 | 2583.14 | 2583.14 |  |  |  | 1 | 1 |  |  |  |  | 140922.25 | 2583.14 | 140922.25 | 2583.14 | 8.8441 | [5 empty] | 101.1172 |  |  | #VALUE!
16.01.2008 11:00 | 3600 | 2 | 762.2 | GGB | 765.201 | 769.805 | 769.597 | 263.98 | GGB | 10893.4 | GGB | 9.83 | GGB | 1007.85 | GGB | 58.22 | GGB | 171594.37 | GGB | 140714.09 | GGB | 0 | 0 | 2597 | 3600 | 2582.01 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 115922.71 | GGB | 115924.07 | 2582.01 | 2582.01 |  |  |  | 1 | 1 |  |  |  |  | 140714.09 | 2582.01 | 140714.09 | 2582.01 | 9.0741 | [5 empty] | 100.9237 |  |  | #VALUE!
16.01.2008 12:00 | 3600 | 2 | 763.05 | GGB | 764.102 | 768.563 | 768.498 | 263.14 | GGB | 10909.1 | GGB | 9.84 | GGB | 1007.33 | GGB | 58.03 | GGB | 171642.79 | GGB | 140761.98 | GGB | 0 | 0 | 2573 | 3600 | 2557.28 | GGB | 100 | GGB | 41.94 | GGB | 41.94 | GGB | 115964.65 | GGB | 115966.01 | 2557.28 | 2557.28 |  |  |  | 1 | 1 |  |  |  |  | 140761.98 | 2557.28 | 140761.98 | 2557.28 | 8.5829 | [5 empty] | 99.9911 |  |  | #VALUE!
16.01.2008 13:00 | 3600 | 2 | 763.03 | GGB | 765.201 | 769.688 | 769.597 | 262.44 | GGB | 10888.1 | GGB | 9.84 | GGB | 1006.79 | GGB | 57.97 | GGB | 171054.11 | GGB | 140229.77 | GGB | 0 | 0 | 2565 | 3600 | 2549.24 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 116004.82 | GGB | 116006.18 | 2549.24 | 2549.24 |  |  |  | 1 | 1 |  |  |  |  | 140229.77 | 2549.24 | 140229.77 | 2549.24 | 8.8992 | [5 empty] | 99.2998 |  |  | #VALUE!
16.01.2008 14:00 | 3600 | 2 | 762.83 | GGB | 765.201 | 769.641 | 769.597 | 261.94 | GGB | 10867.9 | GGB | 9.84 | GGB | 1006.42 | GGB | 58.04 | GGB | 170457.72 | GGB | 139659.29 | GGB | 0 | 0 | 2559 | 3600 | 2543.67 | GGB | 100 | GGB | 42.03 | GGB | 42.03 | GGB | 116046.84 | GGB | 116048.21 | 2543.67 | 2543.67 |  |  |  | 1 | 1 |  |  |  |  | 139659.29 | 2543.67 | 139659.29 | 2543.67 | 8.4522 | [5 empty] | 98.6798 |  |  | #VALUE!
16.01.2008 15:00 | 3600 | 2 | 762.84 | GGB | 765.201 | 769.688 | 769.597 | 260.48 | GGB | 10872.1 | GGB | 9.84 | GGB | 1006.2 | GGB | 58.46 | GGB | 168601.45 | GGB | 137935.34 | GGB | 0 | 0 | 2566 | 3600 | 2550.33 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 116086.22 | GGB | 116087.59 | 2550.33 | 2550.33 |  |  |  | 1 | 1 |  |  |  |  | 137935.34 | 2550.33 | 137935.34 | 2550.33 | 8.933 | [5 empty] | 97.7168 |  |  | #VALUE!
16.01.2008 16:00 | 3600 | 2 | 761.82 | GGB | 764.102 | 768.656 | 768.864 | 261.94 | GGB | 10838.2 | GGB | 9.82 | GGB | 1006.1 | GGB | 58.34 | GGB | 169954.87 | GGB | 139077.74 | GGB | 0 | 0 | 2583 | 3600 | 2568.11 | GGB | 100 | GGB | 42.74 | GGB | 42.74 | GGB | 116128.96 | GGB | 116130.33 | 2568.11 | 2568.11 |  |  |  | 1 | 1 |  |  |  |  | 139077.74 | 2568.11 | 139077.74 | 2568.11 | 8.3567 | [5 empty] | 99.213 |  |  | #VALUE!
16.01.2008 17:00 | 3600 | 2 | 762.52 | GGB | 764.102 | 768.656 | 768.864 | 261.62 | GGB | 10887.9 | GGB | 9.84 | GGB | 1006.34 | GGB | 58.39 | GGB | 169522.44 | GGB | 138734.09 | GGB | 0 | 0 | 2581 | 3600 | 2565.76 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 116167.9 | GGB | 116169.27 | 2565.76 | 2565.76 |  |  |  | 1 | 1 |  |  |  |  | 138734.09 | 2565.76 | 138734.09 | 2565.76 | 9.1412 | [5 empty] | 98.8773 |  |  | #VALUE!
16.01.2008 18:00 | 3600 | 2 | 761.39 | GGB | 764.102 | 769.688 | 768.864 | 262.57 | GGB | 10881.3 | GGB | 9.82 | GGB | 1006.93 | GGB | 58.14 | GGB | 170596.36 | GGB | 139799.35 | GGB | 0 | 0 | 2609 | 3600 | 2593.37 | GGB | 100 | GGB | 43.03 | GGB | 43.03 | GGB | 116210.93 | GGB | 116212.3 | 2593.37 | 2593.37 |  |  |  | 1 | 1 |  |  |  |  | 139799.35 | 2593.37 | 139799.35 | 2593.37 | 8.4256 | [5 empty] | 100.7087 |  |  | #VALUE!
16.01.2008 19:00 | 3600 | 2 | 762.6 | GGB | 765.201 | 769.688 | 769.963 | 262.93 | GGB | 10905.1 | GGB | 9.84 | GGB | 1007.17 | GGB | 57.97 | GGB | 171177.34 | GGB | 140384.13 | GGB | 0 | 0 | 2582 | 3600 | 2566.34 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 116250.18 | GGB | 116251.55 | 2566.34 | 2566.34 |  |  |  | 1 | 1 |  |  |  |  | 140384.13 | 2566.34 | 140384.13 | 2566.34 | 9.1789 | [5 empty] | 100.0759 |  |  | #VALUE!
16.01.2008 20:00 | 3600 | 2 | 761.85 | GGB | 764.102 | 768.586 | 767.766 | 262.17 | GGB | 10921.1 | GGB | 9.83 | GGB | 1007.09 | GGB | 58.18 | GGB | 170223.35 | GGB | 139500.25 | GGB | 0 | 0 | 2614 | 3600 | 2598.99 | GGB | 100 | GGB | 42.53 | GGB | 42.53 | GGB | 116292.72 | GGB | 116294.08 | 2598.99 | 2598.99 |  |  |  | 1 | 1 |  |  |  |  | 139500.25 | 2598.99 | 139500.25 | 2598.99 | 8.5248 | [5 empty] | 100.711 |  |  | #VALUE!
16.01.2008 21:00 | 3600 | 2 | 761.86 | GGB | 766.3 | 770.883 | 769.963 | 262.87 | GGB | 10935.6 | GGB | 9.83 | GGB | 1007.63 | GGB | 57.5 | GGB | 171815.54 | GGB | 141172.28 | GGB | 0 | 0 | 2610 | 3600 | 2595.08 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 116332.67 | GGB | 116334.03 | 2595.08 | 2595.08 |  |  |  | 1 | 1 |  |  |  |  | 141172.28 | 2595.08 | 141172.28 | 2595.08 | 9.1703 | [5 empty] | 101.7648 |  |  | #VALUE!
16.01.2008 22:00 | 3600 | 2 | 762.31 | GGB | 765.201 | 771.117 | 769.597 | 263.4 | GGB | 10921.3 | GGB | 9.84 | GGB | 1008.12 | GGB | 58.08 | GGB | 171597.67 | GGB | 140811.47 | GGB | 0 | 0 | 2594 | 3600 | 2578.66 | GGB | 100 | GGB | 42.32 | GGB | 42.32 | GGB | 116374.99 | GGB | 116376.35 | 2578.66 | 2578.66 |  |  |  | 1 | 1 |  |  |  |  | 140811.47 | 2578.66 | 140811.47 | 2578.66 | 8.58 | [5 empty] | 100.8625 |  |  | #VALUE!
16.01.2008 23:00 | 3600 | 2 | 762.11 | GGB | 764.102 | 769.031 | 768.498 | 262.32 | GGB | 10946.4 | GGB | 9.84 | GGB | 1007.91 | GGB | 58.21 | GGB | 170260.76 | GGB | 139634.3 | GGB | 0 | 0 | 2608 | 3600 | 2592.95 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 116415.15 | GGB | 116416.51 | 2592.95 | 2592.95 |  |  |  | 1 | 1 |  |  |  |  | 139634.3 | 2592.95 | 139634.3 | 2592.95 | 9.0156 | [5 empty] | 100.5735 |  |  | #VALUE!
16.01.2008 24:00 | 3600 | 2 | 761.45 | GGB | 764.102 | 768.68 | 768.498 | 262.19 | GGB | 10959.2 | GGB | 9.83 | GGB | 1008.61 | GGB | 58.28 | GGB | 169943.86 | GGB | 139441.98 | GGB | 0 | 0 | 2637 | 3600 | 2621.48 | GGB | 100 | GGB | 42.24 | GGB | 42.24 | GGB | 116457.39 | GGB | 116458.75 | 2621.48 | 2621.48 |  |  |  | 1 | 1 |  |  |  |  | 139441.98 | 2621.48 | 139441.98 | 2621.48 | 8.654 | [5 empty] | 101.5401 |  |  | #VALUE!
17.01.2008 01:00 | 3600 | 2 | 761.68 | GGB | 765.201 | 769.852 | 769.597 | 262.26 | GGB | 10953.8 | GGB | 9.84 | GGB | 1008.79 | GGB | 58.28 | GGB | 169998.88 | GGB | 139508.68 | GGB | 0 | 0 | 2625 | 3600 | 2609.96 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 116498.03 | GGB | 116499.39 | 2609.96 | 2609.96 |  |  |  | 1 | 1 |  |  |  |  | 139508.68 | 2609.96 | 139508.68 | 2609.96 | 8.9595 | [5 empty] | 101.1422 |  |  | #VALUE!
17.01.2008 02:00 | 3600 | 2 | 761.42 | GGB | 764.102 | 768.586 | 768.132 | 262.91 | GGB | 10926.6 | GGB | 9.83 | GGB | 1008.9 | GGB | 58.06 | GGB | 171065.11 | GGB | 140495.45 | GGB | 0 | 0 | 2626 | 3600 | 2610.6 | GGB | 100 | GGB | 41.6 | GGB | 41.6 | GGB | 116539.63 | GGB | 116540.99 | 2610.6 | 2610.6 |  |  |  | 1 | 1 |  |  |  |  | 140495.45 | 2610.6 | 140495.45 | 2610.6 | 8.8168 | [5 empty] | 101.8826 |  |  | #VALUE!
17.01.2008 03:00 | 3600 | 2 | 761.89 | GGB | 763.004 | 767.719 | 767.033 | 263.07 | GGB | 10945.7 | GGB | 9.83 | GGB | 1009.54 | GGB | 58.17 | GGB | 170717.4 | GGB | 140252.83 | GGB | 0 | 0 | 2618 | 3600 | 2602.77 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 116580.41 | GGB | 116581.77 | 2602.77 | 2602.77 |  |  |  | 0 | 1 | [14 empty] | 101.4016 |  |  | #VALUE!
17.01.2008 04:00 | 3600 | 2 | 762.14 | GGB | 766.3 | 769.828 | 770.696 | 264.43 | GGB | 10955.9 | GGB | 9.84 | GGB | 1010.35 | GGB | 57.91 | GGB | 172384.41 | GGB | 141845.3 | GGB | 0 | 0 | 2619 | 3600 | 2603.34 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 116619.89 | GGB | 116621.25 | 2603.34 | 2603.34 |  |  |  | 1 | 1 |  |  |  |  | 141845.3 | 2603.34 | 141845.3 | 2603.34 | 9.3534 | [5 empty] | 102.5754 |  |  | #VALUE!
17.01.2008 05:00 | 3600 | 2 | 761.86 | GGB | 765.201 | 769.828 | 768.498 | 262.95 | GGB | 10987.5 | GGB | 9.84 | GGB | 1010.29 | GGB | 58.34 | GGB | 170532.55 | GGB | 140129.77 | GGB | 0 | 0 | 2629 | 3600 | 2613.8 | GGB | 100 | GGB | 42.83 | GGB | 42.83 | GGB | 116662.71 | GGB | 116664.08 | 2613.8 | 2613.8 |  |  |  | 1 | 1 |  |  |  |  | 140129.77 | 2613.8 | 140129.77 | 2613.8 | 8.5517 | [5 empty] | 101.742 |  |  | #VALUE!
17.01.2008 06:00 | 3600 | 2 | 761.43 | GGB | 764.469 | 768.75 | 768.132 | 263 | GGB | 10982.7 | GGB | 9.83 | GGB | 1010.51 | GGB | 58.22 | GGB | 170793.33 | GGB | 140427.84 | GGB | 0 | 0 | 2650 | 3600 | 2634.78 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 116702.86 | GGB | 116704.23 | 2634.78 | 2634.78 |  |  |  | 1 | 1 |  |  |  |  | 140427.84 | 2634.78 | 140427.84 | 2634.78 | 9.2154 | [5 empty] | 102.7768 |  |  | #VALUE!
17.01.2008 07:00 | 3600 | 2 | 761.47 | GGB | 764.835 | 769.828 | 768.498 | 263.4 | GGB | 10986.8 | GGB | 9.83 | GGB | 1011.37 | GGB | 58.22 | GGB | 170995.79 | GGB | 140711.77 | GGB | 0 | 0 | 2647 | 3600 | 2631.66 | GGB | 100 | GGB | 42.47 | GGB | 42.47 | GGB | 116745.33 | GGB | 116746.7 | 2631.66 | 2631.66 |  |  |  | 1 | 1 |  |  |  |  | 140711.77 | 2631.66 | 140711.77 | 2631.66 | 8.7192 | [5 empty] | 102.8626 |  |  | #VALUE!
17.01.2008 08:00 | 3600 | 2 | 761.69 | GGB | 763.37 | 767.953 | 767.033 | 264.12 | GGB | 10983.1 | GGB | 9.84 | GGB | 1012.29 | GGB | 58.12 | GGB | 171626.28 | GGB | 141403.01 | GGB | 0 | 0 | 2646 | 3600 | 2630.16 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 116786.03 | GGB | 116787.39 | 2630.16 | 2630.16 |  |  |  | 0 | 1 | [14 empty] | 103.309 |  |  | #VALUE!
17.01.2008 09:00 | 3600 | 2 | 761.17 | GGB | 763.37 | 769.008 | 768.498 | 263.79 | GGB | 10998.4 | GGB | 9.83 | GGB | 1012.66 | GGB | 58.27 | GGB | 171103.62 | GGB | 140960.31 | GGB | 0 | 0 | 2672 | 3600 | 2656.93 | GGB | 100 | GGB | 42.09 | GGB | 42.09 | GGB | 116828.12 | GGB | 116829.48 | 2656.93 | 2656.93 |  |  |  | 0 | 1 | [14 empty] | 104.0338 |  |  | #VALUE!
17.01.2008 10:00 | 3600 | 2 | 761.06 | GGB | 763.37 | 767.883 | 767.033 | 264.17 | GGB | 11004.4 | GGB | 9.83 | GGB | 1013.1 | GGB | 58.25 | GGB | 171642.79 | GGB | 141471.97 | GGB | 0 | 0 | 2675 | 3600 | 2660.09 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 116868.81 | GGB | 116870.17 | 2660.09 | 2660.09 |  |  |  | 0 | 1 | [14 empty] | 104.5356 |  |  | #VALUE!
17.01.2008 11:00 | 3600 | 2 | 761.91 | GGB | 765.934 | 770.109 | 769.597 | 264.94 | GGB | 11006.5 | GGB | 9.84 | GGB | 1013.46 | GGB | 57.89 | GGB | 172671.6 | GGB | 142526.52 | GGB | 0 | 0 | 2654 | 3600 | 2638.42 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 116908.06 | GGB | 116909.42 | 2638.42 | 2638.42 |  |  |  | 1 | 1 |  |  |  |  | 142526.52 | 2638.42 | 142526.52 | 2638.42 | 9.5808 | [5 empty] | 104.4569 |  |  | #VALUE!
17.01.2008 12:00 | 3600 | 2 | 761.63 | GGB | 764.835 | 770.086 | 768.498 | 264.23 | GGB | 11006.7 | GGB | 9.83 | GGB | 1014.04 | GGB | 58.38 | GGB | 171355.6 | GGB | 141312.7 | GGB | 0 | 0 | 2661 | 3600 | 2645.39 | GGB | 100 | GGB | 43.08 | GGB | 43.08 | GGB | 116951.14 | GGB | 116952.5 | 2645.39 | 2645.39 |  |  |  | 1 | 1 |  |  |  |  | 141312.7 | 2645.39 | 141312.7 | 2645.39 | 8.6775 | [5 empty] | 103.8409 |  |  | #VALUE!
17.01.2008 13:00 | 3600 | 2 | 761.74 | GGB | 764.469 | 769.078 | 768.498 | 263.83 | GGB | 10999.3 | GGB | 9.84 | GGB | 1013.88 | GGB | 58.48 | GGB | 171045.3 | GGB | 140992.92 | GGB | 0 | 0 | 2657 | 3600 | 2641.31 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 116990.89 | GGB | 116992.25 | 2641.31 | 2641.31 |  |  |  | 1 | 1 |  |  |  |  | 140992.92 | 2641.31 | 140992.92 | 2641.31 | 9.3687 | [5 empty] | 103.4461 |  |  | #VALUE!
17.01.2008 14:00 | 3600 | 2 | 761.98 | GGB | 764.469 | 769.031 | 768.498 | 263.79 | GGB | 10989.3 | GGB | 9.84 | GGB | 1013.83 | GGB | 58.53 | GGB | 170774.62 | GGB | 140741.7 | GGB | 0 | 0 | 2646 | 3600 | 2630.24 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 117032.53 | GGB | 117033.89 | 2630.24 | 2630.24 |  |  |  | 1 | 1 |  |  |  |  | 140741.7 | 2630.24 | 140741.7 | 2630.24 | 8.8901 | [5 empty] | 102.829 |  |  | #VALUE!
17.01.2008 15:00 | 3600 | 2 | 761.98 | GGB | 763.37 | 767.883 | 767.033 | 263.93 | GGB | 10981.9 | GGB | 9.84 | GGB | 1013.79 | GGB | 58.72 | GGB | 170191.44 | GGB | 140175.66 | GGB | 0 | 0 | 2645 | 3600 | 2630.09 | GGB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 117073.86 | GGB | 117075.22 | 2630.09 | 2630.09 |  |  |  | 0 | 1 | [14 empty] | 102.4096 |  |  | #VALUE!
17.01.2008 16:00 | 3600 | 2 | 761.53 | GGB | 764.835 | 769.008 | 769.597 | 264.92 | GGB | 10952 | GGB | 9.83 | GGB | 1013.85 | GGB | 59.11 | GGB | 170234.35 | GGB | 140053.38 | GGB | 0 | 0 | 2656 | 3600 | 2640.85 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 117113.84 | GGB | 117115.2 | 2640.85 | 2640.85 |  |  |  | 1 | 1 |  |  |  |  | 140053.38 | 2640.85 | 140053.38 | 2640.85 | 9.2511 | [5 empty] | 102.7389 |  |  | #VALUE!
17.01.2008 17:00 | 3600 | 2 | 761.46 | GGB | 764.469 | 769.008 | 768.132 | 265.55 | GGB | 10950.4 | GGB | 9.83 | GGB | 1014.17 | GGB | 59.36 | GGB | 170115.52 | GGB | 139894.63 | GGB | 0 | 0 | 2672 | 3600 | 2656.54 | GGB | 100 | GGB | 42.62 | GGB | 42.62 | GGB | 117156.46 | GGB | 117157.82 | 2656.54 | 2656.54 |  |  |  | 1 | 1 |  |  |  |  | 139894.63 | 2656.54 | 139894.63 | 2656.54 | 8.7197 | [5 empty] | 103.2321 |  |  | #VALUE!
17.01.2008 18:00 | 3600 | 2 | 761.75 | GGB | 764.835 | 770.086 | 768.498 | 266.07 | GGB | 10970.5 | GGB | 9.84 | GGB | 1014.42 | GGB | 59.38 | GGB | 170137.52 | GGB | 139938.17 | GGB | 0 | 0 | 2664 | 3600 | 2648.79 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 117196.3 | GGB | 117197.67 | 2648.79 | 2648.79 |  |  |  | 1 | 1 |  |  |  |  | 139938.17 | 2648.79 | 139938.17 | 2648.79 | 9.3016 | [5 empty] | 102.963 |  |  | #VALUE!
17.01.2008 19:00 | 3600 | 2 | 761.9 | GGB | 764.835 | 768.961 | 768.498 | 266.47 | GGB | 10959.1 | GGB | 9.83 | GGB | 1014.18 | GGB | 59.76 | GGB | 170037.39 | GGB | 139662.4 | GGB | 0 | 0 | 2672 | 3600 | 2656.53 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 117236.22 | GGB | 117237.59 | 2656.53 | 2656.53 |  |  |  | 1 | 1 |  |  |  |  | 139662.4 | 2656.53 | 139662.4 | 2656.53 | 9.294 | [5 empty] | 103.0604 |  |  | #VALUE!
17.01.2008 20:00 | 3600 | 2 | 761.91 | GGB | 764.835 | 769.828 | 768.498 | 266.72 | GGB | 10949.9 | GGB | 9.83 | GGB | 1014.53 | GGB | 59.98 | GGB | 169869.04 | GGB | 139482.35 | GGB | 0 | 0 | 2671 | 3600 | 2655.76 | GGB | 100 | GGB | 42.12 | GGB | 42.12 | GGB | 117278.34 | GGB | 117279.71 | 2655.76 | 2655.76 |  |  |  | 1 | 1 |  |  |  |  | 139482.35 | 2655.76 | 139482.35 | 2655.76 | 8.7947 | [5 empty] | 102.8977 |  |  | #VALUE!
17.01.2008 21:00 | 3600 | 2 | 762.45 | GGB | 764.835 | 768.727 | 768.498 | 265.85 | GGB | 10964.5 | GGB | 9.84 | GGB | 1014.24 | GGB | 59.81 | GGB | 170082.51 | GGB | 139687.6 | GGB | 0 | 0 | 2650 | 3600 | 2634.98 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 117318.75 | GGB | 117320.12 | 2634.98 | 2634.98 |  |  |  | 1 | 1 |  |  |  |  | 139687.6 | 2634.98 | 139687.6 | 2634.98 | 9.1085 | [5 empty] | 102.2428 |  |  | #VALUE!
17.01.2008 22:00 | 3600 | 2 | 761.75 | GGB | 763.37 | 768.516 | 767.033 | 266.93 | GGB | 10914.6 | GGB | 9.82 | GGB | 1014.36 | GGB | 59.82 | GGB | 170577.66 | GGB | 140108.13 | GGB | 0 | 0 | 2662 | 3600 | 2646.15 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 117358.79 | GGB | 117360.17 | 2646.15 | 2646.15 |  |  |  | 0 | 1 | [14 empty] | 102.9853 |  |  | #VALUE!
17.01.2008 23:00 | 3600 | 2 | 762.81 | GGB | 764.469 | 769.641 | 768.498 | 265.99 | GGB | 10943.1 | GGB | 9.85 | GGB | 1014.24 | GGB | 59.98 | GGB | 169723.8 | GGB | 139320.36 | GGB | 0 | 0 | 2629 | 3600 | 2613.9 | GGB | 100 | GGB | 42.26 | GGB | 42.26 | GGB | 117401.05 | GGB | 117402.43 | 2613.9 | 2613.9 |  |  |  | 1 | 1 |  |  |  |  | 139320.36 | 2613.9 | 139320.36 | 2613.9 | 8.6174 | [5 empty] | 101.1582 |  |  | #VALUE!
17.01.2008 24:00 | 3600 | 2 | 762.16 | GGB | 764.835 | 769.641 | 769.597 | 265.82 | GGB | 10917.8 | GGB | 9.83 | GGB | 1014.23 | GGB | 60.24 | GGB | 169355.18 | GGB | 138911.17 | GGB | 0 | 0 | 2648 | 3600 | 2632.55 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 117440.53 | GGB | 117441.91 | 2632.55 | 2632.55 |  |  |  | 1 | 1 |  |  |  |  | 138911.17 | 2632.55 | 138911.17 | 2632.55 | 9.2627 | [5 empty] | 101.5807 |  |  | #VALUE!
18.01.2008 01:00 | 3600 | 2 | 762.2 | GGB | 764.835 | 769.688 | 768.498 | 266.8 | GGB | 10898.4 | GGB | 9.83 | GGB | 1014.01 | GGB | 59.62 | GGB | 171022.2 | GGB | 140507.49 | GGB | 0 | 0 | 2642 | 3600 | 2626.59 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 117481.76 | GGB | 117483.14 | 2626.59 | 2626.59 |  |  |  | 1 | 1 |  |  |  |  | 140507.49 | 2626.59 | 140507.49 | 2626.59 | 8.9511 | [5 empty] | 102.5154 |  |  | #VALUE!
18.01.2008 02:00 | 3600 | 2 | 762.61 | GGB | 764.469 | 768.586 | 768.132 | 265.72 | GGB | 10935.5 | GGB | 9.84 | GGB | 1013.74 | GGB | 59.77 | GGB | 169302.37 | GGB | 138996.45 | GGB | 0 | 0 | 2644 | 3600 | 2628.54 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 117522.49 | GGB | 117523.88 | 2628.54 | 2628.54 |  |  |  | 1 | 1 |  |  |  |  | 138996.45 | 2628.54 | 138996.45 | 2628.54 | 8.968 | [5 empty] | 101.4883 |  |  | #VALUE!
18.01.2008 03:00 | 3600 | 2 | 761.56 | GGB | 764.835 | 769.852 | 768.498 | 267.03 | GGB | 10902.4 | GGB | 9.83 | GGB | 1013.77 | GGB | 59.33 | GGB | 170928.67 | GGB | 140520.21 | GGB | 0 | 0 | 2656 | 3600 | 2640.92 | GGB | 100 | GGB | 41.08 | GGB | 41.08 | GGB | 117563.58 | GGB | 117564.96 | 2640.92 | 2640.92 |  |  |  | 1 | 1 |  |  |  |  | 140520.21 | 2640.92 | 140520.21 | 2640.92 | 9.0337 | [5 empty] | 103.0841 |  |  | #VALUE!
18.01.2008 04:00 | 3600 | 2 | 762.81 | GGB | 764.835 | 769.852 | 768.498 | 267.4 | GGB | 10901 | GGB | 9.84 | GGB | 1013.72 | GGB | 59.28 | GGB | 171421.62 | GGB | 140941.83 | GGB | 0 | 0 | 2616 | 3600 | 2600.89 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 117602.69 | GGB | 117604.08 | 2600.89 | 2600.89 |  |  |  | 1 | 1 |  |  |  |  | 140941.83 | 2600.89 | 140941.83 | 2600.89 | 9.3705 | [5 empty] | 101.8262 |  |  | #VALUE!
18.01.2008 05:00 | 3600 | 2 | 762.22 | GGB | 764.469 | 769.805 | 769.597 | 267.09 | GGB | 10896.2 | GGB | 9.83 | GGB | 1013.65 | GGB | 59.38 | GGB | 171103.62 | GGB | 140627.81 | GGB | 0 | 0 | 2634 | 3600 | 2618.18 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 117643.37 | GGB | 117644.75 | 2618.18 | 2618.18 |  |  |  | 1 | 1 |  |  |  |  | 140627.81 | 2618.18 | 140627.81 | 2618.18 | 9.0531 | [5 empty] | 102.2747 |  |  | #VALUE!
18.01.2008 06:00 | 3600 | 2 | 762.67 | GGB | 764.469 | 769.523 | 768.498 | 265.36 | GGB | 10928.6 | GGB | 9.84 | GGB | 1013.16 | GGB | 60.14 | GGB | 169003.08 | GGB | 138517.08 | GGB | 0 | 0 | 2639 | 3600 | 2623.96 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 117684.51 | GGB | 117685.89 | 2623.96 | 2623.96 |  |  |  | 1 | 1 |  |  |  |  | 138517.08 | 2623.96 | 138517.08 | 2623.96 | 8.8348 | [5 empty] | 100.962 |  |  | #VALUE!
18.01.2008 07:00 | 3600 | 2 | 762.16 | GGB | 764.469 | 769.453 | 768.498 | 265.29 | GGB | 10919.6 | GGB | 9.84 | GGB | 1013.13 | GGB | 60.12 | GGB | 169319.97 | GGB | 138778.05 | GGB | 0 | 0 | 2650 | 3600 | 2634.41 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 117725.24 | GGB | 117726.61 | 2634.41 | 2634.41 |  |  |  | 1 | 1 |  |  |  |  | 138778.05 | 2634.41 | 138778.05 | 2634.41 | 8.9783 | [5 empty] | 101.5551 |  |  | #VALUE!
18.01.2008 08:00 | 3600 | 2 | 761.93 | GGB | 763.37 | 768.352 | 767.033 | 265.98 | GGB | 10906.4 | GGB | 9.83 | GGB | 1013.07 | GGB | 59.95 | GGB | 169785.42 | GGB | 139222.4 | GGB | 0 | 0 | 2657 | 3208 | 2642.1 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 117764.79 | GGB | 117766.16 | 2642.1 | 2642.1 |  |  |  | 0 | 1 | [14 empty] | 102.1776 |  |  | #VALUE!
18.01.2008 09:00 | 3600 | 2 | 761.85 | GGB | 764.469 | 769.43 | 768.132 | 267.18 | GGB | 10885.3 | GGB | 9.82 | GGB | 1013.45 | GGB | 59.29 | GGB | 171708.81 | GGB | 141133.56 | GGB | 0 | 0 | 2655 | 3600 | 2639.79 | GGB | 100 | GGB | 42.46 | GGB | 42.46 | GGB | 117807.25 | GGB | 117808.62 | 2639.79 | 2639.79 |  |  |  | 1 | 1 |  |  |  |  | 141133.56 | 2639.79 | 141133.56 | 2639.79 | 8.7744 | [5 empty] | 103.4897 |  |  | #VALUE!
18.01.2008 10:00 | 3600 | 2 | 763.3 | GGB | 765.934 | 769.641 | 769.597 | 266.34 | GGB | 10934.3 | GGB | 9.85 | GGB | 1013.24 | GGB | 59.2 | GGB | 171360 | GGB | 140858 | GGB | 0 | 0 | 2615 | 3600 | 2599.4 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 117846.82 | GGB | 117848.2 | 2599.4 | 2599.4 |  |  |  | 1 | 1 |  |  |  |  | 140858 | 2599.4 | 140858 | 2599.4 | 9.2508 | [5 empty] | 101.7073 |  |  | #VALUE!
18.01.2008 11:00 | 3600 | 2 | 762.54 | GGB | 764.835 | 770.766 | 769.597 | 265.13 | GGB | 10917.7 | GGB | 9.84 | GGB | 1013.4 | GGB | 60.08 | GGB | 169072.4 | GGB | 138631 | GGB | 0 | 0 | 2646 | 3600 | 2631 | GGB | 100 | GGB | 37.96 | GGB | 37.96 | GGB | 117884.79 | GGB | 117886.16 | 2631 | 2631 |  |  |  | 1 | 1 |  |  |  |  | 138631 | 2631 | 138631 | 2631 | 9.6085 | [5 empty] | 101.3162 |  |  | #VALUE!
18.01.2008 12:00 | 3600 | 2 | 762.26 | GGB | 764.835 | 769.477 | 768.498 | 265.13 | GGB | 10891.3 | GGB | 9.83 | GGB | 1013.53 | GGB | 60.38 | GGB | 168376.98 | GGB | 137951.27 | GGB | 0 | 0 | 2646 | 3600 | 2630.32 | GGB | 100 | GGB | 43.67 | GGB | 43.67 | GGB | 117928.46 | GGB | 117929.83 | 2630.32 | 2630.32 |  |  |  | 1 | 1 |  |  |  |  | 137951.27 | 2630.32 | 137951.27 | 2630.32 | 8.309 | [5 empty] | 100.7933 |  |  | #VALUE!
18.01.2008 13:00 | 3600 | 2 | 762.42 | GGB | 763.37 | 768.586 | 767.033 | 265.8 | GGB | 10862.2 | GGB | 9.83 | GGB | 1013.55 | GGB | 60.41 | GGB | 168740.1 | GGB | 138240.65 | GGB | 0 | 0 | 2633 | 3600 | 2617.24 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 117969.09 | GGB | 117970.46 | 2617.24 | 2617.24 |  |  |  | 0 | 1 | [14 empty] | 100.5025 |  |  | #VALUE!
18.01.2008 14:00 | 3600 | 2 | 763 | GGB | 767.033 | 772.008 | 771.795 | 265.93 | GGB | 10881 | GGB | 9.84 | GGB | 1012.74 | GGB | 59.8 | GGB | 170335.58 | GGB | 139695.14 | GGB | 0 | 0 | 2614 | 3600 | 2598.95 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 118009.35 | GGB | 118010.72 | 2598.95 | 2598.95 |  |  |  | 1 | 1 |  |  |  |  | 139695.14 | 2598.95 | 139695.14 | 2598.95 | 9.0179 | [5 empty] | 100.8502 |  |  | #VALUE!
18.01.2008 15:00 | 3600 | 2 | 762.66 | GGB | 764.835 | 769.406 | 768.498 | 263.67 | GGB | 10927.6 | GGB | 9.84 | GGB | 1012.41 | GGB | 59.77 | GGB | 169248.45 | GGB | 138770.01 | GGB | 0 | 0 | 2633 | 3600 | 2617.38 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 118048.87 | GGB | 118050.25 | 2617.38 | 2617.38 |  |  |  | 1 | 1 |  |  |  |  | 138770.01 | 2617.38 | 138770.01 | 2617.38 | 9.1883 | [5 empty] | 100.8927 |  |  | #VALUE!
18.01.2008 16:00 | 3600 | 2 | 761.95 | GGB | 764.469 | 769.453 | 769.597 | 263.59 | GGB | 10930 | GGB | 9.83 | GGB | 1012.35 | GGB | 59.48 | GGB | 169158.22 | GGB | 138807.26 | GGB | 0 | 0 | 2656 | 3600 | 2640.29 | GGB | 100 | GGB | 43.08 | GGB | 43.08 | GGB | 118091.95 | GGB | 118093.33 | 2640.29 | 2640.29 |  |  |  | 1 | 1 |  |  |  |  | 138807.26 | 2640.29 | 138807.26 | 2640.29 | 8.5072 | [5 empty] | 101.8032 |  |  | #VALUE!
18.01.2008 17:00 | 3600 | 2 | 762.22 | GGB | 764.835 | 769.594 | 768.498 | 263.36 | GGB | 10935 | GGB | 9.84 | GGB | 1012.28 | GGB | 59.4 | GGB | 169327.68 | GGB | 138971.12 | GGB | 0 | 0 | 2645 | 3600 | 2629.26 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 118131.28 | GGB | 118132.66 | 2629.26 | 2629.26 |  |  |  | 1 | 1 |  |  |  |  | 138971.12 | 2629.26 | 138971.12 | 2629.26 | 9.2904 | [5 empty] | 101.4976 |  |  | #VALUE!
18.01.2008 18:00 | 3600 | 2 | 762.21 | GGB | 765.934 | 770.766 | 769.597 | 263.32 | GGB | 10925.6 | GGB | 9.84 | GGB | 1012.84 | GGB | 59.28 | GGB | 169261.66 | GGB | 139042.08 | GGB | 0 | 0 | 2639 | 3600 | 2623.32 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 118171.72 | GGB | 118173.1 | 2623.32 | 2623.32 |  |  |  | 1 | 1 |  |  |  |  | 139042.08 | 2623.32 | 139042.08 | 2623.32 | 9.0196 | [5 empty] | 101.32 |  |  | #VALUE!
18.01.2008 19:00 | 3600 | 2 | 762.17 | GGB | 764.835 | 770.672 | 768.498 | 263.93 | GGB | 10896 | GGB | 9.83 | GGB | 1013.09 | GGB | 58.99 | GGB | 170275.07 | GGB | 140031.97 | GGB | 0 | 0 | 2629 | 3600 | 2613.7 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 118211.83 | GGB | 118213.21 | 2613.7 | 2613.7 |  |  |  | 1 | 1 |  |  |  |  | 140031.97 | 2613.7 | 140031.97 | 2613.7 | 9.1249 | [5 empty] | 101.6671 |  |  | #VALUE!
18.01.2008 20:00 | 3600 | 2 | 763.24 | GGB | 767.033 | 772.734 | 771.795 | 263.63 | GGB | 10910 | GGB | 9.85 | GGB | 1012.79 | GGB | 58.61 | GGB | 169740.3 | GGB | 139709.51 | GGB | 0 | 0 | 2597 | 3600 | 2581.26 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 118253.39 | GGB | 118254.77 | 2581.26 | 2581.26 |  |  |  | 1 | 1 |  |  |  |  | 139709.51 | 2581.26 | 139709.51 | 2581.26 | 8.6773 | [5 empty] | 100.174 |  |  | #VALUE!
18.01.2008 21:00 | 3600 | 2 | 762.39 | GGB | 764.835 | 770.555 | 769.597 | 262.86 | GGB | 10880.7 | GGB | 9.83 | GGB | 1012.59 | GGB | 59.62 | GGB | 167810.31 | GGB | 137678.12 | GGB | 0 | 0 | 2623 | 3600 | 2608.03 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 118292.18 | GGB | 118293.56 | 2608.03 | 2608.03 |  |  |  | 1 | 1 |  |  |  |  | 137678.12 | 2608.03 | 137678.12 | 2608.03 | 9.2567 | [5 empty] | 99.7413 |  |  | #VALUE!
18.01.2008 22:00 | 3600 | 2 | 762.43 | GGB | 764.469 | 769.805 | 768.498 | 263.27 | GGB | 10861.4 | GGB | 9.83 | GGB | 1012.51 | GGB | 60.13 | GGB | 167370.17 | GGB | 137092.99 | GGB | 0 | 0 | 2628 | 3600 | 2612.16 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 118333.38 | GGB | 118334.76 | 2612.16 | 2612.16 |  |  |  | 1 | 1 |  |  |  |  | 137092.99 | 2612.16 | 137092.99 | 2612.16 | 8.692 | [5 empty] | 99.4747 |  |  | #VALUE!
18.01.2008 23:00 | 3600 | 2 | 762.27 | GGB | 764.469 | 768.609 | 768.132 | 263.4 | GGB | 10851.2 | GGB | 9.83 | GGB | 1012.85 | GGB | 60.2 | GGB | 168316.47 | GGB | 137888.14 | GGB | 0 | 0 | 2627 | 3600 | 2611.17 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 118373.2 | GGB | 118374.58 | 2611.17 | 2611.17 |  |  |  | 1 | 1 |  |  |  |  | 137888.14 | 2611.17 | 137888.14 | 2611.17 | 9.0419 | [5 empty] | 100.0137 |  |  | #VALUE!
18.01.2008 24:00 | 3600 | 2 | 762.95 | GGB | 765.934 | 770.695 | 769.597 | 265.12 | GGB | 10822.4 | GGB | 9.83 | GGB | 1012.92 | GGB | 60.02 | GGB | 168840.23 | GGB | 138400.18 | GGB | 0 | 0 | 2602 | 3600 | 2586.46 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 118411.97 | GGB | 118413.35 | 2586.46 | 2586.46 |  |  |  | 1 | 1 |  |  |  |  | 138400.18 | 2586.46 | 138400.18 | 2586.46 | 9.2331 | [5 empty] | 99.4351 |  |  | #VALUE!
19.01.2008 01:00 | 3600 | 2 | 763.38 | GGB | 764.835 | 770.695 | 768.498 | 263.95 | GGB | 10842.5 | GGB | 9.84 | GGB | 1012.51 | GGB | 60.69 | GGB | 167381.18 | GGB | 136871.62 | GGB | 0 | 0 | 2600 | 3600 | 2584.67 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 118453 | GGB | 118454.38 | 2584.67 | 2584.67 |  |  |  | 1 | 1 |  |  |  |  | 136871.62 | 2584.67 | 136871.62 | 2584.67 | 8.6222 | [5 empty] | 98.2689 |  |  | #VALUE!
19.01.2008 02:00 | 3600 | 2 | 762.89 | GGB | 767.033 | 771.656 | 769.963 | 265.1 | GGB | 10803.5 | GGB | 9.83 | GGB | 1012 | GGB | 60.02 | GGB | 169135.12 | GGB | 138516.68 | GGB | 0 | 0 | 2596 | 3600 | 2581.01 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 118493.94 | GGB | 118495.32 | 2581.01 | 2581.01 |  |  |  | 1 | 1 |  |  |  |  | 138516.68 | 2581.01 | 138516.68 | 2581.01 | 8.7326 | [5 empty] | 99.3091 |  |  | #VALUE!
19.01.2008 03:00 | 3600 | 2 | 763.64 | GGB | 765.934 | 770.625 | 769.963 | 263.99 | GGB | 10831.9 | GGB | 9.84 | GGB | 1011.52 | GGB | 60.51 | GGB | 167517.62 | GGB | 136926.13 | GGB | 0 | 0 | 2586 | 3600 | 2571.04 | GGB | 100 | GGB | 38.25 | GGB | 38.25 | GGB | 118532.19 | GGB | 118533.57 | 2571.04 | 2571.04 |  |  |  | 1 | 1 |  |  |  |  | 136926.13 | 2571.04 | 136926.13 | 2571.04 | 9.2037 | [5 empty] | 97.7896 |  |  | #VALUE!
19.01.2008 04:00 | 3600 | 2 | 762.83 | GGB | 765.934 | 770.719 | 769.597 | 263.27 | GGB | 10820.1 | GGB | 9.83 | GGB | 1010.61 | GGB | 60.85 | GGB | 166638.45 | GGB | 135943.26 | GGB | 0 | 0 | 2610 | 3600 | 2594.92 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 118572.97 | GGB | 118574.35 | 2594.92 | 2594.92 |  |  |  | 1 | 1 |  |  |  |  | 135943.26 | 2594.92 | 135943.26 | 2594.92 | 8.6504 | [5 empty] | 97.9894 |  |  | #VALUE!
19.01.2008 05:00 | 3600 | 2 | 763.26 | GGB | 765.934 | 770.766 | 769.597 | 262.89 | GGB | 10812.2 | GGB | 9.84 | GGB | 1010.12 | GGB | 60.89 | GGB | 166329.26 | GGB | 135608.32 | GGB | 0 | 0 | 2601 | 3600 | 2585.89 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 118612.41 | GGB | 118613.8 | 2585.89 | 2585.89 |  |  |  | 1 | 1 |  |  |  |  | 135608.32 | 2585.89 | 135608.32 | 2585.89 | 8.8889 | [5 empty] | 97.4078 |  |  | #VALUE!
19.01.2008 06:00 | 3600 | 2 | 763.08 | GGB | 764.835 | 770.766 | 769.597 | 262.51 | GGB | 10793.8 | GGB | 9.83 | GGB | 1009.22 | GGB | 60.89 | GGB | 166121.29 | GGB | 135319.24 | GGB | 0 | 0 | 2597 | 3600 | 2581.27 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 118651.66 | GGB | 118653.05 | 2581.27 | 2581.27 |  |  |  | 1 | 1 |  |  |  |  | 135319.24 | 2581.27 | 135319.24 | 2581.27 | 8.8992 | [5 empty] | 97.0265 |  |  | #VALUE!
19.01.2008 07:00 | 3600 | 2 | 763.18 | GGB | 764.835 | 770.766 | 768.498 | 262.26 | GGB | 10784.5 | GGB | 9.83 | GGB | 1008.08 | GGB | 60.9 | GGB | 165835.2 | GGB | 134929.98 | GGB | 0 | 0 | 2594 | 3600 | 2578.54 | GGB | 100 | GGB | 42.36 | GGB | 42.36 | GGB | 118694.02 | GGB | 118695.41 | 2578.54 | 2578.54 |  |  |  | 1 | 1 |  |  |  |  | 134929.98 | 2578.54 | 134929.98 | 2578.54 | 8.2135 | [5 empty] | 96.6451 |  |  | #VALUE!
19.01.2008 08:00 | 3600 | 2 | 762.97 | GGB | 765.934 | 770.766 | 769.597 | 262.24 | GGB | 10782.7 | GGB | 9.84 | GGB | 1007.35 | GGB | 60.86 | GGB | 165928.73 | GGB | 134925.74 | GGB | 0 | 0 | 2592 | 3600 | 2576.3 | GGB | 100 | GGB | 38.41 | GGB | 38.41 | GGB | 118732.42 | GGB | 118733.82 | 2576.3 | 2576.3 |  |  |  | 1 | 1 |  |  |  |  | 134925.74 | 2576.3 | 134925.74 | 2576.3 | 9.05 | [5 empty] | 96.5581 |  |  | #VALUE!
19.01.2008 09:00 | 3600 | 2 | 763.37 | GGB | 764.835 | 770.648 | 769.597 | 261.26 | GGB | 10764.8 | GGB | 9.84 | GGB | 1005.54 | GGB | 60.84 | GGB | 165308.14 | GGB | 134185.04 | GGB | 0 | 0 | 2577 | 3600 | 2561.51 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 118772.89 | GGB | 118774.29 | 2561.51 | 2561.51 |  |  |  | 1 | 1 |  |  |  |  | 134185.04 | 2561.51 | 134185.04 | 2561.51 | 8.4931 | [5 empty] | 95.4768 |  |  | #VALUE!
19.01.2008 10:00 | 3600 | 2 | 763 | GGB | 764.835 | 770.578 | 769.597 | 260.7 | GGB | 10735.5 | GGB | 9.83 | GGB | 1004.17 | GGB | 60.84 | GGB | 164986.84 | GGB | 133745.26 | GGB | 0 | 0 | 2580 | 3600 | 2564.3 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 118811.9 | GGB | 118813.3 | 2564.3 | 2564.3 |  |  |  | 1 | 1 |  |  |  |  | 133745.26 | 2564.3 | 133745.26 | 2564.3 | 8.7917 | [5 empty] | 95.2675 |  |  | #VALUE!
19.01.2008 11:00 | 3600 | 2 | 762.82 | GGB | 765.934 | 770.484 | 769.597 | 260.43 | GGB | 10741.1 | GGB | 9.84 | GGB | 1003.78 | GGB | 60.2 | GGB | 164591.82 | GGB | 133625.18 | GGB | 0 | 0 | 2578 | 3600 | 2562.85 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 118852.15 | GGB | 118853.55 | 2562.85 | 2562.85 |  |  |  | 1 | 1 |  |  |  |  | 133625.18 | 2562.85 | 133625.18 | 2562.85 | 8.5084 | [5 empty] | 95.1281 |  |  | #VALUE!
19.01.2008 12:00 | 3600 | 2 | 763.01 | GGB | 764.835 | 769.453 | 768.498 | 259.69 | GGB | 10716.6 | GGB | 9.83 | GGB | 1002.48 | GGB | 60.26 | GGB | 164199 | GGB | 133110.02 | GGB | 0 | 0 | 2571 | 3600 | 2555.85 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 118890.61 | GGB | 118892.02 | 2555.85 | 2555.85 |  |  |  | 1 | 1 |  |  |  |  | 133110.02 | 2555.85 | 133110.02 | 2555.85 | 8.8435 | [5 empty] | 94.5026 |  |  | #VALUE!
19.01.2008 13:00 | 3600 | 2 | 762.83 | GGB | 764.835 | 770.578 | 768.498 | 259.42 | GGB | 10729.6 | GGB | 9.84 | GGB | 1001.35 | GGB | 59.81 | GGB | 164139.58 | GGB | 133091.96 | GGB | 0 | 0 | 2573 | 3600 | 2557.94 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 118931.15 | GGB | 118932.55 | 2557.94 | 2557.94 |  |  |  | 1 | 1 |  |  |  |  | 133091.96 | 2557.94 | 133091.96 | 2557.94 | 8.3997 | [5 empty] | 94.567 |  |  | #VALUE!
19.01.2008 14:00 | 3600 | 2 | 762.75 | GGB | 765.934 | 770.719 | 769.597 | 260.62 | GGB | 10684.7 | GGB | 9.83 | GGB | 1001.11 | GGB | 59.58 | GGB | 165744.98 | GGB | 134456.8 | GGB | 0 | 0 | 2553 | 3600 | 2538.13 | GGB | 100 | GGB | 37.46 | GGB | 37.46 | GGB | 118968.6 | GGB | 118970.01 | 2538.13 | 2538.13 |  |  |  | 1 | 1 |  |  |  |  | 134456.8 | 2538.13 | 134456.8 | 2538.13 | 9.1102 | [5 empty] | 94.7969 |  |  | #VALUE!
19.01.2008 15:00 | 3600 | 2 | 763.94 | GGB | 765.934 | 770.531 | 769.597 | 259.21 | GGB | 10702.1 | GGB | 9.85 | GGB | 1000.3 | GGB | 60.03 | GGB | 163915.11 | GGB | 132685.39 | GGB | 0 | 0 | 2526 | 3600 | 2511.09 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 119008.59 | GGB | 119009.99 | 2511.09 | 2511.09 |  |  |  | 1 | 1 |  |  |  |  | 132685.39 | 2511.09 | 132685.39 | 2511.09 | 8.3338 | [5 empty] | 92.5514 |  |  | #VALUE!
19.01.2008 16:00 | 3600 | 2 | 762.79 | GGB | 764.835 | 769.336 | 768.498 | 259.62 | GGB | 10658.5 | GGB | 9.83 | GGB | 1000.08 | GGB | 60.08 | GGB | 164362.95 | GGB | 132997.38 | GGB | 0 | 0 | 2552 | 3600 | 2537.04 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 119048.54 | GGB | 119049.95 | 2537.04 | 2537.04 |  |  |  | 1 | 1 |  |  |  |  | 132997.38 | 2537.04 | 132997.38 | 2537.04 | 8.4439 | [5 empty] | 93.7277 |  |  | #VALUE!
19.01.2008 17:00 | 3600 | 2 | 763.65 | GGB | 764.835 | 769.477 | 768.498 | 260.14 | GGB | 10635 | GGB | 9.83 | GGB | 1000.24 | GGB | 60.02 | GGB | 164979.14 | GGB | 133542.13 | GGB | 0 | 0 | 2518 | 3600 | 2502.67 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 119086.09 | GGB | 119087.5 | 2502.67 | 2502.67 |  |  |  | 1 | 1 |  |  |  |  | 133542.13 | 2502.67 | 133542.13 | 2502.67 | 8.9004 | [5 empty] | 92.8366 |  |  | #VALUE!
19.01.2008 18:00 | 3600 | 2 | 763.77 | GGB | 765.934 | 770.484 | 769.597 | 258.54 | GGB | 10657.5 | GGB | 9.84 | GGB | 1000.09 | GGB | 60.81 | GGB | 162469.27 | GGB | 131179.8 | GGB | 0 | 0 | 2532 | 3600 | 2516.77 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 119127.06 | GGB | 119128.46 | 2516.77 | 2516.77 |  |  |  | 1 | 1 |  |  |  |  | 131179.8 | 2516.77 | 131179.8 | 2516.77 | 8.0603 | [5 empty] | 91.7082 |  |  | #VALUE!
19.01.2008 19:00 | 3600 | 2 | 763.2 | GGB | 764.835 | 769.453 | 768.498 | 259.3 | GGB | 10603 | GGB | 9.83 | GGB | 1000.17 | GGB | 60.83 | GGB | 163232.9 | GGB | 131797.75 | GGB | 0 | 0 | 2526 | 3600 | 2510.68 | GGB | 100 | GGB | 37.62 | GGB | 37.62 | GGB | 119164.67 | GGB | 119166.08 | 2510.68 | 2510.68 |  |  |  | 1 | 1 |  |  |  |  | 131797.75 | 2510.68 | 131797.75 | 2510.68 | 8.7959 | [5 empty] | 91.9172 |  |  | #VALUE!
19.01.2008 20:00 | 3600 | 2 | 762.97 | GGB | 767.033 | 772.758 | 771.795 | 259.54 | GGB | 10631.3 | GGB | 9.83 | GGB | 1000.18 | GGB | 60.39 | GGB | 164049.36 | GGB | 132634.28 | GGB | 0 | 0 | 2538 | 3600 | 2522.52 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 119204.26 | GGB | 119205.66 | 2522.52 | 2522.52 |  |  |  | 1 | 1 |  |  |  |  | 132634.28 | 2522.52 | 132634.28 | 2522.52 | 8.4531 | [5 empty] | 92.9368 |  |  | #VALUE!
19.01.2008 21:00 | 3600 | 2 | 763.36 | GGB | 765.934 | 769.617 | 769.597 | 257.66 | GGB | 10668.1 | GGB | 9.84 | GGB | 1000.49 | GGB | 60.7 | GGB | 162854.39 | GGB | 131584.29 | GGB | 0 | 0 | 2526 | 3600 | 2511.25 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 119243.63 | GGB | 119245.03 | 2511.25 | 2511.25 |  |  |  | 1 | 1 |  |  |  |  | 131584.29 | 2511.25 | 131584.29 | 2511.25 | 8.3932 | [5 empty] | 91.7892 |  |  | #VALUE!
19.01.2008 22:00 | 3600 | 2 | 763.06 | GGB | 763.37 | 768.211 | 767.033 | 257.63 | GGB | 10715.1 | GGB | 9.83 | GGB | 1000.72 | GGB | 60.17 | GGB | 164283.73 | GGB | 132981.49 | GGB | 0 | 0 | 2542 | 3600 | 2526.61 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 119282 | GGB | 119283.4 | 2526.61 | 2526.61 |  |  |  | 0 | 1 | [14 empty] | 93.3312 |  |  | #VALUE!
19.01.2008 23:00 | 3600 | 2 | 762.66 | GGB | 765.934 | 770.438 | 769.597 | 258.6 | GGB | 10750.5 | GGB | 9.84 | GGB | 1000.88 | GGB | 59.64 | GGB | 165202.51 | GGB | 133961.42 | GGB | 0 | 0 | 2565 | 3600 | 2549.62 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 119322.75 | GGB | 119324.15 | 2549.62 | 2549.62 |  |  |  | 1 | 1 |  |  |  |  | 133961.42 | 2549.62 | 133961.42 | 2549.62 | 8.3816 | [5 empty] | 94.8752 |  |  | #VALUE!
19.01.2008 24:00 | 3600 | 2 | 762.31 | GGB | 765.934 | 769.289 | 768.132 | 258.51 | GGB | 10750.7 | GGB | 9.83 | GGB | 1001.07 | GGB | 59.36 | GGB | 165250.92 | GGB | 134137.81 | GGB | 0 | 0 | 2566 | 3600 | 2551.2 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 119361.19 | GGB | 119362.59 | 2551.2 | 2551.2 |  |  |  | 1 | 1 |  |  |  |  | 134137.81 | 2551.2 | 134137.81 | 2551.2 | 8.9025 | [5 empty] | 95.059 |  |  | #VALUE!
20.01.2008 01:00 | 3600 | 2 | 762.2 | GGB | 764.469 | 769.289 | 768.498 | 259.02 | GGB | 10764.7 | GGB | 9.83 | GGB | 1001.34 | GGB | 59.17 | GGB | 165934.23 | GGB | 134804.74 | GGB | 0 | 0 | 2570 | 3600 | 2554.49 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 119400.53 | GGB | 119401.93 | 2554.49 | 2554.49 |  |  |  | 1 | 1 |  |  |  |  | 134804.74 | 2554.49 | 134804.74 | 2554.49 | 8.7534 | [5 empty] | 95.6548 |  |  | #VALUE!
20.01.2008 02:00 | 3600 | 2 | 762.49 | GGB | 764.835 | 769.266 | 768.498 | 260.47 | GGB | 10755.5 | GGB | 9.83 | GGB | 1001.79 | GGB | 58.33 | GGB | 168194.33 | GGB | 137049.71 | GGB | 0 | 0 | 2552 | 3600 | 2536.3 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 119440.55 | GGB | 119441.95 | 2536.3 | 2536.3 |  |  |  | 1 | 1 |  |  |  |  | 137049.71 | 2536.3 | 137049.71 | 2536.3 | 8.6856 | [5 empty] | 96.5553 |  |  | #VALUE!
20.01.2008 03:00 | 3600 | 2 | 762.51 | GGB | 764.835 | 769.43 | 768.498 | 259.34 | GGB | 10796.5 | GGB | 9.84 | GGB | 1002.14 | GGB | 58.59 | GGB | 166834.31 | GGB | 135884.8 | GGB | 0 | 0 | 2564 | 3600 | 2548.4 | GGB | 100 | GGB | 38.35 | GGB | 38.35 | GGB | 119478.9 | GGB | 119480.3 | 2548.4 | 2548.4 |  |  |  | 1 | 1 |  |  |  |  | 135884.8 | 2548.4 | 135884.8 | 2548.4 | 9.0297 | [5 empty] | 96.1913 |  |  | #VALUE!
20.01.2008 04:00 | 3600 | 2 | 762.28 | GGB | 764.469 | 769.547 | 768.498 | 259.7 | GGB | 10789.7 | GGB | 9.83 | GGB | 1002.91 | GGB | 58.52 | GGB | 167224.93 | GGB | 136335.54 | GGB | 0 | 0 | 2571 | 3600 | 2555.66 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 119519.79 | GGB | 119521.19 | 2555.66 | 2555.66 |  |  |  | 1 | 1 |  |  |  |  | 136335.54 | 2555.66 | 136335.54 | 2555.66 | 8.5211 | [5 empty] | 96.7854 |  |  | #VALUE!
20.01.2008 05:00 | 3600 | 2 | 762.74 | GGB | 764.835 | 769.5 | 768.498 | 260.58 | GGB | 10788.5 | GGB | 9.83 | GGB | 1003.29 | GGB | 57.98 | GGB | 168644.37 | GGB | 137770.75 | GGB | 0 | 0 | 2549 | 3600 | 2533.65 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 119558.79 | GGB | 119560.19 | 2533.65 | 2533.65 |  |  |  | 1 | 1 |  |  |  |  | 137770.75 | 2533.65 | 137770.75 | 2533.65 | 8.9503 | [5 empty] | 96.9619 |  |  | #VALUE!
20.01.2008 06:00 | 3600 | 2 | 762.11 | GGB | 763.37 | 768.352 | 767.033 | 259.72 | GGB | 10824.9 | GGB | 9.83 | GGB | 1003.68 | GGB | 58.45 | GGB | 166938.84 | GGB | 136236.39 | GGB | 0 | 0 | 2592 | 3600 | 2576.67 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 119598.1 | GGB | 119599.5 | 2576.67 | 2576.67 |  |  |  | 0 | 1 | [14 empty] | 97.5101 |  |  | #VALUE!
20.01.2008 07:00 | 3600 | 2 | 762.05 | GGB | 764.835 | 769.781 | 768.498 | 260.73 | GGB | 10844.1 | GGB | 9.84 | GGB | 1004.08 | GGB | 58.3 | GGB | 167969.86 | GGB | 137194.23 | GGB | 0 | 0 | 2601 | 3600 | 2585.39 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 119638.9 | GGB | 119640.3 | 2585.39 | 2585.39 |  |  |  | 1 | 1 |  |  |  |  | 137194.23 | 2585.39 | 137194.23 | 2585.39 | 8.6936 | [5 empty] | 98.5279 |  |  | #VALUE!
20.01.2008 08:00 | 3600 | 2 | 762.15 | GGB | 764.835 | 768.727 | 768.498 | 260.96 | GGB | 10833.5 | GGB | 9.84 | GGB | 1004.66 | GGB | 58.34 | GGB | 168045.78 | GGB | 137316.3 | GGB | 0 | 0 | 2593 | 3600 | 2578.04 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 119677.29 | GGB | 119678.68 | 2578.04 | 2578.04 |  |  |  | 1 | 1 |  |  |  |  | 137316.3 | 2578.04 | 137316.3 | 2578.04 | 9.2237 | [5 empty] | 98.3353 |  |  | #VALUE!
20.01.2008 09:00 | 3600 | 2 | 762.35 | GGB | 765.934 | 769.828 | 768.498 | 261.64 | GGB | 10803.7 | GGB | 9.83 | GGB | 1005.17 | GGB | 58.18 | GGB | 169172.53 | GGB | 138377.47 | GGB | 0 | 0 | 2582 | 3600 | 2566.58 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 119718.2 | GGB | 119719.6 | 2566.58 | 2566.58 |  |  |  | 1 | 1 |  |  |  |  | 138377.47 | 2566.58 | 138377.47 | 2566.58 | 8.6793 | [5 empty] | 98.6547 |  |  | #VALUE!
20.01.2008 10:00 | 3600 | 2 | 762.36 | GGB | 763.37 | 768.82 | 767.033 | 261.06 | GGB | 10838.6 | GGB | 9.83 | GGB | 1005.51 | GGB | 58.38 | GGB | 168032.58 | GGB | 137404.67 | GGB | 0 | 0 | 2594 | 3600 | 2578.96 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 119757.2 | GGB | 119758.59 | 2578.96 | 2578.96 |  |  |  | 0 | 1 | [14 empty] | 98.4337 |  |  | #VALUE!
20.01.2008 11:00 | 3600 | 2 | 762.35 | GGB | 764.469 | 768.75 | 768.132 | 260.77 | GGB | 10841.6 | GGB | 9.83 | GGB | 1006.31 | GGB | 58.58 | GGB | 167581.44 | GGB | 137062.45 | GGB | 0 | 0 | 2597 | 3600 | 2581.41 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 119797.28 | GGB | 119798.67 | 2581.41 | 2581.41 |  |  |  | 1 | 1 |  |  |  |  | 137062.45 | 2581.41 | 137062.45 | 2581.41 | 8.8277 | [5 empty] | 98.2818 |  |  | #VALUE!
20.01.2008 12:00 | 3600 | 2 | 762.99 | GGB | 765.934 | 769.898 | 769.597 | 261.61 | GGB | 10816.7 | GGB | 9.83 | GGB | 1006.62 | GGB | 58.17 | GGB | 169170.33 | GGB | 138577.96 | GGB | 0 | 0 | 2563 | 3600 | 2548 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 119837.72 | GGB | 119839.12 | 2548 | 2548 |  |  |  | 1 | 1 |  |  |  |  | 138577.96 | 2548 | 138577.96 | 2548 | 8.7292 | [5 empty] | 98.0824 |  |  | #VALUE!
20.01.2008 13:00 | 3600 | 2 | 763.16 | GGB | 764.835 | 769.828 | 768.498 | 260.51 | GGB | 10833 | GGB | 9.84 | GGB | 1006.77 | GGB | 58.58 | GGB | 167506.62 | GGB | 137065.51 | GGB | 0 | 0 | 2568 | 3600 | 2552.84 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 119875.91 | GGB | 119877.3 | 2552.84 | 2552.84 |  |  |  | 1 | 1 |  |  |  |  | 137065.51 | 2552.84 | 137065.51 | 2552.84 | 9.1646 | [5 empty] | 97.1962 |  |  | #VALUE!
20.01.2008 14:00 | 3600 | 2 | 762.64 | GGB | 764.835 | 769.805 | 768.498 | 259.91 | GGB | 10833.7 | GGB | 9.83 | GGB | 1006.66 | GGB | 58.77 | GGB | 166920.14 | GGB | 136490.83 | GGB | 0 | 0 | 2584 | 3600 | 2568.69 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 119917.55 | GGB | 119918.94 | 2568.69 | 2568.69 |  |  |  | 1 | 1 |  |  |  |  | 136490.83 | 2568.69 | 136490.83 | 2568.69 | 8.4199 | [5 empty] | 97.3896 |  |  | #VALUE!
20.01.2008 15:00 | 3600 | 2 | 762.75 | GGB | 765.934 | 770.133 | 768.132 | 261.24 | GGB | 10795.9 | GGB | 9.83 | GGB | 1006.69 | GGB | 58.18 | GGB | 168906.25 | GGB | 138368 | GGB | 0 | 0 | 2560 | 3600 | 2544.57 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 119956.28 | GGB | 119957.67 | 2544.57 | 2544.57 |  |  |  | 1 | 1 |  |  |  |  | 138368 | 2544.57 | 138368 | 2544.57 | 9.0908 | [5 empty] | 97.802 |  |  | #VALUE!
20.01.2008 16:00 | 3600 | 2 | 763.09 | GGB | 764.835 | 769.992 | 768.498 | 260.39 | GGB | 10831 | GGB | 9.84 | GGB | 1007 | GGB | 58.7 | GGB | 167311.86 | GGB | 136888.89 | GGB | 0 | 0 | 2569 | 3600 | 2553.25 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 119996 | GGB | 119997.4 | 2553.25 | 2553.25 |  |  |  | 1 | 1 |  |  |  |  | 136888.89 | 2553.25 | 136888.89 | 2553.25 | 8.7972 | [5 empty] | 97.0865 |  |  | #VALUE!
20.01.2008 17:00 | 3600 | 2 | 762.04 | GGB | 763.37 | 767.953 | 767.033 | 261.25 | GGB | 10840.3 | GGB | 9.82 | GGB | 1007.21 | GGB | 58.64 | GGB | 168056.79 | GGB | 137551.44 | GGB | 0 | 0 | 2607 | 3600 | 2591.35 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 120036.71 | GGB | 120038.1 | 2591.35 | 2591.35 |  |  |  | 0 | 1 | [14 empty] | 99.0122 |  |  | #VALUE!
20.01.2008 18:00 | 3600 | 2 | 762.33 | GGB | 764.835 | 769.148 | 768.132 | 262.25 | GGB | 10879.2 | GGB | 9.84 | GGB | 1008.01 | GGB | 58.63 | GGB | 168811.62 | GGB | 138283.35 | GGB | 0 | 0 | 2611 | 3600 | 2595.67 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 120075.2 | GGB | 120076.59 | 2595.67 | 2595.67 |  |  |  | 1 | 1 |  |  |  |  | 138283.35 | 2595.67 | 138283.35 | 2595.67 | 9.3255 | [5 empty] | 99.705 |  |  | #VALUE!
20.01.2008 19:00 | 3600 | 2 | 761.45 | GGB | 764.469 | 769.055 | 767.766 | 264.19 | GGB | 10866.6 | GGB | 9.82 | GGB | 1007.99 | GGB | 58.2 | GGB | 171137.73 | GGB | 140367.9 | GGB | 0 | 0 | 2632 | 3600 | 2616.51 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 120116.48 | GGB | 120117.87 | 2616.51 | 2616.51 |  |  |  | 1 | 1 |  |  |  |  | 140367.9 | 2616.51 | 140367.9 | 2616.51 | 8.8971 | [5 empty] | 102.0206 |  |  | #VALUE!
20.01.2008 20:00 | 3600 | 2 | 762.17 | GGB | 764.469 | 768.891 | 767.766 | 263.66 | GGB | 10935.2 | GGB | 9.84 | GGB | 1007.4 | GGB | 58.14 | GGB | 170262.96 | GGB | 139591.6 | GGB | 0 | 0 | 2639 | 3600 | 2623.97 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 120155.4 | GGB | 120156.79 | 2623.97 | 2623.97 |  |  |  | 1 | 1 |  |  |  |  | 139591.6 | 2623.97 | 139591.6 | 2623.97 | 9.4112 | [5 empty] | 101.7456 |  |  | #VALUE!
20.01.2008 21:00 | 3600 | 2 | 761.43 | GGB | 764.469 | 768.727 | 767.766 | 263.98 | GGB | 10936.5 | GGB | 9.83 | GGB | 1007.45 | GGB | 58.38 | GGB | 170368.6 | GGB | 139586.99 | GGB | 0 | 0 | 2672 | 3600 | 2656.34 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 120195.77 | GGB | 120197.17 | 2656.34 | 2656.34 |  |  |  | 1 | 1 |  |  |  |  | 139586.99 | 2656.34 | 139586.99 | 2656.34 | 9.1825 | [5 empty] | 102.9974 |  |  | #VALUE!
20.01.2008 22:00 | 3600 | 2 | 761.4 | GGB | 763.37 | 768.773 | 767.766 | 265.47 | GGB | 10952.5 | GGB | 9.83 | GGB | 1007.04 | GGB | 57.74 | GGB | 172549.46 | GGB | 141588.83 | GGB | 0 | 0 | 2680 | 3600 | 2664.65 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 120236.3 | GGB | 120237.7 | 2664.65 | 2664.65 |  |  |  | 0 | 1 | [14 empty] | 104.8013 |  |  | #VALUE!
20.01.2008 23:00 | 3600 | 2 | 760.85 | GGB | 763.37 | 767.602 | 766.667 | 265.95 | GGB | 10994.8 | GGB | 9.83 | GGB | 1006.41 | GGB | 57.98 | GGB | 172666.1 | GGB | 141495.15 | GGB | 0 | 0 | 2720 | 3600 | 2704.33 | GGB | 100 | GGB | 37.54 | GGB | 37.54 | GGB | 120273.85 | GGB | 120275.24 | 2704.33 | 2670.9608 |  |  |  | 0 | 1 | [14 empty] | 106.2915 | 2670.9608 |  | 104.98
20.01.2008 24:00 | 3600 | 2 | 761.81 | GGB | 764.469 | 768.82 | 767.766 | 266.62 | GGB | 11032.9 | GGB | 9.84 | GGB | 1006.3 | GGB | 57.44 | GGB | 174038.22 | GGB | 142836.73 | GGB | 0 | 0 | 2689 | 3600 | 2674.08 | GGB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 120315.17 | GGB | 120316.57 | 2674.08 | 2645.8741 |  |  |  | 1 | 1 |  |  |  |  | 142836.73 | 2645.8741 | 142836.73 | 2645.8741 | 9.1442 | [5 empty] | 106.0991 | 2645.8741 |  | 104.98
21.01.2008 01:00 | 3600 | 2 | 760.52 | GGB | 762.271 | 767.484 | 766.3 | 266.54 | GGB | 10993.5 | GGB | 9.82 | GGB | 1005.95 | GGB | 57.89 | GGB | 173221.77 | GGB | 141920.83 | GGB | 0 | 0 | 2738 | 3600 | 2722.43 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 120355.84 | GGB | 120357.24 | 2722.43 | 2662.9495 |  |  |  | 0 | 1 | [14 empty] | 107.3249 | 2662.9495 |  | 104.98
21.01.2008 02:00 | 3600 | 2 | 762.23 | GGB | 764.835 | 769.664 | 768.864 | 266.78 | GGB | 10992 | GGB | 9.85 | GGB | 1005.18 | GGB | 57.58 | GGB | 173734.53 | GGB | 142368.45 | GGB | 0 | 0 | 2658 | 3600 | 2642.4 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 120395.92 | GGB | 120397.32 | 2642.4 | 2642.4 |  |  |  | 1 | 1 |  |  |  |  | 142368.45 | 2642.4 | 142368.45 | 2642.4 | 9.3861 | [5 empty] | 104.4984 |  |  | #VALUE!
21.01.2008 03:00 | 3600 | 2 | 761.41 | GGB | 764.469 | 768.445 | 767.766 | 264.73 | GGB | 10968.3 | GGB | 9.84 | GGB | 1004.65 | GGB | 58.37 | GGB | 170886.85 | GGB | 139626.79 | GGB | 0 | 0 | 2686 | 3600 | 2671.08 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 120436.11 | GGB | 120437.51 | 2671.08 | 2671.08 |  |  |  | 1 | 1 |  |  |  |  | 139626.79 | 2671.08 | 139626.79 | 2671.08 | 9.2798 | [5 empty] | 103.5984 |  |  | #VALUE!
21.01.2008 04:00 | 3600 | 2 | 761.54 | GGB | 764.469 | 768.445 | 767.766 | 264.29 | GGB | 10928.2 | GGB | 9.84 | GGB | 1003.91 | GGB | 58.53 | GGB | 170819.73 | GGB | 139399.61 | GGB | 0 | 0 | 2667 | 3600 | 2651.56 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 120476.59 | GGB | 120477.99 | 2651.56 | 2651.56 |  |  |  | 1 | 1 |  |  |  |  | 139399.61 | 2651.56 | 139399.61 | 2651.56 | 9.1311 | [5 empty] | 102.674 |  |  | #VALUE!
21.01.2008 05:00 | 3600 | 2 | 761.38 | GGB | 764.469 | 769.617 | 767.766 | 265.35 | GGB | 10890.4 | GGB | 9.83 | GGB | 1003.41 | GGB | 58.13 | GGB | 172128.04 | GGB | 140567.85 | GGB | 0 | 0 | 2651 | 3600 | 2635.43 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 120516.41 | GGB | 120517.8 | 2635.43 | 2635.43 |  |  |  | 1 | 1 |  |  |  |  | 140567.85 | 2635.43 | 140567.85 | 2635.43 | 9.3056 | [5 empty] | 102.9046 |  |  | #VALUE!
21.01.2008 06:00 | 3600 | 2 | 762.11 | GGB | 764.469 | 768.422 | 767.766 | 263.67 | GGB | 10923.5 | GGB | 9.85 | GGB | 1002.85 | GGB | 58.74 | GGB | 169680.88 | GGB | 138234.94 | GGB | 0 | 0 | 2648 | 3600 | 2632.71 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 120556.38 | GGB | 120557.77 | 2632.71 | 2632.71 |  |  |  | 1 | 1 |  |  |  |  | 138234.94 | 2632.71 | 138234.94 | 2632.71 | 9.1051 | [5 empty] | 101.0924 |  |  | #VALUE!
21.01.2008 07:00 | 3600 | 2 | 761.17 | GGB | 762.271 | 767.367 | 766.667 | 264.05 | GGB | 10889 | GGB | 9.83 | GGB | 1002.4 | GGB | 58.82 | GGB | 170117.72 | GGB | 138496.69 | GGB | 0 | 0 | 2679 | 3600 | 2663.48 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 120596.47 | GGB | 120597.87 | 2663.48 | 2663.48 |  |  |  | 0 | 1 | [14 empty] | 102.4675 |  |  | #VALUE!
21.01.2008 08:00 | 3600 | 2 | 762.67 | GGB | 764.835 | 769.711 | 768.864 | 264.14 | GGB | 10886.3 | GGB | 9.85 | GGB | 1002.28 | GGB | 58.75 | GGB | 170188.14 | GGB | 138568.55 | GGB | 0 | 0 | 2623 | 3600 | 2607.86 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 120636.19 | GGB | 120637.59 | 2607.86 | 2607.86 |  |  |  | 1 | 1 |  |  |  |  | 138568.55 | 2607.86 | 138568.55 | 2607.86 | 9.0979 | [5 empty] | 100.3798 |  |  | #VALUE!
21.01.2008 09:00 | 3600 | 2 | 760.4 | GGB | 764.469 | 769.781 | 768.132 | 265.25 | GGB | 10858.7 | GGB | 9.81 | GGB | 1002.04 | GGB | 58.77 | GGB | 170843.94 | GGB | 139059.84 | GGB | 0 | 0 | 2707 | 3600 | 2691.81 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 120676.28 | GGB | 120677.68 | 2691.81 | 2691.81 |  |  |  | 1 | 1 |  |  |  |  | 139059.84 | 2691.81 | 139059.84 | 2691.81 | 9.3371 | [5 empty] | 103.9785 |  |  | #VALUE!
21.01.2008 10:00 | 3600 | 2 | 761.8 | GGB | 763.37 | 768.938 | 768.132 | 266.73 | GGB | 10893.6 | GGB | 9.84 | GGB | 1000.98 | GGB | 58.19 | GGB | 171947.58 | GGB | 140053.68 | GGB | 0 | 0 | 2653 | 3600 | 2637.15 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 120716.4 | GGB | 120717.8 | 2637.15 | 2637.15 |  |  |  | 0 | 1 | [14 empty] | 102.5952 |  |  | #VALUE!
21.01.2008 11:00 | 3600 | 2 | 761.62 | GGB | 760.806 | 766.195 | 764.469 | 265.04 | GGB | 10877 | GGB | 9.83 | GGB | 1000.58 | GGB | 58.86 | GGB | 169531.24 | GGB | 137753.11 | GGB | 0 | 0 | 2678 | 3600 | 2662.67 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 120756.04 | GGB | 120757.43 | 2662.67 | 2662.67 |  |  |  | 0 | 1 | [14 empty] | 101.8864 |  |  | #VALUE!
21.01.2008 12:00 | 3600 | 2 | 762.95 | GGB | 764.835 | 770.484 | 768.498 | 264.87 | GGB | 10872.8 | GGB | 9.86 | GGB | 999.98 | GGB | 58.79 | GGB | 169738.1 | GGB | 137869.69 | GGB | 0 | 0 | 2614 | 3600 | 2598.7 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 120796.39 | GGB | 120797.78 | 2598.7 | 2598.7 |  |  |  | 1 | 1 |  |  |  |  | 137869.69 | 2598.7 | 137869.69 | 2598.7 | 8.8794 | [5 empty] | 99.5228 |  |  | #VALUE!
21.01.2008 13:00 | 3600 | 2 | 761.89 | GGB | 764.469 | 769.523 | 768.132 | 264.86 | GGB | 10824.5 | GGB | 9.83 | GGB | 999.09 | GGB | 58.71 | GGB | 170050.6 | GGB | 138031.63 | GGB | 0 | 0 | 2639 | 3600 | 2623.76 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 120835.69 | GGB | 120837.08 | 2623.76 | 2623.76 |  |  |  | 1 | 1 |  |  |  |  | 138031.63 | 2623.76 | 138031.63 | 2623.76 | 9.2153 | [5 empty] | 100.6005 |  |  | #VALUE!
21.01.2008 14:00 | 3600 | 2 | 761.9 | GGB | 764.469 | 768.375 | 768.132 | 264.98 | GGB | 10822.7 | GGB | 9.83 | GGB | 998.06 | GGB | 58.32 | GGB | 170567.76 | GGB | 138470.2 | GGB | 0 | 0 | 2626 | 3600 | 2610.93 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 120876.11 | GGB | 120877.51 | 2610.93 | 2610.93 |  |  |  | 1 | 1 |  |  |  |  | 138470.2 | 2610.93 | 138470.2 | 2610.93 | 8.9423 | [5 empty] | 100.4267 |  |  | #VALUE!
21.01.2008 15:00 | 3600 | 2 | 761.89 | GGB | 764.469 | 769.313 | 768.132 | 265.06 | GGB | 10825.9 | GGB | 9.84 | GGB | 997.64 | GGB | 58.3 | GGB | 170630.48 | GGB | 138470.15 | GGB | 0 | 0 | 2629 | 3600 | 2614.12 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 120915.25 | GGB | 120916.65 | 2614.12 | 2614.12 |  |  |  | 1 | 1 |  |  |  |  | 138470.15 | 2614.12 | 138470.15 | 2614.12 | 9.2483 | [5 empty] | 100.5493 |  |  | #VALUE!
21.01.2008 16:00 | 3600 | 2 | 762.15 | GGB | 764.469 | 769.359 | 768.132 | 262.96 | GGB | 10847.9 | GGB | 9.85 | GGB | 996.63 | GGB | 59.16 | GGB | 167904.94 | GGB | 135771.55 | GGB | 0 | 0 | 2630 | 3600 | 2614.18 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 120955.23 | GGB | 120956.63 | 2614.18 | 2614.18 |  |  |  | 1 | 1 |  |  |  |  | 135771.55 | 2614.18 | 135771.55 | 2614.18 | 8.8777 | [5 empty] | 98.592 |  |  | #VALUE!
21.01.2008 17:00 | 3600 | 2 | 761.45 | GGB | 764.469 | 768.328 | 768.132 | 263.2 | GGB | 10793.5 | GGB | 9.83 | GGB | 995.96 | GGB | 59.02 | GGB | 168468.31 | GGB | 136192.52 | GGB | 0 | 0 | 2634 | 3600 | 2618.21 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 120994.98 | GGB | 120996.38 | 2618.21 | 2618.21 |  |  |  | 1 | 1 |  |  |  |  | 136192.52 | 2618.21 | 136192.52 | 2618.21 | 8.9706 | [5 empty] | 99.0502 |  |  | #VALUE!
21.01.2008 18:00 | 3600 | 2 | 762.23 | GGB | 763.37 | 768.023 | 768.132 | 263.5 | GGB | 10773.9 | GGB | 9.84 | GGB | 995 | GGB | 58.69 | GGB | 169321.07 | GGB | 136883.87 | GGB | 0 | 0 | 2600 | 3600 | 2584.61 | GGB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 121036.55 | GGB | 121037.95 | 2584.61 | 2584.61 |  |  |  | 0 | 1 | [14 empty] | 98.2754 |  |  | #VALUE!
21.01.2008 19:00 | 3600 | 2 | 762.39 | GGB | 763.37 | 769.289 | 767.033 | 262.15 | GGB | 10786.7 | GGB | 9.84 | GGB | 994.19 | GGB | 58.95 | GGB | 167593.54 | GGB | 135272.79 | GGB | 0 | 0 | 2600 | 3600 | 2584.78 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 121075.87 | GGB | 121077.27 | 2584.78 | 2584.78 |  |  |  | 0 | 1 | [14 empty] | 97.1251 |  |  | #VALUE!
21.01.2008 20:00 | 3600 | 2 | 761.61 | GGB | 763.37 | 769.266 | 768.132 | 261.81 | GGB | 10781.2 | GGB | 9.83 | GGB | 993.13 | GGB | 59.19 | GGB | 167012.56 | GGB | 134561.9 | GGB | 0 | 0 | 2624 | 3600 | 2608.84 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 121115.5 | GGB | 121116.9 | 2608.84 | 2608.84 |  |  |  | 0 | 1 | [14 empty] | 97.514 |  |  | #VALUE!
21.01.2008 21:00 | 3600 | 2 | 762.17 | GGB | 764.835 | 770.484 | 768.498 | 262.77 | GGB | 10748.7 | GGB | 9.84 | GGB | 992.67 | GGB | 58.61 | GGB | 168512.33 | GGB | 135945.05 | GGB | 0 | 0 | 2591 | 3600 | 2575.56 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 121154.84 | GGB | 121156.24 | 2575.56 | 2575.56 |  |  |  | 1 | 1 |  |  |  |  | 135945.05 | 2575.56 | 135945.05 | 2575.56 | 8.9002 | [5 empty] | 97.2596 |  |  | #VALUE!
21.01.2008 22:00 | 3600 | 2 | 761.46 | GGB | 764.469 | 769.641 | 768.132 | 261.1 | GGB | 10760.6 | GGB | 9.83 | GGB | 991.65 | GGB | 59.13 | GGB | 166625.25 | GGB | 134075.25 | GGB | 0 | 0 | 2618 | 3600 | 2602.92 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 121193.29 | GGB | 121194.69 | 2602.92 | 2602.92 |  |  |  | 1 | 1 |  |  |  |  | 134075.25 | 2602.92 | 134075.25 | 2602.92 | 9.0764 | [5 empty] | 96.9409 |  |  | #VALUE!
21.01.2008 23:00 | 3600 | 2 | 761.75 | GGB | 764.469 | 768.773 | 768.132 | 261.97 | GGB | 10741.6 | GGB | 9.83 | GGB | 991.53 | GGB | 58.98 | GGB | 167360.27 | GGB | 134709.58 | GGB | 0 | 0 | 2604 | 3600 | 2588.49 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 121233.83 | GGB | 121235.23 | 2588.49 | 2588.49 |  |  |  | 1 | 1 |  |  |  |  | 134709.58 | 2588.49 | 134709.58 | 2588.49 | 8.6012 | [5 empty] | 96.8596 |  |  | #VALUE!
21.01.2008 24:00 | 3600 | 2 | 761.42 | GGB | 764.469 | 768.82 | 768.132 | 262.22 | GGB | 10753 | GGB | 9.83 | GGB | 991.17 | GGB | 58.53 | GGB | 168194.33 | GGB | 135516.36 | GGB | 0 | 0 | 2604 | 3600 | 2588.7 | GGB | 100 | GGB | 38.26 | GGB | 38.26 | GGB | 121272.08 | GGB | 121273.49 | 2588.7 | 2588.7 |  |  |  | 1 | 1 |  |  |  |  | 135516.36 | 2588.7 | 135516.36 | 2588.7 | 9.1691 | [5 empty] | 97.4476 |  |  | #VALUE!
22.01.2008 01:00 | 3600 | 2 | 761.17 | GGB | 763.37 | 767.766 | 767.033 | 262.71 | GGB | 10788.3 | GGB | 9.83 | GGB | 991.29 | GGB | 58.99 | GGB | 168051.28 | GGB | 135228.28 | GGB | 0 | 0 | 2639 | 3600 | 2623.78 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 121310.33 | GGB | 121311.73 | 2623.78 | 2623.78 |  |  |  | 0 | 1 | [14 empty] | 98.5581 |  |  | #VALUE!
22.01.2008 02:00 | 3600 | 2 | 761.31 | GGB | 763.37 | 767.625 | 767.033 | 263.16 | GGB | 10813.8 | GGB | 9.83 | GGB | 990.97 | GGB | 58.2 | GGB | 170165.03 | GGB | 137211.51 | GGB | 0 | 0 | 2636 | 3600 | 2621.06 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 121351.02 | GGB | 121352.42 | 2621.06 | 2621.06 |  |  |  | 0 | 1 | [14 empty] | 99.8999 |  |  | #VALUE!
22.01.2008 03:00 | 3600 | 2 | 761 | GGB | 763.37 | 768.586 | 767.033 | 263.12 | GGB | 10849.3 | GGB | 9.83 | GGB | 990.93 | GGB | 58.59 | GGB | 169270.46 | GGB | 136324.87 | GGB | 0 | 0 | 2670 | 3600 | 2654.52 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 121390.28 | GGB | 121391.68 | 2654.52 | 2654.52 |  |  |  | 0 | 1 | [14 empty] | 100.5214 |  |  | #VALUE!
22.01.2008 04:00 | 3600 | 2 | 760.92 | GGB | 764.469 | 768.445 | 767.033 | 263.48 | GGB | 10871.8 | GGB | 9.83 | GGB | 990.84 | GGB | 58.53 | GGB | 169637.97 | GGB | 136632.07 | GGB | 0 | 0 | 2682 | 3600 | 2666.45 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 121430.61 | GGB | 121432.02 | 2666.45 | 2666.45 |  |  |  | 1 | 1 |  |  |  |  | 136632.07 | 2666.45 | 136632.07 | 2666.45 | 9.0313 | [5 empty] | 101.2007 |  |  | #VALUE!
22.01.2008 05:00 | 3600 | 2 | 760.81 | GGB | 763.37 | 768.445 | 767.033 | 263.37 | GGB | 10876 | GGB | 9.83 | GGB | 990.51 | GGB | 58.34 | GGB | 169852.54 | GGB | 136836.97 | GGB | 0 | 0 | 2684 | 3600 | 2668.24 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 121469.85 | GGB | 121471.25 | 2668.24 | 2668.24 |  |  |  | 0 | 1 | [14 empty] | 101.4205 |  |  | #VALUE!
22.01.2008 06:00 | 3600 | 2 | 760.85 | GGB | 763.37 | 768.703 | 767.033 | 263.21 | GGB | 10872.5 | GGB | 9.84 | GGB | 990.67 | GGB | 58.33 | GGB | 169684.18 | GGB | 136728.65 | GGB | 0 | 0 | 2683 | 3600 | 2667.48 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 121509.95 | GGB | 121511.35 | 2667.48 | 2667.48 |  |  |  | 0 | 1 | [14 empty] | 101.3114 |  |  | #VALUE!
22.01.2008 07:00 | 3600 | 2 | 760.84 | GGB | 764.469 | 768.703 | 768.132 | 263.23 | GGB | 10870.4 | GGB | 9.84 | GGB | 990.84 | GGB | 58.45 | GGB | 169485.02 | GGB | 136542.79 | GGB | 0 | 0 | 2679 | 3600 | 2663.98 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 121549.81 | GGB | 121551.21 | 2663.98 | 2663.98 |  |  |  | 1 | 1 |  |  |  |  | 136542.79 | 2663.98 | 136542.79 | 2663.98 | 9.1256 | [5 empty] | 101.0409 |  |  | #VALUE!
22.01.2008 08:00 | 3600 | 2 | 760.66 | GGB | 762.271 | 766.945 | 765.934 | 265.17 | GGB | 10831.3 | GGB | 9.82 | GGB | 991.41 | GGB | 58.02 | GGB | 171812.24 | GGB | 138678.89 | GGB | 0 | 0 | 2681 | 3600 | 2665.44 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 121589.01 | GGB | 121590.41 | 2665.44 | 2665.44 |  |  |  | 0 | 1 | [14 empty] | 102.6779 |  |  | #VALUE!
22.01.2008 09:00 | 3600 | 2 | 761.28 | GGB | 764.469 | 768.656 | 768.132 | 263.85 | GGB | 10881.8 | GGB | 9.84 | GGB | 992.07 | GGB | 58.47 | GGB | 169964.77 | GGB | 137090.61 | GGB | 0 | 0 | 2676 | 3600 | 2660.43 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 121628.66 | GGB | 121630.06 | 2660.43 | 2660.43 |  |  |  | 1 | 1 |  |  |  |  | 137090.61 | 2660.43 | 137090.61 | 2660.43 | 9.1985 | [5 empty] | 101.3111 |  |  | #VALUE!
22.01.2008 10:00 | 3600 | 2 | 760.83 | GGB | 764.469 | 768.703 | 768.132 | 264.79 | GGB | 10844.7 | GGB | 9.83 | GGB | 992.33 | GGB | 58.19 | GGB | 170993.59 | GGB | 138073.33 | GGB | 0 | 0 | 2676 | 3600 | 2660.96 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 121668.71 | GGB | 121670.1 | 2660.96 | 2660.96 |  |  |  | 1 | 1 |  |  |  |  | 138073.33 | 2660.96 | 138073.33 | 2660.96 | 9.176 | [5 empty] | 102.0577 |  |  | #VALUE!
22.01.2008 11:00 | 3600 | 2 | 761.62 | GGB | 764.469 | 770.039 | 768.132 | 264.32 | GGB | 10864.1 | GGB | 9.84 | GGB | 992.95 | GGB | 57.96 | GGB | 170672.29 | GGB | 137997.95 | GGB | 0 | 0 | 2643 | 3600 | 2627.51 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 121707.62 | GGB | 121709.02 | 2627.51 | 2627.51 |  |  |  | 1 | 1 |  |  |  |  | 137997.95 | 2627.51 | 137997.95 | 2627.51 | 9.3163 | [5 empty] | 100.7197 |  |  | #VALUE!
22.01.2008 12:00 | 3600 | 2 | 760.93 | GGB | 763.37 | 768.984 | 767.033 | 263.18 | GGB | 10857.1 | GGB | 9.83 | GGB | 993.31 | GGB | 58.68 | GGB | 168963.46 | GGB | 136365.24 | GGB | 0 | 0 | 2678 | 3600 | 2662.34 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 121747.74 | GGB | 121749.14 | 2662.34 | 2662.34 |  |  |  | 0 | 1 | [14 empty] | 100.8474 |  |  | #VALUE!
22.01.2008 13:00 | 3600 | 2 | 761.24 | GGB | 765.934 | 770.32 | 768.132 | 264.65 | GGB | 10828.9 | GGB | 9.83 | GGB | 994.31 | GGB | 58.26 | GGB | 170969.38 | GGB | 138301.91 | GGB | 0 | 0 | 2645 | 3600 | 2629.85 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 121787.28 | GGB | 121788.68 | 2629.85 | 2629.85 |  |  |  | 1 | 1 |  |  |  |  | 138301.91 | 2629.85 | 138301.91 | 2629.85 | 9.1986 | [5 empty] | 101.0315 |  |  | #VALUE!
22.01.2008 14:00 | 3600 | 2 | 761.53 | GGB | 763.37 | 768.352 | 767.033 | 263.41 | GGB | 10865.3 | GGB | 9.83 | GGB | 995.21 | GGB | 58.46 | GGB | 169668.78 | GGB | 137291.5 | GGB | 0 | 0 | 2648 | 3600 | 2632.5 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 121826.75 | GGB | 121828.15 | 2632.5 | 2632.5 |  |  |  | 0 | 1 | [14 empty] | 100.3944 |  |  | #VALUE!
22.01.2008 15:00 | 3600 | 2 | 761.2 | GGB | 765.934 | 770.484 | 769.597 | 265.18 | GGB | 10871.4 | GGB | 9.83 | GGB | 996.28 | GGB | 57.86 | GGB | 171987.19 | GGB | 139566.3 | GGB | 0 | 0 | 2662 | 3600 | 2646.62 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 121867.02 | GGB | 121868.42 | 2646.62 | 2646.62 |  |  |  | 1 | 1 |  |  |  |  | 139566.3 | 2646.62 | 139566.3 | 2646.62 | 9.1726 | [5 empty] | 102.6053 |  |  | #VALUE!
22.01.2008 16:00 | 3600 | 2 | 762.12 | GGB | 763.37 | 767.508 | 767.033 | 264.18 | GGB | 10915.1 | GGB | 9.85 | GGB | 996.97 | GGB | 58.29 | GGB | 170920.96 | GGB | 138619.78 | GGB | 0 | 0 | 2638 | 3600 | 2623.09 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 121906.17 | GGB | 121907.56 | 2623.09 | 2623.09 |  |  |  | 0 | 1 | [14 empty] | 101.0034 |  |  | #VALUE!
22.01.2008 17:00 | 3600 | 2 | 760.8 | GGB | 762.271 | 766.453 | 765.934 | 264.9 | GGB | 10899.8 | GGB | 9.82 | GGB | 997.91 | GGB | 57.93 | GGB | 171292.88 | GGB | 139204.98 | GGB | 0 | 0 | 2698 | 3600 | 2682.81 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 121946.75 | GGB | 121948.14 | 2682.81 | 2682.81 |  |  |  | 0 | 1 | [14 empty] | 103.739 |  |  | #VALUE!
22.01.2008 18:00 | 3600 | 2 | 761.77 | GGB | 764.469 | 769.641 | 768.132 | 265.75 | GGB | 10918.6 | GGB | 9.84 | GGB | 999.08 | GGB | 57.43 | GGB | 172310.69 | GGB | 140406.87 | GGB | 0 | 0 | 2666 | 3600 | 2650.73 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 121985.82 | GGB | 121987.21 | 2650.73 | 2650.73 |  |  |  | 1 | 1 |  |  |  |  | 140406.87 | 2650.73 | 140406.87 | 2650.73 | 9.526 | [5 empty] | 103.3835 |  |  | #VALUE!
22.01.2008 19:00 | 3600 | 2 | 761.17 | GGB | 764.469 | 768.516 | 767.033 | 264.85 | GGB | 10932 | GGB | 9.83 | GGB | 1000.13 | GGB | 57.99 | GGB | 170722.9 | GGB | 139023.8 | GGB | 0 | 0 | 2701 | 3600 | 2686.07 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 122026.41 | GGB | 122027.8 | 2686.07 | 2686.07 |  |  |  | 1 | 1 |  |  |  |  | 139023.8 | 2686.07 | 139023.8 | 2686.07 | 9.2 | [5 empty] | 103.7299 |  |  | #VALUE!
22.01.2008 20:00 | 3600 | 2 | 760.8 | GGB | 763.37 | 768.539 | 767.033 | 266.76 | GGB | 10918.1 | GGB | 9.82 | GGB | 1000.92 | GGB | 57.38 | GGB | 172857.56 | GGB | 141135.35 | GGB | 0 | 0 | 2709 | 3600 | 2694.07 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 122066.21 | GGB | 122067.6 | 2694.07 | 2677.77 |  |  |  | 0 | 1 | [14 empty] | 105.619 | 2677.77 |  | 104.98
22.01.2008 21:00 | 3600 | 2 | 761.18 | GGB | 763.37 | 768.563 | 767.033 | 266.22 | GGB | 10960.3 | GGB | 9.84 | GGB | 1001.89 | GGB | 57.72 | GGB | 171883.76 | GGB | 140329.33 | GGB | 0 | 0 | 2703 | 3600 | 2687.28 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 122107.4 | GGB | 122108.79 | 2687.28 | 2687.28 |  |  |  | 0 | 1 | [14 empty] | 104.7512 |  |  | #VALUE!
22.01.2008 22:00 | 3600 | 2 | 760.42 | GGB | 762.271 | 767.461 | 765.934 | 266.55 | GGB | 10956.4 | GGB | 9.83 | GGB | 1002.99 | GGB | 57.74 | GGB | 172093.92 | GGB | 140647.61 | GGB | 0 | 0 | 2747 | 3600 | 2731.15 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 122148.02 | GGB | 122149.41 | 2731.15 | 2687.056 |  |  |  | 0 | 1 | [14 empty] | 106.7027 | 2687.056 |  | 104.98
22.01.2008 23:00 | 3600 | 2 | 761.06 | GGB | 764.469 | 769.594 | 768.132 | 267.75 | GGB | 10950.2 | GGB | 9.83 | GGB | 1004.38 | GGB | 57.04 | GGB | 173810.45 | GGB | 142549.55 | GGB | 0 | 0 | 2711 | 3600 | 2695.11 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 122187.73 | GGB | 122189.13 | 2695.11 | 2651.2044 |  |  |  | 1 | 1 |  |  |  |  | 142549.55 | 2651.2044 | 142549.55 | 2651.2044 | 9.5148 | [5 empty] | 106.7185 | 2651.2044 |  | 104.98
22.01.2008 24:00 | 3600 | 2 | 761.88 | GGB | 764.835 | 769.617 | 768.498 | 265.11 | GGB | 10993.8 | GGB | 9.85 | GGB | 1005.37 | GGB | 58.12 | GGB | 171222.46 | GGB | 140106.16 | GGB | 0 | 0 | 2690 | 3600 | 2674.3 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 122227.87 | GGB | 122229.27 | 2674.3 | 2674.3 |  |  |  | 1 | 1 |  |  |  |  | 140106.16 | 2674.3 | 140106.16 | 2674.3 | 9.3345 | [5 empty] | 104.0794 |  |  | #VALUE!
23.01.2008 01:00 | 3600 | 2 | 760.53 | GGB | 764.835 | 770.109 | 768.132 | 265.93 | GGB | 10963.3 | GGB | 9.82 | GGB | 1006.27 | GGB | 58.31 | GGB | 171124.53 | GGB | 140072.81 | GGB | 0 | 0 | 2755 | 3600 | 2739.72 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 122268.17 | GGB | 122269.57 | 2739.72 | 2698.0825 |  |  |  | 1 | 1 |  |  |  |  | 140072.81 | 2698.0825 | 140072.81 | 2698.0825 | 9.3779 | [5 empty] | 106.6001 | 2698.0825 |  | 104.98
23.01.2008 02:00 | 3600 | 2 | 760.68 | GGB | 763.37 | 767.977 | 766.667 | 266.7 | GGB | 10982.5 | GGB | 9.83 | GGB | 1007.25 | GGB | 58.32 | GGB | 171760.52 | GGB | 140721.01 | GGB | 0 | 0 | 2754 | 3600 | 2738.73 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 122308.3 | GGB | 122309.7 | 2738.73 | 2685.6544 |  |  |  | 0 | 1 | [14 empty] | 107.0547 | 2685.6544 |  | 104.98
23.01.2008 03:00 | 3600 | 2 | 760.85 | GGB | 762.271 | 766.875 | 765.201 | 266.99 | GGB | 10997.1 | GGB | 9.83 | GGB | 1008.37 | GGB | 58.31 | GGB | 172118.13 | GGB | 141178.71 | GGB | 0 | 0 | 2747 | 3600 | 2731.71 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 122348.37 | GGB | 122349.77 | 2731.71 | 2676.9475 |  |  |  | 0 | 1 | [14 empty] | 107.1276 | 2676.9475 |  | 104.98
23.01.2008 04:00 | 3600 | 2 | 761.11 | GGB | 762.271 | 767.063 | 766.3 | 267.18 | GGB | 11022.6 | GGB | 9.84 | GGB | 1009.02 | GGB | 58.11 | GGB | 172199.56 | GGB | 141421.75 | GGB | 0 | 0 | 2751 | 3600 | 2735.52 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 122388.58 | GGB | 122389.98 | 2735.52 | 2672.3471 |  |  |  | 0 | 1 | [14 empty] | 107.4617 | 2672.3471 |  | 104.98
23.01.2008 05:00 | 3600 | 2 | 760.61 | GGB | 763.37 | 768.234 | 766.3 | 267.43 | GGB | 11019.8 | GGB | 9.83 | GGB | 1010.03 | GGB | 58.19 | GGB | 172407.52 | GGB | 141699.28 | GGB | 0 | 0 | 2775 | 3600 | 2759.49 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 122428.77 | GGB | 122430.18 | 2759.49 | 2667.1131 |  |  |  | 0 | 1 | [14 empty] | 108.616 | 2667.1131 |  | 104.98
23.01.2008 06:00 | 3600 | 2 | 761.14 | GGB | 764.469 | 769.172 | 767.766 | 267.42 | GGB | 11033.8 | GGB | 9.84 | GGB | 1011.26 | GGB | 58.12 | GGB | 172498.85 | GGB | 141977.14 | GGB | 0 | 0 | 2753 | 3600 | 2737.99 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 122469.32 | GGB | 122470.73 | 2737.99 | 2661.8933 |  |  |  | 1 | 1 |  |  |  |  | 141977.14 | 2661.8933 | 141977.14 | 2661.8933 | 9.32 | [5 empty] | 107.9811 | 2661.8933 |  | 104.98
23.01.2008 07:00 | 3600 | 2 | 761.23 | GGB | 763.37 | 767.977 | 766.667 | 267.39 | GGB | 11030.5 | GGB | 9.83 | GGB | 1011.86 | GGB | 58.21 | GGB | 172406.42 | GGB | 141946.88 | GGB | 0 | 0 | 2748 | 3600 | 2732.88 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 122509.31 | GGB | 122510.72 | 2732.88 | 2662.4608 |  |  |  | 0 | 1 | [14 empty] | 107.7566 | 2662.4608 |  | 104.98
23.01.2008 08:00 | 3600 | 2 | 761.22 | GGB | 764.835 | 769.711 | 768.864 | 267.65 | GGB | 11038.4 | GGB | 9.84 | GGB | 1012.83 | GGB | 58.27 | GGB | 172569.27 | GGB | 142192.62 | GGB | 0 | 0 | 2756 | 3600 | 2740.57 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 122550.13 | GGB | 122551.53 | 2740.57 | 2657.8595 |  |  |  | 1 | 1 |  |  |  |  | 142192.62 | 2657.8595 | 142192.62 | 2657.8595 | 9.2607 | [5 empty] | 108.2469 | 2657.8595 |  | 104.98
23.01.2008 09:00 | 3600 | 2 | 761.25 | GGB | 764.469 | 769.688 | 768.864 | 267.74 | GGB | 11042.5 | GGB | 9.83 | GGB | 1014.35 | GGB | 58.29 | GGB | 172581.37 | GGB | 142405.88 | GGB | 0 | 0 | 2756 | 3600 | 2740.52 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 122590.16 | GGB | 122591.56 | 2740.52 | 2653.8792 |  |  |  | 1 | 1 |  |  |  |  | 142405.88 | 2653.8792 | 142405.88 | 2653.8792 | 9.4411 | [5 empty] | 108.4073 | 2653.8792 |  | 104.98
23.01.2008 10:00 | 3600 | 2 | 761.12 | GGB | 763.37 | 767.578 | 766.667 | 268.25 | GGB | 11053.6 | GGB | 9.83 | GGB | 1015.05 | GGB | 58.19 | GGB | 173012.71 | GGB | 142901.99 | GGB | 0 | 0 | 2766 | 3600 | 2750.85 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 122630.86 | GGB | 122632.26 | 2750.85 | 2644.6658 |  |  |  | 0 | 1 | [14 empty] | 109.195 | 2644.6658 |  | 104.98
23.01.2008 11:00 | 3600 | 2 | 760.33 | GGB | 762.271 | 766.688 | 766.3 | 268.8 | GGB | 11056.1 | GGB | 9.83 | GGB | 1016.03 | GGB | 58.02 | GGB | 173602.49 | GGB | 143603.6 | GGB | 0 | 0 | 2771 | 3600 | 2755.92 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 122671.25 | GGB | 122672.66 | 2755.92 | 2631.7446 |  |  |  | 0 | 1 | [14 empty] | 109.9333 | 2631.7446 |  | 104.98
23.01.2008 12:00 | 3600 | 2 | 760.92 | GGB | 762.271 | 766.664 | 766.3 | 268.97 | GGB | 11055.1 | GGB | 9.84 | GGB | 1016.82 | GGB | 58.08 | GGB | 173914.98 | GGB | 143947.22 | GGB | 0 | 0 | 2749 | 3600 | 2733.67 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 122711.64 | GGB | 122713.05 | 2733.67 | 2625.4623 |  |  |  | 0 | 1 | [14 empty] | 109.3067 | 2625.4623 |  | 104.98
23.01.2008 13:00 | 3600 | 2 | 762.03 | GGB | 765.934 | 770.789 | 769.963 | 268.85 | GGB | 11043.2 | GGB | 9.85 | GGB | 1017.53 | GGB | 58.13 | GGB | 173473.75 | GGB | 143658.33 | GGB | 0 | 0 | 2694 | 3600 | 2678.5 | GGB | 100 | GGB | 41.39 | GGB | 41.39 | GGB | 122753.03 | GGB | 122754.44 | 2678.5 | 2630.742 |  |  |  | 1 | 1 |  |  |  |  | 143658.33 | 2630.742 | 143658.33 | 2630.742 | 9.1309 | [5 empty] | 106.8858 | 2630.742 |  | 104.98
23.01.2008 14:00 | 3600 | 2 | 761.29 | GGB | 763.37 | 768.633 | 767.033 | 268.01 | GGB | 11023.9 | GGB | 9.83 | GGB | 1018.13 | GGB | 58.78 | GGB | 172227.07 | GGB | 142434.41 | GGB | 0 | 0 | 2715 | 3600 | 2699.78 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 122793.17 | GGB | 122794.58 | 2699.78 | 2653.3476 |  |  |  | 0 | 1 | [14 empty] | 106.8171 | 2653.3476 |  | 104.98
23.01.2008 15:00 | 3600 | 2 | 761.74 | GGB | 764.469 | 768.914 | 768.498 | 268.71 | GGB | 11039.1 | GGB | 9.84 | GGB | 1018.52 | GGB | 58.41 | GGB | 173033.61 | GGB | 143312.61 | GGB | 0 | 0 | 2705 | 3600 | 2689.97 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 122834.1 | GGB | 122835.51 | 2689.97 | 2637.0883 |  |  |  | 1 | 1 |  |  |  |  | 143312.61 | 2637.0883 | 143312.61 | 2637.0883 | 9.2335 | [5 empty] | 107.0852 | 2637.0883 |  | 104.98
23.01.2008 16:00 | 3600 | 2 | 761.43 | GGB | 764.835 | 768.797 | 768.498 | 269.43 | GGB | 11015.7 | GGB | 9.82 | GGB | 1018.84 | GGB | 58.29 | GGB | 173901.78 | GGB | 144129.86 | GGB | 0 | 0 | 2710 | 3600 | 2694.23 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 122873.93 | GGB | 122875.34 | 2694.23 | 2622.1353 |  |  |  | 1 | 1 |  |  |  |  | 144129.86 | 2622.1353 | 144129.86 | 2622.1353 | 9.4885 | [5 empty] | 107.8664 | 2622.1353 |  | 104.98
23.01.2008 17:00 | 3600 | 2 | 761.49 | GGB | 764.469 | 768.797 | 768.132 | 269.19 | GGB | 11067.9 | GGB | 9.84 | GGB | 1019.3 | GGB | 58.57 | GGB | 173082.03 | GGB | 143394.28 | GGB | 0 | 0 | 2735 | 3600 | 2719.81 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 122914.63 | GGB | 122916.04 | 2719.81 | 2635.5863 |  |  |  | 1 | 1 |  |  |  |  | 143394.28 | 2635.5863 | 143394.28 | 2635.5863 | 9.2857 | [5 empty] | 108.3348 | 2635.5863 |  | 104.98
23.01.2008 18:00 | 3600 | 2 | 760.9 | GGB | 765.934 | 770.742 | 769.963 | 271.29 | GGB | 11064.7 | GGB | 9.83 | GGB | 1020.4 | GGB | 57.88 | GGB | 175405.94 | GGB | 145778.89 | GGB | 0 | 0 | 2768 | 3600 | 2752.93 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 122954.66 | GGB | 122956.07 | 2752.93 | 2592.4741 |  |  |  | 1 | 1 |  |  |  |  | 145778.89 | 2592.4741 | 145778.89 | 2592.4741 | 9.4411 | [5 empty] | 111.4775 | 2592.4741 |  | 104.98
23.01.2008 19:00 | 3600 | 2 | 760.95 | GGB | 762.271 | 767.438 | 765.201 | 270.45 | GGB | 11082.6 | GGB | 9.83 | GGB | 1021 | GGB | 58.27 | GGB | 174204.37 | GGB | 144694.61 | GGB | 0 | 0 | 2776 | 3600 | 2760.49 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 122995.39 | GGB | 122996.8 | 2760.49 | 2611.901 |  |  |  | 0 | 1 | [14 empty] | 110.9522 | 2611.901 |  | 104.98
23.01.2008 20:00 | 3600 | 2 | 760.84 | GGB | 763.37 | 767.859 | 767.766 | 271.96 | GGB | 11067.8 | GGB | 9.82 | GGB | 1021.43 | GGB | 57.81 | GGB | 176076.05 | GGB | 146517.62 | GGB | 0 | 0 | 2777 | 3600 | 2761.41 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 123035.98 | GGB | 123037.39 | 2761.41 | 2579.4031 |  |  |  | 0 | 1 | [14 empty] | 112.3876 | 2579.4031 |  | 104.98
23.01.2008 21:00 | 3600 | 2 | 761.67 | GGB | 763.37 | 768.727 | 766.3 | 271.1 | GGB | 11120.6 | GGB | 9.84 | GGB | 1021.51 | GGB | 58.43 | GGB | 174453.05 | GGB | 144904.36 | GGB | 0 | 0 | 2773 | 3600 | 2757.3 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 123075.95 | GGB | 123077.37 | 2757.3 | 2608.1203 |  |  |  | 0 | 1 | [14 empty] | 110.9847 | 2608.1203 |  | 104.98
23.01.2008 22:00 | 3600 | 2 | 760.61 | GGB | 763.37 | 768.703 | 767.766 | 271.92 | GGB | 11086.6 | GGB | 9.82 | GGB | 1021.73 | GGB | 58.21 | GGB | 175593 | GGB | 145980.59 | GGB | 0 | 0 | 2801 | 3600 | 2785.43 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 123117.51 | GGB | 123118.93 | 2785.43 | 2588.8921 |  |  |  | 0 | 1 | [14 empty] | 112.9496 | 2588.8921 |  | 104.98
23.01.2008 23:00 | 3600 | 2 | 761.23 | GGB | 764.469 | 768.891 | 767.766 | 272.14 | GGB | 11127.7 | GGB | 9.84 | GGB | 1022.28 | GGB | 58.14 | GGB | 175820.77 | GGB | 146278.27 | GGB | 0 | 0 | 2777 | 3600 | 2761.74 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 123157.01 | GGB | 123158.43 | 2761.74 | 2583.6237 |  |  |  | 1 | 1 |  |  |  |  | 146278.27 | 2583.6237 | 146278.27 | 2583.6237 | 9.5678 | [5 empty] | 112.2174 | 2583.6237 |  | 104.98
23.01.2008 24:00 | 3600 | 2 | 759.86 | GGB | 762.271 | 766.711 | 766.3 | 272.06 | GGB | 11121.5 | GGB | 9.82 | GGB | 1022.64 | GGB | 57.93 | GGB | 176461.17 | GGB | 146957.15 | GGB | 0 | 0 | 2852 | 3600 | 2836.6 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 123198.56 | GGB | 123199.98 | 2836.6 | 2571.6884 |  |  |  | 0 | 1 | [14 empty] | 115.7941 | 2571.6884 |  | 104.98
24.01.2008 01:00 | 3600 | 2 | 760.61 | GGB | 765.934 | 769.828 | 768.864 | 273.84 | GGB | 11146.5 | GGB | 9.84 | GGB | 1023.01 | GGB | 57.68 | GGB | 177755.16 | GGB | 148198.12 | GGB | 0 | 0 | 2820 | 3600 | 2804.95 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 123239.2 | GGB | 123240.62 | 2804.95 | 2550.1538 |  |  |  | 1 | 1 |  |  |  |  | 148198.12 | 2550.1538 | 148198.12 | 2550.1538 | 9.2994 | [5 empty] | 115.469 | 2550.1538 |  | 104.98
24.01.2008 02:00 | 3600 | 2 | 760.4 | GGB | 764.469 | 768.633 | 766.667 | 272.72 | GGB | 11171.6 | GGB | 9.84 | GGB | 1023.57 | GGB | 58.18 | GGB | 176533.79 | GGB | 147040.57 | GGB | 0 | 0 | 2851 | 3600 | 2835.77 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 123280.05 | GGB | 123281.47 | 2835.77 | 2570.2294 |  |  |  | 1 | 1 |  |  |  |  | 147040.57 | 2570.2294 | 147040.57 | 2570.2294 | 9.2516 | [5 empty] | 115.8259 | 2570.2294 |  | 104.98
24.01.2008 03:00 | 3600 | 2 | 760.42 | GGB | 763.37 | 768.891 | 766.667 | 273.57 | GGB | 11171.9 | GGB | 9.84 | GGB | 1023.27 | GGB | 57.96 | GGB | 177444.87 | GGB | 147855.34 | GGB | 0 | 0 | 2844 | 3600 | 2828.41 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 123321.42 | GGB | 123322.84 | 2828.41 | 2556.0659 |  |  |  | 0 | 1 | [14 empty] | 116.1654 | 2556.0659 |  | 104.98
24.01.2008 04:00 | 3600 | 2 | 759.95 | GGB | 763.37 | 768.75 | 766.667 | 275.23 | GGB | 11145.6 | GGB | 9.82 | GGB | 1022.74 | GGB | 57.24 | GGB | 179309.94 | GGB | 149657.59 | GGB | 0 | 0 | 2864 | 3600 | 2848.63 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 123361.85 | GGB | 123363.26 | 2848.63 | 2525.2846 |  |  |  | 0 | 1 | [14 empty] | 118.422 | 2525.2846 |  | 104.98
24.01.2008 05:00 | 3600 | 2 | 760.59 | GGB | 763.37 | 767.719 | 766.667 | 273.53 | GGB | 11197 | GGB | 9.84 | GGB | 1022.62 | GGB | 58 | GGB | 177146.68 | GGB | 147493.53 | GGB | 0 | 0 | 2854 | 3600 | 2838.63 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 123403.02 | GGB | 123404.44 | 2838.63 | 2562.3361 |  |  |  | 0 | 1 | [14 empty] | 116.2999 | 2562.3361 |  | 104.98
24.01.2008 06:00 | 3600 | 2 | 760.33 | GGB | 764.835 | 770.414 | 768.864 | 273.9 | GGB | 11167.7 | GGB | 9.84 | GGB | 1022.16 | GGB | 57.7 | GGB | 177732.06 | GGB | 148048.41 | GGB | 0 | 0 | 2859 | 3600 | 2843.25 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 123443.56 | GGB | 123444.98 | 2843.25 | 2552.7326 |  |  |  | 1 | 1 |  |  |  |  | 148048.41 | 2552.7326 | 148048.41 | 2552.7326 | 9.3223 | [5 empty] | 116.9274 | 2552.7326 |  | 104.98
24.01.2008 07:00 | 3600 | 2 | 759.85 | GGB | 763.37 | 768.305 | 766.3 | 273.94 | GGB | 11147.6 | GGB | 9.82 | GGB | 1021.83 | GGB | 57.59 | GGB | 178109.47 | GGB | 148364.46 | GGB | 0 | 0 | 2872 | 3600 | 2856.28 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 123484.78 | GGB | 123486.2 | 2856.28 | 2547.2947 |  |  |  | 0 | 1 | [14 empty] | 117.714 | 2547.2947 |  | 104.98
24.01.2008 08:00 | 3600 | 2 | 760.94 | GGB | 762.271 | 767.133 | 765.201 | 273.46 | GGB | 11197.1 | GGB | 9.85 | GGB | 1021.58 | GGB | 57.73 | GGB | 177748.56 | GGB | 147965.86 | GGB | 0 | 0 | 2842 | 3600 | 2826.58 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 123525.12 | GGB | 123526.54 | 2826.58 | 2554.1567 |  |  |  | 0 | 1 | [14 empty] | 116.177 | 2554.1567 |  | 104.98
24.01.2008 09:00 | 3600 | 2 | 759.75 | GGB | 763.37 | 768.469 | 767.766 | 273.23 | GGB | 11159.3 | GGB | 9.83 | GGB | 1020.82 | GGB | 57.53 | GGB | 178236.01 | GGB | 148349.23 | GGB | 0 | 0 | 2880 | 3600 | 2864.46 | GGB | 100 | GGB | 41.43 | GGB | 41.43 | GGB | 123566.55 | GGB | 123567.97 | 2864.46 | 2547.5562 |  |  |  | 0 | 1 | [14 empty] | 118.039 | 2547.5562 |  | 104.98
24.01.2008 10:00 | 3600 | 2 | 761.17 | GGB | 764.835 | 770.273 | 767.766 | 272.85 | GGB | 11182.1 | GGB | 9.86 | GGB | 1020.5 | GGB | 57.42 | GGB | 177636.33 | GGB | 147855.82 | GGB | 0 | 0 | 2805 | 3600 | 2789.02 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 123606.92 | GGB | 123608.34 | 2789.02 | 2556.0577 |  |  |  | 1 | 1 |  |  |  |  | 147855.82 | 2556.0577 | 147855.82 | 2556.0577 | 9.3616 | [5 empty] | 114.548 | 2556.0577 |  | 104.98
24.01.2008 11:00 | 3600 | 2 | 760.2 | GGB | 763.37 | 768.094 | 766.667 | 271.6 | GGB | 11150.1 | GGB | 9.84 | GGB | 1019.95 | GGB | 58.1 | GGB | 176077.15 | GGB | 146175.47 | GGB | 0 | 0 | 2847 | 3600 | 2831.13 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 123647.86 | GGB | 123649.27 | 2831.13 | 2585.4406 |  |  |  | 0 | 1 | [14 empty] | 114.956 | 2585.4406 |  | 104.98
24.01.2008 12:00 | 3600 | 2 | 760.25 | GGB | 763.37 | 769.078 | 766.667 | 272.4 | GGB | 11102.2 | GGB | 9.83 | GGB | 1019.47 | GGB | 57.56 | GGB | 177419.56 | GGB | 147461.55 | GGB | 0 | 0 | 2812 | 3600 | 2796.07 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 123689.04 | GGB | 123690.45 | 2796.07 | 2562.8918 |  |  |  | 0 | 1 | [14 empty] | 114.5313 | 2562.8918 |  | 104.98
24.01.2008 13:00 | 3600 | 2 | 760.75 | GGB | 764.469 | 769.008 | 767.766 | 272.03 | GGB | 11097 | GGB | 9.84 | GGB | 1018.4 | GGB | 58.11 | GGB | 178236.01 | GGB | 147737.81 | GGB | 0 | 0 | 2785 | 3169 | 2769.64 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 123729.02 | GGB | 123730.44 | 2769.64 | 2558.0994 |  |  |  | 1 | 1 |  |  |  |  | 147737.81 | 2558.0994 | 147737.81 | 2558.0994 | 9.4506 | [5 empty] | 113.6613 | 2558.0994 |  | 104.98
24.01.2008 14:00 | 3600 | 2 | 761.06 | GGB | 763.37 | 768.094 | 766.667 | 270.18 | GGB | 11113.7 | GGB | 9.85 | GGB | 1016.46 | GGB | 57.85 | GGB | 175694.23 | GGB | 145470.84 | GGB | 0 | 0 | 2777 | 3600 | 2761.59 | GGB | 100 | GGB | 41.08 | GGB | 41.08 | GGB | 123770.1 | GGB | 123771.52 | 2761.59 | 2597.964 |  |  |  | 0 | 1 | [14 empty] | 111.5919 | 2597.964 |  | 104.98
24.01.2008 15:00 | 3600 | 2 | 760.44 | GGB | 763.37 | 768.141 | 766.667 | 269.36 | GGB | 11080.2 | GGB | 9.84 | GGB | 1015.38 | GGB | 58.09 | GGB | 174468.45 | GGB | 144193.69 | GGB | 0 | 0 | 2805 | 3600 | 2789.76 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 123811.13 | GGB | 123812.55 | 2789.76 | 2620.9746 |  |  |  | 0 | 1 | [14 empty] | 111.7405 | 2620.9746 |  | 104.98
24.01.2008 16:00 | 3600 | 2 | 760.96 | GGB | 765.934 | 770.602 | 768.864 | 269.99 | GGB | 11040.4 | GGB | 9.83 | GGB | 1014.54 | GGB | 57.81 | GGB | 175665.62 | GGB | 145185.63 | GGB | 0 | 0 | 2758 | 3600 | 2742.55 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 123850.81 | GGB | 123852.23 | 2742.55 | 2603.0675 |  |  |  | 1 | 1 |  |  |  |  | 145185.63 | 2603.0675 | 145185.63 | 2603.0675 | 9.5244 | [5 empty] | 110.6052 | 2603.0675 |  | 104.98
24.01.2008 17:00 | 3600 | 2 | 761.38 | GGB | 763.37 | 768.445 | 766.667 | 268.29 | GGB | 11057.1 | GGB | 9.84 | GGB | 1013.59 | GGB | 58.42 | GGB | 173353.81 | GGB | 142878.79 | GGB | 0 | 0 | 2756 | 3600 | 2740.79 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 123891.69 | GGB | 123893.11 | 2740.79 | 2645.0952 |  |  |  | 0 | 1 | [14 empty] | 108.778 | 2645.0952 |  | 104.98
24.01.2008 18:00 | 3600 | 2 | 760.96 | GGB | 765.934 | 770.602 | 768.864 | 269.21 | GGB | 11016.9 | GGB | 9.83 | GGB | 1012.9 | GGB | 58.16 | GGB | 174425.54 | GGB | 143780.27 | GGB | 0 | 0 | 2757 | 3600 | 2741.74 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 123932.13 | GGB | 123933.55 | 2741.74 | 2628.5109 |  |  |  | 1 | 1 |  |  |  |  | 143780.27 | 2628.5109 | 143780.27 | 2628.5109 | 9.3454 | [5 empty] | 109.5023 | 2628.5109 |  | 104.98
24.01.2008 19:00 | 3600 | 2 | 762 | GGB | 764.469 | 769.5 | 767.766 | 267.6 | GGB | 11037.1 | GGB | 9.85 | GGB | 1012.19 | GGB | 58.64 | GGB | 172515.35 | GGB | 141898.91 | GGB | 0 | 0 | 2720 | 3600 | 2704.43 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 123972.18 | GGB | 123973.6 | 2704.43 | 2663.3608 |  |  |  | 1 | 1 |  |  |  |  | 141898.91 | 2663.3608 | 141898.91 | 2663.3608 | 9.4364 | [5 empty] | 106.5988 | 2663.3608 |  | 104.98
24.01.2008 20:00 | 3600 | 2 | 761.91 | GGB | 765.934 | 770.508 | 769.963 | 268.07 | GGB | 10986.8 | GGB | 9.84 | GGB | 1011.62 | GGB | 58.32 | GGB | 173394.52 | GGB | 142678.36 | GGB | 0 | 0 | 2704 | 3600 | 2689.04 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 124013.19 | GGB | 124014.62 | 2689.04 | 2648.8109 |  |  |  | 1 | 1 |  |  |  |  | 142678.36 | 2648.8109 | 142678.36 | 2648.8109 | 9.2133 | [5 empty] | 106.5744 | 2648.8109 |  | 104.98
24.01.2008 21:00 | 3600 | 2 | 761.79 | GGB | 764.469 | 769.641 | 767.766 | 267.31 | GGB | 10970.8 | GGB | 9.83 | GGB | 1011.5 | GGB | 58.78 | GGB | 172048.81 | GGB | 141355.86 | GGB | 0 | 0 | 2703 | 3600 | 2687.93 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 124052.79 | GGB | 124054.22 | 2687.93 | 2673.5927 |  |  |  | 1 | 1 |  |  |  |  | 141355.86 | 2673.5927 | 141355.86 | 2673.5927 | 9.5436 | [5 empty] | 105.543 | 2673.5927 |  | 104.98
24.01.2008 22:00 | 3600 | 2 | 763 | GGB | 764.835 | 769.594 | 767.766 | 266.29 | GGB | 10980.1 | GGB | 9.85 | GGB | 1010.91 | GGB | 59.27 | GGB | 170567.76 | GGB | 139853.19 | GGB | 0 | 0 | 2666 | 3600 | 2651.02 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 124093.45 | GGB | 124094.88 | 2651.02 | 2651.02 |  |  |  | 1 | 1 |  |  |  |  | 139853.19 | 2651.02 | 139853.19 | 2651.02 | 9.1184 | [5 empty] | 102.9871 |  |  | #VALUE!
24.01.2008 23:00 | 3600 | 2 | 762.12 | GGB | 763.37 | 768.305 | 767.766 | 264.82 | GGB | 10951.3 | GGB | 9.83 | GGB | 1009.99 | GGB | 59.33 | GGB | 169839.33 | GGB | 139102.42 | GGB | 0 | 0 | 2684 | 3600 | 2668.3 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 124133.01 | GGB | 124134.44 | 2668.3 | 2668.3 |  |  |  | 0 | 1 | [14 empty] | 103.1019 |  |  | #VALUE!
24.01.2008 24:00 | 3600 | 2 | 763.24 | GGB | 765.934 | 771.445 | 769.963 | 265.02 | GGB | 10945 | GGB | 9.84 | GGB | 1009.26 | GGB | 59.58 | GGB | 169209.94 | GGB | 138384.78 | GGB | 0 | 0 | 2654 | 3600 | 2638.84 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 124174.06 | GGB | 124175.5 | 2638.84 | 2638.84 |  |  |  | 1 | 1 |  |  |  |  | 138384.78 | 2638.84 | 138384.78 | 2638.84 | 8.8937 | [5 empty] | 101.4376 |  |  | #VALUE!
25.01.2008 01:00 | 3600 | 2 | 763.09 | GGB | 764.835 | 769.242 | 767.766 | 264.39 | GGB | 10909.2 | GGB | 9.83 | GGB | 1008.6 | GGB | 59.53 | GGB | 168460.61 | GGB | 137701.09 | GGB | 0 | 0 | 2644 | 3600 | 2628.27 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 124213.44 | GGB | 124214.87 | 2628.27 | 2628.27 |  |  |  | 1 | 1 |  |  |  |  | 137701.09 | 2628.27 | 137701.09 | 2628.27 | 9.1927 | [5 empty] | 100.5321 |  |  | #VALUE!
25.01.2008 02:00 | 3600 | 2 | 763.15 | GGB | 765.934 | 771.469 | 769.963 | 264.17 | GGB | 10897.3 | GGB | 9.83 | GGB | 1008.37 | GGB | 59.38 | GGB | 168079.89 | GGB | 137422.1 | GGB | 0 | 0 | 2638 | 3600 | 2622.36 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 124253.71 | GGB | 124255.14 | 2622.36 | 2622.36 |  |  |  | 1 | 1 |  |  |  |  | 137422.1 | 2622.36 | 137422.1 | 2622.36 | 8.9489 | [5 empty] | 100.1028 |  |  | #VALUE!
25.01.2008 03:00 | 3600 | 2 | 763.74 | GGB | 768.132 | 773.625 | 771.429 | 264.46 | GGB | 10875.9 | GGB | 9.84 | GGB | 1008.11 | GGB | 59.47 | GGB | 168447.41 | GGB | 137648.21 | GGB | 0 | 0 | 2606 | 3600 | 2590.73 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 124293.64 | GGB | 124295.07 | 2590.73 | 2590.73 |  |  |  | 1 | 1 |  |  |  |  | 137648.21 | 2590.73 | 137648.21 | 2590.73 | 8.9309 | [5 empty] | 99.0582 |  |  | #VALUE!
25.01.2008 04:00 | 3600 | 2 | 764.46 | GGB | 767.033 | 771.586 | 770.33 | 264.85 | GGB | 10836.8 | GGB | 9.83 | GGB | 1007.28 | GGB | 59.71 | GGB | 168997.57 | GGB | 137886.18 | GGB | 0 | 0 | 2560 | 3600 | 2544.98 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 124333.3 | GGB | 124334.73 | 2544.98 | 2544.98 |  |  |  | 1 | 1 |  |  |  |  | 137886.18 | 2544.98 | 137886.18 | 2544.98 | 8.8481 | [5 empty] | 97.4771 |  |  | #VALUE!
25.01.2008 05:00 | 3600 | 2 | 764.86 | GGB | 767.033 | 772.758 | 771.429 | 263.31 | GGB | 10864.4 | GGB | 9.85 | GGB | 1006.61 | GGB | 60.15 | GGB | 167162.21 | GGB | 136117.2 | GGB | 0 | 0 | 2555 | 3600 | 2539.62 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 124373.3 | GGB | 124374.73 | 2539.62 | 2539.62 |  |  |  | 1 | 1 |  |  |  |  | 136117.2 | 2539.62 | 136117.2 | 2539.62 | 8.6421 | [5 empty] | 96.0239 |  |  | #VALUE!
25.01.2008 06:00 | 3600 | 2 | 763.75 | GGB | 767.033 | 771.469 | 769.963 | 263.93 | GGB | 10830.8 | GGB | 9.82 | GGB | 1006.79 | GGB | 60.08 | GGB | 167913.74 | GGB | 136782.62 | GGB | 0 | 0 | 2583 | 3600 | 2567.48 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 124412.82 | GGB | 124414.25 | 2567.48 | 2567.48 |  |  |  | 1 | 1 |  |  |  |  | 136782.62 | 2567.48 | 136782.62 | 2567.48 | 8.8863 | [5 empty] | 97.5518 |  |  | #VALUE!
25.01.2008 07:00 | 3600 | 2 | 764.42 | GGB | 765.934 | 770.602 | 768.864 | 264.38 | GGB | 10840.5 | GGB | 9.83 | GGB | 1006.76 | GGB | 59.66 | GGB | 168668.57 | GGB | 137564.83 | GGB | 0 | 0 | 2552 | 3600 | 2537.16 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 124453.27 | GGB | 124454.7 | 2537.16 | 2537.16 |  |  |  | 1 | 1 |  |  |  |  | 137564.83 | 2537.16 | 137564.83 | 2537.16 | 8.6285 | [5 empty] | 96.9511 |  |  | #VALUE!
25.01.2008 08:00 | 3600 | 2 | 763.17 | GGB | 767.033 | 771.891 | 771.429 | 263.77 | GGB | 10889.2 | GGB | 9.83 | GGB | 1007.43 | GGB | 59.83 | GGB | 168565.14 | GGB | 137502.3 | GGB | 0 | 0 | 2600 | 3208 | 2584.79 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 124492.09 | GGB | 124493.51 | 2584.79 | 2584.79 |  |  |  | 1 | 1 |  |  |  |  | 137502.3 | 2584.79 | 137502.3 | 2584.79 | 9.1578 | [5 empty] | 98.7263 |  |  | #VALUE!
25.01.2008 09:00 | 3600 | 2 | 763.19 | GGB | 765.934 | 770.648 | 769.963 | 265.11 | GGB | 10911.6 | GGB | 9.83 | GGB | 1008.15 | GGB | 58.51 | GGB | 171572.36 | GGB | 140612.17 | GGB | 0 | 0 | 2604 | 3600 | 2588.95 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 124533.31 | GGB | 124534.74 | 2588.95 | 2588.95 |  |  |  | 1 | 1 |  |  |  |  | 140612.17 | 2588.95 | 140612.17 | 2588.95 | 8.8294 | [5 empty] | 101.1216 |  |  | #VALUE!
25.01.2008 10:00 | 3600 | 2 | 762.31 | GGB | 764.469 | 769.641 | 767.766 | 264.61 | GGB | 10958.8 | GGB | 9.83 | GGB | 1009.83 | GGB | 58.41 | GGB | 171293.98 | GGB | 140664.13 | GGB | 0 | 0 | 2644 | 3600 | 2629.08 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 124571.87 | GGB | 124573.3 | 2629.08 | 2629.08 |  |  |  | 1 | 1 |  |  |  |  | 140664.13 | 2629.08 | 140664.13 | 2629.08 | 9.5907 | [5 empty] | 102.727 |  |  | #VALUE!
25.01.2008 11:00 | 3600 | 2 | 763.28 | GGB | 765.934 | 771.773 | 769.963 | 264.62 | GGB | 10986 | GGB | 9.84 | GGB | 1011.34 | GGB | 58.13 | GGB | 171641.69 | GGB | 141279.52 | GGB | 0 | 0 | 2626 | 3600 | 2610.54 | GGB | 100 | GGB | 41.89 | GGB | 41.89 | GGB | 124613.76 | GGB | 124615.19 | 2610.54 | 2610.54 |  |  |  | 1 | 1 |  |  |  |  | 141279.52 | 2610.54 | 141279.52 | 2610.54 | 8.8044 | [5 empty] | 102.4488 |  |  | #VALUE!
25.01.2008 12:00 | 3600 | 2 | 762.77 | GGB | 764.835 | 770.344 | 768.864 | 264.34 | GGB | 10954.3 | GGB | 9.83 | GGB | 1011.85 | GGB | 58.31 | GGB | 171383.11 | GGB | 141059.8 | GGB | 0 | 0 | 2630 | 3600 | 2614.8 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 124652.09 | GGB | 124653.52 | 2614.8 | 2614.8 |  |  |  | 1 | 1 |  |  |  |  | 141059.8 | 2614.8 | 141059.8 | 2614.8 | 9.6228 | [5 empty] | 102.4564 |  |  | #VALUE!
25.01.2008 13:00 | 3600 | 2 | 763.75 | GGB | 765.934 | 770.32 | 768.864 | 264.27 | GGB | 10949.3 | GGB | 9.84 | GGB | 1011.79 | GGB | 57.76 | GGB | 171934.38 | GGB | 141740.53 | GGB | 0 | 0 | 2591 | 3600 | 2575.44 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 124692.79 | GGB | 124694.22 | 2575.44 | 2575.44 |  |  |  | 1 | 1 |  |  |  |  | 141740.53 | 2575.44 | 141740.53 | 2575.44 | 8.9691 | [5 empty] | 101.4012 |  |  | #VALUE!
25.01.2008 14:00 | 3600 | 2 | 764.12 | GGB | 767.033 | 771.422 | 769.963 | 262.96 | GGB | 10966.3 | GGB | 9.85 | GGB | 1011.22 | GGB | 58.24 | GGB | 170435.72 | GGB | 140223.99 | GGB | 0 | 0 | 2583 | 3600 | 2567.98 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 124733.93 | GGB | 124735.36 | 2567.98 | 2567.98 |  |  |  | 1 | 1 |  |  |  |  | 140223.99 | 2567.98 | 140223.99 | 2567.98 | 8.7529 | [5 empty] | 100.0257 |  |  | #VALUE!
25.01.2008 15:00 | 3600 | 2 | 763.42 | GGB | 765.934 | 771.422 | 768.864 | 262.49 | GGB | 10937.9 | GGB | 9.83 | GGB | 1010.43 | GGB | 58.62 | GGB | 169505.93 | GGB | 139188.44 | GGB | 0 | 0 | 2607 | 3600 | 2592.06 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 124773.53 | GGB | 124774.96 | 2592.06 | 2592.06 |  |  |  | 1 | 1 |  |  |  |  | 139188.44 | 2592.06 | 139188.44 | 2592.06 | 9.1107 | [5 empty] | 100.218 |  |  | #VALUE!
25.01.2008 16:00 | 3600 | 2 | 763.78 | GGB | 764.835 | 769.313 | 768.864 | 262.66 | GGB | 10919.6 | GGB | 9.84 | GGB | 1009.22 | GGB | 58.37 | GGB | 169877.84 | GGB | 139433.65 | GGB | 0 | 0 | 2582 | 3600 | 2566.73 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 124813.07 | GGB | 124814.5 | 2566.73 | 2566.73 |  |  |  | 1 | 1 |  |  |  |  | 139433.65 | 2566.73 | 139433.65 | 2566.73 | 9.0513 | [5 empty] | 99.4135 |  |  | #VALUE!
25.01.2008 17:00 | 3600 | 2 | 763.08 | GGB | 764.835 | 770.391 | 768.864 | 263.82 | GGB | 10920.2 | GGB | 9.82 | GGB | 1009.04 | GGB | 57.5 | GGB | 171355.6 | GGB | 140989.08 | GGB | 0 | 0 | 2611 | 3600 | 2595.79 | GGB | 100 | GGB | 42.34 | GGB | 42.34 | GGB | 124855.4 | GGB | 124856.84 | 2595.79 | 2595.79 |  |  |  | 1 | 1 |  |  |  |  | 140989.08 | 2595.79 | 140989.08 | 2595.79 | 8.6438 | [5 empty] | 101.6606 |  |  | #VALUE!
25.01.2008 18:00 | 3600 | 2 | 761.62 | GGB | 764.469 | 769.336 | 766.667 | 263.72 | GGB | 10987 | GGB | 9.83 | GGB | 1008.26 | GGB | 57.22 | GGB | 171150.94 | GGB | 140830.34 | GGB | 0 | 0 | 2690 | 3600 | 2674.51 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 124894.7 | GGB | 124896.13 | 2674.51 | 2674.51 |  |  |  | 1 | 1 |  |  |  |  | 140830.34 | 2674.51 | 140830.34 | 2674.51 | 9.5865 | [5 empty] | 104.6256 |  |  | #VALUE!
25.01.2008 19:00 | 3600 | 2 | 761 | GGB | 764.469 | 769.758 | 768.864 | 264.65 | GGB | 10981.8 | GGB | 9.83 | GGB | 1007.27 | GGB | 56.86 | GGB | 172819.05 | GGB | 142221.93 | GGB | 0 | 0 | 2715 | 3600 | 2699.36 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 124936.07 | GGB | 124937.51 | 2699.36 | 2657.3117 |  |  |  | 1 | 1 |  |  |  |  | 142221.93 | 2657.3117 | 142221.93 | 2657.3117 | 9.1331 | [5 empty] | 106.6412 | 2657.3117 |  | 104.98
25.01.2008 20:00 | 3600 | 2 | 761.16 | GGB | 762.271 | 767.695 | 766.3 | 264.07 | GGB | 10996.5 | GGB | 9.84 | GGB | 1006.31 | GGB | 56.68 | GGB | 172336 | GGB | 141763.57 | GGB | 0 | 0 | 2703 | 3600 | 2688.04 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 124975.21 | GGB | 124976.65 | 2688.04 | 2665.9035 |  |  |  | 0 | 1 | [14 empty] | 105.8517 | 2665.9035 |  | 104.98
25.01.2008 21:00 | 3600 | 2 | 761.35 | GGB | 764.469 | 768.75 | 766.667 | 264.07 | GGB | 10985.2 | GGB | 9.84 | GGB | 1005.35 | GGB | 56.89 | GGB | 172410.82 | GGB | 141600.66 | GGB | 0 | 0 | 2696 | 3600 | 2681.09 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 125016.53 | GGB | 125017.97 | 2681.09 | 2668.9706 |  |  |  | 1 | 1 |  |  |  |  | 141600.66 | 2668.9706 | 141600.66 | 2668.9706 | 9.1464 | [5 empty] | 105.4567 | 2668.9706 |  | 104.98
25.01.2008 22:00 | 3600 | 2 | 761.7 | GGB | 763.37 | 767.602 | 766.667 | 263.11 | GGB | 10975.9 | GGB | 9.84 | GGB | 1004.41 | GGB | 56.73 | GGB | 171280.78 | GGB | 140608.95 | GGB | 0 | 0 | 2679 | 3600 | 2663.44 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 125056.07 | GGB | 125057.51 | 2663.44 | 2663.44 |  |  |  | 0 | 1 | [14 empty] | 104.0288 |  |  | #VALUE!
25.01.2008 23:00 | 3600 | 2 | 761.12 | GGB | 764.835 | 770.859 | 768.864 | 264.67 | GGB | 10959.4 | GGB | 9.83 | GGB | 1003.74 | GGB | 56.11 | GGB | 173480.35 | GGB | 142586.27 | GGB | 0 | 0 | 2695 | 3600 | 2679.46 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 125097.02 | GGB | 125098.46 | 2679.46 | 2650.5217 |  |  |  | 1 | 1 |  |  |  |  | 142586.27 | 2650.5217 | 142586.27 | 2650.5217 | 9.229 | [5 empty] | 106.1262 | 2650.5217 |  | 104.98
25.01.2008 24:00 | 3600 | 2 | 761 | GGB | 762.271 | 766.523 | 765.934 | 262.45 | GGB | 10976.4 | GGB | 9.84 | GGB | 1002.59 | GGB | 56.05 | GGB | 171782.53 | GGB | 141056.33 | GGB | 0 | 0 | 2710 | 3600 | 2694.86 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 125134.19 | GGB | 125135.62 | 2694.86 | 2679.27 |  |  |  | 0 | 1 | [14 empty] | 105.5909 | 2679.27 |  | 104.98
26.01.2008 01:00 | 3600 | 2 | 761.37 | GGB | 764.835 | 769.711 | 768.498 | 263.72 | GGB | 10965.3 | GGB | 9.85 | GGB | 1002 | GGB | 56.36 | GGB | 172205.06 | GGB | 141186.12 | GGB | 0 | 0 | 2693 | 3600 | 2677.32 | GGB | 100 | GGB | 43.24 | GGB | 43.24 | GGB | 125177.43 | GGB | 125178.86 | 2677.32 | 2676.807 |  |  |  | 1 | 1 |  |  |  |  | 141186.12 | 2676.807 | 141186.12 | 2676.807 | 8.7402 | [5 empty] | 105.0001 | 2676.807 |  | 104.98
26.01.2008 02:00 | 3600 | 2 | 762.58 | GGB | 765.934 | 771.164 | 769.597 | 260.96 | GGB | 10896.8 | GGB | 9.85 | GGB | 1000.73 | GGB | 57.11 | GGB | 169497.13 | GGB | 138476.62 | GGB | 0 | 0 | 2624 | 3600 | 2608.46 | GGB | 100 | GGB | 38.01 | GGB | 38.01 | GGB | 125215.44 | GGB | 125216.87 | 2608.46 | 2608.46 |  |  |  | 1 | 1 |  |  |  |  | 138476.62 | 2608.46 | 138476.62 | 2608.46 | 9.503 | [5 empty] | 100.3363 |  |  | #VALUE!
26.01.2008 03:00 | 3600 | 2 | 763.48 | GGB | 764.835 | 770.109 | 768.498 | 258.89 | GGB | 10844.9 | GGB | 9.84 | GGB | 999.79 | GGB | 58.07 | GGB | 166897.03 | GGB | 135829.27 | GGB | 0 | 0 | 2574 | 3600 | 2559.04 | GGB | 100 | GGB | 41.48 | GGB | 41.48 | GGB | 125256.93 | GGB | 125258.35 | 2559.04 | 2559.04 |  |  |  | 1 | 1 |  |  |  |  | 135829.27 | 2559.04 | 135829.27 | 2559.04 | 8.3798 | [5 empty] | 96.5535 |  |  | #VALUE!
26.01.2008 04:00 | 3600 | 2 | 763.76 | GGB | 767.033 | 772.266 | 770.696 | 259.94 | GGB | 10794.7 | GGB | 9.83 | GGB | 999.48 | GGB | 58.36 | GGB | 167511.02 | GGB | 136165.45 | GGB | 0 | 0 | 2548 | 3600 | 2532.38 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 125295.49 | GGB | 125296.92 | 2532.38 | 2532.38 |  |  |  | 1 | 1 |  |  |  |  | 136165.45 | 2532.38 | 136165.45 | 2532.38 | 8.9402 | [5 empty] | 95.7841 |  |  | #VALUE!
26.01.2008 05:00 | 3600 | 2 | 764.68 | GGB | 767.033 | 772.125 | 770.696 | 259.1 | GGB | 10797.1 | GGB | 9.84 | GGB | 999.06 | GGB | 58.83 | GGB | 166168.61 | GGB | 134827.76 | GGB | 0 | 0 | 2512 | 3600 | 2496.72 | GGB | 100 | GGB | 41.58 | GGB | 41.58 | GGB | 125337.07 | GGB | 125338.5 | 2496.72 | 2496.72 |  |  |  | 1 | 1 |  |  |  |  | 134827.76 | 2496.72 | 134827.76 | 2496.72 | 8.0959 | [5 empty] | 93.5075 |  |  | #VALUE!
26.01.2008 06:00 | 3600 | 2 | 763.79 | GGB | 765.934 | 771.047 | 769.597 | 258.36 | GGB | 10798.7 | GGB | 9.83 | GGB | 998.59 | GGB | 58.81 | GGB | 165191.51 | GGB | 133980.3 | GGB | 0 | 0 | 2552 | 3600 | 2537.12 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 125375.72 | GGB | 125377.15 | 2537.12 | 2537.12 |  |  |  | 1 | 1 |  |  |  |  | 133980.3 | 2537.12 | 133980.3 | 2537.12 | 8.7949 | [5 empty] | 94.4234 |  |  | #VALUE!
26.01.2008 07:00 | 3600 | 2 | 764.29 | GGB | 767.033 | 773.133 | 770.696 | 259.78 | GGB | 10792.8 | GGB | 9.84 | GGB | 998.95 | GGB | 58.92 | GGB | 166756.19 | GGB | 135252.44 | GGB | 0 | 0 | 2527 | 3600 | 2511.92 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 125416.15 | GGB | 125417.58 | 2511.92 | 2511.92 |  |  |  | 1 | 1 |  |  |  |  | 135252.44 | 2511.92 | 135252.44 | 2511.92 | 8.4032 | [5 empty] | 94.3731 |  |  | #VALUE!
26.01.2008 08:00 | 3600 | 2 | 764.18 | GGB | 767.033 | 771.984 | 769.597 | 259.58 | GGB | 10771.8 | GGB | 9.83 | GGB | 999.55 | GGB | 59.18 | GGB | 166552.62 | GGB | 135063.91 | GGB | 0 | 0 | 2522 | 3600 | 2507.04 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 125454.7 | GGB | 125456.13 | 2507.04 | 2507.04 |  |  |  | 1 | 1 |  |  |  |  | 135063.91 | 2507.04 | 135063.91 | 2507.04 | 8.7837 | [5 empty] | 94.0585 |  |  | #VALUE!
26.01.2008 09:00 | 3600 | 2 | 764.75 | GGB | 767.033 | 771.961 | 770.696 | 259.38 | GGB | 10810.8 | GGB | 9.84 | GGB | 1000.3 | GGB | 59.44 | GGB | 166067.37 | GGB | 134665.75 | GGB | 0 | 0 | 2514 | 3600 | 2498.55 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 125495.28 | GGB | 125496.71 | 2498.55 | 2498.55 |  |  |  | 1 | 1 |  |  |  |  | 134665.75 | 2498.55 | 134665.75 | 2498.55 | 8.2915 | [5 empty] | 93.4636 |  |  | #VALUE!
26.01.2008 10:00 | 3600 | 2 | 764.48 | GGB | 767.033 | 772.758 | 770.696 | 260.1 | GGB | 10795.1 | GGB | 9.83 | GGB | 1001.02 | GGB | 59.33 | GGB | 166912.43 | GGB | 135491.26 | GGB | 0 | 0 | 2521 | 3600 | 2505.67 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 125533.93 | GGB | 125535.35 | 2505.67 | 2505.67 |  |  |  | 1 | 1 |  |  |  |  | 135491.26 | 2505.67 | 135491.26 | 2505.67 | 8.7861 | [5 empty] | 94.3046 |  |  | #VALUE!
26.01.2008 11:00 | 3600 | 2 | 764.46 | GGB | 768.132 | 773.93 | 771.795 | 260.32 | GGB | 10794.7 | GGB | 9.83 | GGB | 1001.38 | GGB | 59.5 | GGB | 166744.08 | GGB | 135336.66 | GGB | 0 | 0 | 2521 | 3600 | 2505.75 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 125574.45 | GGB | 125575.88 | 2505.75 | 2505.75 |  |  |  | 1 | 1 |  |  |  |  | 135336.66 | 2505.75 | 135336.66 | 2505.75 | 8.3671 | [5 empty] | 94.2 |  |  | #VALUE!
26.01.2008 12:00 | 3600 | 2 | 765.14 | GGB | 768.132 | 772.852 | 770.696 | 259.96 | GGB | 10799.2 | GGB | 9.84 | GGB | 1001.47 | GGB | 59.48 | GGB | 166473.4 | GGB | 135134.01 | GGB | 0 | 0 | 2490 | 3600 | 2475.14 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 125613.05 | GGB | 125614.47 | 2475.14 | 2475.14 |  |  |  | 1 | 1 |  |  |  |  | 135134.01 | 2475.14 | 135134.01 | 2475.14 | 8.6674 | [5 empty] | 92.9099 |  |  | #VALUE!
26.01.2008 13:00 | 3600 | 2 | 764.35 | GGB | 765.934 | 771.539 | 769.597 | 259.44 | GGB | 10788.3 | GGB | 9.83 | GGB | 1000.27 | GGB | 59.62 | GGB | 166177.41 | GGB | 134677.98 | GGB | 0 | 0 | 2521 | 3600 | 2505.52 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 125653.59 | GGB | 125655.01 | 2505.52 | 2505.52 |  |  |  | 1 | 1 |  |  |  |  | 134677.98 | 2505.52 | 134677.98 | 2505.52 | 8.3236 | [5 empty] | 93.7329 |  |  | #VALUE!
26.01.2008 14:00 | 3600 | 2 | 764.91 | GGB | 766.667 | 772.781 | 770.696 | 259.7 | GGB | 10788.8 | GGB | 9.84 | GGB | 999.27 | GGB | 59.25 | GGB | 166869.52 | GGB | 135253.76 | GGB | 0 | 0 | 2489 | 3600 | 2474.15 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 125692.47 | GGB | 125693.89 | 2474.15 | 2474.15 |  |  |  | 1 | 1 |  |  |  |  | 135253.76 | 2474.15 | 135253.76 | 2474.15 | 8.6069 | [5 empty] | 92.955 |  |  | #VALUE!
26.01.2008 15:00 | 3600 | 2 | 764.6 | GGB | 767.766 | 773.719 | 771.795 | 259.28 | GGB | 10772.9 | GGB | 9.83 | GGB | 997.57 | GGB | 59.42 | GGB | 166190.61 | GGB | 134403.11 | GGB | 0 | 0 | 2502 | 3600 | 2487.02 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 125732.63 | GGB | 125734.05 | 2487.02 | 2487.02 |  |  |  | 1 | 1 |  |  |  |  | 134403.11 | 2487.02 | 134403.11 | 2487.02 | 8.3233 | [5 empty] | 92.8509 |  |  | #VALUE!
26.01.2008 16:00 | 3600 | 2 | 763.63 | GGB | 765.201 | 770.648 | 768.498 | 259.28 | GGB | 10791.2 | GGB | 9.83 | GGB | 996.67 | GGB | 59.06 | GGB | 165738.37 | GGB | 134063.05 | GGB | 0 | 0 | 2547 | 3600 | 2531.27 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 125771.9 | GGB | 125773.32 | 2531.27 | 2531.27 |  |  |  | 1 | 1 |  |  |  |  | 134063.05 | 2531.27 | 134063.05 | 2531.27 | 8.6415 | [5 empty] | 94.2638 |  |  | #VALUE!
26.01.2008 17:00 | 3600 | 2 | 762.23 | GGB | 764.102 | 768.445 | 767.033 | 259.96 | GGB | 10817.1 | GGB | 9.83 | GGB | 994.81 | GGB | 58.1 | GGB | 167179.82 | GGB | 135368.07 | GGB | 0 | 0 | 2605 | 3600 | 2589.65 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 125811.71 | GGB | 125813.13 | 2589.65 | 2589.65 |  |  |  | 1 | 1 |  |  |  |  | 135368.07 | 2589.65 | 135368.07 | 2589.65 | 8.8057 | [5 empty] | 97.3766 |  |  | #VALUE!
26.01.2008 18:00 | 3600 | 2 | 760.88 | GGB | 762.637 | 767.133 | 765.934 | 261.55 | GGB | 10848.3 | GGB | 9.83 | GGB | 993.03 | GGB | 57.82 | GGB | 168982.17 | GGB | 136697.96 | GGB | 0 | 0 | 2662 | 3600 | 2646.51 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 125851.12 | GGB | 125852.55 | 2646.51 | 2646.51 |  |  |  | 0 | 1 | [14 empty] | 100.4924 |  |  | #VALUE!
26.01.2008 19:00 | 3600 | 2 | 760.77 | GGB | 764.102 | 769.219 | 767.033 | 262.21 | GGB | 10886.7 | GGB | 9.84 | GGB | 990.65 | GGB | 57.99 | GGB | 170356.49 | GGB | 137411.97 | GGB | 0 | 0 | 2693 | 3600 | 2677.38 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 125890.92 | GGB | 125892.34 | 2677.38 | 2677.38 |  |  |  | 1 | 1 |  |  |  |  | 137411.97 | 2677.38 | 137411.97 | 2677.38 | 9.2461 | [5 empty] | 102.1956 |  |  | #VALUE!
26.01.2008 20:00 | 3600 | 2 | 762.88 | GGB | 765.201 | 770.531 | 768.498 | 258.48 | GGB | 10837.1 | GGB | 9.86 | GGB | 988.01 | GGB | 58.21 | GGB | 167751.99 | GGB | 134856.75 | GGB | 0 | 0 | 2578 | 3600 | 2562.81 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 125930.17 | GGB | 125931.59 | 2562.81 | 2562.81 |  |  |  | 1 | 1 |  |  |  |  | 134856.75 | 2562.81 | 134856.75 | 2562.81 | 8.8054 | [5 empty] | 96.0034 |  |  | #VALUE!
26.01.2008 21:00 | 3600 | 2 | 762.89 | GGB | 765.201 | 770.531 | 769.597 | 256.44 | GGB | 10746.3 | GGB | 9.83 | GGB | 986.21 | GGB | 58.38 | GGB | 165281.73 | GGB | 132563.99 | GGB | 0 | 0 | 2549 | 3600 | 2533.77 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 125970.88 | GGB | 125972.3 | 2533.77 | 2533.77 |  |  |  | 1 | 1 |  |  |  |  | 132563.99 | 2533.77 | 132563.99 | 2533.77 | 8.2507 | [5 empty] | 93.3019 |  |  | #VALUE!
26.01.2008 22:00 | 3600 | 2 | 761.15 | GGB | 761.538 | 767.133 | 764.835 | 257.12 | GGB | 10764.1 | GGB | 9.81 | GGB | 986.33 | GGB | 57.2 | GGB | 166638.45 | GGB | 134144 | GGB | 0 | 0 | 2611 | 3600 | 2595.99 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 126010.25 | GGB | 126011.68 | 2595.99 | 2595.99 |  |  |  | 0 | 1 | [14 empty] | 96.7324 |  |  | #VALUE!
26.01.2008 23:00 | 3600 | 2 | 759.54 | GGB | 762.637 | 768.281 | 767.033 | 261.53 | GGB | 10868.1 | GGB | 9.82 | GGB | 987.66 | GGB | 56.13 | GGB | 170294.87 | GGB | 137720.25 | GGB | 0 | 0 | 2731 | 3600 | 2715.54 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 126048.12 | GGB | 126049.54 | 2715.54 | 2715.54 |  |  |  | 0 | 1 | [14 empty] | 103.8847 |  |  | #VALUE!
26.01.2008 24:00 | 3600 | 2 | 760.26 | GGB | 764.102 | 768.469 | 767.033 | 263.71 | GGB | 10885.7 | GGB | 9.83 | GGB | 989.7 | GGB | 56.31 | GGB | 173033.61 | GGB | 140145.18 | GGB | 0 | 0 | 2699 | 3600 | 2683.28 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 126086.78 | GGB | 126088.21 | 2683.28 | 2683.28 |  |  |  | 1 | 1 |  |  |  |  | 140145.18 | 2683.28 | 140145.18 | 2683.28 | 9.7246 | [5 empty] | 104.458 |  |  | #VALUE!
27.01.2008 01:00 | 3600 | 2 | 761.06 | GGB | 762.637 | 768.047 | 765.934 | 262.25 | GGB | 10908.5 | GGB | 9.84 | GGB | 991.29 | GGB | 57.09 | GGB | 171507.44 | GGB | 138805.64 | GGB | 0 | 0 | 2677 | 3600 | 2661.34 | GGB | 100 | GGB | 43.46 | GGB | 43.46 | GGB | 126130.24 | GGB | 126131.67 | 2661.34 | 2661.34 |  |  |  | 0 | 1 | [14 empty] | 102.6136 |  |  | #VALUE!
27.01.2008 02:00 | 3600 | 2 | 760.81 | GGB | 764.102 | 768.961 | 767.033 | 261.81 | GGB | 10903 | GGB | 9.84 | GGB | 992.48 | GGB | 57.51 | GGB | 170688.79 | GGB | 138133.54 | GGB | 0 | 0 | 2694 | 3600 | 2678.64 | GGB | 100 | GGB | 35.93 | GGB | 35.93 | GGB | 126166.17 | GGB | 126167.6 | 2678.64 | 2678.64 |  |  |  | 1 | 1 |  |  |  |  | 138133.54 | 2678.64 | 138133.54 | 2678.64 | 10.2981 | [5 empty] | 102.7806 |  |  | #VALUE!
27.01.2008 03:00 | 3600 | 2 | 761.12 | GGB | 764.102 | 769.758 | 768.132 | 262.65 | GGB | 10868.6 | GGB | 9.83 | GGB | 993.52 | GGB | 57.52 | GGB | 171408.41 | GGB | 138854.45 | GGB | 0 | 0 | 2664 | 3600 | 2648.79 | GGB | 100 | GGB | 43.61 | GGB | 43.61 | GGB | 126209.78 | GGB | 126211.21 | 2648.79 | 2648.79 |  |  |  | 1 | 1 |  |  |  |  | 138854.45 | 2648.79 | 138854.45 | 2648.79 | 8.4338 | [5 empty] | 102.1656 |  |  | #VALUE!
27.01.2008 04:00 | 3600 | 2 | 761.17 | GGB | 762.637 | 767.414 | 765.934 | 262.52 | GGB | 10886.9 | GGB | 9.83 | GGB | 994.23 | GGB | 57.36 | GGB | 171232.36 | GGB | 138881.41 | GGB | 0 | 0 | 2672 | 3600 | 2656.59 | GGB | 100 | GGB | 37 | GGB | 37 | GGB | 126246.78 | GGB | 126248.21 | 2656.59 | 2656.59 |  |  |  | 0 | 1 | [14 empty] | 102.4864 |  |  | #VALUE!
27.01.2008 05:00 | 3600 | 2 | 760.79 | GGB | 763.004 | 768.82 | 767.033 | 262.28 | GGB | 10904.4 | GGB | 9.84 | GGB | 994.67 | GGB | 57.57 | GGB | 170589.76 | GGB | 138330.47 | GGB | 0 | 0 | 2698 | 3600 | 2682.44 | GGB | 100 | GGB | 43.29 | GGB | 43.29 | GGB | 126290.07 | GGB | 126291.5 | 2682.44 | 2682.44 |  |  |  | 0 | 1 | [14 empty] | 103.0731 |  |  | #VALUE!
27.01.2008 06:00 | 3600 | 2 | 761.5 | GGB | 765.201 | 769.969 | 768.864 | 263.5 | GGB | 10872.4 | GGB | 9.83 | GGB | 995.01 | GGB | 57.04 | GGB | 172161.05 | GGB | 139879.61 | GGB | 0 | 0 | 2652 | 3600 | 2636.4 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 126327.88 | GGB | 126329.31 | 2636.4 | 2636.4 |  |  |  | 1 | 1 |  |  |  |  | 139879.61 | 2636.4 | 139879.61 | 2636.4 | 9.7535 | [5 empty] | 102.4385 |  |  | #VALUE!
27.01.2008 07:00 | 3600 | 2 | 761.08 | GGB | 762.637 | 767.578 | 765.201 | 261.86 | GGB | 10901.9 | GGB | 9.83 | GGB | 994.79 | GGB | 56.76 | GGB | 170338.89 | GGB | 138486.72 | GGB | 0 | 0 | 2685 | 3600 | 2669.6 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 126368.51 | GGB | 126369.94 | 2669.6 | 2669.6 |  |  |  | 0 | 1 | [14 empty] | 102.6956 |  |  | #VALUE!
27.01.2008 08:00 | 3600 | 2 | 760.35 | GGB | 762.637 | 767.555 | 766.3 | 262.53 | GGB | 10932.8 | GGB | 9.83 | GGB | 994.99 | GGB | 56.64 | GGB | 170929.77 | GGB | 139044.06 | GGB | 0 | 0 | 2730 | 3600 | 2714.21 | GGB | 100 | GGB | 42.04 | GGB | 42.04 | GGB | 126410.55 | GGB | 126411.98 | 2714.21 | 2714.21 |  |  |  | 0 | 1 | [14 empty] | 104.8319 |  |  | #VALUE!
27.01.2008 09:00 | 3600 | 2 | 760.35 | GGB | 764.102 | 769.641 | 767.766 | 263.93 | GGB | 10892.1 | GGB | 9.83 | GGB | 995.45 | GGB | 56.29 | GGB | 172611.08 | GGB | 140626.45 | GGB | 0 | 0 | 2717 | 3600 | 2702.02 | GGB | 100 | GGB | 37.33 | GGB | 37.33 | GGB | 126447.88 | GGB | 126449.31 | 2702.02 | 2687.4603 |  |  |  | 1 | 1 |  |  |  |  | 140626.45 | 2687.4603 | 140626.45 | 2687.4603 | 10.124 | [5 empty] | 105.5487 | 2687.4603 |  | 104.98
27.01.2008 10:00 | 3600 | 2 | 760.97 | GGB | 764.102 | 769.688 | 767.766 | 263.2 | GGB | 10911.8 | GGB | 9.84 | GGB | 995.56 | GGB | 56.63 | GGB | 172147.84 | GGB | 140119.65 | GGB | 0 | 0 | 2690 | 3600 | 2674.38 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 126487.63 | GGB | 126489.06 | 2674.38 | 2674.38 |  |  |  | 1 | 1 |  |  |  |  | 140119.65 | 2674.38 | 140119.65 | 2674.38 | 9.4273 | [5 empty] | 104.0926 |  |  | #VALUE!
27.01.2008 11:00 | 3600 | 2 | 760.88 | GGB | 763.004 | 768.609 | 766.667 | 261.32 | GGB | 10887 | GGB | 9.84 | GGB | 996.31 | GGB | 57.67 | GGB | 169889.95 | GGB | 137951.15 | GGB | 0 | 0 | 2691 | 3600 | 2675.98 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 126527.5 | GGB | 126528.93 | 2675.98 | 2675.98 |  |  |  | 0 | 1 | [14 empty] | 102.5429 |  |  | #VALUE!
27.01.2008 12:00 | 3600 | 2 | 761.2 | GGB | 764.102 | 769.734 | 767.766 | 262.49 | GGB | 10857.4 | GGB | 9.83 | GGB | 996.51 | GGB | 57.13 | GGB | 171375.4 | GGB | 139411.66 | GGB | 0 | 0 | 2659 | 3600 | 2643.71 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 126568.1 | GGB | 126569.53 | 2643.71 | 2643.71 |  |  |  | 1 | 1 |  |  |  |  | 139411.66 | 2643.71 | 139411.66 | 2643.71 | 9.0779 | [5 empty] | 102.3789 |  |  | #VALUE!
27.01.2008 13:00 | 3600 | 2 | 761.53 | GGB | 763.004 | 768.75 | 766.667 | 261.04 | GGB | 10869.2 | GGB | 9.84 | GGB | 996.6 | GGB | 57.99 | GGB | 169110.91 | GGB | 137226.87 | GGB | 0 | 0 | 2656 | 3600 | 2640.27 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 126607.53 | GGB | 126608.96 | 2640.27 | 2640.27 |  |  |  | 0 | 1 | [14 empty] | 100.6433 |  |  | #VALUE!
27.01.2008 14:00 | 3600 | 2 | 761.49 | GGB | 764.102 | 769.688 | 767.766 | 261.13 | GGB | 10882 | GGB | 9.84 | GGB | 996.34 | GGB | 57.79 | GGB | 169541.14 | GGB | 137620.15 | GGB | 0 | 0 | 2668 | 3600 | 2652.63 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 126647.57 | GGB | 126649.01 | 2652.63 | 2652.63 |  |  |  | 1 | 1 |  |  |  |  | 137620.15 | 2652.63 | 137620.15 | 2652.63 | 9.115 | [5 empty] | 101.4043 |  |  | #VALUE!
27.01.2008 15:00 | 3600 | 2 | 761.82 | GGB | 764.102 | 769.734 | 767.766 | 262.15 | GGB | 10859.7 | GGB | 9.84 | GGB | 996.53 | GGB | 57.79 | GGB | 170156.23 | GGB | 138144.68 | GGB | 0 | 0 | 2643 | 3600 | 2627.24 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 126687.73 | GGB | 126689.16 | 2627.24 | 2627.24 |  |  |  | 1 | 1 |  |  |  |  | 138144.68 | 2627.24 | 138144.68 | 2627.24 | 9.0396 | [5 empty] | 100.8165 |  |  | #VALUE!
27.01.2008 16:00 | 3600 | 2 | 761.16 | GGB | 765.201 | 769.758 | 768.864 | 262.12 | GGB | 10856.4 | GGB | 9.83 | GGB | 997.22 | GGB | 57.88 | GGB | 170424.71 | GGB | 138423.93 | GGB | 0 | 0 | 2670 | 3600 | 2654.32 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 126727.58 | GGB | 126729.01 | 2654.32 | 2654.32 |  |  |  | 1 | 1 |  |  |  |  | 138423.93 | 2654.32 | 138423.93 | 2654.32 | 9.2201 | [5 empty] | 102.0615 |  |  | #VALUE!
27.01.2008 17:00 | 3600 | 2 | 761.1 | GGB | 763.004 | 768.656 | 766.3 | 262.38 | GGB | 10888.9 | GGB | 9.83 | GGB | 997.85 | GGB | 58.07 | GGB | 170184.84 | GGB | 138237.41 | GGB | 0 | 0 | 2686 | 3600 | 2670.68 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 126767.25 | GGB | 126768.68 | 2670.68 | 2670.68 |  |  |  | 0 | 1 | [14 empty] | 102.5522 |  |  | #VALUE!
27.01.2008 18:00 | 3600 | 2 | 760.71 | GGB | 764.102 | 769.852 | 766.667 | 264.27 | GGB | 10890.1 | GGB | 9.83 | GGB | 999 | GGB | 57.38 | GGB | 172515.35 | GGB | 140584.31 | GGB | 0 | 0 | 2696 | 3600 | 2680.69 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 126807.56 | GGB | 126808.99 | 2680.69 | 2680.69 |  |  |  | 1 | 1 |  |  |  |  | 140584.31 | 2680.69 | 140584.31 | 2680.69 | 9.3491 | [5 empty] | 104.6842 |  |  | #VALUE!
27.01.2008 19:00 | 3600 | 2 | 761.1 | GGB | 763.004 | 768.914 | 766.667 | 264 | GGB | 10926.7 | GGB | 9.84 | GGB | 1000.36 | GGB | 57.5 | GGB | 172048.81 | GGB | 140342.05 | GGB | 0 | 0 | 2697 | 3600 | 2681.35 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 126846.78 | GGB | 126848.21 | 2681.35 | 2681.35 |  |  |  | 0 | 1 | [14 empty] | 104.5295 |  |  | #VALUE!
27.01.2008 20:00 | 3600 | 2 | 760.26 | GGB | 762.637 | 767.883 | 766.3 | 263.91 | GGB | 10946.6 | GGB | 9.83 | GGB | 1001.82 | GGB | 57.86 | GGB | 171602.07 | GGB | 140029.39 | GGB | 0 | 0 | 2752 | 3600 | 2736.34 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 126887.27 | GGB | 126888.69 | 2736.34 | 2698.9191 |  |  |  | 0 | 1 | [14 empty] | 106.4356 | 2698.9191 |  | 104.98
27.01.2008 21:00 | 3600 | 2 | 760.47 | GGB | 763.004 | 768.867 | 766.667 | 264.83 | GGB | 10962.2 | GGB | 9.83 | GGB | 1003.43 | GGB | 57.56 | GGB | 172538.46 | GGB | 141146.59 | GGB | 0 | 0 | 2753 | 3600 | 2738.03 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 126927.16 | GGB | 126928.59 | 2738.03 | 2677.5567 |  |  |  | 0 | 1 | [14 empty] | 107.351 | 2677.5567 |  | 104.98
27.01.2008 22:00 | 3600 | 2 | 760.84 | GGB | 766.3 | 771.445 | 769.963 | 266.24 | GGB | 10964.7 | GGB | 9.84 | GGB | 1004.75 | GGB | 56.98 | GGB | 174689.62 | GGB | 143348.63 | GGB | 0 | 0 | 2735 | 3600 | 2719.56 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 126967.03 | GGB | 126968.45 | 2719.56 | 2636.4256 |  |  |  | 1 | 1 |  |  |  |  | 143348.63 | 2636.4256 | 143348.63 | 2636.4256 | 9.4814 | [5 empty] | 108.2903 | 2636.4256 |  | 104.98
27.01.2008 23:00 | 3600 | 2 | 760.13 | GGB | 764.102 | 769.477 | 767.766 | 266.34 | GGB | 10975.8 | GGB | 9.82 | GGB | 1005.69 | GGB | 57.63 | GGB | 172871.86 | GGB | 141709.53 | GGB | 0 | 0 | 2787 | 3600 | 2771.04 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 127007 | GGB | 127008.43 | 2771.04 | 2666.9201 |  |  |  | 1 | 1 |  |  |  |  | 141709.53 | 2666.9201 | 141709.53 | 2666.9201 | 9.4529 | [5 empty] | 109.0785 | 2666.9201 |  | 104.98
27.01.2008 24:00 | 3600 | 2 | 760.2 | GGB | 764.102 | 768.305 | 766.3 | 267.27 | GGB | 10966.7 | GGB | 9.82 | GGB | 1006.75 | GGB | 57.94 | GGB | 173448.44 | GGB | 142197.74 | GGB | 0 | 0 | 2786 | 3600 | 2770.39 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 127047.41 | GGB | 127048.84 | 2770.39 | 2657.7638 |  |  |  | 1 | 1 |  |  |  |  | 142197.74 | 2657.7638 | 142197.74 | 2657.7638 | 9.3523 | [5 empty] | 109.4287 | 2657.7638 |  | 104.98
28.01.2008 01:00 | 3600 | 2 | 761.34 | GGB | 764.102 | 769.43 | 766.667 | 268.28 | GGB | 10976.4 | GGB | 9.84 | GGB | 1007.54 | GGB | 57.6 | GGB | 174684.12 | GGB | 143472.94 | GGB | 0 | 0 | 2734 | 3600 | 2718.92 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 127087.29 | GGB | 127088.72 | 2718.92 | 2634.1413 |  |  |  | 1 | 1 |  |  |  |  | 143472.94 | 2634.1413 | 143472.94 | 2634.1413 | 9.4766 | [5 empty] | 108.3587 | 2634.1413 |  | 104.98
28.01.2008 02:00 | 3600 | 2 | 761.43 | GGB | 765.201 | 769.523 | 768.132 | 267.45 | GGB | 11011 | GGB | 9.85 | GGB | 1008.7 | GGB | 57.64 | GGB | 173679.51 | GGB | 142795.68 | GGB | 0 | 0 | 2736 | 3600 | 2720.15 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 127127.33 | GGB | 127128.76 | 2720.15 | 2646.6347 |  |  |  | 1 | 1 |  |  |  |  | 142795.68 | 2646.6347 | 142795.68 | 2646.6347 | 9.4388 | [5 empty] | 107.896 | 2646.6347 |  | 104.98
28.01.2008 03:00 | 3600 | 2 | 760.81 | GGB | 764.102 | 768.516 | 768.132 | 266.9 | GGB | 11009.8 | GGB | 9.83 | GGB | 1010.31 | GGB | 58.05 | GGB | 172748.63 | GGB | 142077.82 | GGB | 0 | 0 | 2769 | 3600 | 2753.05 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 127167.91 | GGB | 127169.34 | 2753.05 | 2660.007 |  |  |  | 1 | 1 |  |  |  |  | 142077.82 | 2660.007 | 142077.82 | 2660.007 | 9.3132 | [5 empty] | 108.652 | 2660.007 |  | 104.98
28.01.2008 04:00 | 3600 | 2 | 760.86 | GGB | 765.201 | 770.672 | 768.498 | 268.81 | GGB | 10993.1 | GGB | 9.82 | GGB | 1011.64 | GGB | 57.31 | GGB | 175113.25 | GGB | 144538.87 | GGB | 0 | 0 | 2765 | 3600 | 2749.51 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 127208.18 | GGB | 127209.62 | 2749.51 | 2614.7153 |  |  |  | 1 | 1 |  |  |  |  | 144538.87 | 2614.7153 | 144538.87 | 2614.7153 | 9.3825 | [5 empty] | 110.392 | 2614.7153 |  | 104.98
28.01.2008 05:00 | 3600 | 2 | 761.05 | GGB | 765.201 | 769.711 | 768.132 | 269.74 | GGB | 11017.7 | GGB | 9.83 | GGB | 1013.37 | GGB | 57.33 | GGB | 175737.14 | GGB | 145289.03 | GGB | 0 | 0 | 2758 | 3600 | 2742.47 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 127248.48 | GGB | 127249.92 | 2742.47 | 2601.215 |  |  |  | 1 | 1 |  |  |  |  | 145289.03 | 2601.215 | 145289.03 | 2601.215 | 9.3779 | [5 empty] | 110.6808 | 2601.215 |  | 104.98
28.01.2008 06:00 | 3600 | 2 | 760.95 | GGB | 763.004 | 768.703 | 767.033 | 268.99 | GGB | 11056.7 | GGB | 9.84 | GGB | 1014.24 | GGB | 57.8 | GGB | 174596.09 | GGB | 144267.61 | GGB | 0 | 0 | 2778 | 3600 | 2762.49 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 127288.86 | GGB | 127290.3 | 2762.49 | 2619.6317 |  |  |  | 0 | 1 | [14 empty] | 110.705 | 2619.6317 |  | 104.98
28.01.2008 07:00 | 3600 | 2 | 761.02 | GGB | 764.102 | 769.594 | 768.132 | 268.14 | GGB | 11066.7 | GGB | 9.84 | GGB | 1015.33 | GGB | 57.89 | GGB | 173845.66 | GGB | 143759.41 | GGB | 0 | 0 | 2782 | 3600 | 2766.65 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 127329.12 | GGB | 127330.56 | 2766.65 | 2628.8923 |  |  |  | 1 | 1 |  |  |  |  | 143759.41 | 2628.8923 | 143759.41 | 2628.8923 | 9.3872 | [5 empty] | 110.4811 | 2628.8923 |  | 104.98
28.01.2008 08:00 | 3600 | 2 | 760.45 | GGB | 764.102 | 769.359 | 767.033 | 269.84 | GGB | 11037.6 | GGB | 9.81 | GGB | 1016.59 | GGB | 57.11 | GGB | 176162.97 | GGB | 146203.14 | GGB | 0 | 0 | 2801 | 3600 | 2785.79 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 127370.08 | GGB | 127371.52 | 2785.79 | 2584.9513 |  |  |  | 1 | 1 |  |  |  |  | 146203.14 | 2584.9513 | 146203.14 | 2584.9513 | 9.2268 | [5 empty] | 113.1365 | 2584.9513 |  | 104.98
28.01.2008 09:00 | 3600 | 2 | 760.72 | GGB | 763.004 | 768.445 | 767.033 | 270.82 | GGB | 11123.3 | GGB | 9.84 | GGB | 1018.21 | GGB | 56.99 | GGB | 176512.88 | GGB | 146780.57 | GGB | 0 | 0 | 2823 | 3600 | 2807.59 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 127409.53 | GGB | 127410.97 | 2807.59 | 2574.7822 |  |  |  | 0 | 1 | [14 empty] | 114.4721 | 2574.7822 |  | 104.98
28.01.2008 10:00 | 3600 | 2 | 760.44 | GGB | 764.102 | 769.406 | 767.033 | 272.45 | GGB | 11110.2 | GGB | 9.82 | GGB | 1019.93 | GGB | 56.55 | GGB | 178782.88 | GGB | 149114.69 | GGB | 0 | 0 | 2833 | 3600 | 2817.87 | GGB | 100 | GGB | 41.75 | GGB | 41.75 | GGB | 127451.28 | GGB | 127452.72 | 2817.87 | 2534.4787 |  |  |  | 1 | 1 |  |  |  |  | 149114.69 | 2534.4787 | 149114.69 | 2534.4787 | 9.0522 | [5 empty] | 116.7183 | 2534.4787 |  | 104.98
28.01.2008 11:00 | 3600 | 2 | 761.48 | GGB | 764.102 | 769.219 | 767.033 | 271.21 | GGB | 11162.2 | GGB | 9.85 | GGB | 1021.46 | GGB | 57.13 | GGB | 177368.94 | GGB | 147899.43 | GGB | 0 | 0 | 2803 | 3600 | 2787.91 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 127491.44 | GGB | 127492.88 | 2787.91 | 2555.304 |  |  |  | 1 | 1 |  |  |  |  | 147899.43 | 2555.304 | 147899.43 | 2555.304 | 9.4106 | [5 empty] | 114.5362 | 2555.304 |  | 104.98
28.01.2008 12:00 | 3600 | 2 | 760 | GGB | 763.004 | 768.188 | 765.934 | 272.01 | GGB | 11141.7 | GGB | 9.82 | GGB | 1022.28 | GGB | 56.89 | GGB | 178067.66 | GGB | 148708.99 | GGB | 0 | 0 | 2862 | 3600 | 2846.45 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 127532.31 | GGB | 127533.75 | 2846.45 | 2541.3931 |  |  |  | 0 | 1 | [14 empty] | 117.5813 | 2541.3931 |  | 104.98
28.01.2008 13:00 | 3600 | 2 | 761.14 | GGB | 765.201 | 770.625 | 769.597 | 272.66 | GGB | 11151.7 | GGB | 9.84 | GGB | 1023.18 | GGB | 56.57 | GGB | 179059.06 | GGB | 149815.57 | GGB | 0 | 0 | 2821 | 3600 | 2805.83 | GGB | 100 | GGB | 41.48 | GGB | 41.48 | GGB | 127573.79 | GGB | 127575.23 | 2805.83 | 2522.6216 |  |  |  | 1 | 1 |  |  |  |  | 149815.57 | 2522.6216 | 149815.57 | 2522.6216 | 9.1111 | [5 empty] | 116.7658 | 2522.6216 |  | 104.98
28.01.2008 14:00 | 3600 | 2 | 761.9 | GGB | 765.201 | 771.469 | 768.498 | 272.02 | GGB | 11137.6 | GGB | 9.84 | GGB | 1023.58 | GGB | 56.92 | GGB | 178198.6 | GGB | 148995.21 | GGB | 0 | 0 | 2780 | 3600 | 2764.36 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 127613.95 | GGB | 127615.39 | 2764.36 | 2536.5111 |  |  |  | 1 | 1 |  |  |  |  | 148995.21 | 2536.5111 | 148995.21 | 2536.5111 | 9.4106 | [5 empty] | 114.4101 | 2536.5111 |  | 104.98
28.01.2008 15:00 | 3600 | 2 | 761.72 | GGB | 764.102 | 769.453 | 767.766 | 270.64 | GGB | 11155.3 | GGB | 9.84 | GGB | 1023.02 | GGB | 57.99 | GGB | 175922 | GGB | 146533.66 | GGB | 0 | 0 | 2799 | 3600 | 2783.13 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 127655.05 | GGB | 127656.49 | 2783.13 | 2579.1207 |  |  |  | 1 | 1 |  |  |  |  | 146533.66 | 2579.1207 | 146533.66 | 2579.1207 | 9.1953 | [5 empty] | 113.284 | 2579.1207 |  | 104.98
28.01.2008 16:00 | 3600 | 2 | 760.95 | GGB | 763.004 | 768.422 | 766.3 | 270.96 | GGB | 11115.4 | GGB | 9.82 | GGB | 1022.8 | GGB | 58.08 | GGB | 176260.9 | GGB | 146745.65 | GGB | 0 | 0 | 2818 | 3600 | 2802.03 | GGB | 100 | GGB | 41.94 | GGB | 41.94 | GGB | 127697 | GGB | 127698.43 | 2802.03 | 2575.3949 |  |  |  | 0 | 1 | [14 empty] | 114.2183 | 2575.3949 |  | 104.98
28.01.2008 17:00 | 3600 | 2 | 761.47 | GGB | 765.201 | 770.32 | 768.864 | 272.27 | GGB | 11115.5 | GGB | 9.83 | GGB | 1023.55 | GGB | 57.53 | GGB | 177604.42 | GGB | 148220.04 | GGB | 0 | 0 | 2807 | 3600 | 2791.97 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 127737.15 | GGB | 127738.58 | 2791.97 | 2549.7767 |  |  |  | 1 | 1 |  |  |  |  | 148220.04 | 2549.7767 | 148220.04 | 2549.7767 | 9.4129 | [5 empty] | 114.9516 | 2549.7767 |  | 104.98
28.01.2008 18:00 | 3600 | 2 | 761.16 | GGB | 764.102 | 769.172 | 766.667 | 271.67 | GGB | 11152.7 | GGB | 9.84 | GGB | 1023.99 | GGB | 58.11 | GGB | 176166.27 | GGB | 146826.22 | GGB | 0 | 0 | 2839 | 3600 | 2823.41 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 127777.6 | GGB | 127779.03 | 2823.41 | 2573.9817 |  |  |  | 1 | 1 |  |  |  |  | 146826.22 | 2573.9817 | 146826.22 | 2573.9817 | 9.3431 | [5 empty] | 115.1529 | 2573.9817 |  | 104.98
28.01.2008 19:00 | 3600 | 2 | 760.35 | GGB | 763.004 | 768.188 | 766.667 | 274.24 | GGB | 11131.4 | GGB | 9.82 | GGB | 1024.06 | GGB | 57.39 | GGB | 179097.57 | GGB | 149600.97 | GGB | 0 | 0 | 2872 | 3600 | 2856.14 | GGB | 100 | GGB | 41.48 | GGB | 41.48 | GGB | 127819.08 | GGB | 127820.51 | 2856.14 | 2526.2403 |  |  |  | 0 | 1 | [14 empty] | 118.6893 | 2526.2403 |  | 104.98
28.01.2008 20:00 | 3600 | 2 | 761.23 | GGB | 765.201 | 770.414 | 767.766 | 273.86 | GGB | 11176.9 | GGB | 9.84 | GGB | 1023.69 | GGB | 57.64 | GGB | 178623.33 | GGB | 149042.82 | GGB | 0 | 0 | 2845 | 3600 | 2829.86 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 127858.93 | GGB | 127860.36 | 2829.86 | 2535.7008 |  |  |  | 1 | 1 |  |  |  |  | 149042.82 | 2535.7008 | 149042.82 | 2535.7008 | 9.4838 | [5 empty] | 117.1584 | 2535.7008 |  | 104.98
28.01.2008 21:00 | 3600 | 2 | 760.15 | GGB | 762.637 | 766.992 | 765.201 | 273.36 | GGB | 11167.9 | GGB | 9.83 | GGB | 1023.55 | GGB | 57.98 | GGB | 177772.77 | GGB | 148159.93 | GGB | 0 | 0 | 2903 | 3600 | 2887.09 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 127899.85 | GGB | 127901.28 | 2887.09 | 2550.8111 |  |  |  | 0 | 1 | [14 empty] | 118.8197 | 2550.8111 |  | 104.98
28.01.2008 22:00 | 3600 | 2 | 760.77 | GGB | 764.102 | 770.32 | 767.766 | 274.68 | GGB | 11159.4 | GGB | 9.83 | GGB | 1023.26 | GGB | 57.59 | GGB | 179306.64 | GGB | 149569.15 | GGB | 0 | 0 | 2871 | 3600 | 2855.82 | GGB | 100 | GGB | 41.46 | GGB | 41.46 | GGB | 127941.31 | GGB | 127942.74 | 2855.82 | 2526.7777 |  |  |  | 1 | 1 |  |  |  |  | 149569.15 | 2526.7777 | 149569.15 | 2526.7777 | 9.1155 | [5 empty] | 118.6507 | 2526.7777 |  | 104.98
28.01.2008 23:00 | 3600 | 2 | 761.07 | GGB | 764.102 | 769.313 | 766.667 | 273.77 | GGB | 11181.2 | GGB | 9.84 | GGB | 1023 | GGB | 57.7 | GGB | 178275.62 | GGB | 148622.27 | GGB | 0 | 0 | 2851 | 3600 | 2835.92 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 127980.82 | GGB | 127982.24 | 2835.92 | 2542.876 |  |  |  | 1 | 1 |  |  |  |  | 148622.27 | 2542.876 | 148622.27 | 2542.876 | 9.5678 | [5 empty] | 117.078 | 2542.876 |  | 104.98
28.01.2008 24:00 | 3600 | 2 | 760.04 | GGB | 764.102 | 769.43 | 766.3 | 274.62 | GGB | 11142 | GGB | 9.82 | GGB | 1022.79 | GGB | 57.65 | GGB | 179053.56 | GGB | 149263.79 | GGB | 0 | 0 | 2901 | 3600 | 2885.91 | GGB | 100 | GGB | 42.57 | GGB | 42.57 | GGB | 128023.38 | GGB | 128024.81 | 2885.91 | 2531.947 |  |  |  | 1 | 1 |  |  |  |  | 149263.79 | 2531.947 | 149263.79 | 2531.947 | 8.8778 | [5 empty] | 119.6561 | 2531.947 |  | 104.98
29.01.2008 01:00 | 3600 | 2 | 761.83 | GGB | 764.102 | 769.313 | 766.667 | 273.09 | GGB | 11181.9 | GGB | 9.86 | GGB | 1021.97 | GGB | 58 | GGB | 177362.34 | GGB | 147579.17 | GGB | 0 | 0 | 2825 | 3600 | 2809.67 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 128063.04 | GGB | 128064.47 | 2809.67 | 2560.8492 |  |  |  | 1 | 1 |  |  |  |  | 147579.17 | 2560.8492 | 147579.17 | 2560.8492 | 9.5292 | [5 empty] | 115.1802 | 2560.8492 |  | 104.98
29.01.2008 02:00 | 3600 | 2 | 761.73 | GGB | 764.102 | 769.43 | 767.766 | 272.91 | GGB | 11106.4 | GGB | 9.84 | GGB | 1021.23 | GGB | 57.84 | GGB | 177883.9 | GGB | 147976.16 | GGB | 0 | 0 | 2807 | 3600 | 2791.65 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 128103.71 | GGB | 128105.13 | 2791.65 | 2553.979 |  |  |  | 1 | 1 |  |  |  |  | 147976.16 | 2553.979 | 147976.16 | 2553.979 | 9.2948 | [5 empty] | 114.7493 | 2553.979 |  | 104.98
29.01.2008 03:00 | 3600 | 2 | 761.1 | GGB | 763.004 | 768.656 | 766.667 | 273.12 | GGB | 11087.8 | GGB | 9.83 | GGB | 1020.77 | GGB | 57.97 | GGB | 177733.16 | GGB | 147725.4 | GGB | 0 | 0 | 2809 | 3600 | 2793.34 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 128144.44 | GGB | 128145.86 | 2793.34 | 2558.3143 |  |  |  | 0 | 1 | [14 empty] | 114.6242 | 2558.3143 |  | 104.98
29.01.2008 04:00 | 3600 | 2 | 761.52 | GGB | 764.102 | 768.422 | 767.766 | 271.95 | GGB | 11138.4 | GGB | 9.85 | GGB | 1020.46 | GGB | 58.6 | GGB | 175826.27 | GGB | 145819.19 | GGB | 0 | 0 | 2827 | 3600 | 2811.61 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 128184.75 | GGB | 128186.17 | 2811.61 | 2591.7576 |  |  |  | 1 | 1 |  |  |  |  | 145819.19 | 2591.7576 | 145819.19 | 2591.7576 | 9.3755 | [5 empty] | 113.8852 | 2591.7576 |  | 104.98
29.01.2008 05:00 | 3600 | 2 | 760.8 | GGB | 764.102 | 769.43 | 766.667 | 272.9 | GGB | 11090.7 | GGB | 9.83 | GGB | 1020.07 | GGB | 58.28 | GGB | 177208.29 | GGB | 147051.28 | GGB | 0 | 0 | 2836 | 3600 | 2820.31 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 128226.04 | GGB | 128227.46 | 2820.31 | 2570.0422 |  |  |  | 1 | 1 |  |  |  |  | 147051.28 | 2570.0422 | 147051.28 | 2570.0422 | 9.153 | [5 empty] | 115.2028 | 2570.0422 |  | 104.98
29.01.2008 06:00 | 3600 | 2 | 762.03 | GGB | 765.201 | 771.539 | 768.864 | 272.75 | GGB | 11094.2 | GGB | 9.84 | GGB | 1019.42 | GGB | 58.13 | GGB | 177374.45 | GGB | 147163.16 | GGB | 0 | 0 | 2772 | 3600 | 2756.77 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 128266.48 | GGB | 128267.91 | 2756.77 | 2568.0884 |  |  |  | 1 | 1 |  |  |  |  | 147163.16 | 2568.0884 | 147163.16 | 2568.0884 | 9.3431 | [5 empty] | 112.6931 | 2568.0884 |  | 104.98
29.01.2008 07:00 | 3600 | 2 | 762.38 | GGB | 765.201 | 769.547 | 767.766 | 270.41 | GGB | 11105.2 | GGB | 9.85 | GGB | 1019.02 | GGB | 58.76 | GGB | 174701.73 | GGB | 144615.46 | GGB | 0 | 0 | 2768 | 3600 | 2752.58 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 128306.42 | GGB | 128307.85 | 2752.58 | 2613.3306 |  |  |  | 1 | 1 |  |  |  |  | 144615.46 | 2613.3306 | 144615.46 | 2613.3306 | 9.4624 | [5 empty] | 110.5738 | 2613.3306 |  | 104.98
29.01.2008 08:00 | 3600 | 2 | 761.57 | GGB | 764.102 | 769.43 | 767.766 | 271.19 | GGB | 11042.5 | GGB | 9.83 | GGB | 1018.77 | GGB | 58.38 | GGB | 175770.15 | GGB | 145630.25 | GGB | 0 | 0 | 2774 | 3600 | 2758.17 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 128348.07 | GGB | 128349.49 | 2758.17 | 2595.1202 |  |  |  | 1 | 1 |  |  |  |  | 145630.25 | 2595.1202 | 145630.25 | 2595.1202 | 9.0761 | [5 empty] | 111.5758 | 2595.1202 |  | 104.98
29.01.2008 09:00 | 3600 | 2 | 761.98 | GGB | 764.102 | 769.336 | 767.766 | 271.69 | GGB | 11048.7 | GGB | 9.83 | GGB | 1019.13 | GGB | 58.33 | GGB | 176011.13 | GGB | 145902.59 | GGB | 0 | 0 | 2762 | 3600 | 2746.87 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 128388.06 | GGB | 128389.48 | 2746.87 | 2590.2762 |  |  |  | 1 | 1 |  |  |  |  | 145902.59 | 2590.2762 | 145902.59 | 2590.2762 | 9.4506 | [5 empty] | 111.3265 | 2590.2762 |  | 104.98
29.01.2008 10:00 | 3600 | 2 | 762.3 | GGB | 766.3 | 771.445 | 768.864 | 271.34 | GGB | 11074.4 | GGB | 9.84 | GGB | 1019.23 | GGB | 58.24 | GGB | 175616.11 | GGB | 145628.87 | GGB | 0 | 0 | 2757 | 3600 | 2741.65 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 128428 | GGB | 128429.43 | 2741.65 | 2595.1448 |  |  |  | 1 | 1 |  |  |  |  | 145628.87 | 2595.1448 | 145628.87 | 2595.1448 | 9.46 | [5 empty] | 110.9065 | 2595.1448 |  | 104.98
29.01.2008 11:00 | 3600 | 2 | 761.82 | GGB | 765.201 | 770.297 | 767.766 | 269.6 | GGB | 11072.4 | GGB | 9.84 | GGB | 1019.22 | GGB | 59.08 | GGB | 173102.93 | GGB | 143179.68 | GGB | 0 | 0 | 2788 | 3600 | 2772.27 | GGB | 100 | GGB | 41.42 | GGB | 41.42 | GGB | 128469.43 | GGB | 128470.85 | 2772.27 | 2639.5366 |  |  |  | 1 | 1 |  |  |  |  | 143179.68 | 2639.5366 | 143179.68 | 2639.5366 | 9.1243 | [5 empty] | 110.2591 | 2639.5366 |  | 104.98
29.01.2008 12:00 | 3600 | 2 | 761.85 | GGB | 765.201 | 771.398 | 768.864 | 270.42 | GGB | 11021.5 | GGB | 9.83 | GGB | 1019.59 | GGB | 58.91 | GGB | 174165.86 | GGB | 144186.52 | GGB | 0 | 0 | 2774 | 3600 | 2758.44 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 128509.52 | GGB | 128510.95 | 2758.44 | 2621.1049 |  |  |  | 1 | 1 |  |  |  |  | 144186.52 | 2621.1049 | 144186.52 | 2621.1049 | 9.4246 | [5 empty] | 110.4805 | 2621.1049 |  | 104.98
29.01.2008 13:00 | 3600 | 2 | 762.94 | GGB | 765.201 | 771.422 | 768.864 | 270.4 | GGB | 11018 | GGB | 9.84 | GGB | 1018.97 | GGB | 58.79 | GGB | 174306.7 | GGB | 144268.12 | GGB | 0 | 0 | 2722 | 3600 | 2706.37 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 128549.86 | GGB | 128551.29 | 2706.37 | 2619.6224 |  |  |  | 1 | 1 |  |  |  |  | 144268.12 | 2619.6224 | 144268.12 | 2619.6224 | 9.3686 | [5 empty] | 108.4564 | 2619.6224 |  | 104.98
29.01.2008 14:00 | 3600 | 2 | 763.37 | GGB | 767.766 | 772.477 | 769.963 | 269.28 | GGB | 11017.4 | GGB | 9.84 | GGB | 1018.29 | GGB | 59.22 | GGB | 172834.45 | GGB | 142768.71 | GGB | 0 | 0 | 2712 | 3600 | 2696.59 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 128590.5 | GGB | 128591.92 | 2696.59 | 2647.1347 |  |  |  | 1 | 1 |  |  |  |  | 142768.71 | 2647.1347 | 142768.71 | 2647.1347 | 9.3017 | [5 empty] | 106.9413 | 2647.1347 |  | 104.98
29.01.2008 15:00 | 3600 | 2 | 762.51 | GGB | 765.201 | 770.344 | 768.864 | 268.57 | GGB | 10987.1 | GGB | 9.83 | GGB | 1017.9 | GGB | 59.77 | GGB | 171758.32 | GGB | 141587.53 | GGB | 0 | 0 | 2731 | 3600 | 2715.2 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 128630.23 | GGB | 128631.66 | 2715.2 | 2669.2181 |  |  |  | 1 | 1 |  |  |  |  | 141587.53 | 2669.2181 | 141587.53 | 2669.2181 | 9.51 | [5 empty] | 106.7885 | 2669.2181 |  | 104.98
29.01.2008 16:00 | 3600 | 2 | 763.5 | GGB | 765.201 | 771.07 | 768.864 | 269.54 | GGB | 10967.1 | GGB | 9.84 | GGB | 1017.69 | GGB | 59.47 | GGB | 172720.02 | GGB | 142481.61 | GGB | 0 | 0 | 2681 | 3600 | 2666.02 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 128670.88 | GGB | 128672.31 | 2666.02 | 2652.4686 |  |  |  | 1 | 1 |  |  |  |  | 142481.61 | 2652.4686 | 142481.61 | 2652.4686 | 9.2971 | [5 empty] | 105.5163 | 2652.4686 |  | 104.98
29.01.2008 17:00 | 3600 | 2 | 764.16 | GGB | 766.667 | 772.125 | 770.33 | 267.88 | GGB | 10985.1 | GGB | 9.85 | GGB | 1017.31 | GGB | 59.98 | GGB | 170736.11 | GGB | 140578.07 | GGB | 0 | 0 | 2669 | 3600 | 2653.33 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 128710.92 | GGB | 128712.35 | 2653.33 | 2653.33 |  |  |  | 1 | 1 |  |  |  |  | 140578.07 | 2653.33 | 140578.07 | 2653.33 | 9.3157 | [5 empty] | 103.6111 |  |  | #VALUE!
29.01.2008 18:00 | 3600 | 2 | 763.4 | GGB | 766.3 | 772.055 | 769.963 | 266.96 | GGB | 10962.2 | GGB | 9.83 | GGB | 1017.07 | GGB | 60.39 | GGB | 169459.72 | GGB | 139321.15 | GGB | 0 | 0 | 2696 | 3600 | 2680.19 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 128750.75 | GGB | 128752.19 | 2680.19 | 2680.19 |  |  |  | 1 | 1 |  |  |  |  | 139321.15 | 2680.19 | 139321.15 | 2680.19 | 9.3727 | [5 empty] | 103.7242 |  |  | #VALUE!
29.01.2008 19:00 | 3600 | 2 | 763.47 | GGB | 766.3 | 770.977 | 769.963 | 267.09 | GGB | 10949.1 | GGB | 9.83 | GGB | 1016.97 | GGB | 60.34 | GGB | 169404.7 | GGB | 139283.87 | GGB | 0 | 0 | 2688 | 3600 | 2672.71 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 128791.77 | GGB | 128793.21 | 2672.71 | 2672.71 |  |  |  | 1 | 1 |  |  |  |  | 139283.87 | 2672.71 | 139283.87 | 2672.71 | 9.0752 | [5 empty] | 103.4071 |  |  | #VALUE!
29.01.2008 20:00 | 3600 | 2 | 763.83 | GGB | 767.766 | 773.203 | 771.429 | 268.59 | GGB | 10928.8 | GGB | 9.83 | GGB | 1017.1 | GGB | 59.54 | GGB | 171641.69 | GGB | 141481.55 | GGB | 0 | 0 | 2655 | 3600 | 2639.67 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 128831.79 | GGB | 128833.23 | 2639.67 | 2639.67 |  |  |  | 1 | 1 |  |  |  |  | 141481.55 | 2639.67 | 141481.55 | 2639.67 | 9.3319 | [5 empty] | 103.7402 |  |  | #VALUE!
29.01.2008 21:00 | 3600 | 2 | 764.3 | GGB | 766.667 | 772.055 | 770.33 | 267.66 | GGB | 10945.5 | GGB | 9.84 | GGB | 1016.96 | GGB | 59.96 | GGB | 170292.67 | GGB | 140171.81 | GGB | 0 | 0 | 2644 | 3600 | 2628.32 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 128871.55 | GGB | 128872.99 | 2628.32 | 2628.32 |  |  |  | 1 | 1 |  |  |  |  | 140171.81 | 2628.32 | 140171.81 | 2628.32 | 9.266 | [5 empty] | 102.3379 |  |  | #VALUE!
29.01.2008 22:00 | 3600 | 2 | 763.55 | GGB | 765.201 | 771.023 | 768.864 | 266.74 | GGB | 10943.8 | GGB | 9.83 | GGB | 1016.74 | GGB | 60.46 | GGB | 169068 | GGB | 138926.34 | GGB | 0 | 0 | 2679 | 3600 | 2663.23 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 128912.33 | GGB | 128913.77 | 2663.23 | 2663.23 |  |  |  | 1 | 1 |  |  |  |  | 138926.34 | 2663.23 | 138926.34 | 2663.23 | 9.0729 | [5 empty] | 102.7758 |  |  | #VALUE!
29.01.2008 23:00 | 3600 | 2 | 763.77 | GGB | 765.201 | 771.094 | 767.766 | 267.27 | GGB | 10926.3 | GGB | 9.83 | GGB | 1017.05 | GGB | 59.73 | GGB | 171427.12 | GGB | 141215.8 | GGB | 0 | 0 | 2651 | 3600 | 2635.96 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 128952.25 | GGB | 128953.69 | 2635.96 | 2635.96 |  |  |  | 1 | 1 |  |  |  |  | 141215.8 | 2635.96 | 141215.8 | 2635.96 | 9.3246 | [5 empty] | 103.3998 |  |  | #VALUE!
29.01.2008 24:00 | 3600 | 2 | 764.4 | GGB | 766.667 | 772.195 | 770.33 | 267.92 | GGB | 10919.4 | GGB | 9.84 | GGB | 1016.77 | GGB | 59.77 | GGB | 170985.88 | GGB | 140796.86 | GGB | 0 | 0 | 2624 | 3600 | 2608.54 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 128992.34 | GGB | 128993.78 | 2608.54 | 2608.54 |  |  |  | 1 | 1 |  |  |  |  | 140796.86 | 2608.54 | 140796.86 | 2608.54 | 9.1612 | [5 empty] | 102.0206 |  |  | #VALUE!
30.01.2008 01:00 | 3600 | 2 | 764.17 | GGB | 767.766 | 773.227 | 771.429 | 267.04 | GGB | 10927.8 | GGB | 9.84 | GGB | 1016.35 | GGB | 59.97 | GGB | 170008.78 | GGB | 139851.58 | GGB | 0 | 0 | 2631 | 3600 | 2615.83 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 129032.37 | GGB | 129033.81 | 2615.83 | 2615.83 |  |  |  | 1 | 1 |  |  |  |  | 139851.58 | 2615.83 | 139851.58 | 2615.83 | 9.1388 | [5 empty] | 101.6189 |  |  | #VALUE!
30.01.2008 02:00 | 3600 | 2 | 763.66 | GGB | 765.201 | 771.094 | 768.864 | 266.94 | GGB | 10916.8 | GGB | 9.83 | GGB | 1016.23 | GGB | 60.19 | GGB | 170103.41 | GGB | 139819.9 | GGB | 0 | 0 | 2649 | 3600 | 2633.38 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 129071.69 | GGB | 129073.13 | 2633.38 | 2633.38 |  |  |  | 1 | 1 |  |  |  |  | 139819.9 | 2633.38 | 139819.9 | 2633.38 | 9.3642 | [5 empty] | 102.2775 |  |  | #VALUE!
30.01.2008 03:00 | 3600 | 2 | 764.4 | GGB | 766.667 | 773.016 | 770.33 | 267.91 | GGB | 10924.7 | GGB | 9.84 | GGB | 1016.7 | GGB | 59.79 | GGB | 171079.41 | GGB | 140855.11 | GGB | 0 | 0 | 2619 | 3600 | 2603.23 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 129112.21 | GGB | 129113.65 | 2603.23 | 2603.23 |  |  |  | 1 | 1 |  |  |  |  | 140855.11 | 2603.23 | 140855.11 | 2603.23 | 9.0493 | [5 empty] | 101.8551 |  |  | #VALUE!
30.01.2008 04:00 | 3600 | 2 | 764.15 | GGB | 767.766 | 774.117 | 771.429 | 267.52 | GGB | 10929.2 | GGB | 9.84 | GGB | 1016.37 | GGB | 59.9 | GGB | 170536.95 | GGB | 140317.18 | GGB | 0 | 0 | 2637 | 3600 | 2621.7 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 129151.84 | GGB | 129153.28 | 2621.7 | 2621.7 |  |  |  | 1 | 1 |  |  |  |  | 140317.18 | 2621.7 | 140317.18 | 2621.7 | 9.2826 | [5 empty] | 102.186 |  |  | #VALUE!
30.01.2008 05:00 | 3600 | 2 | 763.82 | GGB | 765.201 | 770.789 | 768.864 | 266.86 | GGB | 10931.9 | GGB | 9.83 | GGB | 1016.23 | GGB | 60.33 | GGB | 169738.1 | GGB | 139459.88 | GGB | 0 | 0 | 2655 | 3600 | 2639.38 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 129192.21 | GGB | 129193.65 | 2639.38 | 2639.38 |  |  |  | 1 | 1 |  |  |  |  | 139459.88 | 2639.38 | 139459.88 | 2639.38 | 9.1179 | [5 empty] | 102.2466 |  |  | #VALUE!
30.01.2008 06:00 | 3600 | 2 | 764.1 | GGB | 766.667 | 772.922 | 770.33 | 267.98 | GGB | 10924.5 | GGB | 9.83 | GGB | 1016.1 | GGB | 59.73 | GGB | 171388.61 | GGB | 141053.33 | GGB | 0 | 0 | 2639 | 3600 | 2624.04 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 129232.75 | GGB | 129234.19 | 2624.04 | 2624.04 |  |  |  | 1 | 1 |  |  |  |  | 141053.33 | 2624.04 | 141053.33 | 2624.04 | 9.13 | [5 empty] | 102.8138 |  |  | #VALUE!
30.01.2008 07:00 | 3600 | 2 | 764.14 | GGB | 767.766 | 772.688 | 771.429 | 267.7 | GGB | 10921.3 | GGB | 9.84 | GGB | 1015.79 | GGB | 59.71 | GGB | 171297.28 | GGB | 140944.9 | GGB | 0 | 0 | 2635 | 3600 | 2619.9 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 129271.97 | GGB | 129273.4 | 2619.9 | 2619.9 |  |  |  | 1 | 1 |  |  |  |  | 140944.9 | 2619.9 | 140944.9 | 2619.9 | 9.4175 | [5 empty] | 102.5727 |  |  | #VALUE!
30.01.2008 08:00 | 3600 | 2 | 764.3 | GGB | 766.3 | 771.469 | 769.963 | 265.63 | GGB | 10946.1 | GGB | 9.84 | GGB | 1015.53 | GGB | 60.27 | GGB | 168994.27 | GGB | 138778.19 | GGB | 0 | 0 | 2634 | 3600 | 2618.39 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 129312.48 | GGB | 129313.92 | 2618.39 | 2618.39 |  |  |  | 1 | 1 |  |  |  |  | 138778.19 | 2618.39 | 138778.19 | 2618.39 | 8.9678 | [5 empty] | 100.9376 |  |  | #VALUE!
30.01.2008 09:00 | 3600 | 2 | 763.8 | GGB | 766.667 | 772.523 | 771.429 | 267.37 | GGB | 10891.9 | GGB | 9.82 | GGB | 1015.53 | GGB | 59.97 | GGB | 170702 | GGB | 140306.47 | GGB | 0 | 0 | 2644 | 3600 | 2629.08 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 129352.94 | GGB | 129354.38 | 2629.08 | 2629.08 |  |  |  | 1 | 1 |  |  |  |  | 140306.47 | 2629.08 | 140306.47 | 2629.08 | 9.1171 | [5 empty] | 102.4658 |  |  | #VALUE!
30.01.2008 10:00 | 3600 | 2 | 764.8 | GGB | 768.864 | 773.695 | 771.429 | 267.36 | GGB | 10908 | GGB | 9.84 | GGB | 1015.08 | GGB | 59.92 | GGB | 170735.01 | GGB | 140294.63 | GGB | 0 | 0 | 2598 | 3600 | 2583.15 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 129391.78 | GGB | 129393.22 | 2583.15 | 2583.15 |  |  |  | 1 | 1 |  |  |  |  | 140294.63 | 2583.15 | 140294.63 | 2583.15 | 9.3306 | [5 empty] | 100.6672 |  |  | #VALUE!
30.01.2008 11:00 | 3600 | 2 | 765.02 | GGB | 768.864 | 773.695 | 772.527 | 265.71 | GGB | 10919.1 | GGB | 9.85 | GGB | 1014.86 | GGB | 60.37 | GGB | 168932.65 | GGB | 138596.82 | GGB | 0 | 0 | 2592 | 3600 | 2576.65 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 129433 | GGB | 129434.44 | 2576.65 | 2576.65 |  |  |  | 1 | 1 |  |  |  |  | 138596.82 | 2576.65 | 138596.82 | 2576.65 | 8.6636 | [5 empty] | 99.1987 |  |  | #VALUE!
30.01.2008 12:00 | 3600 | 2 | 763.79 | GGB | 765.201 | 771.563 | 768.864 | 266.25 | GGB | 10867.3 | GGB | 9.82 | GGB | 1014.63 | GGB | 60.46 | GGB | 169310.07 | GGB | 138834.87 | GGB | 0 | 0 | 2639 | 3600 | 2623.71 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 129473.65 | GGB | 129475.09 | 2623.71 | 2623.71 |  |  |  | 1 | 1 |  |  |  |  | 138834.87 | 2623.71 | 138834.87 | 2623.71 | 8.9609 | [5 empty] | 101.184 |  |  | #VALUE!
30.01.2008 13:00 | 3600 | 2 | 764.27 | GGB | 766.3 | 772.805 | 769.963 | 266.86 | GGB | 10877.6 | GGB | 9.82 | GGB | 1014.08 | GGB | 60.12 | GGB | 170484.13 | GGB | 139866.32 | GGB | 0 | 0 | 2609 | 3600 | 2593.22 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 129512.64 | GGB | 129514.08 | 2593.22 | 2593.22 |  |  |  | 1 | 1 |  |  |  |  | 139866.32 | 2593.22 | 139866.32 | 2593.22 | 9.3025 | [5 empty] | 100.7511 |  |  | #VALUE!
30.01.2008 14:00 | 3600 | 2 | 765.84 | GGB | 767.766 | 773.109 | 770.33 | 266.52 | GGB | 10930.1 | GGB | 9.85 | GGB | 1013.62 | GGB | 60.37 | GGB | 169870.14 | GGB | 139194.84 | GGB | 0 | 0 | 2563 | 3600 | 2548.07 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 129552.58 | GGB | 129554.02 | 2548.07 | 2548.07 |  |  |  | 1 | 1 |  |  |  |  | 139194.84 | 2548.07 | 139194.84 | 2548.07 | 8.8803 | [5 empty] | 98.5217 |  |  | #VALUE!
30.01.2008 15:00 | 3600 | 2 | 764.31 | GGB | 765.201 | 770.859 | 768.864 | 265.98 | GGB | 10900.8 | GGB | 9.83 | GGB | 1012.67 | GGB | 60.83 | GGB | 169186.83 | GGB | 138312.79 | GGB | 0 | 0 | 2625 | 3600 | 2609.33 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 129592.65 | GGB | 129594.1 | 2609.33 | 2609.33 |  |  |  | 1 | 1 |  |  |  |  | 138312.79 | 2609.33 | 138312.79 | 2609.33 | 9.0046 | [5 empty] | 100.251 |  |  | #VALUE!
30.01.2008 16:00 | 3600 | 2 | 764.9 | GGB | 767.766 | 773.039 | 771.429 | 267.16 | GGB | 10889.8 | GGB | 9.83 | GGB | 1012.2 | GGB | 60.47 | GGB | 170753.71 | GGB | 139677.9 | GGB | 0 | 0 | 2587 | 3600 | 2572.04 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 129632.15 | GGB | 129633.6 | 2572.04 | 2572.04 |  |  |  | 1 | 1 |  |  |  |  | 139677.9 | 2572.04 | 139677.9 | 2572.04 | 9.0951 | [5 empty] | 99.7937 |  |  | #VALUE!
30.01.2008 17:00 | 3600 | 2 | 765.13 | GGB | 766.667 | 773.039 | 770.33 | 266.36 | GGB | 10884.2 | GGB | 9.84 | GGB | 1011.23 | GGB | 60.54 | GGB | 170071.5 | GGB | 138958.2 | GGB | 0 | 0 | 2567 | 3600 | 2552.19 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 129671.94 | GGB | 129673.39 | 2552.19 | 2552.19 |  |  |  | 1 | 1 |  |  |  |  | 138958.2 | 2552.19 | 138958.2 | 2552.19 | 8.913 | [5 empty] | 98.5133 |  |  | #VALUE!
30.01.2008 18:00 | 3600 | 2 | 765.22 | GGB | 767.766 | 773.016 | 771.429 | 263.92 | GGB | 10901.9 | GGB | 9.85 | GGB | 1010.38 | GGB | 60.93 | GGB | 167581.44 | GGB | 136647.68 | GGB | 0 | 0 | 2576 | 3600 | 2561.14 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 129712.08 | GGB | 129713.54 | 2561.14 | 2561.14 |  |  |  | 1 | 1 |  |  |  |  | 136647.68 | 2561.14 | 136647.68 | 2561.14 | 8.7167 | [5 empty] | 97.215 |  |  | #VALUE!
30.01.2008 19:00 | 3600 | 2 | 764.83 | GGB | 767.766 | 773.039 | 771.429 | 265.21 | GGB | 10850.1 | GGB | 9.83 | GGB | 1010.07 | GGB | 60.34 | GGB | 169470.72 | GGB | 138392.47 | GGB | 0 | 0 | 2567 | 3600 | 2551.45 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 129752.32 | GGB | 129753.78 | 2551.45 | 2551.45 |  |  |  | 1 | 1 |  |  |  |  | 138392.47 | 2551.45 | 138392.47 | 2551.45 | 8.7749 | [5 empty] | 98.0837 |  |  | #VALUE!
30.01.2008 20:00 | 3600 | 2 | 765.64 | GGB | 767.766 | 773.016 | 771.429 | 265.05 | GGB | 10853.4 | GGB | 9.83 | GGB | 1009.64 | GGB | 60.3 | GGB | 169272.66 | GGB | 138187.49 | GGB | 0 | 0 | 2543 | 3600 | 2527.69 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 129791.81 | GGB | 129793.27 | 2527.69 | 2527.69 |  |  |  | 1 | 1 |  |  |  |  | 138187.49 | 2527.69 | 138187.49 | 2527.69 | 8.8452 | [5 empty] | 97.0264 |  |  | #VALUE!
30.01.2008 21:00 | 3600 | 2 | 765.04 | GGB | 766.667 | 773.039 | 770.33 | 263.79 | GGB | 10881 | GGB | 9.84 | GGB | 1008.82 | GGB | 60.57 | GGB | 167899.44 | GGB | 136845.7 | GGB | 0 | 0 | 2572 | 3600 | 2556.59 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 129831.59 | GGB | 129833.05 | 2556.59 | 2556.59 |  |  |  | 1 | 1 |  |  |  |  | 136845.7 | 2556.59 | 136845.7 | 2556.59 | 8.7948 | [5 empty] | 97.1829 |  |  | #VALUE!
30.01.2008 22:00 | 3600 | 2 | 764.27 | GGB | 766.667 | 773.039 | 771.429 | 265.4 | GGB | 10854.4 | GGB | 9.82 | GGB | 1008.61 | GGB | 60.19 | GGB | 169588.46 | GGB | 138349.28 | GGB | 0 | 0 | 2600 | 3600 | 2584.93 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 129872.05 | GGB | 129873.52 | 2584.93 | 2584.93 |  |  |  | 1 | 1 |  |  |  |  | 138349.28 | 2584.93 | 138349.28 | 2584.93 | 8.8367 | [5 empty] | 99.3398 |  |  | #VALUE!
30.01.2008 23:00 | 3600 | 2 | 765.14 | GGB | 769.963 | 776.297 | 773.626 | 265.21 | GGB | 10892.3 | GGB | 9.85 | GGB | 1007.81 | GGB | 59.8 | GGB | 170616.17 | GGB | 139243 | GGB | 0 | 0 | 2563 | 3600 | 2547.31 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 129911.48 | GGB | 129912.94 | 2547.31 | 2547.31 |  |  |  | 1 | 1 |  |  |  |  | 139243 | 2547.31 | 139243 | 2547.31 | 8.9978 | [5 empty] | 98.5264 |  |  | #VALUE!
30.01.2008 24:00 | 3600 | 2 | 764.77 | GGB | 767.766 | 773.789 | 771.429 | 264.44 | GGB | 10872.7 | GGB | 9.84 | GGB | 1007.39 | GGB | 60.02 | GGB | 168974.47 | GGB | 137751.81 | GGB | 0 | 0 | 2578 | 3600 | 2562.85 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 129951.05 | GGB | 129952.51 | 2562.85 | 2562.85 |  |  |  | 1 | 1 |  |  |  |  | 137751.81 | 2562.85 | 137751.81 | 2562.85 | 8.9218 | [5 empty] | 98.0659 |  |  | #VALUE!
31.01.2008 01:00 | 3600 | 2 | 764.01 | GGB | 766.3 | 771.539 | 768.864 | 264.41 | GGB | 10858.2 | GGB | 9.82 | GGB | 1006.93 | GGB | 60.34 | GGB | 168873.24 | GGB | 137476.07 | GGB | 0 | 0 | 2614 | 3600 | 2598.3 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 129992.05 | GGB | 129993.51 | 2598.3 | 2598.3 |  |  |  | 1 | 1 |  |  |  |  | 137476.07 | 2598.3 | 137476.07 | 2598.3 | 8.7123 | [5 empty] | 99.2234 |  |  | #VALUE!
31.01.2008 02:00 | 3600 | 2 | 764.5 | GGB | 766.667 | 772.43 | 770.33 | 265.37 | GGB | 10866.5 | GGB | 9.83 | GGB | 1006.81 | GGB | 59.63 | GGB | 170303.68 | GGB | 138918.5 | GGB | 0 | 0 | 2581 | 3600 | 2565.69 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 130031.36 | GGB | 130032.81 | 2565.69 | 2565.69 |  |  |  | 1 | 1 |  |  |  |  | 138918.5 | 2565.69 | 138918.5 | 2565.69 | 9.0693 | [5 empty] | 99.0061 |  |  | #VALUE!
31.01.2008 03:00 | 3600 | 2 | 764.32 | GGB | 766.667 | 772.523 | 770.33 | 265.11 | GGB | 10888.1 | GGB | 9.84 | GGB | 1006.31 | GGB | 59.6 | GGB | 169921.86 | GGB | 138553.81 | GGB | 0 | 0 | 2601 | 3600 | 2585.86 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 130070.86 | GGB | 130072.31 | 2585.86 | 2585.86 |  |  |  | 1 | 1 |  |  |  |  | 138553.81 | 2585.86 | 138553.81 | 2585.86 | 9.0704 | [5 empty] | 99.5224 |  |  | #VALUE!
31.01.2008 04:00 | 3600 | 2 | 763.43 | GGB | 766.3 | 771.656 | 769.963 | 264.45 | GGB | 10884.5 | GGB | 9.83 | GGB | 1005.99 | GGB | 60.09 | GGB | 168811.62 | GGB | 137398.41 | GGB | 0 | 0 | 2642 | 3600 | 2626.43 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 130111.75 | GGB | 130113.21 | 2626.43 | 2626.43 |  |  |  | 1 | 1 |  |  |  |  | 137398.41 | 2626.43 | 137398.41 | 2626.43 | 8.8232 | [5 empty] | 100.2409 |  |  | #VALUE!
31.01.2008 05:00 | 3600 | 2 | 763.72 | GGB | 766.3 | 771.773 | 768.864 | 265.26 | GGB | 10886.8 | GGB | 9.83 | GGB | 1005.86 | GGB | 59.34 | GGB | 169492.73 | GGB | 138249.63 | GGB | 0 | 0 | 2626 | 3600 | 2610.42 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 130151.01 | GGB | 130152.46 | 2610.42 | 2610.42 |  |  |  | 1 | 1 |  |  |  |  | 138249.63 | 2610.42 | 138249.63 | 2610.42 | 9.1946 | [5 empty] | 100.2471 |  |  | #VALUE!
31.01.2008 06:00 | 3600 | 2 | 762.94 | GGB | 766.667 | 772.758 | 769.963 | 265.4 | GGB | 10889.8 | GGB | 9.83 | GGB | 1005.77 | GGB | 59.86 | GGB | 169611.56 | GGB | 138117.53 | GGB | 0 | 0 | 2664 | 3600 | 2648.46 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 130190.43 | GGB | 130191.89 | 2648.46 | 2648.46 |  |  |  | 1 | 1 |  |  |  |  | 138117.53 | 2648.46 | 138117.53 | 2648.46 | 9.2772 | [5 empty] | 101.6108 |  |  | #VALUE!
31.01.2008 07:00 | 3600 | 2 | 763.06 | GGB | 765.201 | 770.578 | 768.864 | 266.76 | GGB | 10876.4 | GGB | 9.82 | GGB | 1005.93 | GGB | 59.29 | GGB | 171457.93 | GGB | 139882.88 | GGB | 0 | 0 | 2652 | 3600 | 2636.98 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 130231.31 | GGB | 130232.77 | 2636.98 | 2636.98 |  |  |  | 1 | 1 |  |  |  |  | 139882.88 | 2636.98 | 139882.88 | 2636.98 | 9.0232 | [5 empty] | 102.4634 |  |  | #VALUE!
31.01.2008 08:00 | 3600 | 2 | 763.75 | GGB | 766.3 | 771.703 | 768.864 | 264.96 | GGB | 10923.8 | GGB | 9.85 | GGB | 1007.05 | GGB | 60.11 | GGB | 169000.88 | GGB | 137690.91 | GGB | 0 | 0 | 2645 | 3600 | 2630.03 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 130270.24 | GGB | 130271.7 | 2630.03 | 2630.03 |  |  |  | 1 | 1 |  |  |  |  | 137690.91 | 2630.03 | 137690.91 | 2630.03 | 9.3021 | [5 empty] | 100.592 |  |  | #VALUE!
31.01.2008 09:00 | 3600 | 2 | 762.31 | GGB | 765.201 | 770.695 | 767.766 | 266.33 | GGB | 10885.1 | GGB | 9.81 | GGB | 1007.74 | GGB | 59.58 | GGB | 170748.21 | GGB | 139431.74 | GGB | 0 | 0 | 2685 | 3600 | 2669.53 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 130310.68 | GGB | 130312.15 | 2669.53 | 2669.53 |  |  |  | 1 | 1 |  |  |  |  | 139431.74 | 2669.53 | 139431.74 | 2669.53 | 9.2019 | [5 empty] | 103.3937 |  |  | #VALUE!
31.01.2008 10:00 | 3600 | 2 | 763.93 | GGB | 766.667 | 773.133 | 769.963 | 266.27 | GGB | 10962.1 | GGB | 9.85 | GGB | 1008.52 | GGB | 59.24 | GGB | 171116.82 | GGB | 139985.87 | GGB | 0 | 0 | 2647 | 3600 | 2631.19 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 130350.95 | GGB | 130352.42 | 2631.19 | 2631.19 |  |  |  | 1 | 1 |  |  |  |  | 139985.87 | 2631.19 | 139985.87 | 2631.19 | 9.1465 | [5 empty] | 102.3137 |  |  | #VALUE!
31.01.2008 11:00 | 3600 | 2 | 762.4 | GGB | 765.201 | 770.695 | 768.864 | 267.11 | GGB | 10922.7 | GGB | 9.82 | GGB | 1009.07 | GGB | 59.05 | GGB | 172374.51 | GGB | 141171.92 | GGB | 0 | 0 | 2693 | 3600 | 2677.71 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 130390.19 | GGB | 130391.66 | 2677.71 | 2677.0763 |  |  |  | 1 | 1 |  |  |  |  | 141171.92 | 2677.0763 | 141171.92 | 2677.0763 | 9.6312 | [5 empty] | 105.0049 | 2677.0763 |  | 104.98
31.01.2008 12:00 | 3600 | 2 | 763.88 | GGB | 766.667 | 772.453 | 770.33 | 266.72 | GGB | 10959.6 | GGB | 9.85 | GGB | 1009.5 | GGB | 59.16 | GGB | 171851.85 | GGB | 140755.65 | GGB | 0 | 0 | 2646 | 3600 | 2630.32 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 130430.97 | GGB | 130432.44 | 2630.32 | 2630.32 |  |  |  | 1 | 1 |  |  |  |  | 140755.65 | 2630.32 | 140755.65 | 2630.32 | 9.0788 | [5 empty] | 102.8423 |  |  | #VALUE!
31.01.2008 13:00 | 3600 | 2 | 762.82 | GGB | 765.201 | 771.305 | 768.864 | 266.11 | GGB | 10945.2 | GGB | 9.83 | GGB | 1009.91 | GGB | 59.35 | GGB | 170963.88 | GGB | 140006.33 | GGB | 0 | 0 | 2686 | 3600 | 2670.95 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 130470.5 | GGB | 130471.98 | 2670.95 | 2670.95 |  |  |  | 1 | 1 |  |  |  |  | 140006.33 | 2670.95 | 140006.33 | 2670.95 | 9.4575 | [5 empty] | 103.875 |  |  | #VALUE!
31.01.2008 14:00 | 3600 | 2 | 763.51 | GGB | 766.3 | 772.477 | 769.963 | 267.17 | GGB | 10919.2 | GGB | 9.83 | GGB | 1010.35 | GGB | 59.08 | GGB | 172306.29 | GGB | 141281.47 | GGB | 0 | 0 | 2643 | 3600 | 2627.96 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 130510.42 | GGB | 130511.89 | 2627.96 | 2627.96 |  |  |  | 1 | 1 |  |  |  |  | 141281.47 | 2627.96 | 141281.47 | 2627.96 | 9.303 | [5 empty] | 103.1339 |  |  | #VALUE!
31.01.2008 15:00 | 3600 | 2 | 763.96 | GGB | 765.201 | 771.328 | 768.864 | 266.82 | GGB | 10949 | GGB | 9.84 | GGB | 1010.98 | GGB | 59.42 | GGB | 171495.34 | GGB | 140560.48 | GGB | 0 | 0 | 2634 | 3600 | 2619.13 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 130550.44 | GGB | 130551.91 | 2619.13 | 2619.13 |  |  |  | 1 | 1 |  |  |  |  | 140560.48 | 2619.13 | 140560.48 | 2619.13 | 9.1991 | [5 empty] | 102.2628 |  |  | #VALUE!
31.01.2008 16:00 | 3600 | 2 | 762.59 | GGB | 764.102 | 770.203 | 767.766 | 266.41 | GGB | 10963.8 | GGB | 9.83 | GGB | 1011.23 | GGB | 59.68 | GGB | 170762.52 | GGB | 139883.59 | GGB | 0 | 0 | 2703 | 3600 | 2687.45 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 130590.31 | GGB | 130591.79 | 2687.45 | 2687.45 |  |  |  | 1 | 1 |  |  |  |  | 139883.59 | 2687.45 | 139883.59 | 2687.45 | 9.4265 | [5 empty] | 104.425 |  |  | #VALUE!
31.01.2008 17:00 | 3600 | 2 | 762.52 | GGB | 765.201 | 771.305 | 768.864 | 267.74 | GGB | 10946.7 | GGB | 9.82 | GGB | 1011 | GGB | 59.57 | GGB | 172316.19 | GGB | 141173.14 | GGB | 0 | 0 | 2713 | 3600 | 2697.25 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 130631.19 | GGB | 130632.67 | 2697.25 | 2677.0532 |  |  |  | 1 | 1 |  |  |  |  | 141173.14 | 2677.0532 | 141173.14 | 2677.0532 | 9.2448 | [5 empty] | 105.772 | 2677.0532 |  | 104.98
31.01.2008 18:00 | 3600 | 2 | 763.72 | GGB | 766.3 | 772.336 | 768.864 | 268.08 | GGB | 10963.1 | GGB | 9.84 | GGB | 1011.22 | GGB | 59.4 | GGB | 172644.09 | GGB | 141541.5 | GGB | 0 | 0 | 2661 | 3600 | 2645.26 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 130670.89 | GGB | 130672.37 | 2645.26 | 2645.26 |  |  |  | 1 | 1 |  |  |  |  | 141541.5 | 2645.26 | 141541.5 | 2645.26 | 9.4311 | [5 empty] | 104.0039 |  |  | #VALUE!
31.01.2008 19:00 | 3600 | 2 | 762.3 | GGB | 765.201 | 771.352 | 768.864 | 268.06 | GGB | 10982.8 | GGB | 9.83 | GGB | 1011.34 | GGB | 59.8 | GGB | 172085.12 | GGB | 140933.28 | GGB | 0 | 0 | 2734 | 3600 | 2718.12 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 130710.46 | GGB | 130711.94 | 2718.12 | 2681.6093 |  |  |  | 1 | 1 |  |  |  |  | 140933.28 | 2681.6093 | 140933.28 | 2681.6093 | 9.5509 | [5 empty] | 106.4093 | 2681.6093 |  | 104.98
31.01.2008 20:00 | 3600 | 2 | 762.33 | GGB | 765.201 | 771.375 | 768.864 | 269.75 | GGB | 10962.7 | GGB | 9.83 | GGB | 1011.08 | GGB | 59.13 | GGB | 174319.91 | GGB | 143014.63 | GGB | 0 | 0 | 2724 | 3600 | 2708.26 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 130751.74 | GGB | 130753.22 | 2708.26 | 2642.5828 |  |  |  | 1 | 1 |  |  |  |  | 143014.63 | 2642.5828 | 143014.63 | 2642.5828 | 9.1552 | [5 empty] | 107.5891 | 2642.5828 |  | 104.98
31.01.2008 21:00 | 3600 | 2 | 762.87 | GGB | 764.102 | 770.203 | 767.766 | 268.79 | GGB | 10993.9 | GGB | 9.84 | GGB | 1010.64 | GGB | 59.09 | GGB | 173317.5 | GGB | 142146.57 | GGB | 0 | 0 | 2708 | 3600 | 2692.92 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 130791.07 | GGB | 130792.56 | 2692.92 | 2658.7205 |  |  |  | 1 | 1 |  |  |  |  | 142146.57 | 2658.7205 | 142146.57 | 2658.7205 | 9.6067 | [5 empty] | 106.3304 | 2658.7205 |  | 104.98
31.01.2008 22:00 | 3600 | 2 | 762.08 | GGB | 766.3 | 771.328 | 768.864 | 268.32 | GGB | 10991.8 | GGB | 9.84 | GGB | 1010.61 | GGB | 59.49 | GGB | 172485.64 | GGB | 141292.22 | GGB | 0 | 0 | 2744 | 3600 | 2728.65 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 130831.52 | GGB | 130833.01 | 2728.65 | 2674.797 |  |  |  | 1 | 1 |  |  |  |  | 141292.22 | 2674.797 | 141292.22 | 2674.797 | 9.3431 | [5 empty] | 107.0936 | 2674.797 |  | 104.98
31.01.2008 23:00 | 3600 | 2 | 762.19 | GGB | 764.102 | 770.203 | 768.864 | 269.24 | GGB | 10966.1 | GGB | 9.83 | GGB | 1010.3 | GGB | 58.87 | GGB | 174560.88 | GGB | 143214.19 | GGB | 0 | 0 | 2722 | 3600 | 2706.48 | GGB | 100 | GGB | 41.39 | GGB | 41.39 | GGB | 130872.91 | GGB | 130874.4 | 2706.48 | 2638.9005 |  |  |  | 1 | 1 |  |  |  |  | 143214.19 | 2638.9005 | 143214.19 | 2638.9005 | 9.1309 | [5 empty] | 107.6684 | 2638.9005 |  | 104.98
31.01.2008 24:00 | 3600 | 2 | 762.57 | GGB | 766.3 | 771.352 | 768.864 | 268.76 | GGB | 10991.8 | GGB | 9.84 | GGB | 1010.61 | GGB | 58.97 | GGB | 173491.35 | GGB | 142337.34 | GGB | 0 | 0 | 2723 | 3600 | 2707.54 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 130911.11 | GGB | 130912.6 | 2707.54 | 2655.1571 |  |  |  | 1 | 1 |  |  |  |  | 142337.34 | 2655.1571 | 142337.34 | 2655.1571 | 9.8934 | [5 empty] | 107.0511 | 2655.1571 |  | 104.98
01.02.2008 01:00 | 3600 | 2 | 761.82 | GGB | 764.102 | 770.273 | 767.766 | 267.82 | GGB | 10983.2 | GGB | 9.83 | GGB | 1009.95 | GGB | 59.62 | GGB | 172258.98 | GGB | 140957.64 | GGB | 0 | 0 | 2747 | 3600 | 2731.21 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 130951.76 | GGB | 130953.25 | 2731.21 | 2681.1459 |  |  |  | 1 | 1 |  |  |  |  | 140957.64 | 2681.1459 | 140957.64 | 2681.1459 | 9.2971 | [5 empty] | 106.9403 | 2681.1459 |  | 104.98
01.02.2008 02:00 | 3600 | 2 | 762.01 | GGB | 766.3 | 771.281 | 768.864 | 269.39 | GGB | 10963.6 | GGB | 9.83 | GGB | 1009.56 | GGB | 58.92 | GGB | 174542.18 | GGB | 143071.64 | GGB | 0 | 0 | 2729 | 3600 | 2713.24 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 130992.73 | GGB | 130994.22 | 2713.24 | 2641.5298 |  |  |  | 1 | 1 |  |  |  |  | 143071.64 | 2641.5298 | 143071.64 | 2641.5298 | 9.2245 | [5 empty] | 107.8299 | 2641.5298 |  | 104.98
01.02.2008 03:00 | 3600 | 2 | 762.44 | GGB | 765.201 | 770.414 | 767.766 | 268.42 | GGB | 10991.7 | GGB | 9.84 | GGB | 1008.85 | GGB | 59.01 | GGB | 173581.58 | GGB | 142144.59 | GGB | 0 | 0 | 2716 | 3600 | 2700.52 | GGB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 131031.26 | GGB | 131032.75 | 2700.52 | 2658.7575 |  |  |  | 1 | 1 |  |  |  |  | 142144.59 | 2658.7575 | 142144.59 | 2658.7575 | 9.8087 | [5 empty] | 106.629 | 2658.7575 |  | 104.98
01.02.2008 04:00 | 3600 | 2 | 761.21 | GGB | 764.102 | 769.547 | 766.667 | 267.99 | GGB | 10992.2 | GGB | 9.83 | GGB | 1007.53 | GGB | 59.11 | GGB | 173060.02 | GGB | 141492.22 | GGB | 0 | 0 | 2779 | 3600 | 2763.73 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 131072.4 | GGB | 131073.9 | 2763.73 | 2671.0161 |  |  |  | 1 | 1 |  |  |  |  | 141492.22 | 2671.0161 | 141492.22 | 2671.0161 | 9.1842 | [5 empty] | 108.624 | 2671.0161 |  | 104.98
01.02.2008 05:00 | 3600 | 2 | 761.41 | GGB | 764.102 | 769.5 | 766.667 | 268.67 | GGB | 10998.1 | GGB | 9.84 | GGB | 1006.59 | GGB | 58.57 | GGB | 174575.19 | GGB | 142826.16 | GGB | 0 | 0 | 2768 | 3600 | 2752.39 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 131113.42 | GGB | 131114.92 | 2752.39 | 2646.0699 |  |  |  | 1 | 1 |  |  |  |  | 142826.16 | 2646.0699 | 142826.16 | 2646.0699 | 9.2133 | [5 empty] | 109.1981 | 2646.0699 |  | 104.98
01.02.2008 06:00 | 3600 | 2 | 761.14 | GGB | 764.102 | 769.5 | 767.766 | 268.62 | GGB | 10973.9 | GGB | 9.83 | GGB | 1005.45 | GGB | 57.95 | GGB | 175624.91 | GGB | 143791.53 | GGB | 0 | 0 | 2747 | 3600 | 2731.07 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 131152.37 | GGB | 131153.87 | 2731.07 | 2628.305 |  |  |  | 1 | 1 |  |  |  |  | 143791.53 | 2628.305 | 143791.53 | 2628.305 | 9.7029 | [5 empty] | 109.0846 | 2628.305 |  | 104.98
01.02.2008 07:00 | 3600 | 2 | 761.96 | GGB | 764.102 | 770.367 | 767.766 | 266.48 | GGB | 10996.6 | GGB | 9.85 | GGB | 1004.36 | GGB | 58.21 | GGB | 173502.36 | GGB | 141790.31 | GGB | 0 | 0 | 2726 | 3600 | 2710.11 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 131193.69 | GGB | 131195.18 | 2710.11 | 2665.4008 |  |  |  | 1 | 1 |  |  |  |  | 141790.31 | 2665.4008 | 141790.31 | 2665.4008 | 9.1486 | [5 empty] | 106.7409 | 2665.4008 |  | 104.98
01.02.2008 08:00 | 3600 | 2 | 761.38 | GGB | 765.201 | 771.492 | 768.864 | 266.12 | GGB | 10973.1 | GGB | 9.84 | GGB | 1003.45 | GGB | 58.18 | GGB | 173270.19 | GGB | 141485.55 | GGB | 0 | 0 | 2741 | 3208 | 2725.29 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 131233.45 | GGB | 131234.94 | 2725.29 | 2671.142 |  |  |  | 1 | 1 |  |  |  |  | 141485.55 | 2671.142 | 141485.55 | 2671.142 | 9.5052 | [5 empty] | 107.1081 | 2671.142 |  | 104.98
01.02.2008 09:00 | 3600 | 2 | 761.1 | GGB | 765.201 | 770.32 | 767.766 | 266.49 | GGB | 10944.6 | GGB | 9.83 | GGB | 1002.6 | GGB | 57.9 | GGB | 173847.86 | GGB | 141956.54 | GGB | 0 | 0 | 2739 | 3600 | 2723.74 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 131274 | GGB | 131275.5 | 2723.74 | 2662.2796 |  |  |  | 1 | 1 |  |  |  |  | 141956.54 | 2662.2796 | 141956.54 | 2662.2796 | 9.3178 | [5 empty] | 107.4035 | 2662.2796 |  | 104.98
01.02.2008 10:00 | 3600 | 2 | 762.81 | GGB | 765.201 | 771.563 | 768.864 | 266.39 | GGB | 10957.8 | GGB | 9.85 | GGB | 1002.11 | GGB | 57.96 | GGB | 173609.09 | GGB | 141664.43 | GGB | 0 | 0 | 2676 | 3600 | 2660.36 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 131314 | GGB | 131315.5 | 2660.36 | 2660.36 |  |  |  | 1 | 1 |  |  |  |  | 141664.43 | 2660.36 | 141664.43 | 2660.36 | 9.422 | [5 empty] | 104.6884 |  |  | #VALUE!
01.02.2008 11:00 | 3600 | 2 | 761.76 | GGB | 764.102 | 770.156 | 767.766 | 264.75 | GGB | 10927.6 | GGB | 9.83 | GGB | 1001.22 | GGB | 58.82 | GGB | 171484.34 | GGB | 139446.75 | GGB | 0 | 0 | 2720 | 3600 | 2705.04 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 131353.52 | GGB | 131355.02 | 2705.04 | 2705.04 |  |  |  | 1 | 1 |  |  |  |  | 139446.75 | 2705.04 | 139446.75 | 2705.04 | 9.5448 | [5 empty] | 104.7803 |  |  | #VALUE!
01.02.2008 12:00 | 3600 | 2 | 761.64 | GGB | 764.102 | 769.195 | 766.667 | 264.76 | GGB | 10903.7 | GGB | 9.83 | GGB | 1000.89 | GGB | 59.02 | GGB | 170974.88 | GGB | 138904.2 | GGB | 0 | 0 | 2684 | 3600 | 2668.45 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 131394.15 | GGB | 131395.65 | 2668.45 | 2668.45 |  |  |  | 1 | 1 |  |  |  |  | 138904.2 | 2668.45 | 138904.2 | 2668.45 | 9.1228 | [5 empty] | 102.9608 |  |  | #VALUE!
01.02.2008 13:00 | 3600 | 2 | 762.59 | GGB | 765.201 | 770.367 | 767.766 | 265.35 | GGB | 10873.9 | GGB | 9.84 | GGB | 999.79 | GGB | 58.57 | GGB | 171981.69 | GGB | 139755.83 | GGB | 0 | 0 | 2631 | 3600 | 2615.88 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 131433.68 | GGB | 131435.18 | 2615.88 | 2615.88 |  |  |  | 1 | 1 |  |  |  |  | 139755.83 | 2615.88 | 139755.83 | 2615.88 | 9.2483 | [5 empty] | 101.5512 |  |  | #VALUE!
01.02.2008 14:00 | 3600 | 2 | 762.57 | GGB | 764.102 | 770.32 | 767.766 | 264.17 | GGB | 10885.8 | GGB | 9.84 | GGB | 998.65 | GGB | 58.98 | GGB | 170541.35 | GGB | 138257.48 | GGB | 0 | 0 | 2647 | 3600 | 2631.19 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 131473.03 | GGB | 131474.52 | 2631.19 | 2631.19 |  |  |  | 1 | 1 |  |  |  |  | 138257.48 | 2631.19 | 138257.48 | 2631.19 | 9.2471 | [5 empty] | 101.0505 |  |  | #VALUE!
01.02.2008 15:00 | 3600 | 2 | 761.02 | GGB | 765.201 | 770.32 | 767.766 | 264.62 | GGB | 10906.2 | GGB | 9.83 | GGB | 997.82 | GGB | 58.95 | GGB | 170689.89 | GGB | 138272.98 | GGB | 0 | 0 | 2722 | 3600 | 2706.92 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 131514.06 | GGB | 131515.55 | 2706.92 | 2706.92 |  |  |  | 1 | 1 |  |  |  |  | 138272.98 | 2706.92 | 138272.98 | 2706.92 | 9.1224 | [5 empty] | 103.9705 |  |  | #VALUE!
01.02.2008 16:00 | 3600 | 2 | 760.6 | GGB | 764.102 | 770.297 | 767.766 | 265.76 | GGB | 10887.9 | GGB | 9.83 | GGB | 997.5 | GGB | 58.24 | GGB | 172530.76 | GGB | 140019.14 | GGB | 0 | 0 | 2731 | 3600 | 2716.02 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 131553.69 | GGB | 131555.19 | 2716.02 | 2699.1167 |  |  |  | 1 | 1 |  |  |  |  | 140019.14 | 2699.1167 | 140019.14 | 2699.1167 | 9.534 | [5 empty] | 105.6374 | 2699.1167 |  | 104.98
01.02.2008 17:00 | 3600 | 2 | 761.24 | GGB | 765.201 | 770.344 | 768.864 | 265.83 | GGB | 10911.9 | GGB | 9.84 | GGB | 997.09 | GGB | 57.38 | GGB | 172502.15 | GGB | 140304.67 | GGB | 0 | 0 | 2703 | 3600 | 2687.48 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 131593.57 | GGB | 131595.07 | 2687.48 | 2687.48 |  |  |  | 1 | 1 |  |  |  |  | 140304.67 | 2687.48 | 140304.67 | 2687.48 | 9.455 | [5 empty] | 104.7406 |  |  | #VALUE!
01.02.2008 18:00 | 3600 | 2 | 760.72 | GGB | 763.004 | 769.148 | 766.667 | 264.59 | GGB | 10913.1 | GGB | 9.83 | GGB | 996.72 | GGB | 58.03 | GGB | 170690.99 | GGB | 138507.45 | GGB | 0 | 0 | 2741 | 3600 | 2725.55 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 131633.77 | GGB | 131635.27 | 2725.55 | 2725.55 |  |  |  | 0 | 1 | [14 empty] | 104.8636 |  |  | #VALUE!
01.02.2008 19:00 | 3600 | 2 | 760.85 | GGB | 764.102 | 770.32 | 767.766 | 265 | GGB | 10882.5 | GGB | 9.83 | GGB | 996.34 | GGB | 58.5 | GGB | 171097.02 | GGB | 138586.63 | GGB | 0 | 0 | 2728 | 3600 | 2713.04 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 131673 | GGB | 131674.51 | 2713.04 | 2713.04 |  |  |  | 1 | 1 |  |  |  |  | 138586.63 | 2713.04 | 138586.63 | 2713.04 | 9.5818 | [5 empty] | 104.442 |  |  | #VALUE!
01.02.2008 20:00 | 3600 | 2 | 762.44 | GGB | 764.102 | 770.273 | 768.498 | 264.32 | GGB | 10885.8 | GGB | 9.85 | GGB | 996.52 | GGB | 58.98 | GGB | 170027.49 | GGB | 137546.23 | GGB | 0 | 0 | 2666 | 3600 | 2651.11 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 131713.26 | GGB | 131714.77 | 2651.11 | 2651.11 |  |  |  | 1 | 1 |  |  |  |  | 137546.23 | 2651.11 | 137546.23 | 2651.11 | 9.0574 | [5 empty] | 101.2917 |  |  | #VALUE!
01.02.2008 21:00 | 3600 | 2 | 762.11 | GGB | 765.201 | 771.352 | 768.864 | 264.87 | GGB | 10828.7 | GGB | 9.83 | GGB | 996.71 | GGB | 59.07 | GGB | 170719.6 | GGB | 138095.92 | GGB | 0 | 0 | 2662 | 3600 | 2646.62 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 131752.43 | GGB | 131753.95 | 2646.62 | 2646.62 |  |  |  | 1 | 1 |  |  |  |  | 138095.92 | 2646.62 | 138095.92 | 2646.62 | 9.3284 | [5 empty] | 101.5243 |  |  | #VALUE!
01.02.2008 22:00 | 3600 | 2 | 763.49 | GGB | 767.766 | 773.695 | 771.429 | 263.94 | GGB | 10844.9 | GGB | 9.85 | GGB | 996.39 | GGB | 59.32 | GGB | 169904.25 | GGB | 137285.86 | GGB | 0 | 0 | 2617 | 3600 | 2601.75 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 131792.82 | GGB | 131794.34 | 2601.75 | 2601.75 |  |  |  | 1 | 1 |  |  |  |  | 137285.86 | 2601.75 | 137285.86 | 2601.75 | 8.8434 | [5 empty] | 99.2176 |  |  | #VALUE!
01.02.2008 23:00 | 3600 | 2 | 762.83 | GGB | 765.201 | 771.516 | 768.864 | 262.58 | GGB | 10814.4 | GGB | 9.83 | GGB | 995.79 | GGB | 60.04 | GGB | 167497.81 | GGB | 134970.32 | GGB | 0 | 0 | 2635 | 3600 | 2619.95 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 131831.05 | GGB | 131832.56 | 2619.95 | 2619.95 |  |  |  | 1 | 1 |  |  |  |  | 134970.32 | 2619.95 | 134970.32 | 2619.95 | 9.2521 | [5 empty] | 98.2265 |  |  | #VALUE!
01.02.2008 24:00 | 3600 | 2 | 763.24 | GGB | 766.3 | 772.5 | 769.963 | 262.22 | GGB | 10808.5 | GGB | 9.84 | GGB | 995.46 | GGB | 60.49 | GGB | 166869.52 | GGB | 134235.57 | GGB | 0 | 0 | 2617 | 3600 | 2601.81 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 131871.81 | GGB | 131873.33 | 2601.81 | 2601.81 |  |  |  | 1 | 1 |  |  |  |  | 134235.57 | 2601.81 | 134235.57 | 2601.81 | 8.5665 | [5 empty] | 97.0154 |  |  | #VALUE!
02.02.2008 01:00 | 3600 | 2 | 763.64 | GGB | 765.201 | 771.469 | 768.864 | 262.29 | GGB | 10796.2 | GGB | 9.83 | GGB | 995.09 | GGB | 60.56 | GGB | 166862.92 | GGB | 134154.78 | GGB | 0 | 0 | 2607 | 3600 | 2591.46 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 131911.42 | GGB | 131912.94 | 2591.46 | 2591.46 |  |  |  | 1 | 1 |  |  |  |  | 134154.78 | 2591.46 | 134154.78 | 2591.46 | 8.777 | [5 empty] | 96.5713 |  |  | #VALUE!
02.02.2008 02:00 | 3600 | 2 | 763.5 | GGB | 766.3 | 771.328 | 769.963 | 262.39 | GGB | 10790.4 | GGB | 9.83 | GGB | 995 | GGB | 60.61 | GGB | 166836.51 | GGB | 134100.51 | GGB | 0 | 0 | 2613 | 3600 | 2598.04 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 131949.94 | GGB | 131951.45 | 2598.04 | 2598.04 |  |  |  | 1 | 1 |  |  |  |  | 134100.51 | 2598.04 | 134100.51 | 2598.04 | 9.047 | [5 empty] | 96.7774 |  |  | #VALUE!
02.02.2008 03:00 | 3600 | 2 | 763.82 | GGB | 766.3 | 772.383 | 769.963 | 263.25 | GGB | 10780.8 | GGB | 9.83 | GGB | 994.88 | GGB | 60.27 | GGB | 168145.91 | GGB | 135273.76 | GGB | 0 | 0 | 2591 | 3600 | 2575.64 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 131990.83 | GGB | 131992.34 | 2575.64 | 2575.64 |  |  |  | 1 | 1 |  |  |  |  | 135273.76 | 2575.64 | 135273.76 | 2575.64 | 8.5208 | [5 empty] | 96.7824 |  |  | #VALUE!
02.02.2008 04:00 | 3600 | 2 | 763.36 | GGB | 765.201 | 771.328 | 768.864 | 264.51 | GGB | 10781 | GGB | 9.83 | GGB | 994.29 | GGB | 59.69 | GGB | 169695.19 | GGB | 136678.3 | GGB | 0 | 0 | 2607 | 3600 | 2591.31 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 132029.63 | GGB | 132031.15 | 2591.31 | 2591.31 |  |  |  | 1 | 1 |  |  |  |  | 136678.3 | 2591.31 | 136678.3 | 2591.31 | 9.1259 | [5 empty] | 98.3822 |  |  | #VALUE!
02.02.2008 05:00 | 3600 | 2 | 762.96 | GGB | 765.201 | 770.109 | 768.864 | 263.22 | GGB | 10825.7 | GGB | 9.84 | GGB | 994.04 | GGB | 60.14 | GGB | 167972.06 | GGB | 135071.17 | GGB | 0 | 0 | 2634 | 3600 | 2618.97 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 132068.61 | GGB | 132070.13 | 2618.97 | 2618.97 |  |  |  | 1 | 1 |  |  |  |  | 135071.17 | 2618.97 | 135071.17 | 2618.97 | 9.0751 | [5 empty] | 98.2632 |  |  | #VALUE!
02.02.2008 06:00 | 3600 | 2 | 761.34 | GGB | 763.004 | 769.078 | 766.667 | 265.01 | GGB | 10814.8 | GGB | 9.82 | GGB | 994.38 | GGB | 59.14 | GGB | 170162.83 | GGB | 137294.1 | GGB | 0 | 0 | 2685 | 3600 | 2669.34 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 132109.84 | GGB | 132111.37 | 2669.34 | 2669.34 |  |  |  | 0 | 1 | [14 empty] | 101.8013 |  |  | #VALUE!
02.02.2008 07:00 | 3600 | 2 | 761.76 | GGB | 763.004 | 768.141 | 766.3 | 266.04 | GGB | 10859 | GGB | 9.83 | GGB | 994.69 | GGB | 58.34 | GGB | 171504.14 | GGB | 138753.62 | GGB | 0 | 0 | 2687 | 3600 | 2671.14 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 132148.54 | GGB | 132150.07 | 2671.14 | 2671.14 |  |  |  | 0 | 1 | [14 empty] | 102.9529 |  |  | #VALUE!
02.02.2008 08:00 | 3600 | 2 | 761.19 | GGB | 763.004 | 768.422 | 766.3 | 264.99 | GGB | 10896.8 | GGB | 9.84 | GGB | 995.5 | GGB | 58.32 | GGB | 171560.26 | GGB | 138920.92 | GGB | 0 | 0 | 2723 | 3600 | 2707.87 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 132188.08 | GGB | 132189.61 | 2707.87 | 2707.87 |  |  |  | 0 | 1 | [14 empty] | 104.4944 |  |  | #VALUE!
02.02.2008 09:00 | 3600 | 2 | 761.79 | GGB | 765.201 | 770.766 | 768.864 | 264.91 | GGB | 10897.2 | GGB | 9.85 | GGB | 995.59 | GGB | 57.92 | GGB | 172579.17 | GGB | 139925.83 | GGB | 0 | 0 | 2680 | 3600 | 2664.12 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 132228.45 | GGB | 132229.98 | 2664.12 | 2664.12 |  |  |  | 1 | 1 |  |  |  |  | 139925.83 | 2664.12 | 139925.83 | 2664.12 | 9.2341 | [5 empty] | 103.5498 |  |  | #VALUE!
02.02.2008 10:00 | 3600 | 2 | 761.87 | GGB | 765.201 | 770.695 | 767.766 | 263.97 | GGB | 10881.5 | GGB | 9.84 | GGB | 996.14 | GGB | 57.9 | GGB | 171956.38 | GGB | 139505.33 | GGB | 0 | 0 | 2671 | 3600 | 2655.13 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 132267.36 | GGB | 132268.88 | 2655.13 | 2655.13 |  |  |  | 1 | 1 |  |  |  |  | 139505.33 | 2655.13 | 139505.33 | 2655.13 | 9.522 | [5 empty] | 102.8902 |  |  | #VALUE!
02.02.2008 11:00 | 3600 | 2 | 761.83 | GGB | 765.201 | 770.578 | 768.132 | 261.8 | GGB | 10895.7 | GGB | 9.84 | GGB | 996.66 | GGB | 58.57 | GGB | 169206.64 | GGB | 137071.64 | GGB | 0 | 0 | 2685 | 3600 | 2669.68 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 132308.11 | GGB | 132309.63 | 2669.68 | 2669.68 |  |  |  | 1 | 1 |  |  |  |  | 137071.64 | 2669.68 | 137071.64 | 2669.68 | 8.9801 | [5 empty] | 101.6493 |  |  | #VALUE!
02.02.2008 12:00 | 3600 | 2 | 761.47 | GGB | 764.102 | 770.438 | 767.033 | 262.32 | GGB | 10863.1 | GGB | 9.83 | GGB | 997.26 | GGB | 58.8 | GGB | 169629.17 | GGB | 137401.56 | GGB | 0 | 0 | 2661 | 3600 | 2645.89 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 132348.46 | GGB | 132349.98 | 2645.89 | 2645.89 |  |  |  | 1 | 1 |  |  |  |  | 137401.56 | 2645.89 | 137401.56 | 2645.89 | 9.0099 | [5 empty] | 100.9859 |  |  | #VALUE!
02.02.2008 13:00 | 3600 | 2 | 762.68 | GGB | 765.201 | 771.492 | 769.597 | 262.48 | GGB | 10850.8 | GGB | 9.84 | GGB | 997.39 | GGB | 58.28 | GGB | 170272.87 | GGB | 138153.65 | GGB | 0 | 0 | 2614 | 3600 | 2598.25 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 132387.26 | GGB | 132388.78 | 2598.25 | 2598.25 |  |  |  | 1 | 1 |  |  |  |  | 138153.65 | 2598.25 | 138153.65 | 2598.25 | 9.2515 | [5 empty] | 99.7105 |  |  | #VALUE!
02.02.2008 14:00 | 3600 | 2 | 762.66 | GGB | 765.201 | 771.727 | 768.498 | 261.13 | GGB | 10870.4 | GGB | 9.84 | GGB | 998.03 | GGB | 58.95 | GGB | 168342.87 | GGB | 136403.17 | GGB | 0 | 0 | 2626 | 3600 | 2610.48 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 132427.69 | GGB | 132429.21 | 2610.48 | 2610.48 |  |  |  | 1 | 1 |  |  |  |  | 136403.17 | 2610.48 | 136403.17 | 2610.48 | 8.8073 | [5 empty] | 98.9105 |  |  | #VALUE!
02.02.2008 15:00 | 3600 | 2 | 762.84 | GGB | 766.3 | 771.938 | 769.597 | 262.17 | GGB | 10838.5 | GGB | 9.83 | GGB | 998.05 | GGB | 58.32 | GGB | 170083.61 | GGB | 138075.15 | GGB | 0 | 0 | 2600 | 3600 | 2584.45 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 132467.63 | GGB | 132469.16 | 2584.45 | 2584.45 |  |  |  | 1 | 1 |  |  |  |  | 138075.15 | 2584.45 | 138075.15 | 2584.45 | 8.9324 | [5 empty] | 99.1245 |  |  | #VALUE!
02.02.2008 16:00 | 3600 | 2 | 763.21 | GGB | 765.201 | 770.859 | 769.597 | 261.31 | GGB | 10873.6 | GGB | 9.84 | GGB | 999.23 | GGB | 58.53 | GGB | 168968.97 | GGB | 137247.66 | GGB | 0 | 0 | 2603 | 3600 | 2587.76 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 132506.65 | GGB | 132508.18 | 2587.76 | 2587.76 |  |  |  | 1 | 1 |  |  |  |  | 137247.66 | 2587.76 | 137247.66 | 2587.76 | 9.1021 | [5 empty] | 98.6567 |  |  | #VALUE!
02.02.2008 17:00 | 3600 | 2 | 763.03 | GGB | 765.201 | 771.961 | 769.597 | 262.26 | GGB | 10852.9 | GGB | 9.83 | GGB | 1000.32 | GGB | 58.51 | GGB | 169902.05 | GGB | 138161.99 | GGB | 0 | 0 | 2608 | 3600 | 2592.85 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 132547.47 | GGB | 132548.99 | 2592.85 | 2592.85 |  |  |  | 1 | 1 |  |  |  |  | 138161.99 | 2592.85 | 138161.99 | 2592.85 | 8.7781 | [5 empty] | 99.5093 |  |  | #VALUE!
02.02.2008 18:00 | 3600 | 2 | 763.72 | GGB | 766.667 | 773.109 | 770.696 | 262.6 | GGB | 10873.8 | GGB | 9.84 | GGB | 1001.28 | GGB | 58.35 | GGB | 170181.54 | GGB | 138590.68 | GGB | 0 | 0 | 2587 | 3600 | 2571.85 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 132586.74 | GGB | 132588.26 | 2571.85 | 2571.85 |  |  |  | 1 | 1 |  |  |  |  | 138590.68 | 2571.85 | 138590.68 | 2571.85 | 9.0765 | [5 empty] | 99.0096 |  |  | #VALUE!
02.02.2008 19:00 | 3600 | 2 | 762.78 | GGB | 764.102 | 770.859 | 768.498 | 262.09 | GGB | 10890.7 | GGB | 9.83 | GGB | 1002.38 | GGB | 58.76 | GGB | 169156.02 | GGB | 137737.52 | GGB | 0 | 0 | 2642 | 3600 | 2626.84 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 132626.25 | GGB | 132627.77 | 2626.84 | 2626.84 |  |  |  | 1 | 1 |  |  |  |  | 137737.52 | 2626.84 | 137737.52 | 2626.84 | 9.1575 | [5 empty] | 100.504 |  |  | #VALUE!
02.02.2008 20:00 | 3600 | 2 | 762.45 | GGB | 765.201 | 770.766 | 768.498 | 264.21 | GGB | 10882.8 | GGB | 9.82 | GGB | 1003.47 | GGB | 58.41 | GGB | 171183.95 | GGB | 139687.02 | GGB | 0 | 0 | 2640 | 3600 | 2624.95 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 132667.31 | GGB | 132668.83 | 2624.95 | 2624.95 |  |  |  | 1 | 1 |  |  |  |  | 139687.02 | 2624.95 | 139687.02 | 2624.95 | 8.9301 | [5 empty] | 101.8532 |  |  | #VALUE!
02.02.2008 21:00 | 3600 | 2 | 763.46 | GGB | 766.3 | 771.867 | 769.597 | 263.91 | GGB | 10923.8 | GGB | 9.84 | GGB | 1004.53 | GGB | 58.52 | GGB | 170724 | GGB | 139410.91 | GGB | 0 | 0 | 2629 | 3600 | 2613.62 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 132705.87 | GGB | 132707.38 | 2613.62 | 2613.62 |  |  |  | 1 | 1 |  |  |  |  | 139410.91 | 2613.62 | 139410.91 | 2613.62 | 9.4518 | [5 empty] | 101.2131 |  |  | #VALUE!
02.02.2008 22:00 | 3600 | 2 | 761.98 | GGB | 764.102 | 769.781 | 767.033 | 264.11 | GGB | 10931.6 | GGB | 9.82 | GGB | 1005.26 | GGB | 58.51 | GGB | 170884.65 | GGB | 139648.88 | GGB | 0 | 0 | 2683 | 3600 | 2667.5 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 132746.41 | GGB | 132747.93 | 2667.5 | 2667.5 |  |  |  | 1 | 1 |  |  |  |  | 139648.88 | 2667.5 | 139648.88 | 2667.5 | 9.1865 | [5 empty] | 103.4759 |  |  | #VALUE!
02.02.2008 23:00 | 3600 | 2 | 762.1 | GGB | 765.201 | 770.813 | 768.132 | 266.24 | GGB | 10934.8 | GGB | 9.83 | GGB | 1006.61 | GGB | 57.97 | GGB | 173356.01 | GGB | 142090.13 | GGB | 0 | 0 | 2676 | 3600 | 2660.73 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 132787.05 | GGB | 132788.57 | 2660.73 | 2659.7766 |  |  |  | 1 | 1 |  |  |  |  | 142090.13 | 2659.7766 | 142090.13 | 2659.7766 | 9.2994 | [5 empty] | 105.0176 | 2659.7766 |  | 104.98
02.02.2008 24:00 | 3600 | 2 | 761.85 | GGB | 763.004 | 768.375 | 765.934 | 265.2 | GGB | 10986.5 | GGB | 9.84 | GGB | 1007.55 | GGB | 57.86 | GGB | 172770.63 | GGB | 141789.02 | GGB | 0 | 0 | 2703 | 3600 | 2687.56 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 132825.6 | GGB | 132827.12 | 2687.56 | 2665.425 |  |  |  | 0 | 1 | [14 empty] | 105.8518 | 2665.425 |  | 104.98
03.02.2008 01:00 | 3600 | 2 | 760.89 | GGB | 763.004 | 768.328 | 767.033 | 266.11 | GGB | 11005.7 | GGB | 9.83 | GGB | 1008.61 | GGB | 58.25 | GGB | 172742.02 | GGB | 141750.39 | GGB | 0 | 0 | 2767 | 3600 | 2751.3 | GGB | 100 | GGB | 42.01 | GGB | 42.01 | GGB | 132867.62 | GGB | 132869.13 | 2751.3 | 2666.1514 |  |  |  | 0 | 1 | [14 empty] | 108.3327 | 2666.1514 |  | 104.98
03.02.2008 02:00 | 3600 | 2 | 760.97 | GGB | 766.3 | 771.422 | 769.597 | 268.24 | GGB | 10998.4 | GGB | 9.83 | GGB | 1009.3 | GGB | 57.41 | GGB | 175563.29 | GGB | 144528.37 | GGB | 0 | 0 | 2756 | 3600 | 2740.31 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 132907.38 | GGB | 132908.89 | 2740.31 | 2614.9053 |  |  |  | 1 | 1 |  |  |  |  | 144528.37 | 2614.9053 | 144528.37 | 2614.9053 | 9.5052 | [5 empty] | 110.0146 | 2614.9053 |  | 104.98
03.02.2008 03:00 | 3600 | 2 | 760.88 | GGB | 763.004 | 768.141 | 765.934 | 267.29 | GGB | 11053.5 | GGB | 9.84 | GGB | 1010.14 | GGB | 57.47 | GGB | 174206.57 | GGB | 143505.66 | GGB | 0 | 0 | 2787 | 3600 | 2771.96 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 132946.67 | GGB | 132948.18 | 2771.96 | 2633.5407 |  |  |  | 0 | 1 | [14 empty] | 110.4978 | 2633.5407 |  | 104.98
03.02.2008 04:00 | 3600 | 2 | 760.17 | GGB | 765.201 | 770.367 | 768.132 | 268.52 | GGB | 11053.9 | GGB | 9.83 | GGB | 1011.32 | GGB | 57.27 | GGB | 175594.1 | GGB | 144904.73 | GGB | 0 | 0 | 2832 | 3600 | 2816.92 | GGB | 100 | GGB | 42.28 | GGB | 42.28 | GGB | 132988.95 | GGB | 132990.46 | 2816.92 | 2608.1136 |  |  |  | 1 | 1 |  |  |  |  | 144904.73 | 2608.1136 | 144904.73 | 2608.1136 | 8.9387 | [5 empty] | 113.3847 | 2608.1136 |  | 104.98
03.02.2008 05:00 | 3600 | 2 | 760.86 | GGB | 764.102 | 769.336 | 768.132 | 269.43 | GGB | 11059.4 | GGB | 9.84 | GGB | 1012.25 | GGB | 56.71 | GGB | 176999.23 | GGB | 146444.59 | GGB | 0 | 0 | 2792 | 3600 | 2776.31 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 133027.92 | GGB | 133029.43 | 2776.31 | 2580.6894 |  |  |  | 1 | 1 |  |  |  |  | 146444.59 | 2580.6894 | 146444.59 | 2580.6894 | 9.6979 | [5 empty] | 112.9377 | 2580.6894 |  | 104.98
03.02.2008 06:00 | 3600 | 2 | 761.08 | GGB | 763.004 | 769.219 | 767.033 | 268.57 | GGB | 11076.7 | GGB | 9.84 | GGB | 1013.27 | GGB | 57.19 | GGB | 175597.4 | GGB | 145220.19 | GGB | 0 | 0 | 2785 | 3600 | 2769.24 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 133068.78 | GGB | 133070.29 | 2769.24 | 2602.448 |  |  |  | 0 | 1 | [14 empty] | 111.7082 | 2602.448 |  | 104.98
03.02.2008 07:00 | 3600 | 2 | 759.79 | GGB | 761.538 | 767.016 | 764.835 | 269.06 | GGB | 11071.2 | GGB | 9.82 | GGB | 1014.17 | GGB | 57.51 | GGB | 175624.91 | GGB | 145231.08 | GGB | 0 | 0 | 2856 | 3600 | 2840.2 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 133110 | GGB | 133111.51 | 2840.2 | 2602.2529 |  |  |  | 0 | 1 | [14 empty] | 114.5793 | 2602.2529 |  | 104.98
03.02.2008 08:00 | 3600 | 2 | 760.79 | GGB | 764.102 | 769.453 | 768.132 | 270.94 | GGB | 11100.8 | GGB | 9.84 | GGB | 1015.14 | GGB | 56.7 | GGB | 177990.63 | GGB | 147693.68 | GGB | 0 | 0 | 2822 | 3600 | 2806.12 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 133150.36 | GGB | 133151.87 | 2806.12 | 2558.8637 |  |  |  | 1 | 1 |  |  |  |  | 147693.68 | 2558.8637 | 147693.68 | 2558.8637 | 9.3639 | [5 empty] | 115.1239 | 2558.8637 |  | 104.98
03.02.2008 09:00 | 3600 | 2 | 760.51 | GGB | 764.102 | 768.305 | 765.934 | 270.34 | GGB | 11137.5 | GGB | 9.84 | GGB | 1016.45 | GGB | 56.86 | GGB | 176967.32 | GGB | 146961.31 | GGB | 0 | 0 | 2856 | 3600 | 2840.53 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 133190.51 | GGB | 133192.02 | 2840.53 | 2571.6156 |  |  |  | 1 | 1 |  |  |  |  | 146961.31 | 2571.6156 | 146961.31 | 2571.6156 | 9.4129 | [5 empty] | 115.9578 | 2571.6156 |  | 104.98
03.02.2008 10:00 | 3600 | 2 | 760.38 | GGB | 764.102 | 769.313 | 768.132 | 270.56 | GGB | 11113.5 | GGB | 9.83 | GGB | 1017.42 | GGB | 56.83 | GGB | 177520.79 | GGB | 147574.37 | GGB | 0 | 0 | 2850 | 3600 | 2833.99 | GGB | 100 | GGB | 41.42 | GGB | 41.42 | GGB | 133231.92 | GGB | 133233.44 | 2833.99 | 2560.9325 |  |  |  | 1 | 1 |  |  |  |  | 147574.37 | 2560.9325 | 147574.37 | 2560.9325 | 9.1243 | [5 empty] | 116.1734 | 2560.9325 |  | 104.98
03.02.2008 11:00 | 3600 | 2 | 761.77 | GGB | 765.201 | 770.18 | 768.498 | 269.98 | GGB | 11104.1 | GGB | 9.84 | GGB | 1018.07 | GGB | 56.76 | GGB | 177037.74 | GGB | 147298.16 | GGB | 0 | 0 | 2769 | 3600 | 2753.07 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 133272.35 | GGB | 133273.87 | 2753.07 | 2565.7347 |  |  |  | 1 | 1 |  |  |  |  | 147298.16 | 2565.7347 | 147298.16 | 2565.7347 | 9.3477 | [5 empty] | 112.645 | 2565.7347 |  | 104.98
03.02.2008 12:00 | 3600 | 2 | 762.88 | GGB | 765.201 | 771.211 | 768.498 | 268.47 | GGB | 11100 | GGB | 9.85 | GGB | 1018.26 | GGB | 57.35 | GGB | 175166.07 | GGB | 145506.85 | GGB | 0 | 0 | 2732 | 3600 | 2716.7 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 133312.73 | GGB | 133314.25 | 2716.7 | 2597.321 |  |  |  | 1 | 1 |  |  |  |  | 145506.85 | 2597.321 | 145506.85 | 2597.321 | 9.3593 | [5 empty] | 109.8051 | 2597.321 |  | 104.98
03.02.2008 13:00 | 3600 | 2 | 762.65 | GGB | 766.3 | 771.188 | 768.498 | 266.68 | GGB | 11071.2 | GGB | 9.84 | GGB | 1018.44 | GGB | 58.21 | GGB | 172704.61 | GGB | 143115.09 | GGB | 0 | 0 | 2728 | 3600 | 2712.12 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 133353.64 | GGB | 133355.16 | 2712.12 | 2640.7278 |  |  |  | 1 | 1 |  |  |  |  | 143115.09 | 2640.7278 | 143115.09 | 2640.7278 | 9.238 | [5 empty] | 107.8181 | 2640.7278 |  | 104.98
03.02.2008 14:00 | 3600 | 2 | 763.21 | GGB | 765.201 | 770.109 | 768.498 | 266.35 | GGB | 11039.3 | GGB | 9.83 | GGB | 1018.32 | GGB | 58.24 | GGB | 172479.04 | GGB | 142898.13 | GGB | 0 | 0 | 2689 | 3600 | 2673.65 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 133394.23 | GGB | 133395.75 | 2673.65 | 2644.7372 |  |  |  | 1 | 1 |  |  |  |  | 142898.13 | 2644.7372 | 142898.13 | 2644.7372 | 9.3109 | [5 empty] | 106.1277 | 2644.7372 |  | 104.98
03.02.2008 15:00 | 3600 | 2 | 764.11 | GGB | 766.667 | 772.383 | 769.597 | 267.18 | GGB | 11025.4 | GGB | 9.84 | GGB | 1018.14 | GGB | 57.91 | GGB | 173931.49 | GGB | 144220.58 | GGB | 0 | 0 | 2639 | 3600 | 2623.66 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 133434.78 | GGB | 133436.31 | 2623.66 | 2620.4859 |  |  |  | 1 | 1 |  |  |  |  | 144220.58 | 2620.4859 | 144220.58 | 2620.4859 | 9.3178 | [5 empty] | 105.1072 | 2620.4859 |  | 104.98
03.02.2008 16:00 | 3600 | 2 | 763.44 | GGB | 766.3 | 771.445 | 769.597 | 266.08 | GGB | 11048.2 | GGB | 9.83 | GGB | 1018.26 | GGB | 58.43 | GGB | 172424.03 | GGB | 142764.25 | GGB | 0 | 0 | 2684 | 3600 | 2669.06 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 133475 | GGB | 133476.53 | 2669.06 | 2647.2174 |  |  |  | 1 | 1 |  |  |  |  | 142764.25 | 2647.2174 | 142764.25 | 2647.2174 | 9.3965 | [5 empty] | 105.8462 | 2647.2174 |  | 104.98
03.02.2008 17:00 | 3600 | 2 | 762.93 | GGB | 765.201 | 770.367 | 768.498 | 268.09 | GGB | 11021.5 | GGB | 9.82 | GGB | 1018.88 | GGB | 57.97 | GGB | 174402.43 | GGB | 144688.88 | GGB | 0 | 0 | 2684 | 3600 | 2668.65 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 133516.06 | GGB | 133517.59 | 2668.65 | 2612.0045 |  |  |  | 1 | 1 |  |  |  |  | 144688.88 | 2612.0045 | 144688.88 | 2612.0045 | 9.2043 | [5 empty] | 107.2567 | 2612.0045 |  | 104.98
03.02.2008 18:00 | 3600 | 2 | 763.72 | GGB | 765.201 | 771.656 | 768.498 | 267.95 | GGB | 11070.5 | GGB | 9.84 | GGB | 1019.21 | GGB | 58.3 | GGB | 173740.03 | GGB | 144045.31 | GGB | 0 | 0 | 2687 | 3600 | 2671.94 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 133556.74 | GGB | 133558.26 | 2671.94 | 2623.6745 |  |  |  | 1 | 1 |  |  |  |  | 144045.31 | 2623.6745 | 144045.31 | 2623.6745 | 9.2925 | [5 empty] | 106.9112 | 2623.6745 |  | 104.98
03.02.2008 19:00 | 3600 | 2 | 761.8 | GGB | 764.102 | 769.641 | 768.132 | 268.24 | GGB | 11084.6 | GGB | 9.82 | GGB | 1019.69 | GGB | 58.44 | GGB | 174019.52 | GGB | 144283.24 | GGB | 0 | 0 | 2778 | 3600 | 2762.62 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 133597.55 | GGB | 133599.07 | 2762.62 | 2619.3479 |  |  |  | 1 | 1 |  |  |  |  | 144283.24 | 2619.3479 | 144283.24 | 2619.3479 | 9.2607 | [5 empty] | 110.7222 | 2619.3479 |  | 104.98
03.02.2008 20:00 | 3600 | 2 | 761.72 | GGB | 765.201 | 770.719 | 768.132 | 268.52 | GGB | 11115 | GGB | 9.83 | GGB | 1020.13 | GGB | 58.22 | GGB | 174491.56 | GGB | 144833.93 | GGB | 0 | 0 | 2783 | 3600 | 2767.28 | GGB | 100 | GGB | 41.5 | GGB | 41.5 | GGB | 133639.04 | GGB | 133640.57 | 2767.28 | 2609.3886 |  |  |  | 1 | 1 |  |  |  |  | 144833.93 | 2609.3886 | 144833.93 | 2609.3886 | 9.1067 | [5 empty] | 111.3322 | 2609.3886 |  | 104.98
03.02.2008 21:00 | 3600 | 2 | 761.2 | GGB | 763.004 | 769.383 | 765.934 | 269.05 | GGB | 11124.2 | GGB | 9.83 | GGB | 1020.53 | GGB | 58.07 | GGB | 175248.59 | GGB | 145584.92 | GGB | 0 | 0 | 2811 | 3600 | 2795.26 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 133679.02 | GGB | 133680.54 | 2795.26 | 2595.9282 |  |  |  | 0 | 1 | [14 empty] | 113.041 | 2595.9282 |  | 104.98
03.02.2008 22:00 | 3600 | 2 | 761.41 | GGB | 768.864 | 774.234 | 771.795 | 269.56 | GGB | 11156.1 | GGB | 9.84 | GGB | 1021.12 | GGB | 57.82 | GGB | 176823.18 | GGB | 147087.62 | GGB | 0 | 0 | 2830 | 3600 | 2814.66 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 133720.22 | GGB | 133721.74 | 2814.66 | 2569.4073 |  |  |  | 1 | 1 |  |  |  |  | 147087.62 | 2569.4073 | 147087.62 | 2569.4073 | 9.173 | [5 empty] | 115.0005 | 2569.4073 |  | 104.98
03.02.2008 23:00 | 3600 | 2 | 760.56 | GGB | 764.102 | 770.039 | 768.132 | 270.7 | GGB | 11142.7 | GGB | 9.82 | GGB | 1021.25 | GGB | 58.02 | GGB | 176237.8 | GGB | 146532.51 | GGB | 0 | 0 | 2871 | 3600 | 2855.57 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 133760.32 | GGB | 133761.84 | 2855.57 | 2579.141 |  |  |  | 1 | 1 |  |  |  |  | 146532.51 | 2579.141 | 146532.51 | 2579.141 | 9.4246 | [5 empty] | 116.2316 | 2579.141 |  | 104.98
03.02.2008 24:00 | 3600 | 2 | 761.1 | GGB | 763.004 | 768.75 | 767.033 | 272.17 | GGB | 11137.5 | GGB | 9.83 | GGB | 1021.32 | GGB | 58.18 | GGB | 177135.67 | GGB | 147217.87 | GGB | 0 | 0 | 2858 | 3600 | 2842.89 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 133799.31 | GGB | 133800.83 | 2842.89 | 2567.134 |  |  |  | 0 | 1 | [14 empty] | 116.2567 | 2567.134 |  | 104.98
04.02.2008 01:00 | 3600 | 2 | 760.49 | GGB | 761.538 | 767.555 | 764.835 | 272.56 | GGB | 11152.4 | GGB | 9.82 | GGB | 1021.43 | GGB | 58.68 | GGB | 176819.88 | GGB | 146750.42 | GGB | 0 | 0 | 2902 | 3600 | 2886.14 | GGB | 100 | GGB | 42.86 | GGB | 42.86 | GGB | 133842.17 | GGB | 133843.69 | 2886.14 | 2575.3112 |  |  |  | 0 | 1 | [14 empty] | 117.6506 | 2575.3112 |  | 104.98
04.02.2008 02:00 | 3600 | 2 | 760.8 | GGB | 765.201 | 770.883 | 768.132 | 273.1 | GGB | 11178.6 | GGB | 9.84 | GGB | 1021.3 | GGB | 58.67 | GGB | 177272.11 | GGB | 147111.06 | GGB | 0 | 0 | 2896 | 3600 | 2880.55 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 133882.15 | GGB | 133883.67 | 2880.55 | 2568.9979 |  |  |  | 1 | 1 |  |  |  |  | 147111.06 | 2568.9979 | 147111.06 | 2568.9979 | 9.4529 | [5 empty] | 117.7113 | 2568.9979 |  | 104.98
04.02.2008 03:00 | 3600 | 2 | 760.51 | GGB | 762.637 | 767.578 | 765.934 | 273.72 | GGB | 11149.4 | GGB | 9.82 | GGB | 1020.97 | GGB | 58.42 | GGB | 178105.07 | GGB | 147865.53 | GGB | 0 | 0 | 2899 | 3600 | 2883.05 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 133922.77 | GGB | 133924.3 | 2883.05 | 2555.8898 |  |  |  | 0 | 1 | [14 empty] | 118.4177 | 2555.8898 |  | 104.98
04.02.2008 04:00 | 3600 | 2 | 761.13 | GGB | 764.102 | 768.844 | 767.033 | 273.58 | GGB | 11172.4 | GGB | 9.84 | GGB | 1020.72 | GGB | 58.36 | GGB | 177785.97 | GGB | 147588.86 | GGB | 0 | 0 | 2878 | 3600 | 2862.41 | GGB | 100 | GGB | 41.68 | GGB | 41.68 | GGB | 133964.45 | GGB | 133965.98 | 2862.41 | 2560.6811 |  |  |  | 1 | 1 |  |  |  |  | 147588.86 | 2560.6811 | 147588.86 | 2560.6811 | 9.0674 | [5 empty] | 117.35 | 2560.6811 |  | 104.98
04.02.2008 05:00 | 3600 | 2 | 761.05 | GGB | 763.004 | 767.766 | 765.934 | 273.49 | GGB | 11170.3 | GGB | 9.84 | GGB | 1020.2 | GGB | 58.29 | GGB | 178035.75 | GGB | 147755 | GGB | 0 | 0 | 2887 | 3600 | 2871.37 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 134004.61 | GGB | 134006.14 | 2871.37 | 2557.8018 |  |  |  | 0 | 1 | [14 empty] | 117.8498 | 2557.8018 |  | 104.98
04.02.2008 06:00 | 3600 | 2 | 760.52 | GGB | 765.201 | 771.938 | 768.498 | 273.94 | GGB | 11181.8 | GGB | 9.84 | GGB | 1020.05 | GGB | 58.12 | GGB | 178699.25 | GGB | 148357.12 | GGB | 0 | 0 | 2914 | 3600 | 2898.56 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 134045.89 | GGB | 134047.43 | 2898.56 | 2547.4207 |  |  |  | 1 | 1 |  |  |  |  | 148357.12 | 2547.4207 | 148357.12 | 2547.4207 | 9.153 | [5 empty] | 119.4506 | 2547.4207 |  | 104.98
04.02.2008 07:00 | 3600 | 2 | 760.05 | GGB | 763.004 | 768.516 | 765.201 | 273.58 | GGB | 11193.6 | GGB | 9.83 | GGB | 1020.03 | GGB | 58.14 | GGB | 178344.94 | GGB | 148053.35 | GGB | 0 | 0 | 2944 | 3600 | 2928.38 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 134087.17 | GGB | 134088.7 | 2928.38 | 2552.6474 |  |  |  | 0 | 1 | [14 empty] | 120.4324 | 2552.6474 |  | 104.98
04.02.2008 08:00 | 3600 | 2 | 759.94 | GGB | 762.637 | 768.07 | 765.201 | 273.52 | GGB | 11206 | GGB | 9.84 | GGB | 1020.1 | GGB | 57.99 | GGB | 178746.57 | GGB | 148463.02 | GGB | 0 | 0 | 2957 | 3600 | 2941.69 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 134127.68 | GGB | 134129.22 | 2941.69 | 2545.6036 |  |  |  | 0 | 1 | [14 empty] | 121.3145 | 2545.6036 |  | 104.98
04.02.2008 09:00 | 3600 | 2 | 759.44 | GGB | 763.004 | 769.383 | 766.3 | 274.1 | GGB | 11201.5 | GGB | 9.83 | GGB | 1020.54 | GGB | 57.56 | GGB | 179643.34 | GGB | 149468.05 | GGB | 0 | 0 | 2986 | 2634 | 2970.47 | GGB | 100 | GGB | 41.71 | GGB | 41.71 | GGB | 134169.39 | GGB | 134170.93 | 2970.47 | 2528.4869 |  |  |  | 0 | 1 | [14 empty] | 123.3307 | 2528.4869 |  | 104.98
04.02.2008 10:00 | 3600 | 2 | 760.85 | GGB | 765.201 | 770.602 | 767.766 | 274.6 | GGB | 11178 | GGB | 9.85 | GGB | 1020.06 | GGB | 57.28 | GGB | 180484 | GGB | 150221.61 | GGB | 0 | 0 | 2872 | 2537 | 2856.76 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 134210.12 | GGB | 134211.67 | 2856.76 | 2515.8032 |  |  |  | 1 | 1 |  |  |  |  | 150221.61 | 2515.8032 | 150221.61 | 2515.8032 | 9.2766 | [5 empty] | 119.2075 | 2515.8032 |  | 104.98
04.02.2008 11:00 | 3600 | 2 | 761.86 | GGB | 766.3 | 772.477 | 769.963 | 272.67 | GGB | 11140.7 | GGB | 9.85 | GGB | 1019.71 | GGB | 57.68 | GGB | 178397.76 | GGB | 148254.49 | GGB | 0 | 0 | 2816 | 3600 | 2800.21 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 134250.59 | GGB | 134252.14 | 2800.21 | 2549.1842 |  |  |  | 1 | 1 |  |  |  |  | 148254.49 | 2549.1842 | 148254.49 | 2549.1842 | 9.3385 | [5 empty] | 115.3177 | 2549.1842 |  | 104.98
04.02.2008 12:00 | 3600 | 2 | 763.02 | GGB | 766.3 | 771.891 | 769.963 | 269.65 | GGB | 11108.7 | GGB | 9.86 | GGB | 1019.07 | GGB | 58.51 | GGB | 174626.9 | GGB | 144670.48 | GGB | 0 | 0 | 2762 | 3600 | 2746.65 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 134291.38 | GGB | 134292.93 | 2746.65 | 2612.3367 |  |  |  | 1 | 1 |  |  |  |  | 144670.48 | 2612.3367 | 144670.48 | 2612.3367 | 9.2652 | [5 empty] | 110.3775 | 2612.3367 |  | 104.98
04.02.2008 13:00 | 3600 | 2 | 763.47 | GGB | 767.766 | 773.016 | 769.963 | 267.55 | GGB | 11052.9 | GGB | 9.85 | GGB | 1018.3 | GGB | 59.14 | GGB | 172045.51 | GGB | 142151.29 | GGB | 0 | 0 | 2727 | 3600 | 2712.06 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 134332.22 | GGB | 134333.77 | 2712.06 | 2658.6322 |  |  |  | 1 | 1 |  |  |  |  | 142151.29 | 2658.6322 | 142151.29 | 2658.6322 | 9.2539 | [5 empty] | 107.0897 | 2658.6322 |  | 104.98
04.02.2008 14:00 | 3600 | 2 | 764.48 | GGB | 767.766 | 774.281 | 771.429 | 266.26 | GGB | 11001.9 | GGB | 9.84 | GGB | 1017.67 | GGB | 59.78 | GGB | 170064.9 | GGB | 140157.72 | GGB | 0 | 0 | 2660 | 3600 | 2644.86 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 134372.61 | GGB | 134374.17 | 2644.86 | 2644.86 |  |  |  | 1 | 1 |  |  |  |  | 140157.72 | 2644.86 | 140157.72 | 2644.86 | 9.1757 | [5 empty] | 102.9715 |  |  | #VALUE!
04.02.2008 15:00 | 3600 | 2 | 764.68 | GGB | 767.766 | 774.445 | 771.429 | 265.71 | GGB | 10966 | GGB | 9.84 | GGB | 1016.18 | GGB | 60.24 | GGB | 169639.07 | GGB | 139410.34 | GGB | 0 | 0 | 2639 | 3600 | 2623.75 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 134413.02 | GGB | 134414.57 | 2623.75 | 2623.75 |  |  |  | 1 | 1 |  |  |  |  | 139410.34 | 2623.75 | 139410.34 | 2623.75 | 9.0539 | [5 empty] | 101.605 |  |  | #VALUE!
04.02.2008 16:00 | 3600 | 2 | 765.19 | GGB | 768.864 | 774.469 | 771.429 | 265.17 | GGB | 10944.1 | GGB | 9.84 | GGB | 1015.08 | GGB | 60.86 | GGB | 169127.41 | GGB | 138581.15 | GGB | 0 | 0 | 2606 | 3600 | 2590.73 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 134453.4 | GGB | 134454.95 | 2590.73 | 2590.73 |  |  |  | 1 | 1 |  |  |  |  | 138581.15 | 2590.73 | 138581.15 | 2590.73 | 8.8912 | [5 empty] | 99.7295 |  |  | #VALUE!
04.02.2008 17:00 | 3600 | 2 | 764.31 | GGB | 766.3 | 772.477 | 769.963 | 266.02 | GGB | 10931.5 | GGB | 9.82 | GGB | 1014.65 | GGB | 60.86 | GGB | 169728.2 | GGB | 139015.14 | GGB | 0 | 0 | 2640 | 3600 | 2624.34 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 134493.33 | GGB | 134494.88 | 2624.34 | 2624.34 |  |  |  | 1 | 1 |  |  |  |  | 139015.14 | 2624.34 | 139015.14 | 2624.34 | 9.1366 | [5 empty] | 101.3397 |  |  | #VALUE!
04.02.2008 18:00 | 3600 | 2 | 764.02 | GGB | 766.3 | 772.406 | 769.963 | 266.99 | GGB | 10962.7 | GGB | 9.83 | GGB | 1014.44 | GGB | 60.63 | GGB | 170365.29 | GGB | 139603.47 | GGB | 0 | 0 | 2669 | 3600 | 2653.28 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 134533.81 | GGB | 134535.36 | 2653.28 | 2653.28 |  |  |  | 1 | 1 |  |  |  |  | 139603.47 | 2653.28 | 139603.47 | 2653.28 | 9.1504 | [5 empty] | 102.8909 |  |  | #VALUE!
04.02.2008 19:00 | 3600 | 2 | 763.71 | GGB | 766.3 | 772.477 | 769.963 | 267.63 | GGB | 10978.4 | GGB | 9.83 | GGB | 1014.94 | GGB | 60.49 | GGB | 170955.08 | GGB | 140213.41 | GGB | 0 | 0 | 2696 | 3600 | 2680.45 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 134574.33 | GGB | 134575.87 | 2680.45 | 2680.45 |  |  |  | 1 | 1 |  |  |  |  | 140213.41 | 2680.45 | 140213.41 | 2680.45 | 9.2776 | [5 empty] | 104.3986 |  |  | #VALUE!
04.02.2008 20:00 | 3600 | 2 | 763.46 | GGB | 765.201 | 771.352 | 768.864 | 268.08 | GGB | 10991.5 | GGB | 9.83 | GGB | 1015.11 | GGB | 60.34 | GGB | 171238.96 | GGB | 140532.73 | GGB | 0 | 0 | 2700 | 3600 | 2684.6 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 134614.22 | GGB | 134615.76 | 2684.6 | 2684.6 |  |  |  | 1 | 1 |  |  |  |  | 140532.73 | 2684.6 | 140532.73 | 2684.6 | 9.4579 | [5 empty] | 104.7984 |  |  | #VALUE!
04.02.2008 21:00 | 3600 | 2 | 763.18 | GGB | 766.3 | 772.828 | 769.963 | 268.52 | GGB | 11008.7 | GGB | 9.83 | GGB | 1014.58 | GGB | 60.27 | GGB | 171881.56 | GGB | 141016.14 | GGB | 0 | 0 | 2722 | 3600 | 2707.03 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 134654.79 | GGB | 134656.34 | 2707.03 | 2680.0336 |  |  |  | 1 | 1 |  |  |  |  | 141016.14 | 2680.0336 | 141016.14 | 2680.0336 | 9.3132 | [5 empty] | 106.0375 | 2680.0336 |  | 104.98
04.02.2008 22:00 | 3600 | 2 | 762.82 | GGB | 765.201 | 771.281 | 768.864 | 268.65 | GGB | 11013.9 | GGB | 9.83 | GGB | 1014.61 | GGB | 60.18 | GGB | 171958.58 | GGB | 141123.43 | GGB | 0 | 0 | 2729 | 3600 | 2713.55 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 134693.61 | GGB | 134695.16 | 2713.55 | 2677.9961 |  |  |  | 1 | 1 |  |  |  |  | 141123.43 | 2677.9961 | 141123.43 | 2677.9961 | 9.7354 | [5 empty] | 106.3737 | 2677.9961 |  | 104.98
04.02.2008 23:00 | 3600 | 2 | 762.05 | GGB | 766.3 | 771.234 | 768.864 | 268.95 | GGB | 11002.6 | GGB | 9.82 | GGB | 1015.12 | GGB | 59.59 | GGB | 173664.11 | GGB | 142846.7 | GGB | 0 | 0 | 2766 | 3600 | 2750.1 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 134733.72 | GGB | 134735.27 | 2750.1 | 2645.6894 |  |  |  | 1 | 1 |  |  |  |  | 142846.7 | 2645.6894 | 142846.7 | 2645.6894 | 9.4223 | [5 empty] | 109.123 | 2645.6894 |  | 104.98
04.02.2008 24:00 | 3600 | 2 | 763.09 | GGB | 764.102 | 769.922 | 767.766 | 269.53 | GGB | 11042.9 | GGB | 9.84 | GGB | 1015.01 | GGB | 59.68 | GGB | 172984.1 | GGB | 142232.72 | GGB | 0 | 0 | 2742 | 3600 | 2726.68 | GGB | 100 | GGB | 41.72 | GGB | 41.72 | GGB | 134775.44 | GGB | 134776.99 | 2726.68 | 2657.1101 |  |  |  | 1 | 1 |  |  |  |  | 142232.72 | 2657.1101 | 142232.72 | 2657.1101 | 9.0587 | [5 empty] | 107.7286 | 2657.1101 |  | 104.98
05.02.2008 01:00 | 3600 | 2 | 762.14 | GGB | 765.201 | 771.164 | 768.864 | 269.43 | GGB | 11045.4 | GGB | 9.84 | GGB | 1014.84 | GGB | 59.67 | GGB | 173234.97 | GGB | 142422.68 | GGB | 0 | 0 | 2776 | 3600 | 2760.13 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 134815.4 | GGB | 134816.95 | 2760.13 | 2653.5661 |  |  |  | 1 | 1 |  |  |  |  | 142422.68 | 2653.5661 | 142422.68 | 2653.5661 | 9.4577 | [5 empty] | 109.1959 | 2653.5661 |  | 104.98
05.02.2008 02:00 | 3600 | 2 | 761.67 | GGB | 765.201 | 771.047 | 768.864 | 269.54 | GGB | 11050.5 | GGB | 9.83 | GGB | 1014.74 | GGB | 59.43 | GGB | 173473.75 | GGB | 142705.39 | GGB | 0 | 0 | 2794 | 3600 | 2778.19 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 134855.88 | GGB | 134857.43 | 2778.19 | 2648.3092 |  |  |  | 1 | 1 |  |  |  |  | 142705.39 | 2648.3092 | 142705.39 | 2648.3092 | 9.3362 | [5 empty] | 110.1285 | 2648.3092 |  | 104.98
05.02.2008 03:00 | 3600 | 2 | 762.16 | GGB | 766.667 | 773.344 | 770.33 | 270.74 | GGB | 11042.6 | GGB | 9.84 | GGB | 1015.02 | GGB | 59.01 | GGB | 174896.48 | GGB | 144099.55 | GGB | 0 | 0 | 2772 | 3600 | 2756.84 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 134896.77 | GGB | 134898.32 | 2756.84 | 2622.6869 |  |  |  | 1 | 1 |  |  |  |  | 144099.55 | 2622.6869 | 144099.55 | 2622.6869 | 9.2426 | [5 empty] | 110.3498 | 2622.6869 |  | 104.98
05.02.2008 04:00 | 3600 | 2 | 761.43 | GGB | 765.201 | 771.211 | 768.864 | 269.62 | GGB | 11055 | GGB | 9.83 | GGB | 1014.91 | GGB | 59.51 | GGB | 173436.34 | GGB | 142664.13 | GGB | 0 | 0 | 2807 | 3600 | 2791.69 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 134936.89 | GGB | 134938.45 | 2791.69 | 2649.0751 |  |  |  | 1 | 1 |  |  |  |  | 142664.13 | 2649.0751 | 142664.13 | 2649.0751 | 9.4176 | [5 empty] | 110.6317 | 2649.0751 |  | 104.98
05.02.2008 05:00 | 3600 | 2 | 761.95 | GGB | 765.201 | 771.234 | 768.864 | 269.52 | GGB | 11056.7 | GGB | 9.84 | GGB | 1014.51 | GGB | 59.38 | GGB | 173354.91 | GGB | 142595.7 | GGB | 0 | 0 | 2794 | 3600 | 2778.17 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 134977.53 | GGB | 134979.09 | 2778.17 | 2650.3464 |  |  |  | 1 | 1 |  |  |  |  | 142595.7 | 2650.3464 | 142595.7 | 2650.3464 | 9.2994 | [5 empty] | 110.0431 | 2650.3464 |  | 104.98
05.02.2008 06:00 | 3600 | 2 | 761.27 | GGB | 764.102 | 770.227 | 767.766 | 269.91 | GGB | 11025.7 | GGB | 9.82 | GGB | 1014.59 | GGB | 59.21 | GGB | 174038.22 | GGB | 143241.97 | GGB | 0 | 0 | 2806 | 3600 | 2790.25 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 135018.31 | GGB | 135019.87 | 2790.25 | 2638.3887 |  |  |  | 1 | 1 |  |  |  |  | 143241.97 | 2638.3887 | 143241.97 | 2638.3887 | 9.2675 | [5 empty] | 111.0225 | 2638.3887 |  | 104.98
05.02.2008 07:00 | 3600 | 2 | 763.03 | GGB | 765.201 | 771.047 | 767.766 | 270.28 | GGB | 11018.3 | GGB | 9.84 | GGB | 1014.54 | GGB | 58.78 | GGB | 175010.92 | GGB | 144223.26 | GGB | 0 | 0 | 2731 | 3600 | 2716.01 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 135058.29 | GGB | 135059.86 | 2716.01 | 2620.4372 |  |  |  | 1 | 1 |  |  |  |  | 144223.26 | 2620.4372 | 144223.26 | 2620.4372 | 9.4506 | [5 empty] | 108.8088 | 2620.4372 |  | 104.98
05.02.2008 08:00 | 3600 | 2 | 763.31 | GGB | 766.667 | 773.367 | 770.33 | 269.81 | GGB | 11013.6 | GGB | 9.84 | GGB | 1014.82 | GGB | 58.92 | GGB | 174491.56 | GGB | 143775.62 | GGB | 0 | 0 | 2713 | 3600 | 2697.97 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 135098.76 | GGB | 135100.33 | 2697.97 | 2628.5959 |  |  |  | 1 | 1 |  |  |  |  | 143775.62 | 2628.5959 | 143775.62 | 2628.5959 | 9.3385 | [5 empty] | 107.7506 | 2628.5959 |  | 104.98
05.02.2008 09:00 | 3600 | 2 | 763.29 | GGB | 765.201 | 771.328 | 768.864 | 269.54 | GGB | 10991.6 | GGB | 9.83 | GGB | 1014.96 | GGB | 58.96 | GGB | 174199.97 | GGB | 143537 | GGB | 0 | 0 | 2719 | 3600 | 2703.34 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 135139.76 | GGB | 135141.33 | 2703.34 | 2632.9657 |  |  |  | 1 | 1 |  |  |  |  | 143537 | 2632.9657 | 143537 | 2632.9657 | 9.2178 | [5 empty] | 107.7859 | 2632.9657 |  | 104.98
05.02.2008 10:00 | 3600 | 2 | 763.71 | GGB | 766.667 | 773.344 | 770.33 | 268.8 | GGB | 11025.2 | GGB | 9.85 | GGB | 1015.72 | GGB | 59.39 | GGB | 172794.84 | GGB | 142303.04 | GGB | 0 | 0 | 2711 | 3600 | 2695.27 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 135179.44 | GGB | 135181 | 2695.27 | 2655.7971 |  |  |  | 1 | 1 |  |  |  |  | 142303.04 | 2655.7971 | 142303.04 | 2655.7971 | 9.5268 | [5 empty] | 106.5403 | 2655.7971 |  | 104.98
05.02.2008 11:00 | 3600 | 2 | 762.74 | GGB | 766.3 | 772.125 | 769.963 | 267.91 | GGB | 11019.9 | GGB | 9.83 | GGB | 1016.06 | GGB | 59.97 | GGB | 171534.95 | GGB | 141065.42 | GGB | 0 | 0 | 2753 | 3600 | 2737.38 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 135219.64 | GGB | 135221.21 | 2737.38 | 2679.0974 |  |  |  | 1 | 1 |  |  |  |  | 141065.42 | 2679.0974 | 141065.42 | 2679.0974 | 9.3989 | [5 empty] | 107.2638 | 2679.0974 |  | 104.98
05.02.2008 12:00 | 3600 | 2 | 763.28 | GGB | 766.3 | 772.125 | 769.963 | 267.61 | GGB | 11007.4 | GGB | 9.84 | GGB | 1015.88 | GGB | 60.2 | GGB | 171033.2 | GGB | 140530.94 | GGB | 0 | 0 | 2734 | 3600 | 2718.39 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 135259.89 | GGB | 135261.46 | 2718.39 | 2689.2868 |  |  |  | 1 | 1 |  |  |  |  | 140530.94 | 2689.2868 | 140530.94 | 2689.2868 | 9.3895 | [5 empty] | 106.1161 | 2689.2868 |  | 104.98
05.02.2008 13:00 | 3600 | 2 | 763.48 | GGB | 766.667 | 773.273 | 770.33 | 269.35 | GGB | 10962.9 | GGB | 9.83 | GGB | 1016.29 | GGB | 59.73 | GGB | 172979.7 | GGB | 142386.84 | GGB | 0 | 0 | 2696 | 3600 | 2681.06 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 135299.37 | GGB | 135300.95 | 2681.06 | 2654.2341 |  |  |  | 1 | 1 |  |  |  |  | 142386.84 | 2654.2341 | 142386.84 | 2654.2341 | 9.5702 | [5 empty] | 106.041 | 2654.2341 |  | 104.98
05.02.2008 14:00 | 3600 | 2 | 763.89 | GGB | 766.3 | 772.172 | 769.963 | 267.39 | GGB | 10999.2 | GGB | 9.84 | GGB | 1015.49 | GGB | 60.51 | GGB | 170410.41 | GGB | 139833.41 | GGB | 0 | 0 | 2704 | 3600 | 2688.95 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 135340.69 | GGB | 135342.26 | 2688.95 | 2688.95 |  |  |  | 1 | 1 |  |  |  |  | 139833.41 | 2688.95 | 139833.41 | 2688.95 | 9.102 | [5 empty] | 104.4458 |  |  | #VALUE!
05.02.2008 15:00 | 3600 | 2 | 763.9 | GGB | 766.3 | 772.172 | 770.33 | 267.2 | GGB | 10986.6 | GGB | 9.84 | GGB | 1015.14 | GGB | 60.59 | GGB | 170194.74 | GGB | 139575.65 | GGB | 0 | 0 | 2696 | 3600 | 2680.81 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 135380.81 | GGB | 135382.38 | 2680.81 | 2680.81 |  |  |  | 1 | 1 |  |  |  |  | 139575.65 | 2680.81 | 139575.65 | 2680.81 | 9.3264 | [5 empty] | 103.9377 |  |  | #VALUE!
05.02.2008 16:00 | 3600 | 2 | 763.67 | GGB | 765.201 | 771.281 | 768.864 | 267.65 | GGB | 10965.9 | GGB | 9.83 | GGB | 1015 | GGB | 60.5 | GGB | 170643.68 | GGB | 139964 | GGB | 0 | 0 | 2706 | 3600 | 2690.35 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 135420.62 | GGB | 135422.18 | 2690.35 | 2690.35 |  |  |  | 1 | 1 |  |  |  |  | 139964 | 2690.35 | 139964 | 2690.35 | 9.4611 | [5 empty] | 104.5978 |  |  | #VALUE!
05.02.2008 17:00 | 3600 | 2 | 764.08 | GGB | 767.766 | 774.375 | 770.33 | 268.42 | GGB | 10979.6 | GGB | 9.84 | GGB | 1015.14 | GGB | 60.24 | GGB | 171554.76 | GGB | 140841.2 | GGB | 0 | 0 | 2682 | 3600 | 2667.05 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 135461.91 | GGB | 135463.47 | 2667.05 | 2667.05 |  |  |  | 1 | 1 |  |  |  |  | 140841.2 | 2667.05 | 140841.2 | 2667.05 | 9.0974 | [5 empty] | 104.3418 |  |  | #VALUE!
05.02.2008 18:00 | 3600 | 2 | 763.48 | GGB | 766.3 | 772.148 | 769.963 | 268.3 | GGB | 10961.8 | GGB | 9.82 | GGB | 1015.43 | GGB | 60.47 | GGB | 171240.06 | GGB | 140526.18 | GGB | 0 | 0 | 2710 | 3600 | 2694.36 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 135501.26 | GGB | 135502.82 | 2694.36 | 2689.3779 |  |  |  | 1 | 1 |  |  |  |  | 140526.18 | 2689.3779 | 140526.18 | 2689.3779 | 9.6043 | [5 empty] | 105.1745 | 2689.3779 |  | 104.98
05.02.2008 19:00 | 3600 | 2 | 763.95 | GGB | 765.201 | 772.172 | 769.963 | 269.67 | GGB | 10952.5 | GGB | 9.83 | GGB | 1015.91 | GGB | 59.99 | GGB | 172684.81 | GGB | 141983.36 | GGB | 0 | 0 | 2681 | 3600 | 2665.79 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 135541.51 | GGB | 135543.08 | 2665.79 | 2661.7767 |  |  |  | 1 | 1 |  |  |  |  | 141983.36 | 2661.7767 | 141983.36 | 2661.7767 | 9.3872 | [5 empty] | 105.1383 | 2661.7767 |  | 104.98
05.02.2008 20:00 | 3600 | 2 | 764.15 | GGB | 766.667 | 772.359 | 769.963 | 268.84 | GGB | 10993.7 | GGB | 9.84 | GGB | 1015.99 | GGB | 60.42 | GGB | 171249.97 | GGB | 140630.72 | GGB | 0 | 0 | 2687 | 3600 | 2671.6 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 135582.03 | GGB | 135583.6 | 2671.6 | 2671.6 |  |  |  | 1 | 1 |  |  |  |  | 140630.72 | 2671.6 | 140630.72 | 2671.6 | 9.2722 | [5 empty] | 104.3636 |  |  | #VALUE!
05.02.2008 21:00 | 3600 | 2 | 763.61 | GGB | 765.201 | 772.359 | 768.864 | 268.14 | GGB | 10979.1 | GGB | 9.83 | GGB | 1015.79 | GGB | 60.79 | GGB | 170309.18 | GGB | 139675.68 | GGB | 0 | 0 | 2716 | 3600 | 2700.82 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 135621.64 | GGB | 135623.21 | 2700.82 | 2700.82 |  |  |  | 1 | 1 |  |  |  |  | 139675.68 | 2700.82 | 139675.68 | 2700.82 | 9.5238 | [5 empty] | 104.7886 |  |  | #VALUE!
05.02.2008 22:00 | 3600 | 2 | 763.85 | GGB | 767.766 | 773.508 | 771.429 | 268.05 | GGB | 10986 | GGB | 9.84 | GGB | 1015.69 | GGB | 60.83 | GGB | 170321.28 | GGB | 139653.1 | GGB | 0 | 0 | 2712 | 3600 | 2696.46 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 135662.11 | GGB | 135663.68 | 2696.46 | 2696.46 |  |  |  | 1 | 1 |  |  |  |  | 139653.1 | 2696.46 | 139653.1 | 2696.46 | 9.3049 | [5 empty] | 104.6025 |  |  | #VALUE!
05.02.2008 23:00 | 3600 | 2 | 763.67 | GGB | 764.102 | 770.836 | 767.766 | 268.3 | GGB | 10956.4 | GGB | 9.83 | GGB | 1015.54 | GGB | 60.8 | GGB | 170562.25 | GGB | 139844.04 | GGB | 0 | 0 | 2707 | 3600 | 2691.87 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 135702.52 | GGB | 135704.08 | 2691.87 | 2691.87 |  |  |  | 1 | 1 |  |  |  |  | 139844.04 | 2691.87 | 139844.04 | 2691.87 | 9.3179 | [5 empty] | 104.5672 |  |  | #VALUE!
05.02.2008 24:00 | 3600 | 2 | 764.23 | GGB | 767.766 | 774.281 | 771.429 | 269.75 | GGB | 10946.2 | GGB | 9.84 | GGB | 1015.98 | GGB | 60.28 | GGB | 172380.01 | GGB | 141615.9 | GGB | 0 | 0 | 2673 | 3600 | 2657.5 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 135742.21 | GGB | 135743.77 | 2657.5 | 2657.5 |  |  |  | 1 | 1 |  |  |  |  | 141615.9 | 2657.5 | 141615.9 | 2657.5 | 9.4821 | [5 empty] | 104.5401 |  |  | #VALUE!
06.02.2008 01:00 | 3600 | 2 | 764.59 | GGB | 767.766 | 773.531 | 771.429 | 269.26 | GGB | 10944.8 | GGB | 9.84 | GGB | 1015.83 | GGB | 60.57 | GGB | 171358.9 | GGB | 140635.88 | GGB | 0 | 0 | 2658 | 3600 | 2642.32 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 135781.96 | GGB | 135783.52 | 2642.32 | 2642.32 |  |  |  | 1 | 1 |  |  |  |  | 140635.88 | 2642.32 | 140635.88 | 2642.32 | 9.3486 | [5 empty] | 103.2236 |  |  | #VALUE!
06.02.2008 02:00 | 3600 | 2 | 764.42 | GGB | 766.3 | 772.523 | 769.963 | 267.53 | GGB | 10952.2 | GGB | 9.84 | GGB | 1015.69 | GGB | 61.31 | GGB | 169264.96 | GGB | 138590.85 | GGB | 0 | 0 | 2675 | 3600 | 2659.67 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 135822.43 | GGB | 135823.99 | 2659.67 | 2659.67 |  |  |  | 1 | 1 |  |  |  |  | 138590.85 | 2659.67 | 138590.85 | 2659.67 | 9.1081 | [5 empty] | 102.3905 |  |  | #VALUE!
06.02.2008 03:00 | 3600 | 2 | 764.22 | GGB | 766.667 | 772.477 | 769.963 | 267.67 | GGB | 10949.4 | GGB | 9.83 | GGB | 1015.28 | GGB | 61.41 | GGB | 169402.5 | GGB | 138603.5 | GGB | 0 | 0 | 2681 | 3600 | 2665.16 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 135862.7 | GGB | 135864.27 | 2665.16 | 2665.16 |  |  |  | 1 | 1 |  |  |  |  | 138603.5 | 2665.16 | 138603.5 | 2665.16 | 9.1708 | [5 empty] | 102.6113 |  |  | #VALUE!
06.02.2008 04:00 | 3600 | 2 | 764.23 | GGB | 767.766 | 773.508 | 771.429 | 268.13 | GGB | 10929.9 | GGB | 9.83 | GGB | 1014.93 | GGB | 61.1 | GGB | 170270.67 | GGB | 139399.2 | GGB | 0 | 0 | 2672 | 3600 | 2656.2 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 135902.91 | GGB | 135904.48 | 2656.2 | 2656.2 |  |  |  | 1 | 1 |  |  |  |  | 139399.2 | 2656.2 | 139399.2 | 2656.2 | 9.2085 | [5 empty] | 102.8534 |  |  | #VALUE!
06.02.2008 05:00 | 3600 | 2 | 763.99 | GGB | 765.201 | 771.914 | 768.864 | 267.99 | GGB | 10944.3 | GGB | 9.83 | GGB | 1014.51 | GGB | 61.22 | GGB | 169804.12 | GGB | 138905.06 | GGB | 0 | 0 | 2685 | 3600 | 2669.13 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 135943.2 | GGB | 135944.76 | 2669.13 | 2669.13 |  |  |  | 1 | 1 |  |  |  |  | 138905.06 | 2669.13 | 138905.06 | 2669.13 | 9.2045 | [5 empty] | 102.9877 |  |  | #VALUE!
06.02.2008 06:00 | 3600 | 2 | 763.95 | GGB | 766.667 | 773.016 | 770.33 | 269.62 | GGB | 10934.6 | GGB | 9.83 | GGB | 1014.18 | GGB | 60.4 | GGB | 172490.05 | GGB | 141404.85 | GGB | 0 | 0 | 2680 | 3600 | 2664.39 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 135983.36 | GGB | 135984.93 | 2664.39 | 2664.39 |  |  |  | 1 | 1 |  |  |  |  | 141404.85 | 2664.39 | 141404.85 | 2664.39 | 9.3791 | [5 empty] | 104.6549 |  |  | #VALUE!
06.02.2008 07:00 | 3600 | 2 | 764.24 | GGB | 767.766 | 774.094 | 771.429 | 268.91 | GGB | 10968.6 | GGB | 9.84 | GGB | 1013.43 | GGB | 60.35 | GGB | 172057.61 | GGB | 140968.51 | GGB | 0 | 0 | 2676 | 3600 | 2660.89 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 136023.21 | GGB | 136024.78 | 2660.89 | 2660.89 |  |  |  | 1 | 1 |  |  |  |  | 140968.51 | 2660.89 | 140968.51 | 2660.89 | 9.4128 | [5 empty] | 104.1949 |  |  | #VALUE!
06.02.2008 08:00 | 3600 | 2 | 762.91 | GGB | 765.201 | 770.883 | 767.766 | 267.73 | GGB | 10970.3 | GGB | 9.83 | GGB | 1012.9 | GGB | 60.65 | GGB | 170878.05 | GGB | 139804.77 | GGB | 0 | 0 | 2736 | 3600 | 2721.01 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 136063.51 | GGB | 136065.08 | 2721.01 | 2703.2554 |  |  |  | 1 | 1 |  |  |  |  | 139804.77 | 2703.2554 | 139804.77 | 2703.2554 | 9.3779 | [5 empty] | 105.6695 | 2703.2554 |  | 104.98
06.02.2008 09:00 | 3600 | 2 | 763.05 | GGB | 766.3 | 773.039 | 769.963 | 267.58 | GGB | 10976.9 | GGB | 9.84 | GGB | 1012.61 | GGB | 60.5 | GGB | 170939.67 | GGB | 139877.18 | GGB | 0 | 0 | 2733 | 3600 | 2717.75 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 136104.17 | GGB | 136105.73 | 2717.75 | 2701.856 |  |  |  | 1 | 1 |  |  |  |  | 139877.18 | 2701.856 | 139877.18 | 2701.856 | 9.2971 | [5 empty] | 105.5976 | 2701.856 |  | 104.98
06.02.2008 10:00 | 3600 | 2 | 764.1 | GGB | 766.667 | 773.016 | 770.33 | 266.39 | GGB | 10959.7 | GGB | 9.85 | GGB | 1011.97 | GGB | 60.63 | GGB | 169884.45 | GGB | 138871.39 | GGB | 0 | 0 | 2687 | 3600 | 2671.54 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 136143.86 | GGB | 136145.42 | 2671.54 | 2671.54 |  |  |  | 1 | 1 |  |  |  |  | 138871.39 | 2671.54 | 138871.39 | 2671.54 | 9.3475 | [5 empty] | 103.0557 |  |  | #VALUE!
06.02.2008 11:00 | 3600 | 2 | 763.8 | GGB | 767.766 | 773.039 | 769.963 | 266.72 | GGB | 10902.1 | GGB | 9.83 | GGB | 1011.89 | GGB | 60.4 | GGB | 170481.93 | GGB | 139442.32 | GGB | 0 | 0 | 2670 | 3600 | 2654.9 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 136184.28 | GGB | 136185.84 | 2654.9 | 2654.9 |  |  |  | 1 | 1 |  |  |  |  | 139442.32 | 2654.9 | 139442.32 | 2654.9 | 9.159 | [5 empty] | 102.8348 |  |  | #VALUE!
06.02.2008 12:00 | 3600 | 2 | 765.27 | GGB | 768.864 | 775.359 | 772.527 | 265.97 | GGB | 10904.6 | GGB | 9.85 | GGB | 1010.64 | GGB | 60.5 | GGB | 169683.08 | GGB | 138578.1 | GGB | 0 | 0 | 2608 | 3600 | 2593 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 136224.29 | GGB | 136225.85 | 2593 | 2593 |  |  |  | 1 | 1 |  |  |  |  | 138578.1 | 2593 | 138578.1 | 2593 | 8.9811 | [5 empty] | 99.8147 |  |  | #VALUE!
06.02.2008 13:00 | 3600 | 2 | 765.28 | GGB | 767.766 | 774.211 | 771.429 | 263.64 | GGB | 10878.3 | GGB | 9.84 | GGB | 1009.77 | GGB | 61.44 | GGB | 167005.96 | GGB | 135889.54 | GGB | 0 | 0 | 2603 | 3600 | 2588.1 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 136263.48 | GGB | 136265.04 | 2588.1 | 2588.1 |  |  |  | 1 | 1 |  |  |  |  | 135889.54 | 2588.1 | 135889.54 | 2588.1 | 8.9741 | [5 empty] | 97.6933 |  |  | #VALUE!
06.02.2008 14:00 | 3600 | 2 | 765.55 | GGB | 767.766 | 774.07 | 771.429 | 262.78 | GGB | 10830.1 | GGB | 9.84 | GGB | 1008.94 | GGB | 61.9 | GGB | 165938.64 | GGB | 134725 | GGB | 0 | 0 | 2571 | 3600 | 2555.99 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 136304.24 | GGB | 136305.8 | 2555.99 | 2555.99 |  |  |  | 1 | 1 |  |  |  |  | 134725 | 2555.99 | 134725 | 2555.99 | 8.4484 | [5 empty] | 95.6544 |  |  | #VALUE!
06.02.2008 15:00 | 3600 | 2 | 765.8 | GGB | 767.766 | 774.164 | 771.429 | 264.02 | GGB | 10785.5 | GGB | 9.83 | GGB | 1008.48 | GGB | 61.34 | GGB | 167531.92 | GGB | 136183.76 | GGB | 0 | 0 | 2536 | 3600 | 2521.24 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 136343.87 | GGB | 136345.43 | 2521.24 | 2521.24 |  |  |  | 1 | 1 |  |  |  |  | 136183.76 | 2521.24 | 136183.76 | 2521.24 | 8.6639 | [5 empty] | 95.3755 |  |  | #VALUE!
06.02.2008 16:00 | 3600 | 2 | 765.63 | GGB | 768.864 | 775.148 | 771.429 | 264.22 | GGB | 10813.9 | GGB | 9.84 | GGB | 1007.63 | GGB | 61.29 | GGB | 167485.71 | GGB | 136055.13 | GGB | 0 | 0 | 2557 | 3600 | 2541.93 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 136382.88 | GGB | 136384.43 | 2541.93 | 2541.93 |  |  |  | 1 | 1 |  |  |  |  | 136055.13 | 2541.93 | 136055.13 | 2541.93 | 8.8678 | [5 empty] | 96.0674 |  |  | #VALUE!
06.02.2008 17:00 | 3600 | 2 | 764.99 | GGB | 766.667 | 772.828 | 770.33 | 263.17 | GGB | 10833.2 | GGB | 9.83 | GGB | 1006.99 | GGB | 61.55 | GGB | 166134.5 | GGB | 134766.06 | GGB | 0 | 0 | 2588 | 3600 | 2572.87 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 136423.38 | GGB | 136424.93 | 2572.87 | 2572.87 |  |  |  | 1 | 1 |  |  |  |  | 134766.06 | 2572.87 | 134766.06 | 2572.87 | 8.5614 | [5 empty] | 96.3154 |  |  | #VALUE!
06.02.2008 18:00 | 3600 | 2 | 764.56 | GGB | 767.766 | 774.094 | 770.33 | 263.8 | GGB | 10845.7 | GGB | 9.83 | GGB | 1007.1 | GGB | 61.01 | GGB | 166723.18 | GGB | 135473.78 | GGB | 0 | 0 | 2620 | 3600 | 2604.6 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 136463.24 | GGB | 136464.79 | 2604.6 | 2604.6 |  |  |  | 1 | 1 |  |  |  |  | 135473.78 | 2604.6 | 135473.78 | 2604.6 | 8.8524 | [5 empty] | 98.0153 |  |  | #VALUE!
06.02.2008 19:00 | 3600 | 2 | 764.41 | GGB | 767.766 | 774 | 770.33 | 265.6 | GGB | 10835 | GGB | 9.82 | GGB | 1007.43 | GGB | 60.81 | GGB | 168704.88 | GGB | 137213.35 | GGB | 0 | 0 | 2617 | 3600 | 2601.75 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 136502.84 | GGB | 136504.39 | 2601.75 | 2601.75 |  |  |  | 1 | 1 |  |  |  |  | 137213.35 | 2601.75 | 137213.35 | 2601.75 | 9.015 | [5 empty] | 99.1652 |  |  | #VALUE!
06.02.2008 20:00 | 3600 | 2 | 764.81 | GGB | 767.766 | 774.023 | 770.33 | 265.77 | GGB | 10878.2 | GGB | 9.84 | GGB | 1007.87 | GGB | 60.61 | GGB | 168809.42 | GGB | 137440.04 | GGB | 0 | 0 | 2612 | 3600 | 2597.03 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 136542.26 | GGB | 136543.81 | 2597.03 | 2597.03 |  |  |  | 1 | 1 |  |  |  |  | 137440.04 | 2597.03 | 137440.04 | 2597.03 | 9.0547 | [5 empty] | 99.1489 |  |  | #VALUE!
06.02.2008 21:00 | 3600 | 2 | 763.63 | GGB | 765.201 | 771.797 | 768.864 | 265.45 | GGB | 10889 | GGB | 9.83 | GGB | 1007.61 | GGB | 60.87 | GGB | 168471.61 | GGB | 137024.33 | GGB | 0 | 0 | 2673 | 3600 | 2658.08 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 136582.04 | GGB | 136583.6 | 2658.08 | 2658.08 |  |  |  | 1 | 1 |  |  |  |  | 137024.33 | 2658.08 | 137024.33 | 2658.08 | 9.1536 | [5 empty] | 101.1727 |  |  | #VALUE!
06.02.2008 22:00 | 3600 | 2 | 763.71 | GGB | 766.3 | 771.891 | 768.864 | 265.71 | GGB | 10910.4 | GGB | 9.83 | GGB | 1007.23 | GGB | 60.64 | GGB | 169093.3 | GGB | 137570.82 | GGB | 0 | 0 | 2680 | 3600 | 2664.78 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 136622.45 | GGB | 136624 | 2664.78 | 2664.78 |  |  |  | 1 | 1 |  |  |  |  | 137570.82 | 2664.78 | 137570.82 | 2664.78 | 9.0742 | [5 empty] | 101.8322 |  |  | #VALUE!
06.02.2008 23:00 | 3600 | 2 | 763.82 | GGB | 766.667 | 772.781 | 768.864 | 266.21 | GGB | 10898.1 | GGB | 9.83 | GGB | 1007.54 | GGB | 60.76 | GGB | 169433.31 | GGB | 137841.18 | GGB | 0 | 0 | 2671 | 3600 | 2655.67 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 136662.12 | GGB | 136663.68 | 2655.67 | 2655.67 |  |  |  | 1 | 1 |  |  |  |  | 137841.18 | 2655.67 | 137841.18 | 2655.67 | 9.2253 | [5 empty] | 101.6835 |  |  | #VALUE!
06.02.2008 24:00 | 3600 | 2 | 764.71 | GGB | 767.766 | 773.836 | 771.429 | 266.71 | GGB | 10869.4 | GGB | 9.84 | GGB | 1007.62 | GGB | 60.56 | GGB | 169845.93 | GGB | 138271.89 | GGB | 0 | 0 | 2616 | 3600 | 2600.99 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 136701.7 | GGB | 136703.25 | 2600.99 | 2600.99 |  |  |  | 1 | 1 |  |  |  |  | 138271.89 | 2600.99 | 138271.89 | 2600.99 | 9.0888 | [5 empty] | 99.9011 |  |  | #VALUE!
07.02.2008 01:00 | 3600 | 2 | 764.82 | GGB | 767.766 | 773.813 | 771.429 | 264.64 | GGB | 10871.3 | GGB | 9.84 | GGB | 1007.58 | GGB | 61.44 | GGB | 166901.43 | GGB | 135511.17 | GGB | 0 | 0 | 2620 | 3600 | 2604.39 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 136740.46 | GGB | 136742.01 | 2604.39 | 2604.39 |  |  |  | 1 | 1 |  |  |  |  | 135511.17 | 2604.39 | 135511.17 | 2604.39 | 9.1054 | [5 empty] | 98.0344 |  |  | #VALUE!
07.02.2008 02:00 | 3600 | 2 | 764.56 | GGB | 767.766 | 773.813 | 771.429 | 263.99 | GGB | 10835.5 | GGB | 9.83 | GGB | 1007.69 | GGB | 61.69 | GGB | 166144.4 | GGB | 134811.21 | GGB | 0 | 0 | 2626 | 3600 | 2610.93 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 136780.54 | GGB | 136782.09 | 2610.93 | 2610.93 |  |  |  | 1 | 1 |  |  |  |  | 134811.21 | 2610.93 | 134811.21 | 2610.93 | 8.782 | [5 empty] | 97.773 |  |  | #VALUE!
07.02.2008 03:00 | 3600 | 2 | 765.18 | GGB | 767.766 | 773.789 | 770.33 | 263.45 | GGB | 10838.3 | GGB | 9.84 | GGB | 1008.48 | GGB | 61.75 | GGB | 166025.56 | GGB | 134797.02 | GGB | 0 | 0 | 2590 | 3600 | 2574.28 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 136820.97 | GGB | 136822.52 | 2574.28 | 2574.28 |  |  |  | 1 | 1 |  |  |  |  | 134797.02 | 2574.28 | 134797.02 | 2574.28 | 8.5829 | [5 empty] | 96.3904 |  |  | #VALUE!
07.02.2008 04:00 | 3600 | 2 | 765.24 | GGB | 768.864 | 774.797 | 771.429 | 263.42 | GGB | 10851.9 | GGB | 9.84 | GGB | 1009.12 | GGB | 61.68 | GGB | 166182.91 | GGB | 135037.03 | GGB | 0 | 0 | 2593 | 3600 | 2577.4 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 136861.06 | GGB | 136862.6 | 2577.4 | 2577.4 |  |  |  | 1 | 1 |  |  |  |  | 135037.03 | 2577.4 | 135037.03 | 2577.4 | 8.6837 | [5 empty] | 96.679 |  |  | #VALUE!
07.02.2008 05:00 | 3600 | 2 | 764.92 | GGB | 767.766 | 772.922 | 770.33 | 262.85 | GGB | 10841.1 | GGB | 9.83 | GGB | 1009.52 | GGB | 61.74 | GGB | 165885.82 | GGB | 134823.88 | GGB | 0 | 0 | 2606 | 3600 | 2590.48 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 136900.82 | GGB | 136902.36 | 2590.48 | 2590.48 |  |  |  | 1 | 1 |  |  |  |  | 134823.88 | 2590.48 | 134823.88 | 2590.48 | 8.7842 | [5 empty] | 97.0163 |  |  | #VALUE!
07.02.2008 06:00 | 3600 | 2 | 765.19 | GGB | 768.864 | 774.07 | 771.429 | 263.28 | GGB | 10860 | GGB | 9.83 | GGB | 1010.48 | GGB | 61.62 | GGB | 166185.11 | GGB | 135244.5 | GGB | 0 | 0 | 2608 | 3600 | 2592.33 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 136941.02 | GGB | 136942.56 | 2592.33 | 2592.33 |  |  |  | 1 | 1 |  |  |  |  | 135244.5 | 2592.33 | 135244.5 | 2592.33 | 8.7214 | [5 empty] | 97.3884 |  |  | #VALUE!
07.02.2008 07:00 | 3600 | 2 | 765.04 | GGB | 766.667 | 773.156 | 770.696 | 263.64 | GGB | 10866.6 | GGB | 9.83 | GGB | 1011.31 | GGB | 61.38 | GGB | 166601.04 | GGB | 135790.65 | GGB | 0 | 0 | 2613 | 3600 | 2597.39 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 136980.93 | GGB | 136982.47 | 2597.39 | 2597.39 |  |  |  | 1 | 1 |  |  |  |  | 135790.65 | 2597.39 | 135790.65 | 2597.39 | 8.8374 | [5 empty] | 97.9726 |  |  | #VALUE!
07.02.2008 08:00 | 3600 | 2 | 764.87 | GGB | 768.864 | 774.234 | 771.795 | 264.31 | GGB | 10896 | GGB | 9.83 | GGB | 1012.33 | GGB | 61.22 | GGB | 167288.75 | GGB | 136554.44 | GGB | 0 | 0 | 2630 | 3600 | 2614.2 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 137020.76 | GGB | 137022.3 | 2614.2 | 2614.2 |  |  |  | 1 | 1 |  |  |  |  | 136554.44 | 2614.2 | 136554.44 | 2614.2 | 8.9626 | [5 empty] | 99.1613 |  |  | #VALUE!
07.02.2008 09:00 | 3600 | 2 | 764.82 | GGB | 766.667 | 772.031 | 769.597 | 264.56 | GGB | 10904.5 | GGB | 9.83 | GGB | 1013.5 | GGB | 61.15 | GGB | 167703.58 | GGB | 137081.93 | GGB | 0 | 0 | 2629 | 3336 | 2613.22 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 137060.99 | GGB | 137062.53 | 2613.22 | 2613.22 |  |  |  | 1 | 1 |  |  |  |  | 137081.93 | 2613.22 | 137081.93 | 2613.22 | 8.9044 | [5 empty] | 99.507 |  |  | #VALUE!
07.02.2008 10:00 | 3600 | 2 | 764.41 | GGB | 766.3 | 772.125 | 769.597 | 264.85 | GGB | 10912.8 | GGB | 9.83 | GGB | 1014.34 | GGB | 60.88 | GGB | 168056.79 | GGB | 137593.17 | GGB | 0 | 0 | 2656 | 3600 | 2640.42 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 137101.13 | GGB | 137102.68 | 2640.42 | 2640.42 |  |  |  | 1 | 1 |  |  |  |  | 137593.17 | 2640.42 | 137593.17 | 2640.42 | 9.0487 | [5 empty] | 100.9177 |  |  | #VALUE!
07.02.2008 11:00 | 3600 | 2 | 764.82 | GGB | 766.667 | 773.18 | 770.696 | 264.84 | GGB | 10928.8 | GGB | 9.83 | GGB | 1015.39 | GGB | 60.78 | GGB | 168215.23 | GGB | 137909.23 | GGB | 0 | 0 | 2639 | 3600 | 2624 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 137141.03 | GGB | 137142.58 | 2624 | 2624 |  |  |  | 1 | 1 |  |  |  |  | 137909.23 | 2624 | 137909.23 | 2624 | 9.0695 | [5 empty] | 100.5205 |  |  | #VALUE!
07.02.2008 12:00 | 3600 | 2 | 765.24 | GGB | 766.667 | 772.945 | 770.696 | 264.79 | GGB | 10937.1 | GGB | 9.84 | GGB | 1016.38 | GGB | 60.88 | GGB | 168056.79 | GGB | 137872.22 | GGB | 0 | 0 | 2622 | 3600 | 2606.94 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 137181.25 | GGB | 137182.8 | 2606.94 | 2606.94 |  |  |  | 1 | 1 |  |  |  |  | 137872.22 | 2606.94 | 137872.22 | 2606.94 | 8.9365 | [5 empty] | 99.8402 |  |  | #VALUE!
07.02.2008 13:00 | 3600 | 2 | 765.13 | GGB | 766.667 | 772.477 | 770.696 | 264.64 | GGB | 10926.1 | GGB | 9.83 | GGB | 1017.04 | GGB | 60.88 | GGB | 168023.78 | GGB | 137935.16 | GGB | 0 | 0 | 2625 | 3600 | 2609.97 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 137221.3 | GGB | 137222.85 | 2609.97 | 2609.97 |  |  |  | 1 | 1 |  |  |  |  | 137935.16 | 2609.97 | 137935.16 | 2609.97 | 8.9889 | [5 empty] | 100.0018 |  |  | #VALUE!
07.02.2008 14:00 | 3600 | 2 | 765.35 | GGB | 766.667 | 772.5 | 770.696 | 264.71 | GGB | 10933.6 | GGB | 9.83 | GGB | 1017.66 | GGB | 60.91 | GGB | 168227.34 | GGB | 138171.53 | GGB | 0 | 0 | 2613 | 3600 | 2597.97 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 137261.24 | GGB | 137262.79 | 2597.97 | 2597.97 |  |  |  | 1 | 1 |  |  |  |  | 138171.53 | 2597.97 | 138171.53 | 2597.97 | 8.9876 | [5 empty] | 99.7126 |  |  | #VALUE!
07.02.2008 15:00 | 3600 | 2 | 765.91 | GGB | 768.864 | 774.609 | 771.795 | 264.7 | GGB | 10938.2 | GGB | 9.84 | GGB | 1018.6 | GGB | 61.24 | GGB | 168119.5 | GGB | 138076.05 | GGB | 0 | 0 | 2599 | 3600 | 2583.83 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 137301.44 | GGB | 137302.99 | 2583.83 | 2583.83 |  |  |  | 1 | 1 |  |  |  |  | 138076.05 | 2583.83 | 138076.05 | 2583.83 | 8.8748 | [5 empty] | 99.1014 |  |  | #VALUE!
07.02.2008 16:00 | 3600 | 2 | 766.15 | GGB | 768.864 | 775.5 | 772.161 | 264.7 | GGB | 10933.9 | GGB | 9.84 | GGB | 1019.15 | GGB | 61.26 | GGB | 168051.28 | GGB | 138087.59 | GGB | 0 | 0 | 2584 | 3600 | 2568.29 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 137341.51 | GGB | 137343.05 | 2568.29 | 2568.29 |  |  |  | 1 | 1 |  |  |  |  | 138087.59 | 2568.29 | 138087.59 | 2568.29 | 8.8529 | [5 empty] | 98.5136 |  |  | #VALUE!
07.02.2008 17:00 | 3600 | 2 | 765.89 | GGB | 767.766 | 773.93 | 771.795 | 265.03 | GGB | 10937.4 | GGB | 9.83 | GGB | 1019.66 | GGB | 61.17 | GGB | 168458.41 | GGB | 138527.89 | GGB | 0 | 0 | 2596 | 3600 | 2580.29 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 137381.73 | GGB | 137383.28 | 2580.29 | 2580.29 |  |  |  | 1 | 1 |  |  |  |  | 138527.89 | 2580.29 | 138527.89 | 2580.29 | 8.885 | [5 empty] | 99.2895 |  |  | #VALUE!
07.02.2008 18:00 | 3600 | 2 | 765.12 | GGB | 767.766 | 774.047 | 770.696 | 266.18 | GGB | 10952.9 | GGB | 9.82 | GGB | 1020.73 | GGB | 61.14 | GGB | 169158.22 | GGB | 139260.8 | GGB | 0 | 0 | 2637 | 3600 | 2621.32 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 137422.03 | GGB | 137423.57 | 2621.32 | 2621.32 |  |  |  | 1 | 1 |  |  |  |  | 139260.8 | 2621.32 | 139260.8 | 2621.32 | 9.0605 | [5 empty] | 101.402 |  |  | #VALUE!
07.02.2008 19:00 | 3600 | 2 | 765.02 | GGB | 766.667 | 772.828 | 769.597 | 266.78 | GGB | 10981.7 | GGB | 9.83 | GGB | 1021.73 | GGB | 61 | GGB | 169597.26 | GGB | 139818.84 | GGB | 0 | 0 | 2647 | 3600 | 2631.63 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 137462.06 | GGB | 137463.6 | 2631.63 | 2631.63 |  |  |  | 1 | 1 |  |  |  |  | 139818.84 | 2631.63 | 139818.84 | 2631.63 | 9.1919 | [5 empty] | 102.2087 |  |  | #VALUE!
07.02.2008 20:00 | 3600 | 2 | 764.73 | GGB | 766.667 | 772.805 | 769.597 | 267.33 | GGB | 10999.9 | GGB | 9.83 | GGB | 1022.84 | GGB | 60.94 | GGB | 170144.13 | GGB | 140446.99 | GGB | 0 | 0 | 2666 | 3600 | 2650.59 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 137502.53 | GGB | 137504.08 | 2650.59 | 2650.59 |  |  |  | 1 | 1 |  |  |  |  | 140446.99 | 2650.59 | 140446.99 | 2650.59 | 9.1963 | [5 empty] | 103.4076 |  |  | #VALUE!
07.02.2008 21:00 | 3600 | 2 | 764.84 | GGB | 766.667 | 773.555 | 770.696 | 267.5 | GGB | 11005.9 | GGB | 9.83 | GGB | 1023.6 | GGB | 61.02 | GGB | 170271.77 | GGB | 140622.33 | GGB | 0 | 0 | 2665 | 3600 | 2649.36 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 137543.06 | GGB | 137544.61 | 2649.36 | 2649.36 |  |  |  | 1 | 1 |  |  |  |  | 140622.33 | 2649.36 | 140622.33 | 2649.36 | 9.1922 | [5 empty] | 103.4887 |  |  | #VALUE!
07.02.2008 22:00 | 3600 | 2 | 764.95 | GGB | 767.766 | 774.75 | 771.795 | 267.29 | GGB | 11020.1 | GGB | 9.84 | GGB | 1024.17 | GGB | 60.9 | GGB | 170480.83 | GGB | 140922.85 | GGB | 0 | 0 | 2669 | 3600 | 2653.43 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 137583.29 | GGB | 137584.84 | 2653.43 | 2653.43 |  |  |  | 1 | 1 |  |  |  |  | 140922.85 | 2653.43 | 140922.85 | 2653.43 | 9.2948 | [5 empty] | 103.8691 |  |  | #VALUE!
07.02.2008 23:00 | 3600 | 2 | 764.24 | GGB | 766.667 | 772.547 | 769.597 | 267.87 | GGB | 11012.6 | GGB | 9.82 | GGB | 1025.11 | GGB | 60.77 | GGB | 170727.31 | GGB | 141312.97 | GGB | 0 | 0 | 2696 | 3600 | 2680.36 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 137623.99 | GGB | 137625.54 | 2680.36 | 2674.4042 |  |  |  | 1 | 1 |  |  |  |  | 141312.97 | 2674.4042 | 141312.97 | 2674.4042 | 9.2857 | [5 empty] | 105.2138 | 2674.4042 |  | 104.98
07.02.2008 24:00 | 3600 | 2 | 764.61 | GGB | 766.667 | 773.391 | 770.696 | 268.4 | GGB | 11032.4 | GGB | 9.83 | GGB | 1025.92 | GGB | 60.92 | GGB | 170980.38 | GGB | 141570.49 | GGB | 0 | 0 | 2689 | 3600 | 2673.31 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 137664.64 | GGB | 137666.2 | 2673.31 | 2669.5394 |  |  |  | 1 | 1 |  |  |  |  | 141570.49 | 2669.5394 | 141570.49 | 2669.5394 | 9.2948 | [5 empty] | 105.1283 | 2669.5394 |  | 104.98
08.02.2008 01:00 | 3600 | 2 | 764.42 | GGB | 766.667 | 773.063 | 769.597 | 268.77 | GGB | 11036.3 | GGB | 9.83 | GGB | 1026.7 | GGB | 60.87 | GGB | 171333.59 | GGB | 141991.86 | GGB | 0 | 0 | 2702 | 3600 | 2686.5 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 137704.93 | GGB | 137706.48 | 2686.5 | 2661.6174 |  |  |  | 1 | 1 |  |  |  |  | 141991.86 | 2661.6174 | 141991.86 | 2661.6174 | 9.3825 | [5 empty] | 105.9614 | 2661.6174 |  | 104.98
08.02.2008 02:00 | 3600 | 2 | 764.62 | GGB | 766.3 | 772.969 | 769.597 | 268.89 | GGB | 11050.4 | GGB | 9.84 | GGB | 1027.49 | GGB | 60.81 | GGB | 171330.29 | GGB | 142120.96 | GGB | 0 | 0 | 2701 | 3600 | 2685.99 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 137745.52 | GGB | 137747.07 | 2685.99 | 2659.1996 |  |  |  | 1 | 1 |  |  |  |  | 142120.96 | 2659.1996 | 142120.96 | 2659.1996 | 9.3109 | [5 empty] | 106.0376 | 2659.1996 |  | 104.98
08.02.2008 03:00 | 3600 | 2 | 764.6 | GGB | 766.667 | 772.195 | 769.597 | 268.87 | GGB | 11048.3 | GGB | 9.83 | GGB | 1027.83 | GGB | 60.77 | GGB | 171421.62 | GGB | 142261.78 | GGB | 0 | 0 | 2701 | 3600 | 2685.82 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 137786.33 | GGB | 137787.88 | 2685.82 | 2656.5674 |  |  |  | 1 | 1 |  |  |  |  | 142261.78 | 2656.5674 | 142261.78 | 2656.5674 | 9.2607 | [5 empty] | 106.136 | 2656.5674 |  | 104.98
08.02.2008 04:00 | 3600 | 2 | 764.36 | GGB | 766.667 | 772.969 | 769.597 | 269.31 | GGB | 11062.5 | GGB | 9.83 | GGB | 1028.58 | GGB | 60.69 | GGB | 171934.38 | GGB | 142829.76 | GGB | 0 | 0 | 2719 | 3600 | 2703.94 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 137826.58 | GGB | 137828.13 | 2703.94 | 2646.0032 |  |  |  | 1 | 1 |  |  |  |  | 142829.76 | 2646.0032 | 142829.76 | 2646.0032 | 9.3895 | [5 empty] | 107.2786 | 2646.0032 |  | 104.98
08.02.2008 05:00 | 3600 | 2 | 763.9 | GGB | 766.3 | 771.773 | 769.597 | 269.79 | GGB | 11069.8 | GGB | 9.83 | GGB | 1028.94 | GGB | 60.57 | GGB | 172362.41 | GGB | 143282.81 | GGB | 0 | 0 | 2746 | 3600 | 2730.42 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 137867.56 | GGB | 137869.1 | 2730.42 | 2637.6367 |  |  |  | 1 | 1 |  |  |  |  | 143282.81 | 2637.6367 | 143282.81 | 2637.6367 | 9.2245 | [5 empty] | 108.6728 | 2637.6367 |  | 104.98
08.02.2008 06:00 | 3600 | 2 | 764.26 | GGB | 765.201 | 771.75 | 768.498 | 270 | GGB | 11096 | GGB | 9.84 | GGB | 1029.66 | GGB | 60.49 | GGB | 172723.32 | GGB | 143720.97 | GGB | 0 | 0 | 2743 | 3600 | 2727.76 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 137908.32 | GGB | 137909.86 | 2727.76 | 2629.5954 |  |  |  | 1 | 1 |  |  |  |  | 143720.97 | 2629.5954 | 143720.97 | 2629.5954 | 9.272 | [5 empty] | 108.899 | 2629.5954 |  | 104.98
08.02.2008 07:00 | 3600 | 2 | 762.96 | GGB | 765.201 | 771.82 | 769.597 | 271.24 | GGB | 11103.1 | GGB | 9.82 | GGB | 1030.55 | GGB | 60.22 | GGB | 173700.42 | GGB | 144773.27 | GGB | 0 | 0 | 2813 | 3600 | 2797.73 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 137948.8 | GGB | 137950.34 | 2797.73 | 2610.4819 |  |  |  | 1 | 1 |  |  |  |  | 144773.27 | 2610.4819 | 144773.27 | 2610.4819 | 9.3362 | [5 empty] | 112.5101 | 2610.4819 |  | 104.98
08.02.2008 08:00 | 3600 | 2 | 762.88 | GGB | 765.201 | 771.75 | 768.132 | 272.18 | GGB | 11136.5 | GGB | 9.83 | GGB | 1031.4 | GGB | 59.96 | GGB | 174641.21 | GGB | 145792.71 | GGB | 0 | 0 | 2837 | 3209 | 2821.51 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 137989.97 | GGB | 137991.52 | 2821.51 | 2592.2284 |  |  |  | 1 | 1 |  |  |  |  | 145792.71 | 2592.2284 | 145792.71 | 2592.2284 | 9.1775 | [5 empty] | 114.2654 | 2592.2284 |  | 104.98
08.02.2008 09:00 | 3600 | 2 | 762.6 | GGB | 766.667 | 772.688 | 769.597 | 274.14 | GGB | 11123.7 | GGB | 9.82 | GGB | 1032.48 | GGB | 59.03 | GGB | 177607.72 | GGB | 148841.23 | GGB | 0 | 0 | 2842 | 3600 | 2826.92 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 138030.8 | GGB | 138032.35 | 2826.92 | 2539.1352 |  |  |  | 1 | 1 |  |  |  |  | 148841.23 | 2539.1352 | 148841.23 | 2539.1352 | 9.2561 | [5 empty] | 116.8784 | 2539.1352 |  | 104.98
08.02.2008 10:00 | 3600 | 2 | 763.69 | GGB | 766.667 | 772.664 | 769.597 | 273.39 | GGB | 11150.7 | GGB | 9.84 | GGB | 1032.86 | GGB | 59.2 | GGB | 176857.29 | GGB | 148192.68 | GGB | 0 | 0 | 2798 | 3600 | 2782.52 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 138071.19 | GGB | 138072.74 | 2782.52 | 2550.2474 |  |  |  | 1 | 1 |  |  |  |  | 148192.68 | 2550.2474 | 148192.68 | 2550.2474 | 9.357 | [5 empty] | 114.5414 | 2550.2474 |  | 104.98
08.02.2008 11:00 | 3600 | 2 | 763.48 | GGB | 766.667 | 773.016 | 769.597 | 271.64 | GGB | 11160.4 | GGB | 9.84 | GGB | 1032.93 | GGB | 59.9 | GGB | 174267.09 | GGB | 145720.94 | GGB | 0 | 0 | 2812 | 3600 | 2796.88 | GGB | 100 | GGB | 41.45 | GGB | 41.45 | GGB | 138112.64 | GGB | 138114.19 | 2796.88 | 2593.5051 |  |  |  | 1 | 1 |  |  |  |  | 145720.94 | 2593.5051 | 145720.94 | 2593.5051 | 9.1177 | [5 empty] | 113.2122 | 2593.5051 |  | 104.98
08.02.2008 12:00 | 3600 | 2 | 764.95 | GGB | 767.766 | 774.234 | 770.696 | 269.64 | GGB | 11130.6 | GGB | 9.86 | GGB | 1032.93 | GGB | 60.35 | GGB | 172469.14 | GGB | 144024.85 | GGB | 0 | 0 | 2730 | 3600 | 2714.55 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 138153.27 | GGB | 138154.81 | 2714.55 | 2624.0472 |  |  |  | 1 | 1 |  |  |  |  | 144024.85 | 2624.0472 | 144024.85 | 2624.0472 | 9.304 | [5 empty] | 108.6007 | 2624.0472 |  | 104.98
08.02.2008 13:00 | 3600 | 2 | 765.15 | GGB | 768.864 | 775.195 | 772.527 | 268.37 | GGB | 11079.6 | GGB | 9.84 | GGB | 1033.06 | GGB | 60.61 | GGB | 171159.74 | GGB | 142837.26 | GGB | 0 | 0 | 2701 | 3600 | 2685.74 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 138193.87 | GGB | 138195.41 | 2685.74 | 2645.8643 |  |  |  | 1 | 1 |  |  |  |  | 142837.26 | 2645.8643 | 142837.26 | 2645.8643 | 9.3086 | [5 empty] | 106.5622 | 2645.8643 |  | 104.98
08.02.2008 14:00 | 3600 | 2 | 764.83 | GGB | 767.766 | 774.117 | 770.33 | 268.58 | GGB | 11065.5 | GGB | 9.83 | GGB | 1032.82 | GGB | 60.71 | GGB | 171135.53 | GGB | 142741.12 | GGB | 0 | 0 | 2713 | 3600 | 2698.02 | GGB | 100 | GGB | 41.46 | GGB | 41.46 | GGB | 138235.32 | GGB | 138236.87 | 2698.02 | 2647.6463 |  |  |  | 1 | 1 |  |  |  |  | 142741.12 | 2647.6463 | 142741.12 | 2647.6463 | 9.1155 | [5 empty] | 106.9773 | 2647.6463 |  | 104.98
08.02.2008 15:00 | 3600 | 2 | 765.06 | GGB | 767.766 | 773.977 | 771.429 | 269.09 | GGB | 11081 | GGB | 9.84 | GGB | 1032.7 | GGB | 60.67 | GGB | 171428.22 | GGB | 142985.32 | GGB | 0 | 0 | 2712 | 3600 | 2696.59 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 138275.62 | GGB | 138277.17 | 2696.59 | 2643.1245 |  |  |  | 1 | 1 |  |  |  |  | 142985.32 | 2643.1245 | 142985.32 | 2643.1245 | 9.3779 | [5 empty] | 107.1036 | 2643.1245 |  | 104.98
08.02.2008 16:00 | 3600 | 2 | 764.49 | GGB | 767.766 | 773.906 | 770.33 | 269.62 | GGB | 11077.7 | GGB | 9.82 | GGB | 1033.43 | GGB | 60.73 | GGB | 171689 | GGB | 143278.34 | GGB | 0 | 0 | 2740 | 3600 | 2724.82 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 138316.43 | GGB | 138317.99 | 2724.82 | 2637.719 |  |  |  | 1 | 1 |  |  |  |  | 143278.34 | 2637.719 | 143278.34 | 2637.719 | 9.2584 | [5 empty] | 108.4466 | 2637.719 |  | 104.98
08.02.2008 17:00 | 3600 | 2 | 764.76 | GGB | 767.766 | 774.117 | 771.429 | 269.83 | GGB | 11102.4 | GGB | 9.84 | GGB | 1033.57 | GGB | 60.71 | GGB | 171881.56 | GGB | 143466.16 | GGB | 0 | 0 | 2731 | 3600 | 2715.97 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 138357.71 | GGB | 138359.27 | 2715.97 | 2634.2658 |  |  |  | 1 | 1 |  |  |  |  | 143466.16 | 2634.2658 | 143466.16 | 2634.2658 | 9.1552 | [5 empty] | 108.2361 | 2634.2658 |  | 104.98
08.02.2008 18:00 | 3600 | 2 | 764.4 | GGB | 766.667 | 772.969 | 768.864 | 270.08 | GGB | 11099 | GGB | 9.83 | GGB | 1033.87 | GGB | 60.65 | GGB | 172047.71 | GGB | 143675.19 | GGB | 0 | 0 | 2748 | 3600 | 2732.36 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 138397.82 | GGB | 138399.38 | 2732.36 | 2630.4333 |  |  |  | 1 | 1 |  |  |  |  | 143675.19 | 2630.4333 | 143675.19 | 2630.4333 | 9.4223 | [5 empty] | 109.0479 | 2630.4333 |  | 104.98
08.02.2008 19:00 | 3600 | 2 | 764.18 | GGB | 766.667 | 773.039 | 770.33 | 270.56 | GGB | 11116.9 | GGB | 9.83 | GGB | 1034.08 | GGB | 60.56 | GGB | 172731.02 | GGB | 144311.84 | GGB | 0 | 0 | 2767 | 3600 | 2751.4 | GGB | 100 | GGB | 41.34 | GGB | 41.34 | GGB | 138439.17 | GGB | 138440.72 | 2751.4 | 2618.8288 |  |  |  | 1 | 1 |  |  |  |  | 144311.84 | 2618.8288 | 144311.84 | 2618.8288 | 9.1419 | [5 empty] | 110.2943 | 2618.8288 |  | 104.98
08.02.2008 20:00 | 3600 | 2 | 764.17 | GGB | 766.667 | 773.32 | 770.33 | 270.57 | GGB | 11117.1 | GGB | 9.83 | GGB | 1034.46 | GGB | 60.54 | GGB | 172685.91 | GGB | 144335.69 | GGB | 0 | 0 | 2771 | 3600 | 2755.11 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 138480.2 | GGB | 138481.75 | 2755.11 | 2618.396 |  |  |  | 1 | 1 |  |  |  |  | 144335.69 | 2618.396 | 144335.69 | 2618.396 | 9.211 | [5 empty] | 110.4613 | 2618.396 |  | 104.98
08.02.2008 21:00 | 3600 | 2 | 764.33 | GGB | 768.864 | 774.375 | 772.527 | 270.32 | GGB | 11134.1 | GGB | 9.84 | GGB | 1034.58 | GGB | 60.47 | GGB | 173087.53 | GGB | 144720.39 | GGB | 0 | 0 | 2771 | 3600 | 2756.02 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 138520.49 | GGB | 138522.05 | 2756.02 | 2611.4357 |  |  |  | 1 | 1 |  |  |  |  | 144720.39 | 2611.4357 | 144720.39 | 2611.4357 | 9.3779 | [5 empty] | 110.7923 | 2611.4357 |  | 104.98
08.02.2008 22:00 | 3600 | 2 | 763.77 | GGB | 766.667 | 773.391 | 770.33 | 270.88 | GGB | 11114.8 | GGB | 9.83 | GGB | 1034.66 | GGB | 60.44 | GGB | 172908.17 | GGB | 144592.78 | GGB | 0 | 0 | 2792 | 3600 | 2776.59 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 138561.73 | GGB | 138563.29 | 2776.59 | 2613.7405 |  |  |  | 1 | 1 |  |  |  |  | 144592.78 | 2613.7405 | 144592.78 | 2613.7405 | 9.1641 | [5 empty] | 111.5208 | 2613.7405 |  | 104.98
08.02.2008 23:00 | 3600 | 2 | 763.88 | GGB | 766.667 | 773.273 | 769.963 | 271.11 | GGB | 11129.3 | GGB | 9.83 | GGB | 1034.74 | GGB | 60.5 | GGB | 173390.12 | GGB | 144981.4 | GGB | 0 | 0 | 2800 | 3600 | 2784.24 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 138602.93 | GGB | 138604.49 | 2784.24 | 2606.7344 |  |  |  | 1 | 1 |  |  |  |  | 144981.4 | 2606.7344 | 144981.4 | 2606.7344 | 9.173 | [5 empty] | 112.1286 | 2606.7344 |  | 104.98
08.02.2008 24:00 | 3600 | 2 | 763.79 | GGB | 766.667 | 773.32 | 770.33 | 271.24 | GGB | 11137 | GGB | 9.83 | GGB | 1034.99 | GGB | 60.48 | GGB | 173433.04 | GGB | 145063.28 | GGB | 0 | 0 | 2802 | 3600 | 2786.13 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 138642.79 | GGB | 138644.35 | 2786.13 | 2605.263 |  |  |  | 1 | 1 |  |  |  |  | 145063.28 | 2605.263 | 145063.28 | 2605.263 | 9.4814 | [5 empty] | 112.2681 | 2605.263 |  | 104.98
09.02.2008 01:00 | 3600 | 2 | 764.02 | GGB | 767.766 | 773.32 | 770.33 | 271.17 | GGB | 11139.4 | GGB | 9.83 | GGB | 1035.35 | GGB | 60.5 | GGB | 173461.64 | GGB | 145127.57 | GGB | 0 | 0 | 2799 | 3600 | 2783.03 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 138684.07 | GGB | 138685.64 | 2783.03 | 2604.1089 |  |  |  | 1 | 1 |  |  |  |  | 145127.57 | 2604.1089 | 145127.57 | 2604.1089 | 9.153 | [5 empty] | 112.1929 | 2604.1089 |  | 104.98
09.02.2008 02:00 | 3600 | 2 | 763.95 | GGB | 766.667 | 774.234 | 770.33 | 271.16 | GGB | 11136.3 | GGB | 9.83 | GGB | 1035.59 | GGB | 60.45 | GGB | 173332.9 | GGB | 145075.25 | GGB | 0 | 0 | 2799 | 3600 | 2783.93 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 138725.4 | GGB | 138726.96 | 2783.93 | 2605.0481 |  |  |  | 1 | 1 |  |  |  |  | 145075.25 | 2605.0481 | 145075.25 | 2605.0481 | 9.1464 | [5 empty] | 112.1887 | 2605.0481 |  | 104.98
09.02.2008 03:00 | 3600 | 2 | 763.74 | GGB | 767.766 | 773.086 | 769.963 | 271.4 | GGB | 11140.2 | GGB | 9.83 | GGB | 1035.83 | GGB | 60.4 | GGB | 173899.58 | GGB | 145606.02 | GGB | 0 | 0 | 2811 | 3600 | 2795.87 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 138765.51 | GGB | 138767.08 | 2795.87 | 2595.552 |  |  |  | 1 | 1 |  |  |  |  | 145606.02 | 2595.552 | 145606.02 | 2595.552 | 9.4199 | [5 empty] | 113.0821 | 2595.552 |  | 104.98
09.02.2008 04:00 | 3600 | 2 | 763.73 | GGB | 767.766 | 773.039 | 770.33 | 271.62 | GGB | 11153.5 | GGB | 9.83 | GGB | 1035.44 | GGB | 60.35 | GGB | 173925.99 | GGB | 145592.14 | GGB | 0 | 0 | 2811 | 3600 | 2795.81 | GGB | 100 | GGB | 41.5 | GGB | 41.5 | GGB | 138807.02 | GGB | 138808.58 | 2795.81 | 2595.7995 |  |  |  | 1 | 1 |  |  |  |  | 145592.14 | 2595.7995 | 145592.14 | 2595.7995 | 9.1067 | [5 empty] | 113.0689 | 2595.7995 |  | 104.98
09.02.2008 05:00 | 3600 | 2 | 763.29 | GGB | 766.667 | 772.922 | 768.864 | 271.87 | GGB | 11150 | GGB | 9.83 | GGB | 1035.5 | GGB | 60.31 | GGB | 174314.41 | GGB | 145944.93 | GGB | 0 | 0 | 2827 | 3600 | 2811.81 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 138848.13 | GGB | 138849.69 | 2811.81 | 2589.5247 |  |  |  | 1 | 1 |  |  |  |  | 145944.93 | 2589.5247 | 145944.93 | 2589.5247 | 9.1931 | [5 empty] | 113.9915 | 2589.5247 |  | 104.98
09.02.2008 06:00 | 3600 | 2 | 763.63 | GGB | 766.667 | 772.922 | 768.864 | 272.24 | GGB | 11169.3 | GGB | 9.83 | GGB | 1035.86 | GGB | 60.23 | GGB | 174834.87 | GGB | 146465.06 | GGB | 0 | 0 | 2834 | 3600 | 2818.02 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 138888.38 | GGB | 138889.95 | 2818.02 | 2580.3287 |  |  |  | 1 | 1 |  |  |  |  | 146465.06 | 2580.3287 | 146465.06 | 2580.3287 | 9.3872 | [5 empty] | 114.6504 | 2580.3287 |  | 104.98
09.02.2008 07:00 | 3600 | 2 | 763.54 | GGB | 767.766 | 772.875 | 769.963 | 272.38 | GGB | 11179.3 | GGB | 9.84 | GGB | 1036.1 | GGB | 60.15 | GGB | 175023.02 | GGB | 146692.3 | GGB | 0 | 0 | 2839 | 3600 | 2823.14 | GGB | 100 | GGB | 41.83 | GGB | 41.83 | GGB | 138930.22 | GGB | 138931.78 | 2823.14 | 2576.3315 |  |  |  | 1 | 1 |  |  |  |  | 146692.3 | 2576.3315 | 146692.3 | 2576.3315 | 9.0349 | [5 empty] | 115.0369 | 2576.3315 |  | 104.98
09.02.2008 08:00 | 3600 | 2 | 763.63 | GGB | 767.766 | 774.07 | 771.429 | 272.17 | GGB | 11177.5 | GGB | 9.84 | GGB | 1036.58 | GGB | 60.14 | GGB | 174862.37 | GGB | 146629.55 | GGB | 0 | 0 | 2832 | 3600 | 2816.43 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 138971.36 | GGB | 138972.92 | 2816.43 | 2577.4341 |  |  |  | 1 | 1 |  |  |  |  | 146629.55 | 2577.4341 | 146629.55 | 2577.4341 | 9.1864 | [5 empty] | 114.7144 | 2577.4341 |  | 104.98
09.02.2008 09:00 | 3600 | 2 | 763.64 | GGB | 767.766 | 774.164 | 771.429 | 271.93 | GGB | 11171.3 | GGB | 9.84 | GGB | 1036.64 | GGB | 60.08 | GGB | 174619.2 | GGB | 146461.26 | GGB | 0 | 0 | 2823 | 3600 | 2807.27 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 139011.91 | GGB | 139013.48 | 2807.27 | 2580.3957 |  |  |  | 1 | 1 |  |  |  |  | 146461.26 | 2580.3957 | 146461.26 | 2580.3957 | 9.3178 | [5 empty] | 114.2101 | 2580.3957 |  | 104.98
09.02.2008 10:00 | 3600 | 2 | 764.16 | GGB | 767.766 | 774.07 | 771.429 | 271.3 | GGB | 11160.3 | GGB | 9.84 | GGB | 1036.71 | GGB | 60.24 | GGB | 173825.86 | GGB | 145737.52 | GGB | 0 | 0 | 2798 | 3600 | 2782.84 | GGB | 100 | GGB | 41.79 | GGB | 41.79 | GGB | 139053.71 | GGB | 139055.27 | 2782.84 | 2593.21 |  |  |  | 1 | 1 |  |  |  |  | 145737.52 | 2593.21 | 145737.52 | 2593.21 | 9.0435 | [5 empty] | 112.6567 | 2593.21 |  | 104.98
09.02.2008 11:00 | 3600 | 2 | 764.84 | GGB | 769.963 | 775.945 | 772.527 | 270.16 | GGB | 11138.8 | GGB | 9.84 | GGB | 1036.74 | GGB | 60.45 | GGB | 172844.35 | GGB | 144826.58 | GGB | 0 | 0 | 2759 | 3600 | 2744.03 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 139094.39 | GGB | 139095.95 | 2744.03 | 2609.521 |  |  |  | 1 | 1 |  |  |  |  | 144826.58 | 2609.521 | 144826.58 | 2609.521 | 9.2903 | [5 empty] | 110.3912 | 2609.521 |  | 104.98
09.02.2008 12:00 | 3600 | 2 | 765.11 | GGB | 768.864 | 775.055 | 772.527 | 270.5 | GGB | 11082.1 | GGB | 9.83 | GGB | 1036.74 | GGB | 60.37 | GGB | 173524.36 | GGB | 145432.05 | GGB | 0 | 0 | 2716 | 3600 | 2700.3 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 139135.07 | GGB | 139136.63 | 2700.3 | 2598.6569 |  |  |  | 1 | 1 |  |  |  |  | 145432.05 | 2598.6569 | 145432.05 | 2598.6569 | 9.2903 | [5 empty] | 109.0862 | 2598.6569 |  | 104.98
09.02.2008 13:00 | 3600 | 2 | 766.87 | GGB | 769.963 | 777.258 | 773.626 | 269.96 | GGB | 11085.8 | GGB | 9.85 | GGB | 1036.46 | GGB | 60.36 | GGB | 173099.63 | GGB | 145039.55 | GGB | 0 | 0 | 2643 | 3600 | 2627.74 | GGB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 139176.4 | GGB | 139177.96 | 2627.74 | 2605.6893 |  |  |  | 1 | 1 |  |  |  |  | 145039.55 | 2605.6893 | 145039.55 | 2605.6893 | 9.1442 | [5 empty] | 105.8684 | 2605.6893 |  | 104.98
09.02.2008 14:00 | 3600 | 2 | 766.7 | GGB | 768.864 | 775.266 | 772.527 | 267.68 | GGB | 11072.6 | GGB | 9.84 | GGB | 1035.67 | GGB | 61.07 | GGB | 170289.37 | GGB | 142271.84 | GGB | 0 | 0 | 2630 | 3600 | 2614.61 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 139216.25 | GGB | 139217.81 | 2614.61 | 2614.61 |  |  |  | 1 | 1 |  |  |  |  | 142271.84 | 2614.61 | 142271.84 | 2614.61 | 9.3346 | [5 empty] | 103.3293 |  |  | #VALUE!
09.02.2008 15:00 | 3600 | 2 | 766.78 | GGB | 768.864 | 775.148 | 772.527 | 267.7 | GGB | 11064.4 | GGB | 9.83 | GGB | 1035.37 | GGB | 61.14 | GGB | 170426.91 | GGB | 142319.17 | GGB | 0 | 0 | 2626 | 3600 | 2611.15 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 139257.39 | GGB | 139258.95 | 2611.15 | 2611.15 |  |  |  | 1 | 1 |  |  |  |  | 142319.17 | 2611.15 | 142319.17 | 2611.15 | 9.033 | [5 empty] | 103.2269 |  |  | #VALUE!
09.02.2008 16:00 | 3600 | 2 | 766.39 | GGB | 768.864 | 776.344 | 772.527 | 268.16 | GGB | 11068.9 | GGB | 9.83 | GGB | 1035.43 | GGB | 61.09 | GGB | 170838.44 | GGB | 142689.86 | GGB | 0 | 0 | 2642 | 3600 | 2626.52 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 139298.34 | GGB | 139299.9 | 2626.52 | 2626.52 |  |  |  | 1 | 1 |  |  |  |  | 142689.86 | 2626.52 | 142689.86 | 2626.52 | 9.1521 | [5 empty] | 104.1049 |  |  | #VALUE!
09.02.2008 17:00 | 3600 | 2 | 765.86 | GGB | 767.766 | 774.234 | 771.429 | 268.42 | GGB | 11069.5 | GGB | 9.83 | GGB | 1035.31 | GGB | 61.06 | GGB | 171164.14 | GGB | 142959.28 | GGB | 0 | 0 | 2658 | 3600 | 2642.97 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 139338.57 | GGB | 139340.13 | 2642.97 | 2642.97 |  |  |  | 1 | 1 |  |  |  |  | 142959.28 | 2642.97 | 142959.28 | 2642.97 | 9.3919 | [5 empty] | 104.9547 |  |  | #VALUE!
09.02.2008 18:00 | 3600 | 2 | 765.82 | GGB | 767.766 | 774.023 | 771.429 | 269.13 | GGB | 11084.9 | GGB | 9.83 | GGB | 1035.59 | GGB | 61 | GGB | 171596.57 | GGB | 143383.52 | GGB | 0 | 0 | 2669 | 3600 | 2653.65 | GGB | 100 | GGB | 41.43 | GGB | 41.43 | GGB | 139380 | GGB | 139381.56 | 2653.65 | 2635.7841 |  |  |  | 1 | 1 |  |  |  |  | 143383.52 | 2635.7841 | 143383.52 | 2635.7841 | 9.1221 | [5 empty] | 105.6916 | 2635.7841 |  | 104.98
09.02.2008 19:00 | 3600 | 2 | 765.88 | GGB | 768.864 | 775.945 | 772.527 | 270.58 | GGB | 11067.6 | GGB | 9.83 | GGB | 1035.59 | GGB | 60.44 | GGB | 173730.13 | GGB | 145411.82 | GGB | 0 | 0 | 2658 | 3600 | 2643.1 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 139420.77 | GGB | 139422.33 | 2643.1 | 2599.0184 |  |  |  | 1 | 1 |  |  |  |  | 145411.82 | 2599.0184 | 145411.82 | 2599.0184 | 9.2698 | [5 empty] | 106.7606 | 2599.0184 |  | 104.98
09.02.2008 20:00 | 3600 | 2 | 766.34 | GGB | 769.963 | 776.109 | 772.527 | 270.59 | GGB | 11094.3 | GGB | 9.84 | GGB | 1035.52 | GGB | 60.27 | GGB | 173922.69 | GGB | 145637.83 | GGB | 0 | 0 | 2642 | 3600 | 2626.26 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 139460.84 | GGB | 139462.41 | 2626.26 | 2594.9851 |  |  |  | 1 | 1 |  |  |  |  | 145637.83 | 2594.9851 | 145637.83 | 2594.9851 | 9.4293 | [5 empty] | 106.2452 | 2594.9851 |  | 104.98
09.02.2008 21:00 | 3600 | 2 | 765.51 | GGB | 768.864 | 775.008 | 771.795 | 269.76 | GGB | 11116.4 | GGB | 9.83 | GGB | 1035.57 | GGB | 60.65 | GGB | 172607.78 | GGB | 144380.21 | GGB | 0 | 0 | 2699 | 3600 | 2683.31 | GGB | 100 | GGB | 41.49 | GGB | 41.49 | GGB | 139502.33 | GGB | 139503.9 | 2683.31 | 2617.5887 |  |  |  | 1 | 1 |  |  |  |  | 144380.21 | 2617.5887 | 144380.21 | 2617.5887 | 9.1089 | [5 empty] | 107.6158 | 2617.5887 |  | 104.98
09.02.2008 22:00 | 3600 | 2 | 765.4 | GGB | 768.864 | 775.172 | 771.795 | 269.77 | GGB | 11115.3 | GGB | 9.83 | GGB | 1035.8 | GGB | 60.64 | GGB | 172505.45 | GGB | 144329.03 | GGB | 0 | 0 | 2701 | 3600 | 2685.3 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 139543.24 | GGB | 139544.81 | 2685.3 | 2618.5169 |  |  |  | 1 | 1 |  |  |  |  | 144329.03 | 2618.5169 | 144329.03 | 2618.5169 | 9.238 | [5 empty] | 107.6574 | 2618.5169 |  | 104.98
09.02.2008 23:00 | 3600 | 2 | 765.43 | GGB | 768.864 | 776.086 | 773.26 | 269.36 | GGB | 11118.4 | GGB | 9.84 | GGB | 1035.88 | GGB | 60.7 | GGB | 172492.25 | GGB | 144301.59 | GGB | 0 | 0 | 2698 | 3600 | 2682.71 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 139583.83 | GGB | 139585.4 | 2682.71 | 2619.0148 |  |  |  | 1 | 1 |  |  |  |  | 144301.59 | 2619.0148 | 144301.59 | 2619.0148 | 9.3109 | [5 empty] | 107.5331 | 2619.0148 |  | 104.98
09.02.2008 24:00 | 3600 | 2 | 764.92 | GGB | 767.766 | 775.102 | 770.696 | 269.64 | GGB | 11110.9 | GGB | 9.83 | GGB | 1035.7 | GGB | 60.53 | GGB | 172514.25 | GGB | 144371.05 | GGB | 0 | 0 | 2722 | 3600 | 2707.01 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 139625.13 | GGB | 139626.7 | 2707.01 | 2617.7547 |  |  |  | 1 | 1 |  |  |  |  | 144371.05 | 2617.7547 | 144371.05 | 2617.7547 | 9.1508 | [5 empty] | 108.5594 | 2617.7547 |  | 104.98
10.02.2008 01:00 | 3600 | 2 | 765.27 | GGB | 767.766 | 774.047 | 770.696 | 269.8 | GGB | 11115.5 | GGB | 9.84 | GGB | 1034.97 | GGB | 60.65 | GGB | 172417.42 | GGB | 144137.19 | GGB | 0 | 0 | 2707 | 3600 | 2691.48 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 139665.97 | GGB | 139667.54 | 2691.48 | 2622.002 |  |  |  | 1 | 1 |  |  |  |  | 144137.19 | 2622.002 | 144137.19 | 2622.002 | 9.2539 | [5 empty] | 107.7618 | 2622.002 |  | 104.98
10.02.2008 02:00 | 3600 | 2 | 765.29 | GGB | 767.766 | 774.07 | 770.696 | 269.64 | GGB | 11111.3 | GGB | 9.84 | GGB | 1034.81 | GGB | 60.61 | GGB | 172439.43 | GGB | 144149.18 | GGB | 0 | 0 | 2709 | 3600 | 2693.7 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 139706.65 | GGB | 139708.22 | 2693.7 | 2621.7839 |  |  |  | 1 | 1 |  |  |  |  | 144149.18 | 2621.7839 | 144149.18 | 2621.7839 | 9.2903 | [5 empty] | 107.8596 | 2621.7839 |  | 104.98
10.02.2008 03:00 | 3600 | 2 | 765.13 | GGB | 767.766 | 774.281 | 770.696 | 269.55 | GGB | 11105.7 | GGB | 9.84 | GGB | 1034.64 | GGB | 60.62 | GGB | 172389.92 | GGB | 144079.26 | GGB | 0 | 0 | 2712 | 3600 | 2696.88 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 139748.2 | GGB | 139749.77 | 2696.88 | 2623.0562 |  |  |  | 1 | 1 |  |  |  |  | 144079.26 | 2623.0562 | 144079.26 | 2623.0562 | 9.0957 | [5 empty] | 107.9346 | 2623.0562 |  | 104.98
10.02.2008 04:00 | 3600 | 2 | 765.02 | GGB | 767.766 | 774.328 | 771.795 | 269.52 | GGB | 11100.3 | GGB | 9.83 | GGB | 1034.28 | GGB | 60.58 | GGB | 172319.49 | GGB | 143986.13 | GGB | 0 | 0 | 2717 | 3600 | 2701.63 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 139788.67 | GGB | 139790.24 | 2701.63 | 2624.7528 |  |  |  | 1 | 1 |  |  |  |  | 143986.13 | 2624.7528 | 143986.13 | 2624.7528 | 9.3385 | [5 empty] | 108.0548 | 2624.7528 |  | 104.98
10.02.2008 05:00 | 3600 | 2 | 765.22 | GGB | 767.766 | 774.375 | 770.696 | 269.49 | GGB | 11100.2 | GGB | 9.83 | GGB | 1033.99 | GGB | 60.63 | GGB | 172263.38 | GGB | 143878.44 | GGB | 0 | 0 | 2703 | 3600 | 2687.95 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 139829.46 | GGB | 139831.03 | 2687.95 | 2626.7174 |  |  |  | 1 | 1 |  |  |  |  | 143878.44 | 2626.7174 | 143878.44 | 2626.7174 | 9.2652 | [5 empty] | 107.4272 | 2626.7174 |  | 104.98
10.02.2008 06:00 | 3600 | 2 | 765.19 | GGB | 767.766 | 774.398 | 771.795 | 269.71 | GGB | 11106.2 | GGB | 9.83 | GGB | 1034.15 | GGB | 60.63 | GGB | 172375.61 | GGB | 143994.47 | GGB | 0 | 0 | 2712 | 3600 | 2696.8 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 139870.86 | GGB | 139872.43 | 2696.8 | 2624.6008 |  |  |  | 1 | 1 |  |  |  |  | 143994.47 | 2624.6008 | 143994.47 | 2624.6008 | 9.1287 | [5 empty] | 107.8679 | 2624.6008 |  | 104.98
10.02.2008 07:00 | 3600 | 2 | 764.88 | GGB | 767.766 | 774.563 | 770.696 | 269.87 | GGB | 11103.6 | GGB | 9.83 | GGB | 1034.22 | GGB | 60.58 | GGB | 172656.2 | GGB | 144262.02 | GGB | 0 | 0 | 2720 | 3600 | 2704.51 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 139911.08 | GGB | 139912.65 | 2704.51 | 2619.7332 |  |  |  | 1 | 1 |  |  |  |  | 144262.02 | 2619.7332 | 144262.02 | 2619.7332 | 9.3965 | [5 empty] | 108.3772 | 2619.7332 |  | 104.98
10.02.2008 08:00 | 3600 | 2 | 765.16 | GGB | 767.766 | 774.656 | 771.795 | 269.76 | GGB | 11114.7 | GGB | 9.84 | GGB | 1034.31 | GGB | 60.6 | GGB | 172359.11 | GGB | 144015.85 | GGB | 0 | 0 | 2719 | 3600 | 2703.12 | GGB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 139952.05 | GGB | 139953.63 | 2703.12 | 2624.2112 |  |  |  | 1 | 1 |  |  |  |  | 144015.85 | 2624.2112 | 144015.85 | 2624.2112 | 9.2223 | [5 empty] | 108.1367 | 2624.2112 |  | 104.98
10.02.2008 09:00 | 3600 | 2 | 764.92 | GGB | 768.864 | 774.703 | 771.795 | 269.71 | GGB | 11106.3 | GGB | 9.83 | GGB | 1034.3 | GGB | 60.56 | GGB | 172459.24 | GGB | 144115.05 | GGB | 0 | 0 | 2723 | 3600 | 2707.47 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 139993.32 | GGB | 139994.9 | 2707.47 | 2622.4048 |  |  |  | 1 | 1 |  |  |  |  | 144115.05 | 2622.4048 | 144115.05 | 2622.4048 | 9.1575 | [5 empty] | 108.3853 | 2622.4048 |  | 104.98
10.02.2008 10:00 | 3600 | 2 | 765.07 | GGB | 768.864 | 774.609 | 771.795 | 269.54 | GGB | 11102 | GGB | 9.84 | GGB | 1033.92 | GGB | 60.62 | GGB | 172245.77 | GGB | 143860.2 | GGB | 0 | 0 | 2713 | 3600 | 2697.57 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 140033.58 | GGB | 140035.16 | 2697.57 | 2627.0504 |  |  |  | 1 | 1 |  |  |  |  | 143860.2 | 2627.0504 | 143860.2 | 2627.0504 | 9.3872 | [5 empty] | 107.798 | 2627.0504 |  | 104.98
10.02.2008 11:00 | 3600 | 2 | 765.42 | GGB | 768.864 | 775.664 | 771.795 | 269.16 | GGB | 11101.1 | GGB | 9.84 | GGB | 1033.82 | GGB | 60.68 | GGB | 171911.27 | GGB | 143538.22 | GGB | 0 | 0 | 2695 | 3600 | 2679.17 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 140074.89 | GGB | 140076.47 | 2679.17 | 2632.9433 |  |  |  | 1 | 1 |  |  |  |  | 143538.22 | 2632.9433 | 143538.22 | 2632.9433 | 9.1486 | [5 empty] | 106.8231 | 2632.9433 |  | 104.98
10.02.2008 12:00 | 3600 | 2 | 766.29 | GGB | 769.963 | 775.641 | 772.161 | 267.93 | GGB | 11080.3 | GGB | 9.84 | GGB | 1033.64 | GGB | 60.87 | GGB | 170840.64 | GGB | 142538.23 | GGB | 0 | 0 | 2655 | 3600 | 2639.44 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 140115.71 | GGB | 140117.3 | 2639.44 | 2639.44 |  |  |  | 1 | 1 |  |  |  |  | 142538.23 | 2639.44 | 142538.23 | 2639.44 | 9.2143 | [5 empty] | 104.5059 |  |  | #VALUE!
10.02.2008 13:00 | 3600 | 2 | 766.33 | GGB | 768.864 | 775.711 | 772.161 | 267.35 | GGB | 11052.3 | GGB | 9.84 | GGB | 1033.37 | GGB | 60.98 | GGB | 170126.52 | GGB | 141861.33 | GGB | 0 | 0 | 2642 | 3600 | 2626.98 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 140155.97 | GGB | 140157.56 | 2626.98 | 2626.98 |  |  |  | 1 | 1 |  |  |  |  | 141861.33 | 2626.98 | 141861.33 | 2626.98 | 9.2565 | [5 empty] | 103.5186 |  |  | #VALUE!
10.02.2008 14:00 | 3600 | 2 | 766.42 | GGB | 769.963 | 776.625 | 773.26 | 267.33 | GGB | 11044 | GGB | 9.83 | GGB | 1033 | GGB | 61.42 | GGB | 170056.1 | GGB | 141564.03 | GGB | 0 | 0 | 2638 | 3600 | 2622.71 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 140197.36 | GGB | 140198.96 | 2622.71 | 2622.71 |  |  |  | 1 | 1 |  |  |  |  | 141564.03 | 2622.71 | 141564.03 | 2622.71 | 8.9681 | [5 empty] | 103.1337 |  |  | #VALUE!
10.02.2008 15:00 | 3600 | 2 | 766.91 | GGB | 769.963 | 777.492 | 774.359 | 266.77 | GGB | 11037.4 | GGB | 9.84 | GGB | 1032.44 | GGB | 61.48 | GGB | 169581.85 | GGB | 141068.98 | GGB | 0 | 0 | 2616 | 3600 | 2601.17 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 140237.65 | GGB | 140239.24 | 2601.17 | 2601.17 |  |  |  | 1 | 1 |  |  |  |  | 141068.98 | 2601.17 | 141068.98 | 2601.17 | 9.1098 | [5 empty] | 101.929 |  |  | #VALUE!
10.02.2008 16:00 | 3600 | 2 | 766.53 | GGB | 768.864 | 775.336 | 772.161 | 266.74 | GGB | 11025.3 | GGB | 9.83 | GGB | 1032.43 | GGB | 61.53 | GGB | 169629.17 | GGB | 141084.5 | GGB | 0 | 0 | 2615 | 3600 | 2600.16 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 140277.98 | GGB | 140279.57 | 2600.16 | 2600.16 |  |  |  | 1 | 1 |  |  |  |  | 141084.5 | 2600.16 | 141084.5 | 2600.16 | 9.096 | [5 empty] | 101.9006 |  |  | #VALUE!
10.02.2008 17:00 | 3600 | 2 | 766.67 | GGB | 768.864 | 776.156 | 773.26 | 266.77 | GGB | 11031.1 | GGB | 9.83 | GGB | 1031.98 | GGB | 61.4 | GGB | 169822.83 | GGB | 141238.82 | GGB | 0 | 0 | 2617 | 3600 | 2601.43 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 140319.16 | GGB | 140320.75 | 2601.43 | 2601.43 |  |  |  | 1 | 1 |  |  |  |  | 141238.82 | 2601.43 | 141238.82 | 2601.43 | 8.9224 | [5 empty] | 102.0619 |  |  | #VALUE!
10.02.2008 18:00 | 3600 | 2 | 766.37 | GGB | 768.864 | 776.133 | 772.161 | 267.33 | GGB | 11044.7 | GGB | 9.83 | GGB | 1031.6 | GGB | 61.1 | GGB | 170666.79 | GGB | 142015.48 | GGB | 0 | 0 | 2632 | 3600 | 2616.29 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 140359.14 | GGB | 140360.73 | 2616.29 | 2616.29 |  |  |  | 1 | 1 |  |  |  |  | 142015.48 | 2616.29 | 142015.48 | 2616.29 | 9.2935 | [5 empty] | 103.2094 |  |  | #VALUE!
10.02.2008 19:00 | 3600 | 2 | 765.79 | GGB | 767.766 | 774.891 | 771.795 | 268.26 | GGB | 11063.4 | GGB | 9.83 | GGB | 1031.96 | GGB | 60.9 | GGB | 171498.64 | GGB | 142842.69 | GGB | 0 | 0 | 2665 | 3600 | 2649.96 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 140400.14 | GGB | 140401.73 | 2649.96 | 2645.7637 |  |  |  | 1 | 1 |  |  |  |  | 142842.69 | 2645.7637 | 142842.69 | 2645.7637 | 9.2178 | [5 empty] | 105.1465 | 2645.7637 |  | 104.98
10.02.2008 20:00 | 3600 | 2 | 765.45 | GGB | 766.667 | 773.789 | 770.696 | 268.75 | GGB | 11082.2 | GGB | 9.83 | GGB | 1032.08 | GGB | 60.69 | GGB | 172068.62 | GGB | 143424.14 | GGB | 0 | 0 | 2682 | 3600 | 2666.85 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 140441.37 | GGB | 140442.96 | 2666.85 | 2635.0376 |  |  |  | 1 | 1 |  |  |  |  | 143424.14 | 2635.0376 | 143424.14 | 2635.0376 | 9.1663 | [5 empty] | 106.2474 | 2635.0376 |  | 104.98
10.02.2008 21:00 | 3600 | 2 | 765 | GGB | 767.766 | 774.75 | 770.696 | 269.18 | GGB | 11097.6 | GGB | 9.83 | GGB | 1032.08 | GGB | 60.45 | GGB | 172641.89 | GGB | 144005.93 | GGB | 0 | 0 | 2707 | 3600 | 2691.61 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 140481.48 | GGB | 140483.07 | 2691.61 | 2624.3919 |  |  |  | 1 | 1 |  |  |  |  | 144005.93 | 2624.3919 | 144005.93 | 2624.3919 | 9.4223 | [5 empty] | 107.6688 | 2624.3919 |  | 104.98
10.02.2008 22:00 | 3600 | 2 | 764.54 | GGB | 768.864 | 774.961 | 770.696 | 268.83 | GGB | 11118 | GGB | 9.83 | GGB | 1031.8 | GGB | 59.99 | GGB | 173338.41 | GGB | 144747.9 | GGB | 0 | 0 | 2736 | 3600 | 2720.28 | GGB | 100 | GGB | 41.34 | GGB | 41.34 | GGB | 140522.82 | GGB | 140524.41 | 2720.28 | 2610.9394 |  |  |  | 1 | 1 |  |  |  |  | 144747.9 | 2610.9394 | 144747.9 | 2610.9394 | 9.1419 | [5 empty] | 109.3763 | 2610.9394 |  | 104.98
10.02.2008 23:00 | 3600 | 2 | 764.36 | GGB | 766.3 | 772.852 | 769.597 | 269.55 | GGB | 11113.7 | GGB | 9.83 | GGB | 1031.95 | GGB | 60.1 | GGB | 173324.1 | GGB | 144709.54 | GGB | 0 | 0 | 2746 | 3600 | 2730.81 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 140564.2 | GGB | 140565.79 | 2730.81 | 2611.6315 |  |  |  | 1 | 1 |  |  |  |  | 144709.54 | 2611.6315 | 144709.54 | 2611.6315 | 9.1331 | [5 empty] | 109.7706 | 2611.6315 |  | 104.98
10.02.2008 24:00 | 3600 | 2 | 764.25 | GGB | 766.667 | 774.281 | 770.696 | 269.77 | GGB | 11128.8 | GGB | 9.83 | GGB | 1031.8 | GGB | 59.84 | GGB | 173863.27 | GGB | 145250.52 | GGB | 0 | 0 | 2760 | 3600 | 2744.63 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 140604.43 | GGB | 140606.02 | 2744.63 | 2601.9046 |  |  |  | 1 | 1 |  |  |  |  | 145250.52 | 2601.9046 | 145250.52 | 2601.9046 | 9.3942 | [5 empty] | 110.7386 | 2601.9046 |  | 104.98
11.02.2008 01:00 | 3600 | 2 | 763.09 | GGB | 766.3 | 772.289 | 769.597 | 270.85 | GGB | 11142.5 | GGB | 9.83 | GGB | 1031.83 | GGB | 59.5 | GGB | 174768.85 | GGB | 146163.65 | GGB | 0 | 0 | 2823 | 3600 | 2807.2 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 140645.71 | GGB | 140647.3 | 2807.2 | 2585.6497 |  |  |  | 1 | 1 |  |  |  |  | 146163.65 | 2585.6497 | 146163.65 | 2585.6497 | 9.1552 | [5 empty] | 113.9752 | 2585.6497 |  | 104.98
11.02.2008 02:00 | 3600 | 2 | 763.75 | GGB | 765.201 | 772.125 | 768.498 | 270.88 | GGB | 11157.4 | GGB | 9.84 | GGB | 1031.72 | GGB | 59.49 | GGB | 174637.91 | GGB | 146042.06 | GGB | 0 | 0 | 2811 | 3600 | 2795.74 | GGB | 100 | GGB | 41.24 | GGB | 41.24 | GGB | 140686.95 | GGB | 140688.54 | 2795.74 | 2587.8024 |  |  |  | 1 | 1 |  |  |  |  | 146042.06 | 2587.8024 | 146042.06 | 2587.8024 | 9.1641 | [5 empty] | 113.4155 | 2587.8024 |  | 104.98
11.02.2008 03:00 | 3600 | 2 | 763.89 | GGB | 766.667 | 773.25 | 770.696 | 270.67 | GGB | 11154.9 | GGB | 9.84 | GGB | 1031.65 | GGB | 59.48 | GGB | 174602.69 | GGB | 146005.03 | GGB | 0 | 0 | 2803 | 3600 | 2787.27 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 140727.31 | GGB | 140728.9 | 2787.27 | 2588.4588 |  |  |  | 1 | 1 |  |  |  |  | 146005.03 | 2588.4588 | 146005.03 | 2588.4588 | 9.3639 | [5 empty] | 113.0432 | 2588.4588 |  | 104.98
11.02.2008 04:00 | 3600 | 2 | 763.91 | GGB | 766.667 | 773.227 | 769.597 | 270.22 | GGB | 11139.7 | GGB | 9.83 | GGB | 1031.29 | GGB | 59.56 | GGB | 174078.93 | GGB | 145482.24 | GGB | 0 | 0 | 2789 | 3600 | 2773.35 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 140768.82 | GGB | 140770.41 | 2773.35 | 2597.7604 |  |  |  | 1 | 1 |  |  |  |  | 145482.24 | 2597.7604 | 145482.24 | 2597.7604 | 9.1045 | [5 empty] | 112.0759 | 2597.7604 |  | 104.98
11.02.2008 05:00 | 3600 | 2 | 763.73 | GGB | 766.3 | 772.289 | 769.597 | 270.51 | GGB | 11143.4 | GGB | 9.83 | GGB | 1031.58 | GGB | 59.53 | GGB | 174345.22 | GGB | 145760.54 | GGB | 0 | 0 | 2799 | 3600 | 2783.87 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 140809.66 | GGB | 140811.25 | 2783.87 | 2592.8005 |  |  |  | 1 | 1 |  |  |  |  | 145760.54 | 2592.8005 | 145760.54 | 2592.8005 | 9.2539 | [5 empty] | 112.7162 | 2592.8005 |  | 104.98
11.02.2008 06:00 | 3600 | 2 | 763.56 | GGB | 766.3 | 772.336 | 769.597 | 270.58 | GGB | 11147.5 | GGB | 9.83 | GGB | 1031.39 | GGB | 59.44 | GGB | 174593.89 | GGB | 145978.98 | GGB | 0 | 0 | 2808 | 3600 | 2792.84 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 140850.19 | GGB | 140851.78 | 2792.84 | 2588.9207 |  |  |  | 1 | 1 |  |  |  |  | 145978.98 | 2588.9207 | 145978.98 | 2588.9207 | 9.3246 | [5 empty] | 113.2489 | 2588.9207 |  | 104.98
11.02.2008 07:00 | 3600 | 2 | 763.46 | GGB | 765.201 | 771.211 | 768.132 | 270.91 | GGB | 11154.4 | GGB | 9.83 | GGB | 1031.37 | GGB | 59.33 | GGB | 175141.86 | GGB | 146482.64 | GGB | 0 | 0 | 2823 | 3600 | 2807.12 | GGB | 100 | GGB | 41.34 | GGB | 41.34 | GGB | 140891.53 | GGB | 140893.12 | 2807.12 | 2580.019 |  |  |  | 1 | 1 |  |  |  |  | 146482.64 | 2580.019 | 146482.64 | 2580.019 | 9.1419 | [5 empty] | 114.2207 | 2580.019 |  | 104.98
11.02.2008 08:00 | 3600 | 2 | 762.24 | GGB | 766.3 | 771.164 | 768.132 | 271.72 | GGB | 11173.2 | GGB | 9.83 | GGB | 1032.08 | GGB | 59.14 | GGB | 175700.83 | GGB | 147136.97 | GGB | 0 | 0 | 2876 | 3600 | 2860.22 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 140932.58 | GGB | 140934.17 | 2860.22 | 2568.5455 |  |  |  | 1 | 1 |  |  |  |  | 147136.97 | 2568.5455 | 147136.97 | 2568.5455 | 9.2065 | [5 empty] | 116.9011 | 2568.5455 |  | 104.98
11.02.2008 09:00 | 3600 | 2 | 762.18 | GGB | 765.201 | 771.258 | 768.132 | 271.95 | GGB | 11186.4 | GGB | 9.83 | GGB | 1032.48 | GGB | 59.07 | GGB | 175946.21 | GGB | 147431.62 | GGB | 0 | 0 | 2882 | 3600 | 2866.79 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 140973.49 | GGB | 140975.08 | 2866.79 | 2563.4121 |  |  |  | 1 | 1 |  |  |  |  | 147431.62 | 2563.4121 | 147431.62 | 2563.4121 | 9.238 | [5 empty] | 117.4043 | 2563.4121 |  | 104.98
11.02.2008 10:00 | 3600 | 2 | 762.49 | GGB | 766.3 | 772.336 | 769.597 | 271.89 | GGB | 11193.5 | GGB | 9.84 | GGB | 1032.78 | GGB | 59.01 | GGB | 175894.49 | GGB | 147453.98 | GGB | 0 | 0 | 2880 | 3600 | 2864.52 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 141014.59 | GGB | 141016.18 | 2864.52 | 2563.0234 |  |  |  | 1 | 1 |  |  |  |  | 147453.98 | 2563.0234 | 147453.98 | 2563.0234 | 9.1953 | [5 empty] | 117.3291 | 2563.0234 |  | 104.98
11.02.2008 11:00 | 3600 | 2 | 762.44 | GGB | 764.102 | 771.188 | 767.033 | 272.16 | GGB | 11198.8 | GGB | 9.83 | GGB | 1033.24 | GGB | 59.01 | GGB | 176099.15 | GGB | 147693.28 | GGB | 0 | 0 | 2887 | 3600 | 2871.71 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 141055.77 | GGB | 141057.36 | 2871.71 | 2558.8707 |  |  |  | 1 | 1 |  |  |  |  | 147693.28 | 2558.8707 | 147693.28 | 2558.8707 | 9.1775 | [5 empty] | 117.8145 | 2558.8707 |  | 104.98
11.02.2008 12:00 | 3600 | 2 | 761.79 | GGB | 766.3 | 772.453 | 768.498 | 272.64 | GGB | 11217 | GGB | 9.83 | GGB | 1033.45 | GGB | 58.87 | GGB | 176589.9 | GGB | 148199.4 | GGB | 0 | 0 | 2914 | 3600 | 2898.29 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 141096.96 | GGB | 141098.55 | 2898.29 | 2550.1318 |  |  |  | 1 | 1 |  |  |  |  | 148199.4 | 2550.1318 | 148199.4 | 2550.1318 | 9.1752 | [5 empty] | 119.3125 | 2550.1318 |  | 104.98
11.02.2008 13:00 | 3600 | 2 | 762.03 | GGB | 766.3 | 772.453 | 769.597 | 274.25 | GGB | 11186.3 | GGB | 9.82 | GGB | 1033.56 | GGB | 58.29 | GGB | 178755.37 | GGB | 150291.38 | GGB | 0 | 0 | 2886 | 3600 | 2870.61 | GGB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 141138.28 | GGB | 141139.87 | 2870.61 | 2514.6352 |  |  |  | 1 | 1 |  |  |  |  | 150291.38 | 2514.6352 | 150291.38 | 2514.6352 | 9.1464 | [5 empty] | 119.8411 | 2514.6352 |  | 104.98
11.02.2008 14:00 | 3600 | 2 | 762.69 | GGB | 765.201 | 772.406 | 769.597 | 274.46 | GGB | 11198.6 | GGB | 9.83 | GGB | 1033.26 | GGB | 58.13 | GGB | 179148.19 | GGB | 150652.63 | GGB | 0 | 0 | 2865 | 3600 | 2849.46 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 141179.07 | GGB | 141180.66 | 2849.46 | 2508.6054 |  |  |  | 1 | 1 |  |  |  |  | 150652.63 | 2508.6054 | 150652.63 | 2508.6054 | 9.2652 | [5 empty] | 119.2441 | 2508.6054 |  | 104.98
11.02.2008 15:00 | 3600 | 2 | 762.9 | GGB | 765.201 | 771.234 | 768.498 | 273.96 | GGB | 11191.5 | GGB | 9.84 | GGB | 1033.2 | GGB | 58.15 | GGB | 178770.77 | GGB | 150318.29 | GGB | 0 | 0 | 2853 | 3600 | 2837.85 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 141220.12 | GGB | 141221.71 | 2837.85 | 2514.1851 |  |  |  | 1 | 1 |  |  |  |  | 150318.29 | 2514.1851 | 150318.29 | 2514.1851 | 9.2065 | [5 empty] | 118.4947 | 2514.1851 |  | 104.98
11.02.2008 16:00 | 3600 | 2 | 762.46 | GGB | 767.766 | 773.086 | 769.597 | 273.3 | GGB | 11187.8 | GGB | 9.84 | GGB | 1033.53 | GGB | 58.05 | GGB | 178500.09 | GGB | 150182.4 | GGB | 0 | 0 | 2865 | 3600 | 2849.66 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 141261.35 | GGB | 141262.94 | 2849.66 | 2516.46 |  |  |  | 1 | 1 |  |  |  |  | 150182.4 | 2516.46 | 150182.4 | 2516.46 | 9.1663 | [5 empty] | 118.8802 | 2516.46 |  | 104.98
11.02.2008 17:00 | 3600 | 2 | 762.88 | GGB | 766.667 | 774.141 | 770.696 | 271.91 | GGB | 11192.8 | GGB | 9.86 | GGB | 1033.55 | GGB | 58.35 | GGB | 177110.36 | GGB | 148880.34 | GGB | 0 | 0 | 2848 | 3600 | 2832.54 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 141302.07 | GGB | 141303.66 | 2832.54 | 2538.4681 |  |  |  | 1 | 1 |  |  |  |  | 148880.34 | 2538.4681 | 148880.34 | 2538.4681 | 9.2811 | [5 empty] | 117.1415 | 2538.4681 |  | 104.98
11.02.2008 18:00 | 3600 | 2 | 761.2 | GGB | 765.201 | 770.93 | 768.132 | 270.79 | GGB | 11143.1 | GGB | 9.83 | GGB | 1033.62 | GGB | 59.07 | GGB | 174848.07 | GGB | 146672.23 | GGB | 0 | 0 | 2925 | 3600 | 2908.95 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 141343.38 | GGB | 141344.97 | 2908.95 | 2576.6841 |  |  |  | 1 | 1 |  |  |  |  | 146672.23 | 2576.6841 | 146672.23 | 2576.6841 | 9.1486 | [5 empty] | 118.5173 | 2576.6841 |  | 104.98
11.02.2008 19:00 | 3600 | 2 | 761.21 | GGB | 764.835 | 770.836 | 767.033 | 270.79 | GGB | 11124.9 | GGB | 9.83 | GGB | 1033.61 | GGB | 59.39 | GGB | 174108.64 | GGB | 145908.37 | GGB | 0 | 0 | 2918 | 3600 | 2902.1 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 141384.14 | GGB | 141385.73 | 2902.1 | 2590.1735 |  |  |  | 1 | 1 |  |  |  |  | 145908.37 | 2590.1735 | 145908.37 | 2590.1735 | 9.272 | [5 empty] | 117.6224 | 2590.1735 |  | 104.98
11.02.2008 20:00 | 3600 | 2 | 761.26 | GGB | 764.469 | 769.758 | 767.033 | 271.27 | GGB | 11091.8 | GGB | 9.83 | GGB | 1033.93 | GGB | 59.53 | GGB | 174647.81 | GGB | 146344.5 | GGB | 0 | 0 | 2912 | 3600 | 2896 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 141424.82 | GGB | 141426.41 | 2896 | 2582.4544 |  |  |  | 1 | 1 |  |  |  |  | 146344.5 | 2582.4544 | 146344.5 | 2582.4544 | 9.2903 | [5 empty] | 117.726 | 2582.4544 |  | 104.98
11.02.2008 21:00 | 3600 | 2 | 761.85 | GGB | 764.835 | 770.836 | 768.132 | 272.04 | GGB | 11077.4 | GGB | 9.83 | GGB | 1034.15 | GGB | 59.01 | GGB | 175871.38 | GGB | 147630.66 | GGB | 0 | 0 | 2866 | 3600 | 2850.12 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 141466.06 | GGB | 141467.64 | 2850.12 | 2559.956 |  |  |  | 1 | 1 |  |  |  |  | 147630.66 | 2559.956 | 147630.66 | 2559.956 | 9.1663 | [5 empty] | 116.8792 | 2559.956 |  | 104.98
11.02.2008 22:00 | 3600 | 2 | 762.31 | GGB | 764.835 | 770.742 | 768.132 | 272 | GGB | 11078.4 | GGB | 9.84 | GGB | 1033.88 | GGB | 59.13 | GGB | 175734.94 | GGB | 147425.17 | GGB | 0 | 0 | 2856 | 3600 | 2840.8 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 141506.74 | GGB | 141508.32 | 2840.8 | 2563.5243 |  |  |  | 1 | 1 |  |  |  |  | 147425.17 | 2563.5243 | 147425.17 | 2563.5243 | 9.2903 | [5 empty] | 116.3348 | 2563.5243 |  | 104.98
11.02.2008 23:00 | 3600 | 2 | 761.7 | GGB | 764.469 | 770.93 | 768.132 | 271.37 | GGB | 11076.2 | GGB | 9.83 | GGB | 1033.94 | GGB | 59.07 | GGB | 175880.19 | GGB | 147583.8 | GGB | 0 | 0 | 2866 | 3600 | 2850.39 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 141546.03 | GGB | 141547.61 | 2850.39 | 2560.7689 |  |  |  | 1 | 1 |  |  |  |  | 147583.8 | 2560.7689 | 147583.8 | 2560.7689 | 9.6189 | [5 empty] | 116.8532 | 2560.7689 |  | 104.98
11.02.2008 24:00 | 3600 | 2 | 762.59 | GGB | 765.934 | 771.961 | 768.498 | 270.9 | GGB | 11092.2 | GGB | 9.85 | GGB | 1033.81 | GGB | 59.45 | GGB | 174232.98 | GGB | 146016.65 | GGB | 0 | 0 | 2854 | 3600 | 2838.85 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 141586.97 | GGB | 141588.55 | 2838.85 | 2588.2528 |  |  |  | 1 | 1 |  |  |  |  | 146016.65 | 2588.2528 | 146016.65 | 2588.2528 | 9.2313 | [5 empty] | 115.1443 | 2588.2528 |  | 104.98
12.02.2008 01:00 | 3600 | 2 | 761.16 | GGB | 765.934 | 771.094 | 768.132 | 269.57 | GGB | 11077.3 | GGB | 9.83 | GGB | 1033.69 | GGB | 59.95 | GGB | 172755.23 | GGB | 144543.41 | GGB | 0 | 0 | 2910 | 3600 | 2894.89 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 141628.34 | GGB | 141629.92 | 2894.89 | 2614.6332 |  |  |  | 1 | 1 |  |  |  |  | 144543.41 | 2614.6332 | 144543.41 | 2614.6332 | 9.1353 | [5 empty] | 116.2326 | 2614.6332 |  | 104.98
12.02.2008 02:00 | 3600 | 2 | 761.45 | GGB | 764.835 | 770.719 | 768.132 | 269.59 | GGB | 11069.1 | GGB | 9.84 | GGB | 1033.55 | GGB | 60.03 | GGB | 172560.47 | GGB | 144324.24 | GGB | 0 | 0 | 2900 | 3600 | 2884.79 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 141668.14 | GGB | 141669.73 | 2884.79 | 2618.6038 |  |  |  | 1 | 1 |  |  |  |  | 144324.24 | 2618.6038 | 144324.24 | 2618.6038 | 9.4933 | [5 empty] | 115.6514 | 2618.6038 |  | 104.98
12.02.2008 03:00 | 3600 | 2 | 761.2 | GGB | 763.37 | 769.734 | 767.033 | 269.5 | GGB | 11056.5 | GGB | 9.83 | GGB | 1033.18 | GGB | 60.16 | GGB | 172220.46 | GGB | 143933.7 | GGB | 0 | 0 | 2903 | 3600 | 2887.22 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 141709.02 | GGB | 141710.6 | 2887.22 | 2625.7089 |  |  |  | 0 | 1 | [14 empty] | 115.4356 | 2625.7089 |  | 104.98
12.02.2008 04:00 | 3600 | 2 | 761.45 | GGB | 764.835 | 771 | 768.132 | 269.44 | GGB | 11058 | GGB | 9.84 | GGB | 1032.9 | GGB | 60.3 | GGB | 172081.82 | GGB | 143719.74 | GGB | 0 | 0 | 2901 | 3600 | 2885.43 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 141749.92 | GGB | 141751.51 | 2885.43 | 2629.6179 |  |  |  | 1 | 1 |  |  |  |  | 143719.74 | 2629.6179 | 143719.74 | 2629.6179 | 9.238 | [5 empty] | 115.1926 | 2629.6179 |  | 104.98
12.02.2008 05:00 | 3600 | 2 | 761.35 | GGB | 764.469 | 770.039 | 767.033 | 269.06 | GGB | 11037.6 | GGB | 9.83 | GGB | 1033 | GGB | 60.43 | GGB | 171771.53 | GGB | 143417.19 | GGB | 0 | 0 | 2899 | 3600 | 2883.62 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 141789.65 | GGB | 141791.24 | 2883.62 | 2635.1653 |  |  |  | 1 | 1 |  |  |  |  | 143417.19 | 2635.1653 | 143417.19 | 2635.1653 | 9.5124 | [5 empty] | 114.878 | 2635.1653 |  | 104.98
12.02.2008 06:00 | 3600 | 2 | 761.83 | GGB | 764.469 | 770.156 | 767.033 | 269.01 | GGB | 11048.6 | GGB | 9.84 | GGB | 1032.91 | GGB | 60.49 | GGB | 171631.78 | GGB | 143262.85 | GGB | 0 | 0 | 2882 | 3600 | 2866.7 | GGB | 100 | GGB | 41.42 | GGB | 41.42 | GGB | 141831.08 | GGB | 141832.66 | 2866.7 | 2638.0042 |  |  |  | 1 | 1 |  |  |  |  | 143262.85 | 2638.0042 | 143262.85 | 2638.0042 | 9.1243 | [5 empty] | 114.081 | 2638.0042 |  | 104.98
12.02.2008 07:00 | 3600 | 2 | 761.53 | GGB | 764.469 | 770.133 | 768.132 | 268.61 | GGB | 11027.5 | GGB | 9.83 | GGB | 1032.68 | GGB | 60.47 | GGB | 171365.5 | GGB | 143016.24 | GGB | 0 | 0 | 2890 | 3600 | 2874.78 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 141871.61 | GGB | 141873.19 | 2874.78 | 2642.553 |  |  |  | 1 | 1 |  |  |  |  | 143016.24 | 2642.553 | 143016.24 | 2642.553 | 9.3246 | [5 empty] | 114.2056 | 2642.553 |  | 104.98
12.02.2008 08:00 | 3600 | 2 | 761.68 | GGB | 764.469 | 770.133 | 768.132 | 268.56 | GGB | 11023.8 | GGB | 9.84 | GGB | 1032.89 | GGB | 60.53 | GGB | 171304.98 | GGB | 142968.98 | GGB | 0 | 0 | 2883 | 3600 | 2867.64 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 141912.02 | GGB | 141913.61 | 2867.64 | 2643.4266 |  |  |  | 1 | 1 |  |  |  |  | 142968.98 | 2643.4266 | 142968.98 | 2643.4266 | 9.35 | [5 empty] | 113.8843 | 2643.4266 |  | 104.98
12.02.2008 09:00 | 3600 | 2 | 761.57 | GGB | 764.835 | 770.344 | 767.033 | 268.38 | GGB | 11023.4 | GGB | 9.84 | GGB | 1032.96 | GGB | 60.58 | GGB | 171258.77 | GGB | 142920.41 | GGB | 0 | 0 | 2881 | 3600 | 2865.37 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 141952.46 | GGB | 141954.04 | 2865.37 | 2644.3249 |  |  |  | 1 | 1 |  |  |  |  | 142920.41 | 2644.3249 | 142920.41 | 2644.3249 | 9.3477 | [5 empty] | 113.7555 | 2644.3249 |  | 104.98
12.02.2008 10:00 | 3600 | 2 | 762.14 | GGB | 764.835 | 771.352 | 768.132 | 267.67 | GGB | 11017.9 | GGB | 9.84 | GGB | 1033 | GGB | 60.77 | GGB | 170472.03 | GGB | 142188.5 | GGB | 0 | 0 | 2860 | 3600 | 2844.66 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 141993.16 | GGB | 141994.75 | 2844.66 | 2657.9365 |  |  |  | 1 | 1 |  |  |  |  | 142188.5 | 2657.9365 | 142188.5 | 2657.9365 | 9.2834 | [5 empty] | 112.355 | 2657.9365 |  | 104.98
12.02.2008 11:00 | 3600 | 2 | 762.21 | GGB | 767.033 | 772.383 | 770.696 | 268 | GGB | 10978.5 | GGB | 9.83 | GGB | 1033.25 | GGB | 60.67 | GGB | 170931.97 | GGB | 142647.69 | GGB | 0 | 0 | 2843 | 3600 | 2827.79 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 142033.7 | GGB | 142035.29 | 2827.79 | 2649.3804 |  |  |  | 1 | 1 |  |  |  |  | 142647.69 | 2649.3804 | 142647.69 | 2649.3804 | 9.3223 | [5 empty] | 112.0494 | 2649.3804 |  | 104.98
12.02.2008 12:00 | 3600 | 2 | 762.95 | GGB | 765.934 | 771.258 | 769.597 | 266.05 | GGB | 10980.5 | GGB | 9.85 | GGB | 1032.89 | GGB | 61.07 | GGB | 168583.85 | GGB | 140473 | GGB | 0 | 0 | 2796 | 3600 | 2780.87 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 142073.73 | GGB | 142075.32 | 2780.87 | 2690.396 |  |  |  | 1 | 1 |  |  |  |  | 140473 | 2690.396 | 140473 | 2690.396 | 9.4411 | [5 empty] | 108.5103 | 2690.396 |  | 104.98
12.02.2008 13:00 | 3600 | 2 | 763.89 | GGB | 765.934 | 772.336 | 769.597 | 264.89 | GGB | 10945.5 | GGB | 9.85 | GGB | 1032.15 | GGB | 61.6 | GGB | 167281.05 | GGB | 139065.62 | GGB | 0 | 0 | 2756 | 3600 | 2740.73 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 142114.13 | GGB | 142115.72 | 2740.73 | 2717.6235 |  |  |  | 1 | 1 |  |  |  |  | 139065.62 | 2717.6235 | 139065.62 | 2717.6235 | 9.3547 | [5 empty] | 105.8726 | 2717.6235 |  | 104.98
12.02.2008 14:00 | 3600 | 2 | 763.96 | GGB | 765.934 | 772.242 | 769.597 | 264.5 | GGB | 10916.5 | GGB | 9.84 | GGB | 1031.9 | GGB | 61.88 | GGB | 166947.65 | GGB | 138640.09 | GGB | 0 | 0 | 2741 | 3600 | 2725.22 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 142154.31 | GGB | 142155.9 | 2725.22 | 2725.22 |  |  |  | 1 | 1 |  |  |  |  | 138640.09 | 2725.22 | 138640.09 | 2725.22 | 9.4033 | [5 empty] | 104.9513 |  |  | #VALUE!
12.02.2008 15:00 | 3600 | 2 | 763.54 | GGB | 765.934 | 772.266 | 769.597 | 264.42 | GGB | 10904.6 | GGB | 9.83 | GGB | 1031.94 | GGB | 61.6 | GGB | 166788.1 | GGB | 138628.41 | GGB | 0 | 0 | 2746 | 3600 | 2730.19 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 142194.34 | GGB | 142195.93 | 2730.19 | 2726.1944 |  |  |  | 1 | 1 |  |  |  |  | 138628.41 | 2726.1944 | 138628.41 | 2726.1944 | 9.4411 | [5 empty] | 105.1339 | 2726.1944 |  | 104.98
12.02.2008 16:00 | 3600 | 2 | 763.81 | GGB | 764.835 | 771.188 | 767.033 | 264.37 | GGB | 10908.1 | GGB | 9.84 | GGB | 1031.83 | GGB | 61.8 | GGB | 166674.76 | GGB | 138435.54 | GGB | 0 | 0 | 2730 | 3600 | 2714.11 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 142234.65 | GGB | 142236.25 | 2714.11 | 2714.11 |  |  |  | 1 | 1 |  |  |  |  | 138435.54 | 2714.11 | 138435.54 | 2714.11 | 9.3187 | [5 empty] | 104.3692 |  |  | #VALUE!
12.02.2008 17:00 | 3600 | 2 | 763.6 | GGB | 767.033 | 773.133 | 769.597 | 264.74 | GGB | 10910.2 | GGB | 9.83 | GGB | 1031.45 | GGB | 61.84 | GGB | 167095.09 | GGB | 138715.04 | GGB | 0 | 0 | 2748 | 3600 | 2732.4 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 142274.93 | GGB | 142276.53 | 2732.4 | 2724.4919 |  |  |  | 1 | 1 |  |  |  |  | 138715.04 | 2724.4919 | 138715.04 | 2724.4919 | 9.3825 | [5 empty] | 105.2847 | 2724.4919 |  | 104.98
12.02.2008 18:00 | 3600 | 2 | 763.54 | GGB | 765.934 | 772.172 | 769.597 | 264.84 | GGB | 10909.6 | GGB | 9.83 | GGB | 1031.14 | GGB | 61.73 | GGB | 167253.54 | GGB | 138853.18 | GGB | 0 | 0 | 2751 | 3600 | 2735.71 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 142315.15 | GGB | 142316.76 | 2735.71 | 2721.7814 |  |  |  | 1 | 1 |  |  |  |  | 138853.18 | 2721.7814 | 138853.18 | 2721.7814 | 9.3942 | [5 empty] | 105.5172 | 2721.7814 |  | 104.98
12.02.2008 19:00 | 3600 | 2 | 761.98 | GGB | 764.469 | 770.039 | 768.132 | 266 | GGB | 10922.3 | GGB | 9.82 | GGB | 1031.8 | GGB | 61.14 | GGB | 168363.78 | GGB | 140111.44 | GGB | 0 | 0 | 2811 | 3600 | 2795.94 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 142355.69 | GGB | 142357.29 | 2795.94 | 2697.3386 |  |  |  | 1 | 1 |  |  |  |  | 140111.44 | 2697.3386 | 140111.44 | 2697.3386 | 9.3246 | [5 empty] | 108.8175 | 2697.3386 |  | 104.98
12.02.2008 20:00 | 3600 | 2 | 763.3 | GGB | 764.835 | 771 | 768.498 | 266.21 | GGB | 10959.8 | GGB | 9.85 | GGB | 1031.58 | GGB | 61.13 | GGB | 168491.42 | GGB | 140192.17 | GGB | 0 | 0 | 2775 | 3600 | 2759.43 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 142395.43 | GGB | 142397.04 | 2759.43 | 2695.7854 |  |  |  | 1 | 1 |  |  |  |  | 140192.17 | 2695.7854 | 140192.17 | 2695.7854 | 9.5076 | [5 empty] | 107.4585 | 2695.7854 |  | 104.98
12.02.2008 21:00 | 3600 | 2 | 762.63 | GGB | 765.934 | 772.055 | 768.498 | 266 | GGB | 10925.5 | GGB | 9.83 | GGB | 1031.2 | GGB | 61.14 | GGB | 168944.76 | GGB | 140512.33 | GGB | 0 | 0 | 2785 | 3600 | 2769.82 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 142435.9 | GGB | 142437.51 | 2769.82 | 2689.643 |  |  |  | 1 | 1 |  |  |  |  | 140512.33 | 2689.643 | 140512.33 | 2689.643 | 9.3385 | [5 empty] | 108.1094 | 2689.643 |  | 104.98
12.02.2008 22:00 | 3600 | 2 | 762.49 | GGB | 764.835 | 771.961 | 768.132 | 267.49 | GGB | 10903.7 | GGB | 9.82 | GGB | 1031.07 | GGB | 60.61 | GGB | 170922.06 | GGB | 142364.4 | GGB | 0 | 0 | 2774 | 3600 | 2758.79 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 142474.86 | GGB | 142476.47 | 2758.79 | 2654.6524 |  |  |  | 1 | 1 |  |  |  |  | 142364.4 | 2654.6524 | 142364.4 | 2654.6524 | 9.7004 | [5 empty] | 109.0982 | 2654.6524 |  | 104.98
12.02.2008 23:00 | 3600 | 2 | 763.41 | GGB | 764.835 | 771.961 | 769.597 | 265.56 | GGB | 10971.6 | GGB | 9.85 | GGB | 1030.78 | GGB | 60.86 | GGB | 169655.58 | GGB | 141165.22 | GGB | 0 | 0 | 2767 | 3600 | 2751.96 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 142514.87 | GGB | 142516.48 | 2751.96 | 2677.2034 |  |  |  | 1 | 1 |  |  |  |  | 141165.22 | 2677.2034 | 141165.22 | 2677.2034 | 9.4458 | [5 empty] | 107.9114 | 2677.2034 |  | 104.98
12.02.2008 24:00 | 3600 | 2 | 761.61 | GGB | 764.835 | 770.906 | 768.132 | 266.27 | GGB | 10914.7 | GGB | 9.82 | GGB | 1030.42 | GGB | 60.63 | GGB | 169540.04 | GGB | 141113.59 | GGB | 0 | 0 | 2811 | 3600 | 2795.79 | GGB | 100 | GGB | 42.13 | GGB | 42.13 | GGB | 142557 | GGB | 142558.61 | 2795.79 | 2678.1829 |  |  |  | 1 | 1 |  |  |  |  | 141113.59 | 2678.1829 | 141113.59 | 2678.1829 | 8.9705 | [5 empty] | 109.59 | 2678.1829 |  | 104.98
13.02.2008 01:00 | 3600 | 2 | 763.14 | GGB | 765.934 | 771.938 | 769.597 | 266.97 | GGB | 10923 | GGB | 9.84 | GGB | 1030.33 | GGB | 60.12 | GGB | 170444.52 | GGB | 142071.12 | GGB | 0 | 0 | 2759 | 3600 | 2743.47 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 142596.42 | GGB | 142598.03 | 2743.47 | 2660.1325 |  |  |  | 1 | 1 |  |  |  |  | 142071.12 | 2660.1325 | 142071.12 | 2660.1325 | 9.5872 | [5 empty] | 108.2688 | 2660.1325 |  | 104.98
13.02.2008 02:00 | 3600 | 2 | 762.94 | GGB | 764.835 | 770.766 | 768.132 | 265.07 | GGB | 10937.7 | GGB | 9.84 | GGB | 1029.92 | GGB | 60.65 | GGB | 168185.52 | GGB | 139912.23 | GGB | 0 | 0 | 2776 | 3600 | 2760.08 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 142636.17 | GGB | 142637.78 | 2760.08 | 2701.1792 |  |  |  | 1 | 1 |  |  |  |  | 139912.23 | 2701.1792 | 139912.23 | 2701.1792 | 9.5076 | [5 empty] | 107.2692 | 2701.1792 |  | 104.98
13.02.2008 03:00 | 3600 | 2 | 762.44 | GGB | 765.934 | 772.805 | 769.597 | 266.01 | GGB | 10908.5 | GGB | 9.83 | GGB | 1029.83 | GGB | 60.52 | GGB | 169321.07 | GGB | 140898.56 | GGB | 0 | 0 | 2780 | 3600 | 2764.78 | GGB | 100 | GGB | 41.71 | GGB | 41.71 | GGB | 142677.88 | GGB | 142679.49 | 2764.78 | 2682.2701 |  |  |  | 1 | 1 |  |  |  |  | 140898.56 | 2682.2701 | 140898.56 | 2682.2701 | 9.0608 | [5 empty] | 108.2093 | 2682.2701 |  | 104.98
13.02.2008 04:00 | 3600 | 2 | 763.03 | GGB | 765.934 | 771.797 | 769.963 | 266.62 | GGB | 10902.3 | GGB | 9.83 | GGB | 1029.53 | GGB | 60.14 | GGB | 170247.56 | GGB | 141788.29 | GGB | 0 | 0 | 2756 | 3600 | 2740.11 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 142716.44 | GGB | 142718.04 | 2740.11 | 2665.4387 |  |  |  | 1 | 1 |  |  |  |  | 141788.29 | 2665.4387 | 141788.29 | 2665.4387 | 9.8036 | [5 empty] | 107.921 | 2665.4387 |  | 104.98
13.02.2008 05:00 | 3600 | 2 | 762.56 | GGB | 764.469 | 770.508 | 767.766 | 266.49 | GGB | 10893.4 | GGB | 9.83 | GGB | 1029.23 | GGB | 60.11 | GGB | 170289.37 | GGB | 141794.95 | GGB | 0 | 0 | 2767 | 3600 | 2751.46 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 142756.89 | GGB | 142758.49 | 2751.46 | 2665.3135 |  |  |  | 1 | 1 |  |  |  |  | 141794.95 | 2665.3135 | 141794.95 | 2665.3135 | 9.3431 | [5 empty] | 108.3731 | 2665.3135 |  | 104.98
13.02.2008 06:00 | 3600 | 2 | 762.4 | GGB | 763.37 | 770.461 | 766.667 | 266.54 | GGB | 10947.6 | GGB | 9.84 | GGB | 1028.92 | GGB | 60 | GGB | 170253.06 | GGB | 141772.4 | GGB | 0 | 0 | 2783 | 3600 | 2767.44 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 142797.71 | GGB | 142799.32 | 2767.44 | 2665.7375 |  |  |  | 0 | 1 | [14 empty] | 108.9852 | 2665.7375 |  | 104.98
13.02.2008 07:00 | 3600 | 2 | 761.47 | GGB | 764.469 | 770.555 | 767.766 | 265.96 | GGB | 10949.3 | GGB | 9.83 | GGB | 1028.59 | GGB | 60.39 | GGB | 169592.86 | GGB | 141009.85 | GGB | 0 | 0 | 2836 | 3600 | 2820.59 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 142836.25 | GGB | 142837.86 | 2820.59 | 2680.1532 |  |  |  | 1 | 1 |  |  |  |  | 141009.85 | 2680.1532 | 141009.85 | 2680.1532 | 9.8061 | [5 empty] | 110.4808 | 2680.1532 |  | 104.98
13.02.2008 08:00 | 3600 | 2 | 761.62 | GGB | 764.469 | 770.344 | 767.766 | 266.04 | GGB | 10953.7 | GGB | 9.83 | GGB | 1028.67 | GGB | 60.32 | GGB | 169603.86 | GGB | 141061.88 | GGB | 0 | 0 | 2836 | 3600 | 2820.32 | GGB | 100 | GGB | 41.6 | GGB | 41.6 | GGB | 142877.85 | GGB | 142879.46 | 2820.32 | 2679.1646 |  |  |  | 1 | 1 |  |  |  |  | 141061.88 | 2679.1646 | 141061.88 | 2679.1646 | 9.0848 | [5 empty] | 110.511 | 2679.1646 |  | 104.98
13.02.2008 09:00 | 3600 | 2 | 761.72 | GGB | 764.469 | 770.109 | 767.766 | 267.32 | GGB | 10921.1 | GGB | 9.83 | GGB | 1028.47 | GGB | 59.77 | GGB | 171596.57 | GGB | 142927 | GGB | 0 | 0 | 2805 | 3600 | 2789.28 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 142918.13 | GGB | 142919.75 | 2789.28 | 2644.203 |  |  |  | 1 | 1 |  |  |  |  | 142927 | 2644.203 | 142927 | 2644.203 | 9.3802 | [5 empty] | 110.7398 | 2644.203 |  | 104.98
13.02.2008 10:00 | 3600 | 2 | 762.29 | GGB | 765.934 | 771 | 768.864 | 265.61 | GGB | 10969.4 | GGB | 9.85 | GGB | 1027.75 | GGB | 60.12 | GGB | 169785.42 | GGB | 141170.5 | GGB | 0 | 0 | 2806 | 3600 | 2790.63 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 142956.52 | GGB | 142958.13 | 2790.63 | 2677.1032 |  |  |  | 1 | 1 |  |  |  |  | 141170.5 | 2677.1032 | 141170.5 | 2677.1032 | 9.847 | [5 empty] | 109.4318 | 2677.1032 |  | 104.98
13.02.2008 11:00 | 3600 | 2 | 761.3 | GGB | 765.934 | 771.258 | 768.864 | 266.51 | GGB | 10941 | GGB | 9.83 | GGB | 1027.17 | GGB | 59.74 | GGB | 171046.4 | GGB | 142300.96 | GGB | 0 | 0 | 2840 | 3600 | 2824.53 | GGB | 100 | GGB | 42.51 | GGB | 42.51 | GGB | 142999.02 | GGB | 143000.64 | 2824.53 | 2655.8359 |  |  |  | 1 | 1 |  |  |  |  | 142300.96 | 2655.8359 | 142300.96 | 2655.8359 | 8.8903 | [5 empty] | 111.6481 | 2655.8359 |  | 104.98
13.02.2008 12:00 | 3600 | 2 | 761.29 | GGB | 762.271 | 768.938 | 766.3 | 265.56 | GGB | 10933 | GGB | 9.83 | GGB | 1026.85 | GGB | 59.97 | GGB | 169678.68 | GGB | 141020.53 | GGB | 0 | 0 | 2831 | 3600 | 2814.99 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 143038.29 | GGB | 143039.91 | 2814.99 | 2679.9502 |  |  |  | 0 | 1 | [14 empty] | 110.2698 | 2679.9502 |  | 104.98
13.02.2008 13:00 | 3600 | 2 | 762.14 | GGB | 764.835 | 771.422 | 767.766 | 266.55 | GGB | 10910 | GGB | 9.84 | GGB | 1025.99 | GGB | 59.48 | GGB | 171016.69 | GGB | 142222.77 | GGB | 0 | 0 | 2787 | 3600 | 2771.31 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 143077.89 | GGB | 143079.52 | 2771.31 | 2657.296 |  |  |  | 1 | 1 |  |  |  |  | 142222.77 | 2657.296 | 142222.77 | 2657.296 | 9.5412 | [5 empty] | 109.4843 | 2657.296 |  | 104.98
13.02.2008 14:00 | 3600 | 2 | 762.69 | GGB | 765.934 | 771.445 | 768.864 | 265.16 | GGB | 10916.5 | GGB | 9.85 | GGB | 1025.44 | GGB | 59.89 | GGB | 169062.49 | GGB | 140348.02 | GGB | 0 | 0 | 2771 | 3600 | 2755.85 | GGB | 100 | GGB | 41.45 | GGB | 41.45 | GGB | 143119.34 | GGB | 143120.97 | 2755.85 | 2692.7918 |  |  |  | 1 | 1 |  |  |  |  | 140348.02 | 2692.7918 | 140348.02 | 2692.7918 | 9.1177 | [5 empty] | 107.4384 | 2692.7918 |  | 104.98
13.02.2008 15:00 | 3600 | 2 | 761.55 | GGB | 763.37 | 769.313 | 766.667 | 264.51 | GGB | 10896.4 | GGB | 9.83 | GGB | 1024 | GGB | 60.48 | GGB | 168112.9 | GGB | 139119.39 | GGB | 0 | 0 | 2811 | 3600 | 2795.77 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 143157.88 | GGB | 143159.51 | 2795.77 | 2716.5732 |  |  |  | 0 | 1 | [14 empty] | 108.0405 | 2716.5732 |  | 104.98
13.02.2008 16:00 | 3600 | 2 | 761.41 | GGB | 764.469 | 771.398 | 767.766 | 264.68 | GGB | 10899.7 | GGB | 9.83 | GGB | 1023.47 | GGB | 60.65 | GGB | 168196.53 | GGB | 139044.13 | GGB | 0 | 0 | 2820 | 3600 | 2803.99 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 143198.55 | GGB | 143200.18 | 2803.99 | 2718.0435 |  |  |  | 1 | 1 |  |  |  |  | 139044.13 | 2718.0435 | 139044.13 | 2718.0435 | 9.2925 | [5 empty] | 108.2995 | 2718.0435 |  | 104.98
13.02.2008 17:00 | 3600 | 2 | 761.79 | GGB | 764.469 | 770.18 | 767.766 | 264.55 | GGB | 10899 | GGB | 9.83 | GGB | 1023.09 | GGB | 60.48 | GGB | 168286.76 | GGB | 139138.51 | GGB | 0 | 0 | 2802 | 3600 | 2786.91 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 143239.42 | GGB | 143241.04 | 2786.91 | 2716.1999 |  |  |  | 1 | 1 |  |  |  |  | 139138.51 | 2716.1999 | 139138.51 | 2716.1999 | 9.2493 | [5 empty] | 107.7129 | 2716.1999 |  | 104.98
13.02.2008 18:00 | 3600 | 2 | 762.08 | GGB | 764.835 | 771.305 | 768.864 | 265.68 | GGB | 10872.4 | GGB | 9.83 | GGB | 1022.89 | GGB | 60.06 | GGB | 169839.33 | GGB | 140573.26 | GGB | 0 | 0 | 2779 | 3600 | 2763.88 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 143278.41 | GGB | 143280.03 | 2763.88 | 2688.4772 |  |  |  | 1 | 1 |  |  |  |  | 140573.26 | 2688.4772 | 140573.26 | 2688.4772 | 9.6929 | [5 empty] | 107.9243 | 2688.4772 |  | 104.98
13.02.2008 19:00 | 3600 | 2 | 762.48 | GGB | 764.835 | 771.047 | 768.864 | 264.7 | GGB | 10895.4 | GGB | 9.84 | GGB | 1023.1 | GGB | 60.3 | GGB | 168324.17 | GGB | 139243.77 | GGB | 0 | 0 | 2768 | 3600 | 2752.55 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 143318.71 | GGB | 143320.33 | 2752.55 | 2714.1466 |  |  |  | 1 | 1 |  |  |  |  | 139243.77 | 2714.1466 | 139243.77 | 2714.1466 | 9.3779 | [5 empty] | 106.4654 | 2714.1466 |  | 104.98
13.02.2008 20:00 | 3600 | 2 | 761.73 | GGB | 763.37 | 770.18 | 767.766 | 264.6 | GGB | 10882.7 | GGB | 9.83 | GGB | 1022.26 | GGB | 60.41 | GGB | 168347.27 | GGB | 139107.18 | GGB | 0 | 0 | 2799 | 3600 | 2783.57 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 143359.05 | GGB | 143360.67 | 2783.57 | 2716.8116 |  |  |  | 0 | 1 | [14 empty] | 107.5596 | 2716.8116 |  | 104.98
13.02.2008 21:00 | 3600 | 2 | 762.19 | GGB | 764.835 | 770.344 | 767.766 | 265.52 | GGB | 10859.2 | GGB | 9.83 | GGB | 1022.39 | GGB | 59.79 | GGB | 169877.84 | GGB | 140648.03 | GGB | 0 | 0 | 2766 | 3600 | 2750.62 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 143398.92 | GGB | 143400.54 | 2750.62 | 2687.0479 |  |  |  | 1 | 1 |  |  |  |  | 140648.03 | 2687.0479 | 140648.03 | 2687.0479 | 9.479 | [5 empty] | 107.4637 | 2687.0479 |  | 104.98
13.02.2008 22:00 | 3600 | 2 | 762.68 | GGB | 765.934 | 771.469 | 768.864 | 263.62 | GGB | 10895.3 | GGB | 9.85 | GGB | 1022.01 | GGB | 60.23 | GGB | 167819.11 | GGB | 138710.18 | GGB | 0 | 0 | 2761 | 3600 | 2745.76 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 143438.47 | GGB | 143440.09 | 2745.76 | 2724.5873 |  |  |  | 1 | 1 |  |  |  |  | 138710.18 | 2724.5873 | 138710.18 | 2724.5873 | 9.5557 | [5 empty] | 105.7958 | 2724.5873 |  | 104.98
13.02.2008 23:00 | 3600 | 2 | 762.31 | GGB | 764.469 | 771.469 | 767.766 | 262.76 | GGB | 10857.5 | GGB | 9.83 | GGB | 1022.71 | GGB | 60.9 | GGB | 166495.41 | GGB | 137433.34 | GGB | 0 | 0 | 2772 | 3600 | 2756.7 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 143478.54 | GGB | 143480.16 | 2756.7 | 2749.9004 |  |  |  | 1 | 1 |  |  |  |  | 137433.34 | 2749.9004 | 137433.34 | 2749.9004 | 9.4317 | [5 empty] | 105.2396 | 2749.9004 |  | 104.98
13.02.2008 24:00 | 3600 | 2 | 762.34 | GGB | 764.469 | 770.25 | 767.766 | 262.99 | GGB | 10863 | GGB | 9.83 | GGB | 1022.32 | GGB | 60.93 | GGB | 166794.7 | GGB | 137616.33 | GGB | 0 | 0 | 2768 | 3600 | 2752.26 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 143517.77 | GGB | 143519.39 | 2752.26 | 2746.2439 |  |  |  | 1 | 1 |  |  |  |  | 137616.33 | 2746.2439 | 137616.33 | 2746.2439 | 9.6336 | [5 empty] | 105.21 | 2746.2439 |  | 104.98
14.02.2008 01:00 | 3600 | 2 | 762.17 | GGB | 764.835 | 771.633 | 768.864 | 263.66 | GGB | 10884.4 | GGB | 9.83 | GGB | 1022.32 | GGB | 60.53 | GGB | 167844.42 | GGB | 138646.47 | GGB | 0 | 0 | 2790 | 3600 | 2774.27 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 143557.93 | GGB | 143559.56 | 2774.27 | 2725.8393 |  |  |  | 1 | 1 |  |  |  |  | 138646.47 | 2725.8393 | 138646.47 | 2725.8393 | 9.4082 | [5 empty] | 106.8452 | 2725.8393 |  | 104.98
14.02.2008 02:00 | 3600 | 2 | 761.12 | GGB | 764.469 | 770.555 | 767.766 | 264.58 | GGB | 10901.4 | GGB | 9.83 | GGB | 1022.65 | GGB | 60.51 | GGB | 168700.48 | GGB | 139407.06 | GGB | 0 | 0 | 2836 | 3600 | 2820.58 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 143598.18 | GGB | 143599.81 | 2820.58 | 2710.9674 |  |  |  | 1 | 1 |  |  |  |  | 139407.06 | 2710.9674 | 139407.06 | 2710.9674 | 9.3895 | [5 empty] | 109.2247 | 2710.9674 |  | 104.98
14.02.2008 03:00 | 3600 | 2 | 761.18 | GGB | 764.469 | 770.813 | 767.766 | 265.13 | GGB | 10903.9 | GGB | 9.83 | GGB | 1022.43 | GGB | 60.18 | GGB | 169709.49 | GGB | 140350.35 | GGB | 0 | 0 | 2830 | 3600 | 2814.88 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 143638.72 | GGB | 143640.34 | 2814.88 | 2692.7471 |  |  |  | 1 | 1 |  |  |  |  | 140350.35 | 2692.7471 | 140350.35 | 2692.7471 | 9.3246 | [5 empty] | 109.7415 | 2692.7471 |  | 104.98
14.02.2008 04:00 | 3600 | 2 | 760.98 | GGB | 762.271 | 768.75 | 765.201 | 266.03 | GGB | 10916.4 | GGB | 9.83 | GGB | 1022.58 | GGB | 59.5 | GGB | 171116.82 | GGB | 141823.94 | GGB | 0 | 0 | 2838 | 3600 | 2822.96 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 143678.24 | GGB | 143679.87 | 2822.96 | 2664.7687 |  |  |  | 0 | 1 | [14 empty] | 111.212 | 2664.7687 |  | 104.98
14.02.2008 05:00 | 3600 | 2 | 760.63 | GGB | 763.37 | 769.805 | 766.667 | 265.65 | GGB | 10962.4 | GGB | 9.83 | GGB | 1022.99 | GGB | 59.17 | GGB | 170806.53 | GGB | 141766.06 | GGB | 0 | 0 | 2873 | 3600 | 2857.02 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 143718.26 | GGB | 143719.89 | 2857.02 | 2665.8567 |  |  |  | 0 | 1 | [14 empty] | 112.5079 | 2665.8567 |  | 104.98
14.02.2008 06:00 | 3600 | 2 | 760.09 | GGB | 764.469 | 770.789 | 766.667 | 266.39 | GGB | 10980.3 | GGB | 9.83 | GGB | 1023.81 | GGB | 59.08 | GGB | 171698.9 | GGB | 142658.71 | GGB | 0 | 0 | 2905 | 3600 | 2889.02 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 143758.81 | GGB | 143760.44 | 2889.02 | 2649.1758 |  |  |  | 1 | 1 |  |  |  |  | 142658.71 | 2649.1758 | 142658.71 | 2649.1758 | 9.32 | [5 empty] | 114.4844 | 2649.1758 |  | 104.98
14.02.2008 07:00 | 3600 | 2 | 759.95 | GGB | 763.37 | 768.445 | 766.3 | 266.73 | GGB | 10984.5 | GGB | 9.83 | GGB | 1023.96 | GGB | 59.07 | GGB | 171804.54 | GGB | 142771.16 | GGB | 0 | 0 | 2917 | 3600 | 2901.85 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 143798.8 | GGB | 143800.42 | 2901.85 | 2647.0892 |  |  |  | 0 | 1 | [14 empty] | 115.0835 | 2647.0892 |  | 104.98
14.02.2008 08:00 | 3600 | 2 | 759.88 | GGB | 760.806 | 767.367 | 764.469 | 267.46 | GGB | 10977.3 | GGB | 9.83 | GGB | 1024.24 | GGB | 59.21 | GGB | 171916.77 | GGB | 142843.95 | GGB | 0 | 0 | 2932 | 3600 | 2916.41 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 143839.12 | GGB | 143840.75 | 2916.41 | 2645.7403 |  |  |  | 0 | 1 | [14 empty] | 115.7199 | 2645.7403 |  | 104.98
14.02.2008 09:00 | 3600 | 2 | 760.15 | GGB | 763.37 | 769.547 | 767.033 | 268.78 | GGB | 10942.9 | GGB | 9.83 | GGB | 1024.02 | GGB | 59.43 | GGB | 172364.61 | GGB | 143090.41 | GGB | 0 | 0 | 2916 | 3600 | 2900.52 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 143879.27 | GGB | 143880.89 | 2900.52 | 2641.1833 |  |  |  | 0 | 1 | [14 empty] | 115.2879 | 2641.1833 |  | 104.98
14.02.2008 10:00 | 3600 | 2 | 761 | GGB | 763.37 | 769.5 | 767.033 | 268.95 | GGB | 10935.4 | GGB | 9.83 | GGB | 1024.03 | GGB | 59.67 | GGB | 172077.42 | GGB | 142748.69 | GGB | 0 | 0 | 2876 | 3600 | 2860.72 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 143918.94 | GGB | 143920.57 | 2860.72 | 2647.5059 |  |  |  | 0 | 1 | [14 empty] | 113.4345 | 2647.5059 |  | 104.98
14.02.2008 11:00 | 3600 | 2 | 761.89 | GGB | 764.469 | 770.672 | 768.132 | 268.99 | GGB | 10915.8 | GGB | 9.84 | GGB | 1023.64 | GGB | 59.74 | GGB | 172021.3 | GGB | 142619.67 | GGB | 0 | 0 | 2823 | 3600 | 2807.17 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 143959.41 | GGB | 143961.04 | 2807.17 | 2649.901 |  |  |  | 1 | 1 |  |  |  |  | 142619.67 | 2649.901 | 142619.67 | 2649.901 | 9.3385 | [5 empty] | 111.2105 | 2649.901 |  | 104.98
14.02.2008 12:00 | 3600 | 2 | 762.27 | GGB | 764.835 | 770.766 | 768.132 | 268.12 | GGB | 10891.2 | GGB | 9.84 | GGB | 1023.34 | GGB | 60.05 | GGB | 171088.22 | GGB | 141673 | GGB | 0 | 0 | 2783 | 3600 | 2767.28 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 143999.14 | GGB | 144000.77 | 2767.28 | 2667.6078 |  |  |  | 1 | 1 |  |  |  |  | 141673 | 2667.6078 | 141673 | 2667.6078 | 9.5124 | [5 empty] | 108.9025 | 2667.6078 |  | 104.98
14.02.2008 13:00 | 3600 | 2 | 762.98 | GGB | 764.835 | 771.164 | 767.033 | 265.91 | GGB | 10900.3 | GGB | 9.85 | GGB | 1022.36 | GGB | 60.84 | GGB | 168412.19 | GGB | 138993.14 | GGB | 0 | 0 | 2767 | 3600 | 2752.02 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 144038.45 | GGB | 144040.08 | 2752.02 | 2719.0407 |  |  |  | 1 | 1 |  |  |  |  | 138993.14 | 2719.0407 | 138993.14 | 2719.0407 | 9.614 | [5 empty] | 106.2533 | 2719.0407 |  | 104.98
14.02.2008 14:00 | 3600 | 2 | 762.25 | GGB | 764.835 | 771.164 | 768.498 | 265.81 | GGB | 10868 | GGB | 9.83 | GGB | 1021.52 | GGB | 61.28 | GGB | 168142.61 | GGB | 138474.61 | GGB | 0 | 0 | 2790 | 3600 | 2774.6 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 144079.27 | GGB | 144080.89 | 2774.6 | 2729.2223 |  |  |  | 1 | 1 |  |  |  |  | 138474.61 | 2729.2223 | 138474.61 | 2729.2223 | 9.2607 | [5 empty] | 106.7255 | 2729.2223 |  | 104.98
14.02.2008 15:00 | 3600 | 2 | 763.25 | GGB | 767.033 | 773.32 | 770.696 | 264.9 | GGB | 10852.3 | GGB | 9.85 | GGB | 1020.75 | GGB | 61.23 | GGB | 167234.83 | GGB | 137642.15 | GGB | 0 | 0 | 2737 | 3600 | 2721.96 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 144118.71 | GGB | 144120.33 | 2721.96 | 2721.96 |  |  |  | 1 | 1 |  |  |  |  | 137642.15 | 2721.96 | 137642.15 | 2721.96 | 9.4994 | [5 empty] | 104.0712 |  |  | #VALUE!
14.02.2008 16:00 | 3600 | 2 | 763.46 | GGB | 765.934 | 772.523 | 769.963 | 264.27 | GGB | 10816.4 | GGB | 9.83 | GGB | 1019.66 | GGB | 61.38 | GGB | 166854.12 | GGB | 137120.56 | GGB | 0 | 0 | 2716 | 3600 | 2701 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 144158.32 | GGB | 144159.94 | 2701 | 2701 |  |  |  | 1 | 1 |  |  |  |  | 137120.56 | 2701 | 137120.56 | 2701 | 9.3502 | [5 empty] | 102.8785 |  |  | #VALUE!
14.02.2008 17:00 | 3600 | 2 | 761.66 | GGB | 765.934 | 771.609 | 768.864 | 266.99 | GGB | 10799.7 | GGB | 9.81 | GGB | 1018.93 | GGB | 60.21 | GGB | 170060.5 | GGB | 140144.18 | GGB | 0 | 0 | 2771 | 3600 | 2755.4 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 144199.25 | GGB | 144200.87 | 2755.4 | 2696.7085 |  |  |  | 1 | 1 |  |  |  |  | 140144.18 | 2696.7085 | 140144.18 | 2696.7085 | 9.2335 | [5 empty] | 107.2648 | 2696.7085 |  | 104.98
14.02.2008 18:00 | 3600 | 2 | 761.1 | GGB | 762.271 | 769.219 | 765.934 | 267.54 | GGB | 10886.2 | GGB | 9.83 | GGB | 1019.15 | GGB | 59.92 | GGB | 170474.23 | GGB | 140643.05 | GGB | 0 | 0 | 2836 | 3600 | 2820.73 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 144238.25 | GGB | 144239.87 | 2820.73 | 2687.1431 |  |  |  | 0 | 1 | [14 empty] | 110.1989 | 2687.1431 |  | 104.98
14.02.2008 19:00 | 3600 | 2 | 760.87 | GGB | 763.37 | 768.914 | 765.934 | 267.45 | GGB | 10921.8 | GGB | 9.84 | GGB | 1019.38 | GGB | 60.16 | GGB | 170289.37 | GGB | 140417.98 | GGB | 0 | 0 | 2867 | 3600 | 2851.28 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 144278.66 | GGB | 144280.29 | 2851.28 | 2691.4502 |  |  |  | 0 | 1 | [14 empty] | 111.2142 | 2691.4502 |  | 104.98
14.02.2008 20:00 | 3600 | 2 | 760.31 | GGB | 762.271 | 768.188 | 765.934 | 267.67 | GGB | 10919.3 | GGB | 9.83 | GGB | 1019.07 | GGB | 59.87 | GGB | 170863.75 | GGB | 140970.54 | GGB | 0 | 0 | 2895 | 3600 | 2879.76 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 144318.79 | GGB | 144320.42 | 2879.76 | 2680.9006 |  |  |  | 0 | 1 | [14 empty] | 112.767 | 2680.9006 |  | 104.98
14.02.2008 21:00 | 3600 | 2 | 759.99 | GGB | 762.271 | 768.938 | 765.934 | 268.41 | GGB | 10948.2 | GGB | 9.83 | GGB | 1019.06 | GGB | 59.46 | GGB | 171884.86 | GGB | 141989.11 | GGB | 0 | 0 | 2917 | 3600 | 2901.79 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 144358.87 | GGB | 144360.5 | 2901.79 | 2661.6689 |  |  |  | 0 | 1 | [14 empty] | 114.4507 | 2661.6689 |  | 104.98
14.02.2008 22:00 | 3600 | 2 | 759.67 | GGB | 761.172 | 766.758 | 764.469 | 268.04 | GGB | 10959.5 | GGB | 9.83 | GGB | 1018.98 | GGB | 59.31 | GGB | 172269.98 | GGB | 142360.15 | GGB | 0 | 0 | 2939 | 3600 | 2923.58 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 144399.03 | GGB | 144400.66 | 2923.58 | 2654.7317 |  |  |  | 0 | 1 | [14 empty] | 115.6115 | 2654.7317 |  | 104.98
14.02.2008 23:00 | 3600 | 2 | 760.02 | GGB | 763.37 | 769.102 | 765.934 | 268.59 | GGB | 10966.1 | GGB | 9.84 | GGB | 1018.92 | GGB | 59.26 | GGB | 172234.77 | GGB | 142343.86 | GGB | 0 | 0 | 2939 | 3600 | 2923.75 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 144439.49 | GGB | 144441.11 | 2923.75 | 2655.0355 |  |  |  | 0 | 1 | [14 empty] | 115.605 | 2655.0355 |  | 104.98
14.02.2008 24:00 | 3600 | 2 | 759.02 | GGB | 762.271 | 767.977 | 765.201 | 269.25 | GGB | 10973.1 | GGB | 9.83 | GGB | 1018.78 | GGB | 58.91 | GGB | 173089.73 | GGB | 143180.89 | GGB | 0 | 0 | 2987 | 3600 | 2971.28 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 144479.62 | GGB | 144481.24 | 2971.28 | 2639.5143 |  |  |  | 0 | 1 | [14 empty] | 118.1751 | 2639.5143 |  | 104.98
15.02.2008 01:00 | 3600 | 2 | 758.86 | GGB | 761.172 | 767.367 | 764.102 | 270.11 | GGB | 11000.6 | GGB | 9.83 | GGB | 1020.02 | GGB | 58.37 | GGB | 173822.56 | GGB | 144196.02 | GGB | 0 | 0 | 3009 | 3600 | 2993.55 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 144518.4 | GGB | 144520.02 | 2993.55 | 2620.9323 |  |  |  | 0 | 1 | [14 empty] | 119.905 | 2620.9323 |  | 104.98
15.02.2008 02:00 | 3600 | 2 | 759.78 | GGB | 762.271 | 768.516 | 766.3 | 269.37 | GGB | 11032.4 | GGB | 9.85 | GGB | 1019.88 | GGB | 58.47 | GGB | 173782.94 | GGB | 144099.97 | GGB | 0 | 0 | 2982 | 3600 | 2966.06 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 144559.06 | GGB | 144560.69 | 2966.06 | 2622.6792 |  |  |  | 0 | 1 | [14 empty] | 118.7248 | 2622.6792 |  | 104.98
15.02.2008 03:00 | 3600 | 2 | 758.97 | GGB | 762.271 | 768.258 | 765.201 | 269.47 | GGB | 11025.9 | GGB | 9.83 | GGB | 1020.41 | GGB | 58.23 | GGB | 174306.7 | GGB | 144715.15 | GGB | 0 | 0 | 3014 | 3600 | 2998.49 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 144600.03 | GGB | 144601.66 | 2998.49 | 2611.5303 |  |  |  | 0 | 1 | [14 empty] | 120.5353 | 2611.5303 |  | 104.98
15.02.2008 04:00 | 3600 | 2 | 759.29 | GGB | 761.172 | 767.227 | 764.102 | 269.31 | GGB | 11032.4 | GGB | 9.84 | GGB | 1020.86 | GGB | 58.26 | GGB | 174140.55 | GGB | 144626.81 | GGB | 0 | 0 | 2998 | 3600 | 2982.77 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 144640.13 | GGB | 144641.76 | 2982.77 | 2613.1255 |  |  |  | 0 | 1 | [14 empty] | 119.8301 | 2613.1255 |  | 104.98
15.02.2008 05:00 | 3600 | 2 | 759.27 | GGB | 762.271 | 768.188 | 765.201 | 269.29 | GGB | 11028.9 | GGB | 9.84 | GGB | 1021.03 | GGB | 58.43 | GGB | 173946.89 | GGB | 144415.85 | GGB | 0 | 0 | 3000 | 3600 | 2984 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 144680.72 | GGB | 144682.35 | 2984 | 2616.9427 |  |  |  | 0 | 1 | [14 empty] | 119.7047 | 2616.9427 |  | 104.98
15.02.2008 06:00 | 3600 | 2 | 758.75 | GGB | 762.271 | 767.25 | 765.201 | 269.91 | GGB | 11029.5 | GGB | 9.83 | GGB | 1021.43 | GGB | 58.27 | GGB | 174447.55 | GGB | 144957.66 | GGB | 0 | 0 | 3032 | 3600 | 3015.9 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 144721.3 | GGB | 144722.93 | 3015.9 | 2607.1613 |  |  |  | 0 | 1 | [14 empty] | 121.4383 | 2607.1613 |  | 104.98
15.02.2008 07:00 | 3600 | 2 | 758.46 | GGB | 760.806 | 766.148 | 764.102 | 270.49 | GGB | 11039.5 | GGB | 9.82 | GGB | 1021.84 | GGB | 58 | GGB | 174876.68 | GGB | 145494.3 | GGB | 0 | 0 | 3063 | 3600 | 3046.86 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 144761.42 | GGB | 144763.06 | 3046.86 | 2597.5451 |  |  |  | 0 | 1 | [14 empty] | 123.1391 | 2597.5451 |  | 104.98
15.02.2008 08:00 | 3600 | 2 | 759.2 | GGB | 761.172 | 767.813 | 764.469 | 270.38 | GGB | 11078.1 | GGB | 9.84 | GGB | 1022 | GGB | 57.79 | GGB | 175361.93 | GGB | 146009.01 | GGB | 0 | 0 | 3043 | 3206 | 3027.75 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 144801.86 | GGB | 144803.5 | 3027.75 | 2588.3882 |  |  |  | 0 | 1 | [14 empty] | 122.7997 | 2588.3882 |  | 104.98
15.02.2008 09:00 | 3600 | 2 | 758.56 | GGB | 762.271 | 767.719 | 764.835 | 271.41 | GGB | 11034.6 | GGB | 9.82 | GGB | 1022.89 | GGB | 57.36 | GGB | 176817.67 | GGB | 147542.37 | GGB | 0 | 0 | 3058 | 3600 | 3042.15 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 144842.92 | GGB | 144844.57 | 3042.15 | 2561.4879 |  |  |  | 0 | 1 | [14 empty] | 124.6795 | 2561.4879 |  | 104.98
15.02.2008 10:00 | 3600 | 2 | 760.41 | GGB | 762.271 | 767.719 | 764.835 | 271.81 | GGB | 11055.5 | GGB | 9.85 | GGB | 1023.45 | GGB | 57.33 | GGB | 177288.62 | GGB | 148031.29 | GGB | 0 | 0 | 2956 | 3600 | 2940.3 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 144882.77 | GGB | 144884.42 | 2940.3 | 2553.0278 |  |  |  | 0 | 1 | [14 empty] | 120.9046 | 2553.0278 |  | 104.98
15.02.2008 11:00 | 3600 | 2 | 760.45 | GGB | 762.271 | 768.211 | 764.835 | 270.5 | GGB | 11052 | GGB | 9.85 | GGB | 1023.91 | GGB | 58.02 | GGB | 175312.41 | GGB | 146142.82 | GGB | 0 | 0 | 2948 | 3600 | 2932.07 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 144922.95 | GGB | 144924.6 | 2932.07 | 2586.0183 |  |  |  | 0 | 1 | [14 empty] | 119.028 | 2586.0183 |  | 104.98
15.02.2008 12:00 | 3600 | 2 | 760.08 | GGB | 764.469 | 769.547 | 768.132 | 269.19 | GGB | 11032.7 | GGB | 9.84 | GGB | 1024.02 | GGB | 58.5 | GGB | 173720.22 | GGB | 144621.78 | GGB | 0 | 0 | 2970 | 3600 | 2954.27 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 144963.91 | GGB | 144965.56 | 2954.27 | 2613.2163 |  |  |  | 1 | 1 |  |  |  |  | 144621.78 | 2613.2163 | 144621.78 | 2613.2163 | 9.2268 | [5 empty] | 118.6811 | 2613.2163 |  | 104.98
15.02.2008 13:00 | 3600 | 2 | 760.57 | GGB | 764.469 | 769.57 | 767.033 | 269.05 | GGB | 11023.6 | GGB | 9.83 | GGB | 1023.68 | GGB | 58.86 | GGB | 173534.27 | GGB | 144262.2 | GGB | 0 | 0 | 2938 | 3600 | 2922.04 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 145003.67 | GGB | 145005.32 | 2922.04 | 2619.7299 |  |  |  | 1 | 1 |  |  |  |  | 144262.2 | 2619.7299 | 144262.2 | 2619.7299 | 9.5052 | [5 empty] | 117.0944 | 2619.7299 |  | 104.98
15.02.2008 14:00 | 3600 | 2 | 760.58 | GGB | 761.172 | 767.438 | 764.835 | 268.52 | GGB | 11008.7 | GGB | 9.83 | GGB | 1023.54 | GGB | 58.91 | GGB | 173018.21 | GGB | 143791.26 | GGB | 0 | 0 | 2920 | 3600 | 2904 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 145044.35 | GGB | 145046 | 2904 | 2628.31 |  |  |  | 0 | 1 | [14 empty] | 115.9916 | 2628.31 |  | 104.98
15.02.2008 15:00 | 3600 | 2 | 760.52 | GGB | 765.934 | 771.586 | 769.597 | 268.99 | GGB | 11026.3 | GGB | 9.84 | GGB | 1023.62 | GGB | 58.82 | GGB | 173396.72 | GGB | 144156.01 | GGB | 0 | 0 | 2949 | 3600 | 2932.94 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 145085.2 | GGB | 145086.85 | 2932.94 | 2621.6597 |  |  |  | 1 | 1 |  |  |  |  | 144156.01 | 2621.6597 | 144156.01 | 2621.6597 | 9.2516 | [5 empty] | 117.4447 | 2621.6597 |  | 104.98
15.02.2008 16:00 | 3600 | 2 | 760.69 | GGB | 763.37 | 769.43 | 767.033 | 268.69 | GGB | 10998.8 | GGB | 9.83 | GGB | 1023.55 | GGB | 58.87 | GGB | 173020.41 | GGB | 143811.88 | GGB | 0 | 0 | 2914 | 3600 | 2898.84 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 145124.64 | GGB | 145126.3 | 2898.84 | 2627.9331 |  |  |  | 0 | 1 | [14 empty] | 115.8021 | 2627.9331 |  | 104.98
15.02.2008 17:00 | 3600 | 2 | 760.46 | GGB | 762.271 | 768.328 | 765.934 | 269.31 | GGB | 11021.3 | GGB | 9.83 | GGB | 1023.7 | GGB | 58.59 | GGB | 173677.31 | GGB | 144498.25 | GGB | 0 | 0 | 2928 | 3600 | 2912.89 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 145165.33 | GGB | 145166.99 | 2912.89 | 2615.4504 |  |  |  | 0 | 1 | [14 empty] | 116.9188 | 2615.4504 |  | 104.98
15.02.2008 18:00 | 3600 | 2 | 759.79 | GGB | 762.271 | 768.234 | 765.934 | 270.02 | GGB | 11044.2 | GGB | 9.83 | GGB | 1023.79 | GGB | 58.38 | GGB | 174642.31 | GGB | 145408.4 | GGB | 0 | 0 | 2977 | 3600 | 2961.32 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 145206.38 | GGB | 145208.04 | 2961.32 | 2599.0796 |  |  |  | 0 | 1 | [14 empty] | 119.6113 | 2599.0796 |  | 104.98
15.02.2008 19:00 | 3600 | 2 | 759.17 | GGB | 762.271 | 767.273 | 765.934 | 271.13 | GGB | 11071 | GGB | 9.83 | GGB | 1023.94 | GGB | 58.16 | GGB | 175642.51 | GGB | 146359.04 | GGB | 0 | 0 | 3035 | 3600 | 3019.56 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 145246.09 | GGB | 145247.75 | 3019.56 | 2582.1979 |  |  |  | 0 | 1 | [14 empty] | 122.7611 | 2582.1979 |  | 104.98
15.02.2008 20:00 | 3600 | 2 | 758.93 | GGB | 762.271 | 767.438 | 764.469 | 271.49 | GGB | 11075.4 | GGB | 9.83 | GGB | 1024.35 | GGB | 58.06 | GGB | 175618.31 | GGB | 146443.97 | GGB | 0 | 0 | 3045 | 3600 | 3029.1 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 145287.25 | GGB | 145288.92 | 3029.1 | 2580.7003 |  |  |  | 0 | 1 | [14 empty] | 123.2204 | 2580.7003 |  | 104.98
15.02.2008 21:00 | 3600 | 2 | 759.64 | GGB | 761.172 | 766.453 | 764.835 | 271.44 | GGB | 11082.7 | GGB | 9.83 | GGB | 1024.8 | GGB | 58.11 | GGB | 175553.39 | GGB | 146428.94 | GGB | 0 | 0 | 3026 | 3600 | 3010.63 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 145327.76 | GGB | 145329.43 | 3010.63 | 2580.9652 |  |  |  | 0 | 1 | [14 empty] | 122.4565 | 2580.9652 |  | 104.98
15.02.2008 22:00 | 3600 | 2 | 758.31 | GGB | 763.37 | 768.586 | 765.934 | 274.43 | GGB | 11065.4 | GGB | 9.81 | GGB | 1025.44 | GGB | 56.88 | GGB | 179029.35 | GGB | 149980.41 | GGB | 0 | 0 | 3083 | 3600 | 3067.17 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 145367.58 | GGB | 145369.24 | 3067.17 | 2519.8491 |  |  |  | 0 | 1 | [14 empty] | 127.7821 | 2519.8491 |  | 104.98
15.02.2008 23:00 | 3600 | 2 | 758.63 | GGB | 762.271 | 767.32 | 764.835 | 275.33 | GGB | 11136.1 | GGB | 9.83 | GGB | 1026.73 | GGB | 56.41 | GGB | 180138.49 | GGB | 151313.58 | GGB | 0 | 0 | 3094 | 3600 | 3078.37 | GGB | 100 | GGB | 41.47 | GGB | 41.47 | GGB | 145409.05 | GGB | 145410.71 | 3078.37 | 2497.6476 |  |  |  | 0 | 1 | [14 empty] | 129.3887 | 2497.6476 |  | 104.98
15.02.2008 24:00 | 3600 | 2 | 758.01 | GGB | 759.707 | 765.141 | 763.37 | 275.35 | GGB | 11196.7 | GGB | 9.83 | GGB | 1028.13 | GGB | 56.54 | GGB | 179884.32 | GGB | 151247.31 | GGB | 0 | 0 | 3168 | 3600 | 3151.71 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 145449.4 | GGB | 145451.06 | 3151.71 | 2498.742 |  |  |  | 0 | 1 | [14 empty] | 132.4132 | 2498.742 |  | 104.98
16.02.2008 01:00 | 3600 | 2 | 757.28 | GGB | 760.806 | 766.125 | 763.37 | 275.98 | GGB | 11225.1 | GGB | 9.83 | GGB | 1029.22 | GGB | 56.39 | GGB | 180793.19 | GGB | 152241.09 | GGB | 0 | 0 | 3225 | 3600 | 3209.14 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 145489.64 | GGB | 145491.3 | 3209.14 | 2482.431 |  |  |  | 0 | 1 | [14 empty] | 135.7119 | 2482.431 |  | 104.98
16.02.2008 02:00 | 3600 | 2 | 757.79 | GGB | 759.707 | 766.055 | 763.37 | 275.74 | GGB | 11230.8 | GGB | 9.84 | GGB | 1030.08 | GGB | 56.68 | GGB | 180675.46 | GGB | 152137.83 | GGB | 0 | 0 | 3211 | 3600 | 3195.4 | GGB | 100 | GGB | 41.62 | GGB | 41.62 | GGB | 145531.26 | GGB | 145532.92 | 3195.4 | 2484.1159 |  |  |  | 0 | 1 | [14 empty] | 135.0392 | 2484.1159 |  | 104.98
16.02.2008 03:00 | 3600 | 2 | 757.25 | GGB | 761.172 | 767.484 | 763.37 | 276.11 | GGB | 11244.9 | GGB | 9.83 | GGB | 1030.58 | GGB | 56.23 | GGB | 181208.02 | GGB | 152864.54 | GNB | 0 | 0 | 3253 | 3600 | 3236.78 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 145571.95 | GGB | 145573.61 | 3236.78 | 2472.3065 |  |  |  | 0 | 1 | [14 empty] | 137.4414 | 2472.3065 |  | 104.98
16.02.2008 04:00 | 3600 | 2 | 757.18 | GGB | 760.806 | 766.477 | 763.37 | 276.23 | GGB | 11241.7 | GGB | 9.83 | GGB | 1031.55 | GGB | 56.36 | GGB | 181145.3 | GGB | 152897.53 | GNB | 0 | 0 | 3253 | 3600 | 3237.02 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 145612.7 | GGB | 145614.36 | 3237.02 | 2471.7731 |  |  |  | 0 | 1 | [14 empty] | 137.4812 | 2471.7731 |  | 104.98
16.02.2008 05:00 | 3600 | 2 | 758.08 | GGB | 760.806 | 766.148 | 763.37 | 274.7 | GGB | 11251.4 | GGB | 9.84 | GGB | 1032.79 | GGB | 56.33 | GGB | 180526.91 | GGB | 152574.1 | GGB | 0 | 0 | 3201 | 3600 | 3185.62 | GGB | 100 | GGB | 41.81 | GGB | 41.81 | GGB | 145654.5 | GGB | 145656.17 | 3185.62 | 2477.0128 |  |  |  | 0 | 1 | [14 empty] | 135.012 | 2477.0128 |  | 104.98
16.02.2008 06:00 | 3600 | 2 | 758.15 | GGB | 761.172 | 767.414 | 763.37 | 275.69 | GGB | 11248.8 | GGB | 9.84 | GGB | 1033.78 | GGB | 56.46 | GGB | 180660.05 | GGB | 152768.38 | GNB | 0 | 0 | 3207 | 3600 | 3191.31 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 145695.64 | GGB | 145697.31 | 3191.31 | 2473.8627 |  |  |  | 0 | 1 | [14 empty] | 135.4253 | 2473.8627 |  | 104.98
16.02.2008 07:00 | 3600 | 2 | 757.53 | GGB | 762.271 | 768.586 | 764.835 | 277.34 | GGB | 11232.9 | GGB | 9.82 | GGB | 1034.85 | GGB | 56.02 | GGB | 182814.52 | GGB | 154961.43 | GNB | 0 | 0 | 3233 | 3600 | 3216.75 | GGB | 100 | GGB | 41.25 | GGB | 41.25 | GGB | 145736.9 | GGB | 145738.56 | 3216.75 | 2438.852 |  |  |  | 0 | 1 | [14 empty] | 138.4645 | 2438.852 |  | 104.98
16.02.2008 08:00 | 3600 | 2 | 758.13 | GGB | 762.271 | 767.016 | 764.469 | 277.87 | GGB | 11281.7 | GGB | 9.84 | GGB | 1035.81 | GGB | 55.74 | GGB | 183454.91 | GGB | 155777.93 | GNB | 0 | 0 | 3220 | 3600 | 3203.94 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 145778.13 | GGB | 145779.79 | 3203.94 | 2426.069 |  |  |  | 0 | 1 | [14 empty] | 138.6398 | 2426.069 |  | 104.98
16.02.2008 09:00 | 3600 | 2 | 758.26 | GGB | 761.172 | 766.945 | 763.37 | 276.88 | GGB | 11309.7 | GGB | 9.84 | GGB | 1036.92 | GGB | 56.37 | GGB | 181991.46 | GGB | 154404.52 | GNB | 0 | 0 | 3231 | 3600 | 3215.16 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 145818.82 | GGB | 145820.48 | 3215.16 | 2447.6486 |  |  |  | 0 | 1 | [14 empty] | 137.8987 | 2447.6486 |  | 104.98
16.02.2008 10:00 | 3600 | 2 | 758.92 | GGB | 763.37 | 768.258 | 764.835 | 275.5 | GGB | 11279.6 | GGB | 9.84 | GGB | 1037.9 | GGB | 56.68 | GGB | 180436.69 | GGB | 153089.3 | GNB | 0 | 0 | 3186 | 3600 | 3170.42 | GGB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 145860.7 | GGB | 145862.36 | 3170.42 | 2468.6768 |  |  |  | 0 | 1 | [14 empty] | 134.8215 | 2468.6768 |  | 104.98
16.02.2008 11:00 | 3600 | 2 | 758.95 | GGB | 762.271 | 768.023 | 764.469 | 275.45 | GGB | 11251.5 | GGB | 9.83 | GGB | 1038.29 | GGB | 56.8 | GGB | 179905.22 | GGB | 152640.84 | GGB | 0 | 0 | 3164 | 3600 | 3148.38 | GGB | 100 | GGB | 41.44 | GGB | 41.44 | GGB | 145902.14 | GGB | 145903.8 | 3148.38 | 2475.9298 |  |  |  | 0 | 1 | [14 empty] | 133.492 | 2475.9298 |  | 104.98
16.02.2008 12:00 | 3600 | 2 | 760.21 | GGB | 762.271 | 767.977 | 764.835 | 274.65 | GGB | 11248.8 | GGB | 9.85 | GGB | 1038.63 | GGB | 57.25 | GGB | 179230.72 | GGB | 151909.04 | GGB | 0 | 0 | 3097 | 3600 | 3080.83 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 145942.09 | GGB | 145943.75 | 3080.83 | 2487.8572 |  |  |  | 0 | 1 | [14 empty] | 130.0016 | 2487.8572 |  | 104.98
16.02.2008 13:00 | 3600 | 2 | 760.5 | GGB | 763.37 | 770.016 | 767.033 | 273.99 | GGB | 11224.4 | GGB | 9.84 | GGB | 1038.62 | GGB | 57.76 | GGB | 178225.01 | GGB | 150822.45 | GGB | 0 | 0 | 3067 | 3600 | 3051.6 | GGB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 145983.42 | GGB | 145985.08 | 3051.6 | 2505.7808 |  |  |  | 0 | 1 | [14 empty] | 127.8472 | 2505.7808 |  | 104.98
16.02.2008 14:00 | 3600 | 2 | 760.82 | GGB | 764.469 | 770.016 | 767.033 | 273.27 | GGB | 11197.4 | GGB | 9.84 | GGB | 1038.44 | GGB | 58.14 | GGB | 177403.05 | GGB | 149928.05 | GGB | 0 | 0 | 3027 | 3600 | 3011.35 | GGB | 100 | GGB | 41.8 | GGB | 41.8 | GGB | 146025.22 | GGB | 146026.88 | 3011.35 | 2520.7291 |  |  |  | 1 | 1 |  |  |  |  | 149928.05 | 2520.7291 | 149928.05 | 2520.7291 | 9.0413 | [5 empty] | 125.4127 | 2520.7291 |  | 104.98
16.02.2008 15:00 | 3600 | 2 | 761.29 | GGB | 764.835 | 771.844 | 768.498 | 273.1 | GGB | 11172.3 | GGB | 9.84 | GGB | 1037.86 | GGB | 58.47 | GGB | 176779.16 | GGB | 149167.45 | GGB | 0 | 0 | 2990 | 3600 | 2974.5 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 146065.61 | GGB | 146067.26 | 2974.5 | 2533.5822 |  |  |  | 1 | 1 |  |  |  |  | 149167.45 | 2533.5822 | 149167.45 | 2533.5822 | 9.3593 | [5 empty] | 123.2496 | 2533.5822 |  | 104.98
16.02.2008 16:00 | 3600 | 2 | 761.66 | GGB | 764.835 | 770.789 | 768.132 | 272.12 | GGB | 11158.8 | GGB | 9.84 | GGB | 1037.34 | GGB | 58.77 | GGB | 176006.73 | GGB | 148311.36 | GGB | 0 | 0 | 2957 | 3600 | 2941.06 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 146106.92 | GGB | 146108.57 | 2941.06 | 2548.2067 |  |  |  | 1 | 1 |  |  |  |  | 148311.36 | 2548.2067 | 148311.36 | 2548.2067 | 9.1486 | [5 empty] | 121.1646 | 2548.2067 |  | 104.98
16.02.2008 17:00 | 3600 | 2 | 760.48 | GGB | 764.469 | 770.813 | 767.033 | 274.14 | GGB | 11111 | GGB | 9.81 | GGB | 1037.51 | GGB | 58.35 | GGB | 178086.36 | GGB | 150277.14 | GGB | 0 | 0 | 3003 | 3600 | 2987.18 | GGB | 100 | GGB | 41.68 | GGB | 41.68 | GGB | 146148.6 | GGB | 146150.25 | 2987.18 | 2514.8735 |  |  |  | 1 | 1 |  |  |  |  | 150277.14 | 2514.8735 | 150277.14 | 2514.8735 | 9.0674 | [5 empty] | 124.6958 | 2514.8735 |  | 104.98
16.02.2008 18:00 | 3600 | 2 | 761.57 | GGB | 762.271 | 768.492 | 765.934 | 274.26 | GGB | 11163.4 | GGB | 9.84 | GGB | 1037.85 | GGB | 58.36 | GGB | 177744.16 | GGB | 150032.99 | GGB | 0 | 0 | 2966 | 3600 | 2950.87 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 146188.3 | GGB | 146189.96 | 2950.87 | 2518.966 |  |  |  | 0 | 1 | [14 empty] | 122.98 | 2518.966 |  | 104.98
16.02.2008 19:00 | 3600 | 2 | 760.28 | GGB | 764.469 | 769.477 | 767.033 | 275.01 | GGB | 11149 | GGB | 9.82 | GGB | 1038.22 | GGB | 58.07 | GGB | 178399.96 | GGB | 150772.22 | GGB | 0 | 0 | 3032 | 3600 | 3015.99 | GGB | 100 | GGB | 41.93 | GGB | 41.93 | GGB | 146230.24 | GGB | 146231.89 | 3015.99 | 2506.6156 |  |  |  | 1 | 1 |  |  |  |  | 150772.22 | 2506.6156 | 150772.22 | 2506.6156 | 9.0133 | [5 empty] | 126.3132 | 2506.6156 |  | 104.98
16.02.2008 20:00 | 3600 | 2 | 760.84 | GGB | 763.37 | 769.453 | 765.934 | 275.75 | GGB | 11185.9 | GGB | 9.84 | GGB | 1038.15 | GGB | 57.89 | GGB | 179050.26 | GGB | 151393.44 | GGB | 0 | 0 | 3013 | 3600 | 2997.56 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 146271.65 | GGB | 146273.3 | 2997.56 | 2496.3301 |  |  |  | 0 | 1 | [14 empty] | 126.0586 | 2496.3301 |  | 104.98
16.02.2008 21:00 | 3600 | 2 | 759.1 | GGB | 762.271 | 768.07 | 765.934 | 274.63 | GGB | 11217.9 | GGB | 9.82 | GGB | 1038.16 | GGB | 57.59 | GGB | 179232.92 | GGB | 151687.66 | GGB | 0 | 0 | 3117 | 3600 | 3101.02 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 146312.09 | GGB | 146313.74 | 3101.02 | 2491.4881 |  |  |  | 0 | 1 | [14 empty] | 130.6629 | 2491.4881 |  | 104.98
16.02.2008 22:00 | 3600 | 2 | 759.34 | GGB | 759.707 | 765.141 | 762.271 | 276.38 | GGB | 11227.8 | GGB | 9.83 | GGB | 1037.69 | GGB | 58 | GGB | 179594.93 | GGB | 151735.3 | GGB | 0 | 0 | 3129 | 3600 | 3113.15 | GGB | 100 | GGB | 41.58 | GGB | 41.58 | GGB | 146353.67 | GGB | 146355.32 | 3113.15 | 2490.7059 |  |  |  | 0 | 1 | [14 empty] | 131.2152 | 2490.7059 |  | 104.98
16.02.2008 23:00 | 3600 | 2 | 758.88 | GGB | 761.172 | 767.18 | 764.102 | 277.21 | GGB | 11257 | GGB | 9.84 | GGB | 1037.37 | GGB | 57.73 | GGB | 180628.14 | GGB | 152686.03 | GNB | 0 | 0 | 3175 | 3600 | 3159.43 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 146394.7 | GGB | 146396.35 | 3159.43 | 2475.197 |  |  |  | 0 | 1 | [14 empty] | 134.0002 | 2475.197 |  | 104.98
16.02.2008 24:00 | 3600 | 2 | 758.5 | GGB | 762.271 | 767.203 | 764.102 | 277.22 | GGB | 11260.6 | GGB | 9.83 | GGB | 1036.83 | GGB | 57.28 | GGB | 181060.58 | GGB | 153178.96 | GNB | 0 | 0 | 3196 | 3600 | 3180.15 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 146435.04 | GGB | 146436.69 | 3180.15 | 2467.2318 |  |  |  | 0 | 1 | [14 empty] | 135.3145 | 2467.2318 |  | 104.98
17.02.2008 01:00 | 3600 | 2 | 758.75 | GGB | 761.172 | 766.453 | 764.102 | 277.19 | GGB | 11263.3 | GGB | 9.84 | GGB | 1036.25 | GGB | 57.37 | GGB | 181107.89 | GGB | 153093.71 | GNB | 0 | 0 | 3187 | 3600 | 3171.2 | GGB | 100 | GGB | 42.32 | GGB | 42.32 | GGB | 146477.36 | GGB | 146479.01 | 3171.2 | 2468.6057 |  |  |  | 0 | 1 | [14 empty] | 134.8585 | 2468.6057 |  | 104.98
17.02.2008 02:00 | 3600 | 2 | 759.34 | GGB | 763.37 | 769.898 | 766.3 | 276.55 | GGB | 11260.1 | GGB | 9.85 | GGB | 1035.19 | GGB | 57.59 | GGB | 180496.1 | GGB | 152319.54 | GGB | 0 | 0 | 3158 | 3600 | 3142.37 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 146517.76 | GGB | 146519.41 | 3142.37 | 2481.1525 |  |  |  | 0 | 1 | [14 empty] | 132.9568 | 2481.1525 |  | 104.98
17.02.2008 03:00 | 3600 | 2 | 759.63 | GGB | 765.934 | 771.234 | 768.864 | 275.2 | GGB | 11226.4 | GGB | 9.85 | GGB | 1033.82 | GGB | 57.79 | GGB | 179262.63 | GGB | 150983.36 | GGB | 0 | 0 | 3113 | 3600 | 3096.78 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 146558.48 | GGB | 146560.13 | 3096.78 | 2503.1103 |  |  |  | 1 | 1 |  |  |  |  | 150983.36 | 2503.1103 | 150983.36 | 2503.1103 | 9.2811 | [5 empty] | 129.8784 | 2503.1103 |  | 104.98
17.02.2008 04:00 | 3600 | 2 | 760.29 | GGB | 764.469 | 770.836 | 767.766 | 273.45 | GGB | 11181.1 | GGB | 9.85 | GGB | 1032.28 | GGB | 58.18 | GGB | 177552.7 | GGB | 149148.46 | GGB | 0 | 0 | 3049 | 3600 | 3033.21 | GGB | 100 | GGB | 42.36 | GGB | 42.36 | GGB | 146600.83 | GGB | 146602.49 | 3033.21 | 2533.9048 |  |  |  | 1 | 1 |  |  |  |  | 149148.46 | 2533.9048 | 149148.46 | 2533.9048 | 8.9218 | [5 empty] | 125.6663 | 2533.9048 |  | 104.98
17.02.2008 05:00 | 3600 | 2 | 760.72 | GGB | 764.469 | 769.547 | 767.766 | 271.58 | GGB | 11132.1 | GGB | 9.85 | GGB | 1030.26 | GGB | 58.29 | GGB | 175828.47 | GGB | 147359.22 | GGB | 0 | 0 | 2993 | 3600 | 2977.58 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 146640.64 | GGB | 146642.3 | 2977.58 | 2564.6716 |  |  |  | 1 | 1 |  |  |  |  | 147359.22 | 2564.6716 | 147359.22 | 2564.6716 | 9.4933 | [5 empty] | 121.8816 | 2564.6716 |  | 104.98
17.02.2008 06:00 | 3600 | 2 | 761.48 | GGB | 767.033 | 772.781 | 768.864 | 270.13 | GGB | 11092.8 | GGB | 9.85 | GGB | 1028.33 | GGB | 58.58 | GGB | 174232.98 | GGB | 145621.57 | GGB | 0 | 0 | 2935 | 3600 | 2919.05 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 146681.78 | GGB | 146683.43 | 2919.05 | 2595.2749 |  |  |  | 1 | 1 |  |  |  |  | 145621.57 | 2595.2749 | 145621.57 | 2595.2749 | 9.1886 | [5 empty] | 118.0768 | 2595.2749 |  | 104.98
17.02.2008 07:00 | 3600 | 2 | 761.78 | GGB | 764.835 | 771.773 | 768.864 | 268.89 | GGB | 11034.2 | GGB | 9.84 | GGB | 1026.68 | GGB | 58.79 | GGB | 172777.23 | GGB | 144083.52 | GGB | 0 | 0 | 2890 | 3600 | 2874.78 | GGB | 100 | GGB | 41.45 | GGB | 41.45 | GGB | 146723.22 | GGB | 146724.88 | 2874.78 | 2622.9787 |  |  |  | 1 | 1 |  |  |  |  | 144083.52 | 2622.9787 | 144083.52 | 2622.9787 | 9.1177 | [5 empty] | 115.0579 | 2622.9787 |  | 104.98
17.02.2008 08:00 | 3600 | 2 | 762.17 | GGB | 764.835 | 770.883 | 768.864 | 267.96 | GGB | 11010.6 | GGB | 9.84 | GGB | 1025.03 | GGB | 59.05 | GGB | 171766.02 | GGB | 142898.79 | GGB | 0 | 0 | 2866 | 3600 | 2850.85 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 146762.43 | GGB | 146764.09 | 2850.85 | 2644.725 |  |  |  | 1 | 1 |  |  |  |  | 142898.79 | 2644.725 | 142898.79 | 2644.725 | 9.6386 | [5 empty] | 113.1619 | 2644.725 |  | 104.98
17.02.2008 09:00 | 3600 | 2 | 762.61 | GGB | 764.835 | 770.906 | 767.766 | 266.44 | GGB | 10995.8 | GGB | 9.84 | GGB | 1023.67 | GGB | 59.09 | GGB | 171025.5 | GGB | 142073.72 | GGB | 0 | 0 | 2835 | 3600 | 2819.08 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 146803.81 | GGB | 146805.47 | 2819.08 | 2660.0838 |  |  |  | 1 | 1 |  |  |  |  | 142073.72 | 2660.0838 | 142073.72 | 2660.0838 | 9.1331 | [5 empty] | 111.2548 | 2660.0838 |  | 104.98
17.02.2008 10:00 | 3600 | 2 | 763.74 | GGB | 765.934 | 773.086 | 769.963 | 264.17 | GGB | 10978.6 | GGB | 9.85 | GGB | 1021.83 | GGB | 59.02 | GGB | 169629.17 | GGB | 140693.11 | GGB | 0 | 0 | 2774 | 3600 | 2758.25 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 146844.96 | GGB | 146846.62 | 2758.25 | 2686.187 |  |  |  | 1 | 1 |  |  |  |  | 140693.11 | 2686.187 | 140693.11 | 2686.187 | 9.1842 | [5 empty] | 107.7963 | 2686.187 |  | 104.98
17.02.2008 11:00 | 3600 | 2 | 763.85 | GGB | 765.934 | 771.914 | 768.864 | 262.36 | GGB | 10926.3 | GGB | 9.84 | GGB | 1020.15 | GGB | 59 | GGB | 168198.73 | GGB | 139285.18 | GGB | 0 | 0 | 2736 | 3600 | 2720.2 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 146884.36 | GGB | 146886.01 | 2720.2 | 2713.3396 |  |  |  | 1 | 1 |  |  |  |  | 139285.18 | 2713.3396 | 139285.18 | 2713.3396 | 9.5945 | [5 empty] | 105.2454 | 2713.3396 |  | 104.98
17.02.2008 12:00 | 3600 | 2 | 763.31 | GGB | 765.934 | 772.031 | 769.963 | 262.47 | GGB | 10886.5 | GGB | 9.83 | GGB | 1019.04 | GGB | 58.77 | GGB | 168406.69 | GGB | 139403.66 | GGB | 0 | 0 | 2737 | 3600 | 2721.53 | GGB | 100 | GGB | 41.84 | GGB | 41.84 | GGB | 146926.2 | GGB | 146927.85 | 2721.53 | 2711.0336 |  |  |  | 1 | 1 |  |  |  |  | 139403.66 | 2711.0336 | 139403.66 | 2711.0336 | 9.0327 | [5 empty] | 105.3865 | 2711.0336 |  | 104.98
17.02.2008 13:00 | 3600 | 2 | 763.66 | GGB | 765.934 | 770.93 | 767.766 | 263.48 | GGB | 10872.7 | GGB | 9.83 | GGB | 1018.33 | GGB | 58.54 | GGB | 169666.58 | GGB | 140442.69 | GGB | 0 | 0 | 2706 | 3600 | 2690.1 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 146965.56 | GGB | 146967.21 | 2690.1 | 2690.1 |  |  |  | 1 | 1 |  |  |  |  | 140442.69 | 2690.1 | 140442.69 | 2690.1 | 9.5987 | [5 empty] | 104.9458 |  |  | #VALUE!
17.02.2008 14:00 | 3600 | 2 | 763.11 | GGB | 764.835 | 772.219 | 768.864 | 263.31 | GGB | 10914.7 | GGB | 9.84 | GGB | 1017.01 | GGB | 58.95 | GGB | 168696.08 | GGB | 139287.53 | GGB | 0 | 0 | 2760 | 3600 | 2744.3 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 147005.06 | GGB | 147006.71 | 2744.3 | 2713.2939 |  |  |  | 1 | 1 |  |  |  |  | 139287.53 | 2713.2939 | 139287.53 | 2713.2939 | 9.5678 | [5 empty] | 106.1797 | 2713.2939 |  | 104.98
17.02.2008 15:00 | 3600 | 2 | 763.43 | GGB | 765.934 | 772.219 | 768.864 | 262.52 | GGB | 10885.5 | GGB | 9.84 | GGB | 1016.14 | GGB | 59.2 | GGB | 167911.54 | GGB | 138415.92 | GGB | 0 | 0 | 2735 | 3600 | 2719.62 | GGB | 100 | GGB | 41.46 | GGB | 41.46 | GGB | 147046.52 | GGB | 147048.17 | 2719.62 | 2719.62 |  |  |  | 1 | 1 |  |  |  |  | 138415.92 | 2719.62 | 138415.92 | 2719.62 | 9.0796 | [5 empty] | 104.5663 |  |  | #VALUE!
17.02.2008 16:00 | 3600 | 2 | 763.29 | GGB | 764.835 | 772.266 | 768.864 | 262.19 | GGB | 10872.2 | GGB | 9.83 | GGB | 1015.16 | GGB | 59.23 | GGB | 167453.8 | GGB | 137895.69 | GGB | 0 | 0 | 2732 | 3600 | 2717.05 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 147085.11 | GGB | 147086.75 | 2717.05 | 2717.05 |  |  |  | 1 | 1 |  |  |  |  | 137895.69 | 2717.05 | 137895.69 | 2717.05 | 9.7115 | [5 empty] | 104.0749 |  |  | #VALUE!
17.02.2008 17:00 | 3600 | 2 | 763.41 | GGB | 764.835 | 772.266 | 768.864 | 261.96 | GGB | 10871.1 | GGB | 9.84 | GGB | 1014.04 | GGB | 59.18 | GGB | 167442.8 | GGB | 137754.49 | GGB | 0 | 0 | 2729 | 3600 | 2713.44 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 147125.81 | GGB | 147127.46 | 2713.44 | 2713.44 |  |  |  | 1 | 1 |  |  |  |  | 137754.49 | 2713.44 | 137754.49 | 2713.44 | 9.1817 | [5 empty] | 103.8302 |  |  | #VALUE!
17.02.2008 18:00 | 3600 | 2 | 762.97 | GGB | 767.033 | 773.156 | 771.429 | 262.32 | GGB | 10849 | GGB | 9.83 | GGB | 1013.84 | GGB | 59.02 | GGB | 168079.89 | GGB | 138315.43 | GGB | 0 | 0 | 2724 | 3600 | 2708.45 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 147166.26 | GGB | 147167.91 | 2708.45 | 2708.45 |  |  |  | 1 | 1 |  |  |  |  | 138315.43 | 2708.45 | 138315.43 | 2708.45 | 9.2613 | [5 empty] | 104.0612 |  |  | #VALUE!
17.02.2008 19:00 | 3600 | 2 | 763.18 | GGB | 765.934 | 771 | 768.864 | 261.85 | GGB | 10862.9 | GGB | 9.83 | GGB | 1013.7 | GGB | 59.08 | GGB | 167073.08 | GGB | 137446.16 | GGB | 0 | 0 | 2731 | 3600 | 2715.09 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 147204.97 | GGB | 147206.62 | 2715.09 | 2715.09 |  |  |  | 1 | 1 |  |  |  |  | 137446.16 | 2715.09 | 137446.16 | 2715.09 | 9.6404 | [5 empty] | 103.6607 |  |  | #VALUE!
17.02.2008 20:00 | 3600 | 2 | 762.69 | GGB | 765.934 | 772.242 | 768.864 | 261.52 | GGB | 10873.1 | GGB | 9.84 | GGB | 1013.53 | GGB | 58.97 | GGB | 167464.8 | GGB | 137789.05 | GGB | 0 | 0 | 2749 | 3600 | 2733.73 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 147245.6 | GGB | 147247.25 | 2733.73 | 2733.73 |  |  |  | 1 | 1 |  |  |  |  | 137789.05 | 2733.73 | 137789.05 | 2733.73 | 9.2709 | [5 empty] | 104.6328 |  |  | #VALUE!
17.02.2008 21:00 | 3600 | 2 | 763.03 | GGB | 764.835 | 770.953 | 768.864 | 261.48 | GGB | 10848.4 | GGB | 9.83 | GGB | 1012.57 | GGB | 59.24 | GGB | 167077.48 | GGB | 137226.78 | GGB | 0 | 0 | 2733 | 3600 | 2717.58 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 147285.62 | GGB | 147287.27 | 2717.58 | 2717.58 |  |  |  | 1 | 1 |  |  |  |  | 137226.78 | 2717.58 | 137226.78 | 2717.58 | 9.3185 | [5 empty] | 103.5902 |  |  | #VALUE!
17.02.2008 22:00 | 3600 | 2 | 763.14 | GGB | 764.835 | 772.172 | 768.864 | 261.34 | GGB | 10844.5 | GGB | 9.84 | GGB | 1012.7 | GGB | 59.31 | GGB | 166602.14 | GGB | 136828.4 | GGB | 0 | 0 | 2732 | 3600 | 2716.45 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 147325.21 | GGB | 147326.85 | 2716.45 | 2716.45 |  |  |  | 1 | 1 |  |  |  |  | 136828.4 | 2716.45 | 136828.4 | 2716.45 | 9.3908 | [5 empty] | 103.2465 |  |  | #VALUE!
17.02.2008 23:00 | 3600 | 2 | 763.14 | GGB | 765.934 | 771.398 | 768.864 | 261.82 | GGB | 10818.9 | GGB | 9.83 | GGB | 1012.52 | GGB | 59.59 | GGB | 166919.04 | GGB | 136948.08 | GGB | 0 | 0 | 2715 | 3600 | 2699.51 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 147365.49 | GGB | 147367.13 | 2699.51 | 2699.51 |  |  |  | 1 | 1 |  |  |  |  | 136948.08 | 2699.51 | 136948.08 | 2699.51 | 9.1781 | [5 empty] | 102.6924 |  |  | #VALUE!
17.02.2008 24:00 | 3600 | 2 | 764.09 | GGB | 765.934 | 772.547 | 768.864 | 262.45 | GGB | 10791.4 | GGB | 9.84 | GGB | 1012.03 | GGB | 59.36 | GGB | 167870.83 | GGB | 137757.72 | GGB | 0 | 0 | 2665 | 3600 | 2649.91 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 147404.47 | GGB | 147406.11 | 2649.91 | 2649.91 |  |  |  | 1 | 1 |  |  |  |  | 137757.72 | 2649.91 | 137757.72 | 2649.91 | 9.3649 | [5 empty] | 101.4015 |  |  | #VALUE!
18.02.2008 01:00 | 3600 | 2 | 764.25 | GGB | 767.033 | 772.5 | 769.963 | 260.56 | GGB | 10803.8 | GGB | 9.84 | GGB | 1011.87 | GGB | 60.16 | GGB | 165322.45 | GGB | 135320.58 | GGB | 0 | 0 | 2667 | 3600 | 2651.86 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 147444.39 | GGB | 147446.03 | 2651.86 | 2651.86 |  |  |  | 1 | 1 |  |  |  |  | 135320.58 | 2651.86 | 135320.58 | 2651.86 | 8.9893 | [5 empty] | 99.6809 |  |  | #VALUE!
18.02.2008 02:00 | 3600 | 2 | 764.02 | GGB | 765.934 | 772.805 | 769.963 | 260.42 | GGB | 10786.6 | GGB | 9.83 | GGB | 1011.56 | GGB | 60.45 | GGB | 164820.69 | GGB | 134751.43 | GGB | 0 | 0 | 2673 | 3600 | 2657.57 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 147484.36 | GGB | 147486 | 2657.57 | 2657.57 |  |  |  | 1 | 1 |  |  |  |  | 134751.43 | 2657.57 | 134751.43 | 2657.57 | 8.9595 | [5 empty] | 99.4754 |  |  | #VALUE!
18.02.2008 03:00 | 3600 | 2 | 764.08 | GGB | 765.934 | 772.711 | 769.963 | 260.28 | GGB | 10786.8 | GGB | 9.84 | GGB | 1011.06 | GGB | 60.55 | GGB | 164625.93 | GGB | 134483.15 | GGB | 0 | 0 | 2670 | 3600 | 2654.74 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 147523.33 | GGB | 147524.97 | 2654.74 | 2654.74 |  |  |  | 1 | 1 |  |  |  |  | 134483.15 | 2654.74 | 134483.15 | 2654.74 | 9.1613 | [5 empty] | 99.1716 |  |  | #VALUE!
18.02.2008 04:00 | 3600 | 2 | 764.17 | GGB | 765.934 | 772.711 | 769.963 | 260.12 | GGB | 10778.8 | GGB | 9.83 | GGB | 1010.49 | GGB | 60.67 | GGB | 164329.94 | GGB | 134118.34 | GGB | 0 | 0 | 2668 | 3600 | 2652.5 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 147563.74 | GGB | 147565.38 | 2652.5 | 2652.5 |  |  |  | 1 | 1 |  |  |  |  | 134118.34 | 2652.5 | 134118.34 | 2652.5 | 8.8035 | [5 empty] | 98.8191 |  |  | #VALUE!
18.02.2008 05:00 | 3600 | 2 | 764.1 | GGB | 765.934 | 772.523 | 768.864 | 260.03 | GGB | 10772 | GGB | 9.83 | GGB | 1010.81 | GGB | 60.64 | GGB | 164395.96 | GGB | 134227.71 | GGB | 0 | 0 | 2668 | 3600 | 2652.17 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 147603.17 | GGB | 147604.81 | 2652.17 | 2652.17 |  |  |  | 1 | 1 |  |  |  |  | 134227.71 | 2652.17 | 134227.71 | 2652.17 | 9.0285 | [5 empty] | 98.8874 |  |  | #VALUE!
18.02.2008 06:00 | 3600 | 2 | 764.24 | GGB | 765.934 | 772.781 | 769.963 | 260.18 | GGB | 10768.7 | GGB | 9.83 | GGB | 1010.5 | GGB | 60.79 | GGB | 164436.67 | GGB | 134158.33 | GGB | 0 | 0 | 2660 | 3600 | 2644.15 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 147641.68 | GGB | 147643.33 | 2644.15 | 2644.15 |  |  |  | 1 | 1 |  |  |  |  | 134158.33 | 2644.15 | 134158.33 | 2644.15 | 9.2091 | [5 empty] | 98.5374 |  |  | #VALUE!
18.02.2008 07:00 | 3600 | 2 | 764.56 | GGB | 767.033 | 773.977 | 770.33 | 259.94 | GGB | 10772.1 | GGB | 9.84 | GGB | 1010.14 | GGB | 61.05 | GGB | 164271.62 | GGB | 133870.33 | GGB | 0 | 0 | 2646 | 3600 | 2630.31 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 147683.19 | GGB | 147684.84 | 2630.31 | 2630.31 |  |  |  | 1 | 1 |  |  |  |  | 133870.33 | 2630.31 | 133870.33 | 2630.31 | 8.4828 | [5 empty] | 97.8112 |  |  | #VALUE!
18.02.2008 08:00 | 3600 | 2 | 764.27 | GGB | 767.033 | 773.203 | 769.963 | 260.05 | GGB | 10758.9 | GGB | 9.83 | GGB | 1010.48 | GGB | 61.27 | GGB | 164348.65 | GGB | 133890.53 | GGB | 0 | 0 | 2652 | 3600 | 2637.05 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 147721.38 | GGB | 147723.03 | 2637.05 | 2637.05 |  |  |  | 1 | 1 |  |  |  |  | 133890.53 | 2637.05 | 133890.53 | 2637.05 | 9.2452 | [5 empty] | 98.0767 |  |  | #VALUE!
18.02.2008 09:00 | 3600 | 2 | 764.24 | GGB | 767.033 | 772.922 | 769.963 | 260.46 | GGB | 10762.9 | GGB | 9.83 | GGB | 1010.59 | GGB | 61.26 | GGB | 164644.64 | GGB | 134152.18 | GGB | 0 | 0 | 2664 | 3600 | 2648.55 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 147761.09 | GGB | 147762.75 | 2648.55 | 2648.55 |  |  |  | 1 | 1 |  |  |  |  | 134152.18 | 2648.55 | 134152.18 | 2648.55 | 8.9453 | [5 empty] | 98.6969 |  |  | #VALUE!
18.02.2008 10:00 | 3600 | 2 | 764.37 | GGB | 765.934 | 771.938 | 769.963 | 260.12 | GGB | 10764.3 | GGB | 9.83 | GGB | 1010.23 | GGB | 61.24 | GGB | 164376.16 | GGB | 133892.17 | GGB | 0 | 0 | 2657 | 3600 | 2642.01 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 147801.12 | GGB | 147802.78 | 2642.01 | 2642.01 |  |  |  | 1 | 1 |  |  |  |  | 133892.17 | 2642.01 | 133892.17 | 2642.01 | 8.837 | [5 empty] | 98.2623 |  |  | #VALUE!
18.02.2008 11:00 | 3600 | 2 | 764.55 | GGB | 767.033 | 772.898 | 770.33 | 259.9 | GGB | 10758.8 | GGB | 9.84 | GGB | 1010.01 | GGB | 61.22 | GGB | 164314.54 | GGB | 133820.96 | GGB | 0 | 0 | 2648 | 3600 | 2632.29 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 147839.72 | GGB | 147841.39 | 2632.29 | 2632.29 |  |  |  | 1 | 1 |  |  |  |  | 133820.96 | 2632.29 | 133820.96 | 2632.29 | 9.1234 | [5 empty] | 97.8488 |  |  | #VALUE!
18.02.2008 12:00 | 3600 | 2 | 764.53 | GGB | 767.033 | 774.07 | 771.429 | 260.63 | GGB | 10729 | GGB | 9.83 | GGB | 1010.26 | GGB | 61 | GGB | 165338.95 | GGB | 134777.99 | GGB | 0 | 0 | 2635 | 3600 | 2620.05 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 147880.84 | GGB | 147882.5 | 2620.05 | 2620.05 |  |  |  | 1 | 1 |  |  |  |  | 134777.99 | 2620.05 | 134777.99 | 2620.05 | 8.5898 | [5 empty] | 98.0903 |  |  | #VALUE!
18.02.2008 13:00 | 3600 | 2 | 765.01 | GGB | 765.934 | 772.852 | 769.963 | 259.84 | GGB | 10735.8 | GGB | 9.84 | GGB | 1009.84 | GGB | 60.99 | GGB | 164564.31 | GGB | 134093.28 | GGB | 0 | 0 | 2612 | 3600 | 2597.03 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 147919.32 | GGB | 147920.98 | 2597.03 | 2597.03 |  |  |  | 1 | 1 |  |  |  |  | 134093.28 | 2597.03 | 134093.28 | 2597.03 | 9.05 | [5 empty] | 96.7345 |  |  | #VALUE!
18.02.2008 14:00 | 3600 | 2 | 764.99 | GGB | 767.033 | 773.836 | 770.33 | 260.31 | GGB | 10704.8 | GGB | 9.83 | GGB | 1009.75 | GGB | 60.97 | GGB | 165219.01 | GGB | 134623.14 | GGB | 0 | 0 | 2598 | 3600 | 2582.89 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 147958.37 | GGB | 147960.03 | 2582.89 | 2582.89 |  |  |  | 1 | 1 |  |  |  |  | 134623.14 | 2582.89 | 134623.14 | 2582.89 | 8.9044 | [5 empty] | 96.588 |  |  | #VALUE!
18.02.2008 15:00 | 3600 | 2 | 765.32 | GGB | 767.033 | 773.813 | 771.429 | 259.8 | GGB | 10703.3 | GGB | 9.84 | GGB | 1009.1 | GGB | 60.95 | GGB | 164522.5 | GGB | 133975.78 | GGB | 0 | 0 | 2579 | 3600 | 2563.92 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 147999.12 | GGB | 148000.78 | 2563.92 | 2563.92 |  |  |  | 1 | 1 |  |  |  |  | 133975.78 | 2563.92 | 133975.78 | 2563.92 | 8.4295 | [5 empty] | 95.4176 |  |  | #VALUE!
18.02.2008 16:00 | 3600 | 2 | 765.04 | GGB | 767.033 | 772.875 | 770.33 | 258.39 | GGB | 10702.6 | GGB | 9.83 | GGB | 1008.31 | GGB | 61.59 | GGB | 162941.32 | GGB | 132331.56 | GGB | 0 | 0 | 2600 | 3600 | 2584.96 | GGB | 100 | GGB | 37.25 | GGB | 37.25 | GGB | 148036.37 | GGB | 148038.03 | 2584.96 | 2584.96 |  |  |  | 1 | 1 |  |  |  |  | 132331.56 | 2584.96 | 132331.56 | 2584.96 | 9.1831 | [5 empty] | 95.0199 |  |  | #VALUE!
18.02.2008 17:00 | 3600 | 2 | 765.33 | GGB | 767.033 | 774 | 770.33 | 259.07 | GGB | 10668.5 | GGB | 9.83 | GGB | 1008.48 | GGB | 60.98 | GGB | 164055.96 | GGB | 133503.62 | GGB | 0 | 0 | 2561 | 3600 | 2546.04 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 148077.59 | GGB | 148079.25 | 2546.04 | 2546.04 |  |  |  | 1 | 1 |  |  |  |  | 133503.62 | 2546.04 | 133503.62 | 2546.04 | 8.2461 | [5 empty] | 94.4182 |  |  | #VALUE!
18.02.2008 18:00 | 3600 | 2 | 765.8 | GGB | 767.033 | 775.055 | 771.429 | 258.82 | GGB | 10670.5 | GGB | 9.84 | GGB | 1008.44 | GGB | 60.93 | GGB | 163845.79 | GGB | 133346.34 | GGB | 0 | 0 | 2549 | 3600 | 2534.03 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 148115.99 | GGB | 148117.65 | 2534.03 | 2534.03 |  |  |  | 1 | 1 |  |  |  |  | 133346.34 | 2534.03 | 133346.34 | 2534.03 | 8.7996 | [5 empty] | 93.8621 |  |  | #VALUE!
18.02.2008 19:00 | 3600 | 2 | 765.03 | GGB | 768.132 | 774.07 | 771.429 | 257.95 | GGB | 10705.9 | GGB | 9.84 | GGB | 1008.36 | GGB | 61.42 | GGB | 162638.72 | GGB | 132161.03 | GGB | 0 | 0 | 2594 | 3600 | 2578.78 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 148154.51 | GGB | 148156.17 | 2578.78 | 2578.78 |  |  |  | 1 | 1 |  |  |  |  | 132161.03 | 2578.78 | 132161.03 | 2578.78 | 8.8477 | [5 empty] | 94.6706 |  |  | #VALUE!
18.02.2008 20:00 | 3600 | 2 | 764.88 | GGB | 765.934 | 773.156 | 770.33 | 258.15 | GGB | 10706.8 | GGB | 9.83 | GGB | 1008.13 | GGB | 61.61 | GGB | 162609.01 | GGB | 132029.33 | GGB | 0 | 0 | 2603 | 3600 | 2587.81 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 148195.66 | GGB | 148197.32 | 2587.81 | 2587.81 |  |  |  | 1 | 1 |  |  |  |  | 132029.33 | 2587.81 | 132029.33 | 2587.81 | 8.303 | [5 empty] | 94.9075 |  |  | #VALUE!
18.02.2008 21:00 | 3600 | 2 | 764.39 | GGB | 765.934 | 771.984 | 769.963 | 257.87 | GGB | 10704.2 | GGB | 9.83 | GGB | 1007.7 | GGB | 60.62 | GGB | 163752.26 | GGB | 133296.93 | GGB | 0 | 0 | 2610 | 3600 | 2594.78 | GGB | 100 | GGB | 37.71 | GGB | 37.71 | GGB | 148233.37 | GGB | 148235.03 | 2594.78 | 2594.78 |  |  |  | 1 | 1 |  |  |  |  | 133296.93 | 2594.78 | 133296.93 | 2594.78 | 9.172 | [5 empty] | 96.0767 |  |  | #VALUE!
18.02.2008 22:00 | 3600 | 2 | 764.99 | GGB | 768.132 | 773.953 | 771.429 | 258.63 | GGB | 10703.4 | GGB | 9.84 | GGB | 1006.8 | GGB | 60.56 | GGB | 163999.84 | GGB | 133404.67 | GGB | 0 | 0 | 2583 | 3600 | 2567.72 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 148273.37 | GGB | 148275.04 | 2567.72 | 2567.72 |  |  |  | 1 | 1 |  |  |  |  | 133404.67 | 2567.72 | 133404.67 | 2567.72 | 8.5615 | [5 empty] | 95.1516 |  |  | #VALUE!
18.02.2008 23:00 | 3600 | 2 | 764.28 | GGB | 767.033 | 772.875 | 769.963 | 257.81 | GGB | 10703.7 | GGB | 9.83 | GGB | 1006.5 | GGB | 61.08 | GGB | 162924.81 | GGB | 132283.25 | GGB | 0 | 0 | 2622 | 3600 | 2606.22 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 148312.38 | GGB | 148314.05 | 2606.22 | 2606.22 |  |  |  | 1 | 1 |  |  |  |  | 132283.25 | 2606.22 | 132283.25 | 2606.22 | 8.8377 | [5 empty] | 95.7665 |  |  | #VALUE!
18.02.2008 24:00 | 3600 | 2 | 764.51 | GGB | 765.934 | 772.852 | 769.963 | 258.91 | GGB | 10681.2 | GGB | 9.83 | GGB | 1006.86 | GGB | 60.52 | GGB | 164806.39 | GGB | 134082.94 | GGB | 0 | 0 | 2590 | 3600 | 2574.68 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 148351 | GGB | 148352.67 | 2574.68 | 2574.68 |  |  |  | 1 | 1 |  |  |  |  | 134082.94 | 2574.68 | 134082.94 | 2574.68 | 8.9389 | [5 empty] | 95.8946 |  |  | #VALUE!
19.02.2008 01:00 | 3600 | 2 | 764.73 | GGB | 767.033 | 772.969 | 770.33 | 258.52 | GGB | 10709.1 | GGB | 9.84 | GGB | 1006.51 | GGB | 60.55 | GGB | 164317.84 | GGB | 133627.55 | GGB | 0 | 0 | 2599 | 3600 | 2583.51 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 148392.15 | GGB | 148393.82 | 2583.51 | 2583.51 |  |  |  | 1 | 1 |  |  |  |  | 133627.55 | 2583.51 | 133627.55 | 2583.51 | 8.3895 | [5 empty] | 95.8967 |  |  | #VALUE!
19.02.2008 02:00 | 3600 | 2 | 763.99 | GGB | 764.835 | 772.195 | 768.864 | 257.6 | GGB | 10714.4 | GGB | 9.83 | GGB | 1006.62 | GGB | 60.66 | GGB | 163311.03 | GGB | 132780.08 | GGB | 0 | 0 | 2633 | 3600 | 2617.26 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 148430.23 | GGB | 148431.9 | 2617.26 | 2617.26 |  |  |  | 1 | 1 |  |  |  |  | 132780.08 | 2617.26 | 132780.08 | 2617.26 | 9.1261 | [5 empty] | 96.5333 |  |  | #VALUE!
19.02.2008 03:00 | 3600 | 2 | 764.23 | GGB | 765.934 | 773.133 | 770.33 | 257.5 | GGB | 10726.3 | GGB | 9.84 | GGB | 1006.47 | GGB | 60.73 | GGB | 163226.3 | GGB | 132664.53 | GGB | 0 | 0 | 2627 | 3600 | 2611.66 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 148470.18 | GGB | 148471.85 | 2611.66 | 2611.66 |  |  |  | 1 | 1 |  |  |  |  | 132664.53 | 2611.66 | 132664.53 | 2611.66 | 8.6727 | [5 empty] | 96.243 |  |  | #VALUE!
19.02.2008 04:00 | 3600 | 2 | 764.39 | GGB | 767.033 | 773.32 | 769.963 | 257.96 | GGB | 10686 | GGB | 9.83 | GGB | 1006.02 | GGB | 60.81 | GGB | 164002.04 | GGB | 133202.45 | GGB | 0 | 0 | 2610 | 3600 | 2594.8 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 148510.55 | GGB | 148512.22 | 2594.8 | 2594.8 |  |  |  | 1 | 1 |  |  |  |  | 133202.45 | 2594.8 | 133202.45 | 2594.8 | 8.5616 | [5 empty] | 96.0094 |  |  | #VALUE!
19.02.2008 05:00 | 3600 | 2 | 764.03 | GGB | 764.835 | 771.703 | 767.766 | 258.14 | GGB | 10712.1 | GGB | 9.83 | GGB | 1006.48 | GGB | 60.86 | GGB | 164310.14 | GGB | 133492.04 | GGB | 0 | 0 | 2636 | 3600 | 2620.97 | GGB | 100 | GGB | 37.68 | GGB | 37.68 | GGB | 148548.23 | GGB | 148549.9 | 2620.97 | 2620.97 |  |  |  | 1 | 1 |  |  |  |  | 133492.04 | 2620.97 | 133492.04 | 2620.97 | 9.2855 | [5 empty] | 97.1885 |  |  | #VALUE!
19.02.2008 06:00 | 3600 | 2 | 764.27 | GGB | 765.934 | 772.898 | 769.963 | 259.13 | GGB | 10714.1 | GGB | 9.83 | GGB | 1007.32 | GGB | 60.39 | GGB | 165288.34 | GGB | 134589.93 | GGB | 0 | 0 | 2617 | 3600 | 2601.75 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 148589.01 | GGB | 148590.69 | 2601.75 | 2601.75 |  |  |  | 1 | 1 |  |  |  |  | 134589.93 | 2601.75 | 134589.93 | 2601.75 | 8.5847 | [5 empty] | 97.2693 |  |  | #VALUE!
19.02.2008 07:00 | 3600 | 2 | 763.77 | GGB | 765.934 | 771.68 | 768.864 | 258.82 | GGB | 10746.1 | GGB | 9.83 | GGB | 1007.93 | GGB | 60.55 | GGB | 164625.93 | GGB | 134067.19 | GGB | 0 | 0 | 2658 | 3600 | 2643.06 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 148628.18 | GGB | 148629.85 | 2643.06 | 2643.06 |  |  |  | 1 | 1 |  |  |  |  | 134067.19 | 2643.06 | 134067.19 | 2643.06 | 9.0487 | [5 empty] | 98.4299 |  |  | #VALUE!
19.02.2008 08:00 | 3600 | 2 | 763.46 | GGB | 765.934 | 772.688 | 769.963 | 259.99 | GGB | 10755.3 | GGB | 9.83 | GGB | 1008.89 | GGB | 60.19 | GGB | 166005.76 | GGB | 135465.42 | GGB | 0 | 0 | 2673 | 3600 | 2658.09 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 148667.36 | GGB | 148669.03 | 2658.09 | 2658.09 |  |  |  | 1 | 1 |  |  |  |  | 135465.42 | 2658.09 | 135465.42 | 2658.09 | 9.1904 | [5 empty] | 100.022 |  |  | #VALUE!
19.02.2008 09:00 | 3600 | 2 | 763.16 | GGB | 763.37 | 769.617 | 767.766 | 260.54 | GGB | 10769.8 | GGB | 9.82 | GGB | 1010.32 | GGB | 59.74 | GGB | 166969.65 | GGB | 136629.58 | GGB | 0 | 0 | 2674 | 3600 | 2658.63 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 148707.13 | GGB | 148708.8 | 2658.63 | 2658.63 |  |  |  | 0 | 1 | [14 empty] | 100.9021 |  |  | #VALUE!
19.02.2008 10:00 | 3600 | 2 | 763.52 | GGB | 763.37 | 770.719 | 767.766 | 261.05 | GGB | 10822.7 | GGB | 9.84 | GGB | 1011.11 | GGB | 59.37 | GGB | 167997.37 | GGB | 137732.32 | GGB | 0 | 0 | 2673 | 3600 | 2658.11 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 148746.7 | GGB | 148748.37 | 2658.11 | 2658.11 |  |  |  | 0 | 1 | [14 empty] | 101.6966 |  |  | #VALUE!
19.02.2008 11:00 | 3600 | 2 | 762.74 | GGB | 764.469 | 771.68 | 767.766 | 260.29 | GGB | 10850.8 | GGB | 9.83 | GGB | 1012.21 | GGB | 59.3 | GGB | 167921.44 | GGB | 137846.78 | GGB | 0 | 0 | 2725 | 3600 | 2709.58 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 148786.17 | GGB | 148787.84 | 2709.58 | 2709.58 |  |  |  | 1 | 1 |  |  |  |  | 137846.78 | 2709.58 | 137846.78 | 2709.58 | 9.4631 | [5 empty] | 103.7519 |  |  | #VALUE!
19.02.2008 12:00 | 3600 | 2 | 762.5 | GGB | 764.835 | 771.398 | 768.864 | 260.62 | GGB | 10865.7 | GGB | 9.84 | GGB | 1013.25 | GGB | 59.01 | GGB | 168569.54 | GGB | 138641.98 | GGB | 0 | 0 | 2716 | 3600 | 2700.9 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 148826.64 | GGB | 148828.32 | 2700.9 | 2700.9 |  |  |  | 1 | 1 |  |  |  |  | 138641.98 | 2700.9 | 138641.98 | 2700.9 | 9.2504 | [5 empty] | 104.0161 |  |  | #VALUE!
19.02.2008 13:00 | 3600 | 2 | 762.14 | GGB | 764.835 | 772.125 | 768.864 | 261.35 | GGB | 10859.2 | GGB | 9.83 | GGB | 1013.92 | GGB | 59.34 | GGB | 168130.51 | GGB | 138235.18 | GGB | 0 | 0 | 2720 | 3600 | 2704.71 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 148866.05 | GGB | 148867.73 | 2704.71 | 2704.71 |  |  |  | 1 | 1 |  |  |  |  | 138235.18 | 2704.71 | 138235.18 | 2704.71 | 9.4871 | [5 empty] | 103.8572 |  |  | #VALUE!
19.02.2008 14:00 | 3600 | 2 | 762.57 | GGB | 764.835 | 772.219 | 768.864 | 261.77 | GGB | 10850.3 | GGB | 9.83 | GGB | 1015.26 | GGB | 59.76 | GGB | 167826.81 | GGB | 137994.2 | GGB | 0 | 0 | 2713 | 3600 | 2697.38 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 148905.75 | GGB | 148907.43 | 2697.38 | 2697.38 |  |  |  | 1 | 1 |  |  |  |  | 137994.2 | 2697.38 | 137994.2 | 2697.38 | 9.3759 | [5 empty] | 103.3952 |  |  | #VALUE!
19.02.2008 15:00 | 3600 | 2 | 763.03 | GGB | 765.934 | 773.625 | 771.429 | 262.62 | GGB | 10839 | GGB | 9.83 | GGB | 1015.24 | GGB | 59.97 | GGB | 168571.74 | GGB | 138518.35 | GGB | 0 | 0 | 2691 | 3600 | 2675.86 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 148945.91 | GGB | 148947.6 | 2675.86 | 2675.86 |  |  |  | 1 | 1 |  |  |  |  | 138518.35 | 2675.86 | 138518.35 | 2675.86 | 9.2272 | [5 empty] | 102.9599 |  |  | #VALUE!
19.02.2008 16:00 | 3600 | 2 | 763.61 | GGB | 764.835 | 771.328 | 768.864 | 263.62 | GGB | 10806.3 | GGB | 9.82 | GGB | 1015.95 | GGB | 59.71 | GGB | 169847.03 | GGB | 139771.78 | GGB | 0 | 0 | 2657 | 3600 | 2642.04 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 148985.35 | GGB | 148987.03 | 2642.04 | 2642.04 |  |  |  | 1 | 1 |  |  |  |  | 139771.78 | 2642.04 | 139771.78 | 2642.04 | 9.3655 | [5 empty] | 102.5785 |  |  | #VALUE!
19.02.2008 17:00 | 3600 | 2 | 763.99 | GGB | 765.934 | 772.477 | 769.597 | 263.13 | GGB | 10863.6 | GGB | 9.84 | GGB | 1016.35 | GGB | 59.92 | GGB | 169061.39 | GGB | 139093.24 | GGB | 0 | 0 | 2667 | 3600 | 2651.39 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 149024.8 | GGB | 149026.49 | 2651.39 | 2651.39 |  |  |  | 1 | 1 |  |  |  |  | 139093.24 | 2651.39 | 139093.24 | 2651.39 | 9.3459 | [5 empty] | 102.4418 |  |  | #VALUE!
19.02.2008 18:00 | 3600 | 2 | 763.11 | GGB | 764.835 | 771.469 | 768.498 | 263.2 | GGB | 10860.4 | GGB | 9.83 | GGB | 1016.94 | GGB | 60.39 | GGB | 168408.89 | GGB | 138441.96 | GGB | 0 | 0 | 2714 | 3600 | 2698.61 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 149065.18 | GGB | 149066.87 | 2698.61 | 2698.61 |  |  |  | 1 | 1 |  |  |  |  | 138441.96 | 2698.61 | 138441.96 | 2698.61 | 9.2521 | [5 empty] | 103.778 |  |  | #VALUE!
19.02.2008 19:00 | 3600 | 2 | 762.61 | GGB | 764.835 | 771.469 | 768.498 | 263.82 | GGB | 10873.4 | GGB | 9.83 | GGB | 1017.5 | GGB | 60.48 | GGB | 168795.11 | GGB | 138795.48 | GGB | 0 | 0 | 2740 | 3600 | 2724.85 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 149104.9 | GGB | 149106.59 | 2724.85 | 2722.9129 |  |  |  | 1 | 1 |  |  |  |  | 138795.48 | 2722.9129 | 138795.48 | 2722.9129 | 9.5148 | [5 empty] | 105.0547 | 2722.9129 |  | 104.98
19.02.2008 20:00 | 3600 | 2 | 761.97 | GGB | 763.37 | 770.461 | 767.033 | 265 | GGB | 10870.7 | GGB | 9.82 | GGB | 1017.64 | GGB | 60.16 | GGB | 170165.03 | GGB | 140075.27 | GGB | 0 | 0 | 2761 | 3600 | 2745.64 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 149144.45 | GGB | 149146.15 | 2745.64 | 2698.0351 |  |  |  | 0 | 1 | [14 empty] | 106.8323 | 2698.0351 |  | 104.98
19.02.2008 21:00 | 3600 | 2 | 761.92 | GGB | 764.469 | 770.508 | 768.132 | 267.16 | GGB | 10893.7 | GGB | 9.83 | GGB | 1017.97 | GGB | 59.27 | GGB | 172626.49 | GGB | 142530.26 | GGB | 0 | 0 | 2777 | 3600 | 2761.27 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 149184.81 | GGB | 149186.51 | 2761.27 | 2651.5633 |  |  |  | 1 | 1 |  |  |  |  | 142530.26 | 2651.5633 | 142530.26 | 2651.5633 | 9.3639 | [5 empty] | 109.3235 | 2651.5633 |  | 104.98
19.02.2008 22:00 | 3600 | 2 | 761.79 | GGB | 764.835 | 770.484 | 768.132 | 265.51 | GGB | 10956.7 | GGB | 9.84 | GGB | 1018.39 | GGB | 59.53 | GGB | 171518.45 | GGB | 141563.3 | GGB | 0 | 0 | 2815 | 3600 | 2799.28 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 149223.52 | GGB | 149225.22 | 2799.28 | 2669.675 |  |  |  | 1 | 1 |  |  |  |  | 141563.3 | 2669.675 | 141563.3 | 2669.675 | 9.7631 | [5 empty] | 110.0765 | 2669.675 |  | 104.98
19.02.2008 23:00 | 3600 | 2 | 760.7 | GGB | 762.271 | 768.516 | 765.934 | 266.24 | GGB | 10942.2 | GGB | 9.82 | GGB | 1018.44 | GGB | 59.56 | GGB | 171435.92 | GGB | 141490.1 | GGB | 0 | 0 | 2868 | 3600 | 2852.61 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 149264.59 | GGB | 149266.29 | 2852.61 | 2671.0561 |  |  |  | 0 | 1 | [14 empty] | 112.1156 | 2671.0561 |  | 104.98
19.02.2008 24:00 | 3600 | 2 | 760.83 | GGB | 764.469 | 770.391 | 767.033 | 266.86 | GGB | 10961.2 | GGB | 9.83 | GGB | 1018.75 | GGB | 59.51 | GGB | 172223.76 | GGB | 142204.99 | GGB | 0 | 0 | 2877 | 3600 | 2861.54 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 149304.32 | GGB | 149306.01 | 2861.54 | 2657.6283 |  |  |  | 1 | 1 |  |  |  |  | 142204.99 | 2657.6283 | 142204.99 | 2657.6283 | 9.5148 | [5 empty] | 113.0348 | 2657.6283 |  | 104.98
20.02.2008 01:00 | 3600 | 2 | 761.01 | GGB | 764.469 | 769.523 | 767.033 | 268.09 | GGB | 10936.9 | GGB | 9.83 | GGB | 1019.15 | GGB | 59 | GGB | 173908.38 | GGB | 143872.57 | GGB | 0 | 0 | 2856 | 3600 | 2840.65 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 149344.99 | GGB | 149346.68 | 2840.65 | 2626.8246 |  |  |  | 1 | 1 |  |  |  |  | 143872.57 | 2626.8246 | 143872.57 | 2626.8246 | 9.2925 | [5 empty] | 113.5254 | 2626.8246 |  | 104.98
20.02.2008 02:00 | 3600 | 2 | 761.64 | GGB | 763.37 | 769.102 | 765.934 | 267.11 | GGB | 10978.7 | GGB | 9.84 | GGB | 1018.42 | GGB | 58.99 | GGB | 172661.7 | GGB | 142740.32 | GGB | 0 | 0 | 2854 | 3600 | 2838.23 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 149384.96 | GGB | 149386.65 | 2838.23 | 2647.6612 |  |  |  | 0 | 1 | [14 empty] | 112.5361 | 2647.6612 |  | 104.98
20.02.2008 03:00 | 3600 | 2 | 761.3 | GGB | 764.835 | 771.211 | 768.498 | 266.2 | GGB | 10960.7 | GGB | 9.84 | GGB | 1018.04 | GGB | 59.16 | GGB | 172000.4 | GGB | 142071.74 | GGB | 0 | 0 | 2861 | 3600 | 2845.4 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 149424.94 | GGB | 149426.63 | 2845.4 | 2660.1209 |  |  |  | 1 | 1 |  |  |  |  | 142071.74 | 2660.1209 | 142071.74 | 2660.1209 | 9.4529 | [5 empty] | 112.2919 | 2660.1209 |  | 104.98
20.02.2008 04:00 | 3600 | 2 | 761.72 | GGB | 764.835 | 771.234 | 768.132 | 267.07 | GGB | 10915.4 | GGB | 9.83 | GGB | 1017.67 | GGB | 58.8 | GGB | 173239.38 | GGB | 143195.91 | GGB | 0 | 0 | 2817 | 3600 | 2801.92 | GGB | 100 | GGB | 41.83 | GGB | 41.83 | GGB | 149466.77 | GGB | 149468.46 | 2801.92 | 2639.2374 |  |  |  | 1 | 1 |  |  |  |  | 143195.91 | 2639.2374 | 143195.91 | 2639.2374 | 9.0349 | [5 empty] | 111.451 | 2639.2374 |  | 104.98
20.02.2008 05:00 | 3600 | 2 | 762.76 | GGB | 767.033 | 772.195 | 769.597 | 265.99 | GGB | 10932.1 | GGB | 9.85 | GGB | 1017.45 | GGB | 59.12 | GGB | 171882.66 | GGB | 141907.55 | GGB | 0 | 0 | 2782 | 3600 | 2766.45 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 149505.15 | GGB | 149506.83 | 2766.45 | 2663.1987 |  |  |  | 1 | 1 |  |  |  |  | 141907.55 | 2663.1987 | 141907.55 | 2663.1987 | 9.8496 | [5 empty] | 109.05 | 2663.1987 |  | 104.98
20.02.2008 06:00 | 3600 | 2 | 762.15 | GGB | 765.934 | 772.148 | 768.498 | 264.72 | GGB | 10919.9 | GGB | 9.84 | GGB | 1017.58 | GGB | 59.87 | GGB | 170027.49 | GGB | 140076.67 | GGB | 0 | 0 | 2809 | 3600 | 2793.9 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 149545.89 | GGB | 149547.57 | 2793.9 | 2698.0082 |  |  |  | 1 | 1 |  |  |  |  | 140076.67 | 2698.0082 | 140076.67 | 2698.0082 | 9.2766 | [5 empty] | 108.7112 | 2698.0082 |  | 104.98
20.02.2008 07:00 | 3600 | 2 | 761.95 | GGB | 765.934 | 772.148 | 769.597 | 265.13 | GGB | 10870.6 | GGB | 9.82 | GGB | 1017.62 | GGB | 59.71 | GGB | 170613.97 | GGB | 140632.67 | GGB | 0 | 0 | 2799 | 3600 | 2783.03 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 149586.34 | GGB | 149588.03 | 2783.03 | 2687.3414 |  |  |  | 1 | 1 |  |  |  |  | 140632.67 | 2687.3414 | 140632.67 | 2687.3414 | 9.3408 | [5 empty] | 108.718 | 2687.3414 |  | 104.98
20.02.2008 08:00 | 3600 | 2 | 763.67 | GGB | 765.934 | 772.055 | 769.597 | 264.98 | GGB | 10869.2 | GGB | 9.84 | GGB | 1017.86 | GGB | 59.83 | GGB | 170105.61 | GGB | 140198.19 | GGB | 0 | 0 | 2724 | 3600 | 2708.73 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 149626.24 | GGB | 149627.92 | 2708.73 | 2695.6696 |  |  |  | 1 | 1 |  |  |  |  | 140198.19 | 2695.6696 | 140198.19 | 2695.6696 | 9.4743 | [5 empty] | 105.4886 | 2695.6696 |  | 104.98
20.02.2008 09:00 | 3600 | 2 | 763.36 | GGB | 765.934 | 772.031 | 768.498 | 262.88 | GGB | 10880.1 | GGB | 9.84 | GGB | 1017.12 | GGB | 60.34 | GGB | 167989.66 | GGB | 138142.79 | GGB | 0 | 0 | 2743 | 3600 | 2727.26 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 149665.93 | GGB | 149667.61 | 2727.26 | 2727.26 |  |  |  | 1 | 1 |  |  |  |  | 138142.79 | 2727.26 | 138142.79 | 2727.26 | 9.4923 | [5 empty] | 104.6531 |  |  | #VALUE!
20.02.2008 10:00 | 3600 | 2 | 763.05 | GGB | 767.033 | 772.195 | 769.597 | 263.05 | GGB | 10847.7 | GGB | 9.83 | GGB | 1016.77 | GGB | 59.97 | GGB | 168942.56 | GGB | 139031.17 | GGB | 0 | 0 | 2741 | 3600 | 2725.87 | GGB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 149706.68 | GGB | 149708.36 | 2725.87 | 2718.2969 |  |  |  | 1 | 1 |  |  |  |  | 139031.17 | 2718.2969 | 139031.17 | 2718.2969 | 9.2743 | [5 empty] | 105.2725 | 2718.2969 |  | 104.98
20.02.2008 11:00 | 3600 | 2 | 763.39 | GGB | 765.934 | 771.281 | 769.597 | 262.95 | GGB | 10838 | GGB | 9.84 | GGB | 1016.93 | GGB | 59.67 | GGB | 169260.55 | GGB | 139439.22 | GGB | 0 | 0 | 2691 | 3600 | 2675.37 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 149746.14 | GGB | 149747.81 | 2675.37 | 2675.37 |  |  |  | 1 | 1 |  |  |  |  | 139439.22 | 2675.37 | 139439.22 | 2675.37 | 9.4563 | [5 empty] | 103.6254 |  |  | #VALUE!
20.02.2008 12:00 | 3600 | 2 | 763.67 | GGB | 765.934 | 772.289 | 769.597 | 262.03 | GGB | 10816.4 | GGB | 9.84 | GGB | 1016.67 | GGB | 59.84 | GGB | 168261.45 | GGB | 138511.15 | GGB | 0 | 0 | 2666 | 3600 | 2650.2 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 149786.3 | GGB | 149787.97 | 2650.2 | 2650.2 |  |  |  | 1 | 1 |  |  |  |  | 138511.15 | 2650.2 | 138511.15 | 2650.2 | 9.1405 | [5 empty] | 101.9673 |  |  | #VALUE!
20.02.2008 13:00 | 3600 | 2 | 764.03 | GGB | 767.033 | 772.266 | 770.696 | 261.41 | GGB | 10800.3 | GGB | 9.84 | GGB | 1016.65 | GGB | 59.97 | GGB | 167662.86 | GGB | 137960.95 | GGB | 0 | 0 | 2646 | 3600 | 2631.04 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 149825.78 | GGB | 149827.45 | 2631.04 | 2631.04 |  |  |  | 1 | 1 |  |  |  |  | 137960.95 | 2631.04 | 137960.95 | 2631.04 | 9.194 | [5 empty] | 100.828 |  |  | #VALUE!
20.02.2008 14:00 | 3600 | 2 | 764.26 | GGB | 764.835 | 772.336 | 768.498 | 259.9 | GGB | 10796.2 | GGB | 9.84 | GGB | 1016.38 | GGB | 60.58 | GGB | 165499.6 | GGB | 135897.65 | GGB | 0 | 0 | 2636 | 3600 | 2620.82 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 149865 | GGB | 149866.68 | 2620.82 | 2620.82 |  |  |  | 1 | 1 |  |  |  |  | 135897.65 | 2620.82 | 135897.65 | 2620.82 | 9.0788 | [5 empty] | 98.9342 |  |  | #VALUE!
20.02.2008 15:00 | 3600 | 2 | 763.9 | GGB | 767.033 | 772.336 | 770.696 | 259.44 | GGB | 10794.5 | GGB | 9.84 | GGB | 1015.7 | GGB | 60.94 | GGB | 164803.09 | GGB | 135088.73 | GGB | 0 | 0 | 2663 | 3600 | 2647.16 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 149905.47 | GGB | 149907.15 | 2647.16 | 2647.16 |  |  |  | 1 | 1 |  |  |  |  | 135088.73 | 2647.16 | 135088.73 | 2647.16 | 8.8362 | [5 empty] | 99.3337 |  |  | #VALUE!
20.02.2008 16:00 | 3600 | 2 | 764.01 | GGB | 765.934 | 772.477 | 769.597 | 259.37 | GGB | 10782.5 | GGB | 9.83 | GGB | 1014.81 | GGB | 61.06 | GGB | 164452.08 | GGB | 134633.75 | GGB | 0 | 0 | 2653 | 3600 | 2637.43 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 149944.92 | GGB | 149946.59 | 2637.43 | 2637.43 |  |  |  | 1 | 1 |  |  |  |  | 134633.75 | 2637.43 | 134633.75 | 2637.43 | 9.0032 | [5 empty] | 98.6353 |  |  | #VALUE!
20.02.2008 17:00 | 3600 | 2 | 764.11 | GGB | 765.934 | 773.648 | 770.696 | 260.64 | GGB | 10752.2 | GGB | 9.83 | GGB | 1014.43 | GGB | 60.73 | GGB | 166011.26 | GGB | 135993.71 | GGB | 0 | 0 | 2636 | 3600 | 2620.49 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 149984.88 | GGB | 149986.55 | 2620.49 | 2620.49 |  |  |  | 1 | 1 |  |  |  |  | 135993.71 | 2620.49 | 135993.71 | 2620.49 | 8.9182 | [5 empty] | 98.9917 |  |  | #VALUE!
20.02.2008 18:00 | 3600 | 2 | 764.46 | GGB | 767.033 | 773.461 | 770.696 | 260.96 | GGB | 10747.7 | GGB | 9.83 | GGB | 1014.49 | GGB | 60.7 | GGB | 166191.71 | GGB | 136159.75 | GGB | 0 | 0 | 2618 | 3600 | 2602.78 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 150024.64 | GGB | 150026.31 | 2602.78 | 2602.78 |  |  |  | 1 | 1 |  |  |  |  | 136159.75 | 2602.78 | 136159.75 | 2602.78 | 8.9133 | [5 empty] | 98.4427 |  |  | #VALUE!
20.02.2008 19:00 | 3600 | 2 | 764.51 | GGB | 765.934 | 772.313 | 769.597 | 259.88 | GGB | 10767 | GGB | 9.84 | GGB | 1014.11 | GGB | 60.84 | GGB | 164801.99 | GGB | 134916.61 | GGB | 0 | 0 | 2624 | 3600 | 2609.15 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 150063.68 | GGB | 150065.35 | 2609.15 | 2609.15 |  |  |  | 1 | 1 |  |  |  |  | 134916.61 | 2609.15 | 134916.61 | 2609.15 | 9.0168 | [5 empty] | 97.7827 |  |  | #VALUE!
20.02.2008 20:00 | 3600 | 2 | 764.11 | GGB | 765.934 | 771.188 | 769.597 | 259.06 | GGB | 10778.3 | GGB | 9.83 | GGB | 1013.86 | GGB | 61 | GGB | 164423.47 | GGB | 134510.16 | GGB | 0 | 0 | 2655 | 3600 | 2639.5 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 150103.46 | GGB | 150105.13 | 2639.5 | 2639.5 |  |  |  | 1 | 1 |  |  |  |  | 134510.16 | 2639.5 | 134510.16 | 2639.5 | 8.9251 | [5 empty] | 98.6221 |  |  | #VALUE!
20.02.2008 21:00 | 3600 | 2 | 763.96 | GGB | 765.934 | 772.266 | 769.597 | 259.43 | GGB | 10779.7 | GGB | 9.83 | GGB | 1013.78 | GGB | 60.41 | GGB | 165499.6 | GGB | 135617.67 | GGB | 0 | 0 | 2656 | 3600 | 2640.99 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 150142.75 | GGB | 150144.42 | 2640.99 | 2640.99 |  |  |  | 1 | 1 |  |  |  |  | 135617.67 | 2640.99 | 135617.67 | 2640.99 | 9.1159 | [5 empty] | 99.4903 |  |  | #VALUE!
20.02.2008 22:00 | 3600 | 2 | 764.05 | GGB | 765.934 | 772.547 | 770.696 | 259.59 | GGB | 10778.9 | GGB | 9.84 | GGB | 1014.12 | GGB | 59.6 | GGB | 166713.27 | GGB | 136992.49 | GGB | 0 | 0 | 2631 | 3600 | 2615.2 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 150183.15 | GGB | 150184.83 | 2615.2 | 2615.2 |  |  |  | 1 | 1 |  |  |  |  | 136992.49 | 2615.2 | 136992.49 | 2615.2 | 8.8657 | [5 empty] | 99.5174 |  |  | #VALUE!
20.02.2008 23:00 | 3600 | 2 | 764.22 | GGB | 767.033 | 773.742 | 771.795 | 260.41 | GGB | 10768.2 | GGB | 9.83 | GGB | 1013.98 | GGB | 60.07 | GGB | 166526.22 | GGB | 136626.79 | GGB | 0 | 0 | 2629 | 3600 | 2613.18 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 150222.72 | GGB | 150224.39 | 2613.18 | 2613.18 |  |  |  | 1 | 1 |  |  |  |  | 136626.79 | 2613.18 | 136626.79 | 2613.18 | 9.025 | [5 empty] | 99.1751 |  |  | #VALUE!
20.02.2008 24:00 | 3600 | 2 | 764.5 | GGB | 767.033 | 772.781 | 770.696 | 260.28 | GGB | 10761.8 | GGB | 9.83 | GGB | 1014.13 | GGB | 60.36 | GGB | 166380.97 | GGB | 136407.52 | GGB | 0 | 0 | 2617 | 3600 | 2601.71 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 150261.93 | GGB | 150263.6 | 2601.71 | 2601.71 |  |  |  | 1 | 1 |  |  |  |  | 136407.52 | 2601.71 | 136407.52 | 2601.71 | 9.0511 | [5 empty] | 98.5813 |  |  | #VALUE!
21.02.2008 01:00 | 3600 | 2 | 764.43 | GGB | 767.033 | 772.781 | 769.597 | 259.25 | GGB | 10776.2 | GGB | 9.84 | GGB | 1014.02 | GGB | 60.71 | GGB | 165060.57 | GGB | 135166.64 | GGB | 0 | 0 | 2634 | 3600 | 2619.15 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 150301.82 | GGB | 150303.49 | 2619.15 | 2619.15 |  |  |  | 1 | 1 |  |  |  |  | 135166.64 | 2619.15 | 135166.64 | 2619.15 | 8.8749 | [5 empty] | 98.3394 |  |  | #VALUE!
21.02.2008 02:00 | 3600 | 2 | 764.07 | GGB | 765.934 | 772.781 | 769.597 | 258.75 | GGB | 10780.3 | GGB | 9.83 | GGB | 1013.88 | GGB | 61.01 | GGB | 164164.89 | GGB | 134297.54 | GGB | 0 | 0 | 2652 | 3600 | 2637.12 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 150341.04 | GGB | 150342.71 | 2637.12 | 2637.12 |  |  |  | 1 | 1 |  |  |  |  | 134297.54 | 2637.12 | 134297.54 | 2637.12 | 9.0301 | [5 empty] | 98.3774 |  |  | #VALUE!
21.02.2008 03:00 | 3600 | 2 | 764.28 | GGB | 765.934 | 772.758 | 770.696 | 258.9 | GGB | 10763.8 | GGB | 9.83 | GGB | 1013.72 | GGB | 60.95 | GGB | 164639.14 | GGB | 134685.91 | GGB | 0 | 0 | 2638 | 3600 | 2622.18 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 150381.15 | GGB | 150382.83 | 2622.18 | 2622.18 |  |  |  | 1 | 1 |  |  |  |  | 134685.91 | 2622.18 | 134685.91 | 2622.18 | 8.8029 | [5 empty] | 98.103 |  |  | #VALUE!
21.02.2008 04:00 | 3600 | 2 | 764.48 | GGB | 765.934 | 772.734 | 770.696 | 259.86 | GGB | 10743.3 | GGB | 9.83 | GGB | 1013.41 | GGB | 60.59 | GGB | 165903.42 | GGB | 135824.54 | GGB | 0 | 0 | 2615 | 3600 | 2599.83 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 150421.26 | GGB | 150422.93 | 2599.83 | 2599.83 |  |  |  | 1 | 1 |  |  |  |  | 135824.54 | 2599.83 | 135824.54 | 2599.83 | 8.806 | [5 empty] | 98.0891 |  |  | #VALUE!
21.02.2008 05:00 | 3600 | 2 | 764.54 | GGB | 765.934 | 772.758 | 770.696 | 260.03 | GGB | 10750.4 | GGB | 9.84 | GGB | 1013.35 | GGB | 60.55 | GGB | 166290.74 | GGB | 136151.24 | GGB | 0 | 0 | 2614 | 3600 | 2599.07 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 150459.98 | GGB | 150461.66 | 2599.07 | 2599.07 |  |  |  | 1 | 1 |  |  |  |  | 136151.24 | 2599.07 | 136151.24 | 2599.07 | 9.1368 | [5 empty] | 98.2963 |  |  | #VALUE!
21.02.2008 06:00 | 3600 | 2 | 764.57 | GGB | 767.033 | 772.711 | 770.696 | 259.1 | GGB | 10769.4 | GGB | 9.84 | GGB | 1013.43 | GGB | 60.89 | GGB | 164772.28 | GGB | 134780.05 | GGB | 0 | 0 | 2624 | 3600 | 2609.1 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 150500.06 | GGB | 150501.74 | 2609.1 | 2609.1 |  |  |  | 1 | 1 |  |  |  |  | 134780.05 | 2609.1 | 134780.05 | 2609.1 | 8.7738 | [5 empty] | 97.6818 |  |  | #VALUE!
21.02.2008 07:00 | 3600 | 2 | 764.32 | GGB | 767.033 | 772.758 | 770.696 | 258.43 | GGB | 10767.6 | GGB | 9.83 | GGB | 1013.1 | GGB | 61.16 | GGB | 163973.43 | GGB | 133975.12 | GGB | 0 | 0 | 2642 | 3600 | 2626.58 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 150539.58 | GGB | 150541.26 | 2626.58 | 2626.58 |  |  |  | 1 | 1 |  |  |  |  | 133975.12 | 2626.58 | 133975.12 | 2626.58 | 8.9043 | [5 empty] | 97.749 |  |  | #VALUE!
21.02.2008 08:00 | 3600 | 2 | 764.08 | GGB | 764.835 | 771.727 | 768.498 | 258.48 | GGB | 10755.9 | GGB | 9.83 | GGB | 1013.11 | GGB | 61.3 | GGB | 163908.51 | GGB | 133868.68 | GGB | 0 | 0 | 2645 | 3600 | 2629.34 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 150578.85 | GGB | 150580.53 | 2629.34 | 2629.34 |  |  |  | 1 | 1 |  |  |  |  | 133868.68 | 2629.34 | 133868.68 | 2629.34 | 8.9632 | [5 empty] | 97.774 |  |  | #VALUE!
21.02.2008 09:00 | 3600 | 2 | 763.47 | GGB | 767.033 | 772.805 | 769.597 | 259.43 | GGB | 10786.6 | GGB | 9.83 | GGB | 1013.31 | GGB | 61.13 | GGB | 164885.61 | GGB | 134759.39 | GGB | 0 | 0 | 2684 | 3600 | 2668.95 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 150619.39 | GGB | 150621.08 | 2668.95 | 2668.95 |  |  |  | 1 | 1 |  |  |  |  | 134759.39 | 2668.95 | 134759.39 | 2668.95 | 8.8697 | [5 empty] | 99.9072 |  |  | #VALUE!
21.02.2008 10:00 | 3600 | 2 | 763.05 | GGB | 767.033 | 772.5 | 769.597 | 261.47 | GGB | 10803.1 | GGB | 9.83 | GGB | 1013.88 | GGB | 60.47 | GGB | 167454.9 | GGB | 137210.11 | GGB | 0 | 0 | 2713 | 3600 | 2697.98 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 150658.82 | GGB | 150660.51 | 2697.98 | 2697.98 |  |  |  | 1 | 1 |  |  |  |  | 137210.11 | 2697.98 | 137210.11 | 2697.98 | 9.3885 | [5 empty] | 102.8306 |  |  | #VALUE!
21.02.2008 11:00 | 3600 | 2 | 763.82 | GGB | 765.934 | 772.547 | 769.597 | 261.71 | GGB | 10800.5 | GGB | 9.84 | GGB | 1014.38 | GGB | 60.18 | GGB | 168173.42 | GGB | 137983.38 | GGB | 0 | 0 | 2680 | 3600 | 2664.95 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 150698.45 | GGB | 150700.14 | 2664.95 | 2664.95 |  |  |  | 1 | 1 |  |  |  |  | 137983.38 | 2664.95 | 137983.38 | 2664.95 | 9.2788 | [5 empty] | 102.1441 |  |  | #VALUE!
21.02.2008 12:00 | 3600 | 2 | 764.04 | GGB | 765.934 | 772.594 | 769.597 | 260.99 | GGB | 10795.5 | GGB | 9.84 | GGB | 1014.29 | GGB | 60.33 | GGB | 167381.18 | GGB | 137261.28 | GGB | 0 | 0 | 2665 | 3600 | 2650 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 150738.54 | GGB | 150740.23 | 2650 | 2650 |  |  |  | 1 | 1 |  |  |  |  | 137261.28 | 2650 | 137261.28 | 2650 | 9.0731 | [5 empty] | 101.0396 |  |  | #VALUE!
21.02.2008 13:00 | 3600 | 2 | 764.07 | GGB | 767.033 | 773.695 | 770.696 | 259.15 | GGB | 10797.8 | GGB | 9.84 | GGB | 1014.11 | GGB | 61.01 | GGB | 165086.97 | GGB | 135078.58 | GGB | 0 | 0 | 2668 | 3600 | 2652.15 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 150777.13 | GGB | 150778.82 | 2652.15 | 2652.15 |  |  |  | 1 | 1 |  |  |  |  | 135078.58 | 2652.15 | 135078.58 | 2652.15 | 9.2835 | [5 empty] | 99.5135 |  |  | #VALUE!
21.02.2008 14:00 | 3600 | 2 | 764.54 | GGB | 767.033 | 774.586 | 771.795 | 259.86 | GGB | 10746 | GGB | 9.83 | GGB | 1013.45 | GGB | 60.9 | GGB | 165802.19 | GGB | 135619.48 | GGB | 0 | 0 | 2623 | 3600 | 2607.27 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 150817.78 | GGB | 150819.47 | 2607.27 | 2607.27 |  |  |  | 1 | 1 |  |  |  |  | 135619.48 | 2607.27 | 135619.48 | 2607.27 | 8.6986 | [5 empty] | 98.2213 |  |  | #VALUE!
21.02.2008 15:00 | 3600 | 2 | 765.15 | GGB | 767.033 | 773.602 | 770.696 | 259.07 | GGB | 10722.1 | GGB | 9.83 | GGB | 1012.15 | GGB | 61.06 | GGB | 164995.65 | GGB | 134722.35 | GGB | 0 | 0 | 2587 | 3600 | 2571.83 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 150857.1 | GGB | 150858.79 | 2571.83 | 2571.83 |  |  |  | 1 | 1 |  |  |  |  | 134722.35 | 2571.83 | 134722.35 | 2571.83 | 8.8119 | [5 empty] | 96.2453 |  |  | #VALUE!
21.02.2008 16:00 | 3600 | 2 | 764.99 | GGB | 765.934 | 773.695 | 769.597 | 257.39 | GGB | 10734.2 | GGB | 9.84 | GGB | 1011.18 | GGB | 61.78 | GGB | 163214.2 | GGB | 132856.02 | GGB | 0 | 0 | 2601 | 3600 | 2585.35 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 150895.48 | GGB | 150897.18 | 2585.35 | 2585.35 |  |  |  | 1 | 1 |  |  |  |  | 132856.02 | 2585.35 | 132856.02 | 2585.35 | 8.9471 | [5 empty] | 95.4109 |  |  | #VALUE!
21.02.2008 17:00 | 3600 | 2 | 764.87 | GGB | 765.934 | 773.648 | 769.597 | 257.67 | GGB | 10741.4 | GGB | 9.84 | GGB | 1010.99 | GGB | 61.86 | GGB | 163426.56 | GGB | 132971.26 | GGB | 0 | 0 | 2608 | 3600 | 2592.52 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 150936.85 | GGB | 150938.55 | 2592.52 | 2592.52 |  |  |  | 1 | 1 |  |  |  |  | 132971.26 | 2592.52 | 132971.26 | 2592.52 | 8.3329 | [5 empty] | 95.7585 |  |  | #VALUE!
21.02.2008 18:00 | 3600 | 2 | 763.98 | GGB | 765.934 | 772.57 | 769.597 | 259.18 | GGB | 10733.9 | GGB | 9.82 | GGB | 1010.57 | GGB | 61.09 | GGB | 165517.21 | GGB | 134928.49 | GGB | 0 | 0 | 2644 | 3600 | 2628.97 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 150975.87 | GGB | 150977.57 | 2628.97 | 2628.97 |  |  |  | 1 | 1 |  |  |  |  | 134928.49 | 2628.97 | 134928.49 | 2628.97 | 9.0908 | [5 empty] | 98.5342 |  |  | #VALUE!
21.02.2008 19:00 | 3600 | 2 | 764.03 | GGB | 765.934 | 772.523 | 769.597 | 260.3 | GGB | 10781.9 | GGB | 9.84 | GGB | 1010.65 | GGB | 60.53 | GGB | 166683.56 | GGB | 136119.28 | GGB | 0 | 0 | 2653 | 3600 | 2637.31 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 151015.3 | GGB | 151017 | 2637.31 | 2637.31 |  |  |  | 1 | 1 |  |  |  |  | 136119.28 | 2637.31 | 136119.28 | 2637.31 | 9.1045 | [5 empty] | 99.7191 |  |  | #VALUE!
21.02.2008 20:00 | 3600 | 2 | 763.21 | GGB | 764.835 | 771.352 | 768.498 | 259.28 | GGB | 10790.3 | GGB | 9.83 | GGB | 1009.79 | GGB | 60.76 | GGB | 165603.03 | GGB | 135026.99 | GGB | 0 | 0 | 2701 | 3600 | 2685.38 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 151054.72 | GGB | 151056.42 | 2685.38 | 2685.38 |  |  |  | 1 | 1 |  |  |  |  | 135026.99 | 2685.38 | 135026.99 | 2685.38 | 9.1983 | [5 empty] | 100.7219 |  |  | #VALUE!
21.02.2008 21:00 | 3600 | 2 | 763.76 | GGB | 765.934 | 772.523 | 770.696 | 259.88 | GGB | 10767.9 | GGB | 9.84 | GGB | 1009.22 | GGB | 60.26 | GGB | 166851.92 | GGB | 136171.01 | GGB | 0 | 0 | 2660 | 3600 | 2645.12 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 151094.8 | GGB | 151096.5 | 2645.12 | 2645.12 |  |  |  | 1 | 1 |  |  |  |  | 136171.01 | 2645.12 | 136171.01 | 2645.12 | 8.9867 | [5 empty] | 100.0524 |  |  | #VALUE!
21.02.2008 22:00 | 3600 | 2 | 763.96 | GGB | 765.934 | 772.477 | 769.597 | 257.82 | GGB | 10772.1 | GGB | 9.84 | GGB | 1008.5 | GGB | 60.43 | GGB | 164891.11 | GGB | 134407.72 | GGB | 0 | 0 | 2651 | 3600 | 2635.25 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 151133.79 | GGB | 151135.5 | 2635.25 | 2635.25 |  |  |  | 1 | 1 |  |  |  |  | 134407.72 | 2635.25 | 134407.72 | 2635.25 | 9.082 | [5 empty] | 98.3883 |  |  | #VALUE!
21.02.2008 23:00 | 3600 | 2 | 763.76 | GGB | 765.934 | 772.359 | 769.597 | 258.66 | GGB | 10746.6 | GGB | 9.83 | GGB | 1008.55 | GGB | 60.26 | GGB | 165817.6 | GGB | 135238.33 | GGB | 0 | 0 | 2651 | 3600 | 2635.59 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 151173.6 | GGB | 151175.31 | 2635.59 | 2635.59 |  |  |  | 1 | 1 |  |  |  |  | 135238.33 | 2635.59 | 135238.33 | 2635.59 | 8.9533 | [5 empty] | 99.0091 |  |  | #VALUE!
21.02.2008 24:00 | 3600 | 2 | 763.75 | GGB | 765.934 | 772.359 | 770.696 | 257.77 | GGB | 10760 | GGB | 9.84 | GGB | 1007.85 | GGB | 60.7 | GGB | 164376.16 | GGB | 133792.43 | GGB | 0 | 0 | 2667 | 3600 | 2652.07 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 151212.74 | GGB | 151214.45 | 2652.07 | 2652.07 |  |  |  | 1 | 1 |  |  |  |  | 133792.43 | 2652.07 | 133792.43 | 2652.07 | 9.0656 | [5 empty] | 98.563 |  |  | #VALUE!
22.02.2008 01:00 | 3600 | 2 | 763.48 | GGB | 765.934 | 772.359 | 769.597 | 257.49 | GGB | 10744.9 | GGB | 9.83 | GGB | 1006.91 | GGB | 60.69 | GGB | 164207.8 | GGB | 133534.47 | GGB | 0 | 0 | 2677 | 3600 | 2661.32 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 151252.43 | GGB | 151254.14 | 2661.32 | 2661.32 |  |  |  | 1 | 1 |  |  |  |  | 133534.47 | 2661.32 | 133534.47 | 2661.32 | 8.9538 | [5 empty] | 98.7161 |  |  | #VALUE!
22.02.2008 02:00 | 3600 | 2 | 763.91 | GGB | 765.934 | 773.672 | 770.696 | 258.36 | GGB | 10721 | GGB | 9.83 | GGB | 1006.41 | GGB | 60.5 | GGB | 165102.38 | GGB | 134270.59 | GGB | 0 | 0 | 2645 | 3600 | 2630.11 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 151292.37 | GGB | 151294.08 | 2630.11 | 2630.11 |  |  |  | 1 | 1 |  |  |  |  | 134270.59 | 2630.11 | 134270.59 | 2630.11 | 8.8419 | [5 empty] | 98.0962 |  |  | #VALUE!
22.02.2008 03:00 | 3600 | 2 | 763.93 | GGB | 765.934 | 772.547 | 769.597 | 257.01 | GGB | 10723.8 | GGB | 9.84 | GGB | 1005.04 | GGB | 60.61 | GGB | 163941.52 | GGB | 133101.57 | GGB | 0 | 0 | 2643 | 3600 | 2627.74 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 151331.58 | GGB | 151333.29 | 2627.74 | 2627.74 |  |  |  | 1 | 1 |  |  |  |  | 133101.57 | 2627.74 | 133101.57 | 2627.74 | 8.9201 | [5 empty] | 97.1545 |  |  | #VALUE!
22.02.2008 04:00 | 3600 | 2 | 763.73 | GGB | 765.934 | 772.57 | 769.597 | 256.65 | GGB | 10718.9 | GGB | 9.84 | GGB | 1004.06 | GGB | 60.69 | GGB | 163797.38 | GGB | 132825.38 | GGB | 0 | 0 | 2653 | 3600 | 2637.38 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 151371.18 | GGB | 151372.89 | 2637.38 | 2637.38 |  |  |  | 1 | 1 |  |  |  |  | 132825.38 | 2637.38 | 132825.38 | 2637.38 | 8.8462 | [5 empty] | 97.3086 |  |  | #VALUE!
22.02.2008 05:00 | 3600 | 2 | 763.63 | GGB | 764.835 | 771.492 | 768.498 | 256.1 | GGB | 10708.9 | GGB | 9.83 | GGB | 1003.09 | GGB | 60.61 | GGB | 163149.28 | GGB | 132202.48 | GGB | 0 | 0 | 2651 | 3600 | 2635.98 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 151410.96 | GGB | 151412.66 | 2635.98 | 2635.98 |  |  |  | 1 | 1 |  |  |  |  | 132202.48 | 2635.98 | 132202.48 | 2635.98 | 8.7625 | [5 empty] | 96.8009 |  |  | #VALUE!
22.02.2008 06:00 | 3600 | 2 | 763.17 | GGB | 765.934 | 771.773 | 769.597 | 255.97 | GGB | 10707.8 | GGB | 9.83 | GGB | 1002.05 | GGB | 60.57 | GGB | 163303.33 | GGB | 132205.88 | GGB | 0 | 0 | 2668 | 3600 | 2652.55 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 151450.19 | GGB | 151451.89 | 2652.55 | 2652.55 |  |  |  | 1 | 1 |  |  |  |  | 132205.88 | 2652.55 | 132205.88 | 2652.55 | 8.9391 | [5 empty] | 97.4119 |  |  | #VALUE!
22.02.2008 07:00 | 3600 | 2 | 762.9 | GGB | 762.271 | 768.492 | 765.934 | 255.82 | GGB | 10704.2 | GGB | 9.83 | GGB | 1000.64 | GGB | 60.24 | GGB | 163437.57 | GGB | 132259.89 | GGB | 0 | 0 | 2677 | 3600 | 2661.81 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 151489.72 | GGB | 151491.42 | 2661.81 | 2661.81 |  |  |  | 0 | 1 | [14 empty] | 97.7919 |  |  | #VALUE!
22.02.2008 08:00 | 3600 | 2 | 761.41 | GGB | 764.469 | 770.227 | 767.033 | 257.5 | GGB | 10745.9 | GGB | 9.83 | GGB | 999.59 | GGB | 59.51 | GGB | 165123.29 | GGB | 133777.66 | GGB | 0 | 0 | 2751 | 3207 | 2735.58 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 151529.4 | GGB | 151531.1 | 2735.58 | 2735.58 |  |  |  | 1 | 1 |  |  |  |  | 133777.66 | 2735.58 | 133777.66 | 2735.58 | 9.2228 | [5 empty] | 101.6554 |  |  | #VALUE!
22.02.2008 09:00 | 3600 | 2 | 761.68 | GGB | 764.835 | 771.305 | 767.033 | 256.87 | GGB | 10736.3 | GGB | 9.84 | GGB | 998.94 | GGB | 59.56 | GGB | 164502.69 | GGB | 133166.82 | GGB | 0 | 0 | 2728 | 3600 | 2712.95 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 151568.44 | GGB | 151570.14 | 2712.95 | 2712.95 |  |  |  | 1 | 1 |  |  |  |  | 133166.82 | 2712.95 | 133166.82 | 2712.95 | 9.254 | [5 empty] | 100.3541 |  |  | #VALUE!
22.02.2008 10:00 | 3600 | 2 | 761.66 | GGB | 764.835 | 771.328 | 768.132 | 256.53 | GGB | 10701.4 | GGB | 9.83 | GGB | 998.32 | GGB | 59.96 | GGB | 163454.07 | GGB | 132075.02 | GGB | 0 | 0 | 2721 | 3600 | 2705.79 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 151608.09 | GGB | 151609.79 | 2705.79 | 2705.79 |  |  |  | 1 | 1 |  |  |  |  | 132075.02 | 2705.79 | 132075.02 | 2705.79 | 9.013 | [5 empty] | 99.2687 |  |  | #VALUE!
22.02.2008 11:00 | 3600 | 2 | 762.74 | GGB | 764.469 | 771.328 | 768.498 | 255.71 | GGB | 10660 | GGB | 9.83 | GGB | 997.86 | GGB | 60.59 | GGB | 162054.44 | GGB | 130640.64 | GGB | 0 | 0 | 2682 | 3600 | 2666.96 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 151647.34 | GGB | 151649.04 | 2666.96 | 2666.96 |  |  |  | 1 | 1 |  |  |  |  | 130640.64 | 2666.96 | 130640.64 | 2666.96 | 8.8768 | [5 empty] | 96.7815 |  |  | #VALUE!
22.02.2008 12:00 | 3600 | 2 | 763.24 | GGB | 764.835 | 772.453 | 768.498 | 255.33 | GGB | 10635 | GGB | 9.84 | GGB | 998.05 | GGB | 60.98 | GGB | 161215.99 | GGB | 129834.54 | GGB | 0 | 0 | 2653 | 3600 | 2637.72 | GGB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 151685.87 | GGB | 151687.57 | 2637.72 | 2637.72 |  |  |  | 1 | 1 |  |  |  |  | 129834.54 | 2637.72 | 129834.54 | 2637.72 | 8.8883 | [5 empty] | 95.1298 |  |  | #VALUE!
22.02.2008 13:00 | 3600 | 2 | 763.34 | GGB | 764.835 | 772.453 | 768.498 | 255.23 | GGB | 10613 | GGB | 9.83 | GGB | 998.07 | GGB | 61.19 | GGB | 160681.22 | GGB | 129327.43 | GGB | 0 | 0 | 2647 | 3600 | 2632.06 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 151725.74 | GGB | 151727.45 | 2632.06 | 2632.06 |  |  |  | 1 | 1 |  |  |  |  | 129327.43 | 2632.06 | 129327.43 | 2632.06 | 8.5355 | [5 empty] | 94.5549 |  |  | #VALUE!
22.02.2008 14:00 | 3600 | 2 | 763.74 | GGB | 765.934 | 772.289 | 769.597 | 254.55 | GGB | 10610 | GGB | 9.84 | GGB | 997.26 | GGB | 61.12 | GGB | 161143.36 | GGB | 129618.78 | GGB | 0 | 0 | 2627 | 3600 | 2612.02 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 151764.65 | GGB | 151766.36 | 2612.02 | 2612.02 |  |  |  | 1 | 1 |  |  |  |  | 129618.78 | 2612.02 | 129618.78 | 2612.02 | 8.7013 | [5 empty] | 94.0463 |  |  | #VALUE!
22.02.2008 15:00 | 3600 | 2 | 763.96 | GGB | 765.934 | 773.367 | 769.597 | 253.84 | GGB | 10606.1 | GGB | 9.84 | GGB | 996.99 | GGB | 60.87 | GGB | 160978.31 | GGB | 129549.74 | GGB | 0 | 0 | 2602 | 3600 | 2587.04 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 151803.51 | GGB | 151805.22 | 2587.04 | 2587.04 |  |  |  | 1 | 1 |  |  |  |  | 129549.74 | 2587.04 | 129549.74 | 2587.04 | 8.6246 | [5 empty] | 93.0973 |  |  | #VALUE!
22.02.2008 16:00 | 3600 | 2 | 763.93 | GGB | 765.934 | 773.367 | 769.597 | 253.85 | GGB | 10623.8 | GGB | 9.83 | GGB | 997.32 | GGB | 60.7 | GGB | 161263.3 | GGB | 129886.03 | GGB | 0 | 0 | 2609 | 3600 | 2593.88 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 151843.29 | GGB | 151845 | 2593.88 | 2593.88 |  |  |  | 1 | 1 |  |  |  |  | 129886.03 | 2593.88 | 129886.03 | 2593.88 | 8.4693 | [5 empty] | 93.5858 |  |  | #VALUE!
22.02.2008 17:00 | 3600 | 2 | 763.88 | GGB | 765.934 | 773.414 | 770.696 | 254.43 | GGB | 10630.7 | GGB | 9.83 | GGB | 998.03 | GGB | 60.37 | GGB | 162377.94 | GGB | 131006.92 | GGB | 0 | 0 | 2610 | 3600 | 2594.7 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 151881.8 | GGB | 151883.51 | 2594.7 | 2594.7 |  |  |  | 1 | 1 |  |  |  |  | 131006.92 | 2594.7 | 131006.92 | 2594.7 | 8.8269 | [5 empty] | 94.4232 |  |  | #VALUE!
22.02.2008 18:00 | 3600 | 2 | 763.56 | GGB | 764.835 | 772.289 | 768.498 | 254.38 | GGB | 10634.1 | GGB | 9.83 | GGB | 997.9 | GGB | 60.39 | GGB | 162321.83 | GGB | 130936.87 | GGB | 0 | 0 | 2624 | 3600 | 2608.31 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 151921.23 | GGB | 151922.94 | 2608.31 | 2608.31 |  |  |  | 1 | 1 |  |  |  |  | 130936.87 | 2608.31 | 130936.87 | 2608.31 | 8.6615 | [5 empty] | 94.8678 |  |  | #VALUE!
22.02.2008 19:00 | 3600 | 2 | 764.1 | GGB | 765.934 | 773.391 | 769.597 | 255.19 | GGB | 10617 | GGB | 9.84 | GGB | 997.41 | GGB | 60.21 | GGB | 163498.09 | GGB | 131892.87 | GGB | 0 | 0 | 2591 | 3600 | 2575.2 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 151960.34 | GGB | 151962.06 | 2575.2 | 2575.2 |  |  |  | 1 | 1 |  |  |  |  | 131892.87 | 2575.2 | 131892.87 | 2575.2 | 8.6823 | [5 empty] | 94.3474 |  |  | #VALUE!
22.02.2008 20:00 | 3600 | 2 | 764.29 | GGB | 764.835 | 772.242 | 768.498 | 253.25 | GGB | 10608.1 | GGB | 9.84 | GGB | 996.27 | GGB | 60.47 | GGB | 161276.5 | GGB | 129849.08 | GGB | 0 | 0 | 2586 | 3600 | 2570.93 | GGB | 100 | GGB | 37.53 | GGB | 37.53 | GGB | 151997.87 | GGB | 151999.59 | 2570.93 | 2570.93 |  |  |  | 1 | 1 |  |  |  |  | 129849.08 | 2570.93 | 129849.08 | 2570.93 | 8.8951 | [5 empty] | 92.7314 |  |  | #VALUE!
22.02.2008 21:00 | 3600 | 2 | 763.53 | GGB | 764.835 | 772.242 | 768.498 | 252.68 | GGB | 10610.9 | GGB | 9.83 | GGB | 995.01 | GGB | 60.55 | GGB | 160761.55 | GGB | 129240.11 | GGB | 0 | 0 | 2616 | 3600 | 2600.19 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 152037.75 | GGB | 152039.47 | 2600.19 | 2600.19 |  |  |  | 1 | 1 |  |  |  |  | 129240.11 | 2600.19 | 129240.11 | 2600.19 | 8.4265 | [5 empty] | 93.3469 |  |  | #VALUE!
22.02.2008 22:00 | 3600 | 2 | 763.47 | GGB | 765.934 | 772.148 | 769.597 | 252.13 | GGB | 10600.8 | GGB | 9.84 | GGB | 992.92 | GGB | 60.56 | GGB | 160376.43 | GGB | 128656.91 | GGB | 0 | 0 | 2611 | 3600 | 2595.58 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 152076.99 | GGB | 152078.71 | 2595.58 | 2595.58 |  |  |  | 1 | 1 |  |  |  |  | 128656.91 | 2595.58 | 128656.91 | 2595.58 | 8.5102 | [5 empty] | 92.7609 |  |  | #VALUE!
22.02.2008 23:00 | 3600 | 2 | 763.5 | GGB | 764.835 | 772.148 | 769.597 | 250.93 | GGB | 10568.4 | GGB | 9.84 | GGB | 990.58 | GGB | 60.37 | GGB | 159462.05 | GGB | 127693.75 | GGB | 0 | 0 | 2597 | 3600 | 2581.25 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 152116.21 | GGB | 152117.93 | 2581.25 | 2581.25 |  |  |  | 1 | 1 |  |  |  |  | 127693.75 | 2581.25 | 127693.75 | 2581.25 | 8.4041 | [5 empty] | 91.5582 |  |  | #VALUE!
22.02.2008 24:00 | 3600 | 2 | 763.45 | GGB | 764.835 | 772.148 | 769.597 | 249.92 | GGB | 10548.7 | GGB | 9.83 | GGB | 989.16 | GGB | 60.02 | GGB | 158878.87 | GGB | 127180.8 | GGB | 0 | 0 | 2588 | 3600 | 2572.63 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 152155.35 | GGB | 152157.07 | 2572.63 | 2572.63 |  |  |  | 1 | 1 |  |  |  |  | 127180.8 | 2572.63 | 127180.8 | 2572.63 | 8.3595 | [5 empty] | 90.8859 |  |  | #VALUE!
23.02.2008 01:00 | 3600 | 2 | 763.81 | GGB | 765.934 | 772.102 | 769.597 | 250.16 | GGB | 10533.4 | GGB | 9.83 | GGB | 988.18 | GGB | 60.56 | GGB | 159067.03 | GGB | 126997.21 | GGB | 0 | 0 | 2570 | 3600 | 2555.2 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 152194.18 | GGB | 152195.9 | 2555.2 | 2555.2 |  |  |  | 1 | 1 |  |  |  |  | 126997.21 | 2555.2 | 126997.21 | 2555.2 | 8.357 | [5 empty] | 90.1398 |  |  | #VALUE!
23.02.2008 02:00 | 3600 | 2 | 763.75 | GGB | 765.934 | 772.102 | 769.597 | 250.42 | GGB | 10533.9 | GGB | 9.83 | GGB | 987.35 | GGB | 60.5 | GGB | 159489.56 | GGB | 127252.34 | GGB | 0 | 0 | 2565 | 3600 | 2549.9 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 152232.37 | GGB | 152234.1 | 2549.9 | 2549.9 |  |  |  | 1 | 1 |  |  |  |  | 127252.34 | 2549.9 | 127252.34 | 2549.9 | 8.4943 | [5 empty] | 90.1335 |  |  | #VALUE!
23.02.2008 03:00 | 3600 | 2 | 763.53 | GGB | 765.934 | 772.102 | 768.498 | 250.99 | GGB | 10556.2 | GGB | 9.83 | GGB | 987.14 | GGB | 60.11 | GGB | 160478.76 | GGB | 128164.38 | GGB | 0 | 0 | 2574 | 3600 | 2558.58 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 152271.86 | GGB | 152273.59 | 2558.58 | 2558.58 |  |  |  | 1 | 1 |  |  |  |  | 128164.38 | 2558.58 | 128164.38 | 2558.58 | 8.3038 | [5 empty] | 91.0886 |  |  | #VALUE!
23.02.2008 04:00 | 3600 | 2 | 762.77 | GGB | 763.37 | 771.094 | 768.132 | 251.79 | GGB | 10584.8 | GGB | 9.83 | GGB | 987.16 | GGB | 59.61 | GGB | 161850.88 | GGB | 129455.65 | GGB | 0 | 0 | 2608 | 3600 | 2593.08 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 152310.13 | GGB | 152311.86 | 2593.08 | 2593.08 |  |  |  | 0 | 1 | [14 empty] | 93.2469 |  |  | #VALUE!
23.02.2008 05:00 | 3600 | 2 | 761.69 | GGB | 763.37 | 771.094 | 767.033 | 252.44 | GGB | 10616.4 | GGB | 9.83 | GGB | 987.01 | GGB | 59.37 | GGB | 162825.78 | GGB | 130311.28 | GGB | 0 | 0 | 2639 | 3600 | 2623.17 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 152348.84 | GGB | 152350.57 | 2623.17 | 2623.17 |  |  |  | 0 | 1 | [14 empty] | 94.9524 |  |  | #VALUE!
23.02.2008 06:00 | 3600 | 2 | 761.72 | GGB | 764.835 | 771.141 | 768.132 | 253.14 | GGB | 10649 | GGB | 9.84 | GGB | 987.64 | GGB | 59.1 | GGB | 163487.08 | GGB | 131027.21 | GGB | 0 | 0 | 2657 | 3600 | 2641.91 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 152388.22 | GGB | 152389.95 | 2641.91 | 2641.91 |  |  |  | 1 | 1 |  |  |  |  | 131027.21 | 2641.91 | 131027.21 | 2641.91 | 8.7903 | [5 empty] | 96.1561 |  |  | #VALUE!
23.02.2008 07:00 | 3600 | 2 | 761.62 | GGB | 763.37 | 769.758 | 767.033 | 254.31 | GGB | 10708.8 | GGB | 9.85 | GGB | 987.96 | GGB | 58.62 | GGB | 164951.63 | GGB | 132435.45 | GGB | 0 | 0 | 2679 | 3600 | 2663.37 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 152427.41 | GGB | 152429.13 | 2663.37 | 2663.37 |  |  |  | 0 | 1 | [14 empty] | 97.9791 |  |  | #VALUE!
23.02.2008 08:00 | 3600 | 2 | 760.88 | GGB | 763.37 | 769.758 | 767.033 | 255.4 | GGB | 10758.9 | GGB | 9.85 | GGB | 989.67 | GGB | 58.22 | GGB | 166242.33 | GGB | 133865.91 | GGB | 0 | 0 | 2735 | 3600 | 2719.67 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 152466.87 | GGB | 152468.59 | 2719.67 | 2719.67 |  |  |  | 0 | 1 | [14 empty] | 101.1309 |  |  | #VALUE!
23.02.2008 09:00 | 3600 | 2 | 761.22 | GGB | 763.37 | 769.828 | 766.667 | 255.67 | GGB | 10777.2 | GGB | 9.85 | GGB | 992.16 | GGB | 58.36 | GGB | 166410.68 | GGB | 134281.41 | GGB | 0 | 0 | 2727 | 3600 | 2711.4 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 152506.41 | GGB | 152508.13 | 2711.4 | 2711.4 |  |  |  | 0 | 1 | [14 empty] | 101.1363 |  |  | #VALUE!
23.02.2008 10:00 | 3600 | 2 | 761.36 | GGB | 764.469 | 771.141 | 767.766 | 255.92 | GGB | 10786.6 | GGB | 9.86 | GGB | 993.92 | GGB | 58.31 | GGB | 166270.94 | GGB | 134425.46 | GGB | 0 | 0 | 2734 | 3600 | 2718.76 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 152546.28 | GGB | 152548 | 2718.76 | 2718.76 |  |  |  | 1 | 1 |  |  |  |  | 134425.46 | 2718.76 | 134425.46 | 2718.76 | 9.1666 | [5 empty] | 101.5196 |  |  | #VALUE!
23.02.2008 11:00 | 3600 | 2 | 762.54 | GGB | 765.934 | 772.031 | 768.864 | 256.48 | GGB | 10749.5 | GGB | 9.85 | GGB | 995.2 | GGB | 58.22 | GGB | 167424.09 | GGB | 135572.2 | GGB | 0 | 0 | 2672 | 3600 | 2656.59 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 152585.62 | GGB | 152587.34 | 2656.59 | 2656.59 |  |  |  | 1 | 1 |  |  |  |  | 135572.2 | 2656.59 | 135572.2 | 2656.59 | 9.1551 | [5 empty] | 100.0444 |  |  | #VALUE!
23.02.2008 12:00 | 3600 | 2 | 763.32 | GGB | 764.469 | 772.008 | 768.864 | 255.28 | GGB | 10751.2 | GGB | 9.86 | GGB | 996.09 | GGB | 58.59 | GGB | 165861.61 | GGB | 134274.22 | GGB | 0 | 0 | 2643 | 3600 | 2628.04 | GGB | 100 | GGB | 37.42 | GGB | 37.42 | GGB | 152623.04 | GGB | 152624.76 | 2628.04 | 2628.04 |  |  |  | 1 | 1 |  |  |  |  | 134274.22 | 2628.04 | 134274.22 | 2628.04 | 9.4302 | [5 empty] | 98.0217 |  |  | #VALUE!
23.02.2008 13:00 | 3600 | 2 | 763.25 | GGB | 764.835 | 772.008 | 768.864 | 254.85 | GGB | 10744.7 | GGB | 9.85 | GGB | 996.97 | GGB | 59.02 | GGB | 164949.43 | GGB | 133480.49 | GGB | 0 | 0 | 2645 | 3600 | 2629.55 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 152663.7 | GGB | 152665.42 | 2629.55 | 2629.55 |  |  |  | 1 | 1 |  |  |  |  | 133480.49 | 2629.55 | 133480.49 | 2629.55 | 8.6324 | [5 empty] | 97.4982 |  |  | #VALUE!
23.02.2008 14:00 | 3600 | 2 | 763.68 | GGB | 765.934 | 771.586 | 768.864 | 254.58 | GGB | 10744.2 | GGB | 9.86 | GGB | 997.39 | GGB | 58.86 | GGB | 164881.21 | GGB | 133545.05 | GGB | 0 | 0 | 2630 | 3600 | 2615.1 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 152704.56 | GGB | 152706.27 | 2615.1 | 2615.1 |  |  |  | 1 | 1 |  |  |  |  | 133545.05 | 2615.1 | 133545.05 | 2615.1 | 8.5492 | [5 empty] | 97.0094 |  |  | #VALUE!
23.02.2008 15:00 | 3600 | 2 | 763.22 | GGB | 764.835 | 771.633 | 768.498 | 254.79 | GGB | 10753.9 | GGB | 9.85 | GGB | 997.96 | GGB | 59.04 | GGB | 164804.19 | GGB | 133488.81 | GGB | 0 | 0 | 2658 | 3600 | 2642.73 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 152742.47 | GGB | 152744.18 | 2642.73 | 2642.73 |  |  |  | 1 | 1 |  |  |  |  | 133488.81 | 2642.73 | 133488.81 | 2642.73 | 9.3056 | [5 empty] | 97.993 |  |  | #VALUE!
23.02.2008 16:00 | 3600 | 2 | 763.15 | GGB | 765.934 | 772.453 | 769.597 | 255.25 | GGB | 10773.6 | GGB | 9.86 | GGB | 998.56 | GGB | 58.99 | GGB | 165075.97 | GGB | 133808.12 | GGB | 0 | 0 | 2670 | 3600 | 2654.88 | GGB | 100 | GGB | 42.04 | GGB | 42.04 | GGB | 152784.5 | GGB | 152786.22 | 2654.88 | 2654.88 |  |  |  | 1 | 1 |  |  |  |  | 133808.12 | 2654.88 | 133808.12 | 2654.88 | 8.4502 | [5 empty] | 98.679 |  |  | #VALUE!
23.02.2008 17:00 | 3600 | 2 | 763.39 | GGB | 764.835 | 772.453 | 768.498 | 255.17 | GGB | 10759.9 | GGB | 9.85 | GGB | 999.48 | GGB | 59.19 | GGB | 164708.46 | GGB | 133555.47 | GGB | 0 | 0 | 2657 | 3600 | 2641.52 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 152823.39 | GGB | 152825.11 | 2641.52 | 2641.52 |  |  |  | 1 | 1 |  |  |  |  | 133555.47 | 2641.52 | 133555.47 | 2641.52 | 9.0715 | [5 empty] | 97.9971 |  |  | #VALUE!
23.02.2008 18:00 | 3600 | 2 | 762.91 | GGB | 764.835 | 771.305 | 768.498 | 255.99 | GGB | 10779.5 | GGB | 9.85 | GGB | 1000.88 | GGB | 59.11 | GGB | 165418.18 | GGB | 134348.88 | GGB | 0 | 0 | 2687 | 3600 | 2671.4 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 152862.27 | GGB | 152863.99 | 2671.4 | 2671.4 |  |  |  | 1 | 1 |  |  |  |  | 134348.88 | 2671.4 | 134348.88 | 2671.4 | 9.231 | [5 empty] | 99.6943 |  |  | #VALUE!
23.02.2008 19:00 | 3600 | 2 | 762.54 | GGB | 765.934 | 772.57 | 769.597 | 256.32 | GGB | 10816.1 | GGB | 9.86 | GGB | 1002.4 | GGB | 59.09 | GGB | 166464.6 | GGB | 135413.24 | GGB | 0 | 0 | 2709 | 3600 | 2693.2 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 152903.46 | GGB | 152905.18 | 2693.2 | 2693.2 |  |  |  | 1 | 1 |  |  |  |  | 135413.24 | 2693.2 | 135413.24 | 2693.2 | 8.854 | [5 empty] | 101.3041 |  |  | #VALUE!
23.02.2008 20:00 | 3600 | 2 | 761.72 | GGB | 763.37 | 770.273 | 767.033 | 258.2 | GGB | 10808 | GGB | 9.84 | GGB | 1003.9 | GGB | 58.88 | GGB | 166533.92 | GGB | 135758.23 | GGB | 0 | 0 | 2747 | 3600 | 2731.15 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 152941.53 | GGB | 152943.26 | 2731.15 | 2731.15 |  |  |  | 0 | 1 | [14 empty] | 102.9934 |  |  | #VALUE!
23.02.2008 21:00 | 3600 | 2 | 762.08 | GGB | 764.469 | 771.445 | 768.132 | 259.57 | GGB | 10819.8 | GGB | 9.85 | GGB | 1005.3 | GGB | 59.33 | GGB | 166868.42 | GGB | 136037.98 | GGB | 0 | 0 | 2748 | 3600 | 2732.79 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 152982.07 | GGB | 152983.79 | 2732.79 | 2732.79 |  |  |  | 1 | 1 |  |  |  |  | 136037.98 | 2732.79 | 136037.98 | 2732.79 | 9.1725 | [5 empty] | 103.2676 |  |  | #VALUE!
23.02.2008 22:00 | 3600 | 2 | 762.13 | GGB | 764.835 | 771.492 | 768.132 | 260.58 | GGB | 10828.4 | GGB | 9.85 | GGB | 1006.35 | GGB | 59.44 | GGB | 166985.06 | GGB | 136230.36 | GGB | 0 | 0 | 2752 | 3600 | 2736.15 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 153021.73 | GGB | 153023.45 | 2736.15 | 2736.15 |  |  |  | 1 | 1 |  |  |  |  | 136230.36 | 2736.15 | 136230.36 | 2736.15 | 9.3986 | [5 empty] | 103.5407 |  |  | #VALUE!
23.02.2008 23:00 | 3600 | 2 | 761.95 | GGB | 764.469 | 771.492 | 767.033 | 261.11 | GGB | 10826 | GGB | 9.85 | GGB | 1006.75 | GGB | 59.67 | GGB | 167319.56 | GGB | 136461.58 | GGB | 0 | 0 | 2756 | 3600 | 2740.84 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 153060.24 | GGB | 153061.96 | 2740.84 | 2740.84 |  |  |  | 1 | 1 |  |  |  |  | 136461.58 | 2740.84 | 136461.58 | 2740.84 | 9.7123 | [5 empty] | 103.8943 |  |  | #VALUE!
23.02.2008 24:00 | 3600 | 2 | 762.34 | GGB | 765.934 | 772.5 | 769.597 | 262.86 | GGB | 10825.3 | GGB | 9.85 | GGB | 1007.28 | GGB | 59.48 | GGB | 168810.52 | GGB | 137827.63 | GGB | 0 | 0 | 2747 | 3600 | 2731.12 | GGB | 100 | GGB | 41.04 | GGB | 41.04 | GGB | 153101.27 | GGB | 153103 | 2731.12 | 2731.12 |  |  |  | 1 | 1 |  |  |  |  | 137827.63 | 2731.12 | 137827.63 | 2731.12 | 9.1721 | [5 empty] | 104.5622 |  |  | #VALUE!
24.02.2008 01:00 | 3600 | 2 | 762.38 | GGB | 764.835 | 772.359 | 768.498 | 261.93 | GGB | 10848.2 | GGB | 9.86 | GGB | 1007.57 | GGB | 59.99 | GGB | 167319.56 | GGB | 136442.51 | GGB | 0 | 0 | 2764 | 3600 | 2748.59 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 153140.16 | GGB | 153141.89 | 2748.59 | 2748.59 |  |  |  | 1 | 1 |  |  |  |  | 136442.51 | 2748.59 | 136442.51 | 2748.59 | 9.6432 | [5 empty] | 104.1735 |  |  | #VALUE!
24.02.2008 02:00 | 3600 | 2 | 762.33 | GGB | 764.469 | 771.164 | 768.498 | 262.06 | GGB | 10837.1 | GGB | 9.85 | GGB | 1008.29 | GGB | 60.27 | GGB | 167154.51 | GGB | 136286.91 | GGB | 0 | 0 | 2764 | 3600 | 2748.36 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 153179.65 | GGB | 153181.38 | 2748.36 | 2748.36 |  |  |  | 1 | 1 |  |  |  |  | 136286.91 | 2748.36 | 136286.91 | 2748.36 | 9.4851 | [5 empty] | 104.046 |  |  | #VALUE!
24.02.2008 03:00 | 3600 | 2 | 762.11 | GGB | 764.835 | 771 | 768.132 | 262.78 | GGB | 10845.7 | GGB | 9.85 | GGB | 1008.73 | GGB | 60.46 | GGB | 167605.65 | GGB | 136639.88 | GGB | 0 | 0 | 2774 | 3600 | 2759 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 153220.55 | GGB | 153222.28 | 2759 | 2759 |  |  |  | 1 | 1 |  |  |  |  | 136639.88 | 2759 | 136639.88 | 2759 | 9.2173 | [5 empty] | 104.7193 |  |  | #VALUE!
24.02.2008 04:00 | 3600 | 2 | 762.38 | GGB | 764.469 | 771.047 | 768.132 | 263.2 | GGB | 10856.9 | GGB | 9.85 | GGB | 1009.05 | GGB | 60.5 | GGB | 168030.38 | GGB | 137013.15 | GGB | 0 | 0 | 2782 | 3600 | 2766.12 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 153259.22 | GGB | 153260.95 | 2766.12 | 2758.3338 |  |  |  | 1 | 1 |  |  |  |  | 137013.15 | 2758.3338 | 137013.15 | 2758.3338 | 9.7732 | [5 empty] | 105.2763 | 2758.3338 |  | 104.98
24.02.2008 05:00 | 3600 | 2 | 762.61 | GGB | 764.835 | 771.07 | 768.498 | 263.02 | GGB | 10863.7 | GGB | 9.86 | GGB | 1009.5 | GGB | 60.53 | GGB | 167956.65 | GGB | 137002.84 | GGB | 0 | 0 | 2771 | 3600 | 2755.52 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 153299.36 | GGB | 153301.09 | 2755.52 | 2755.52 |  |  |  | 1 | 1 |  |  |  |  | 137002.84 | 2755.52 | 137002.84 | 2755.52 | 9.4049 | [5 empty] | 104.865 |  |  | #VALUE!
24.02.2008 06:00 | 3600 | 2 | 762.56 | GGB | 764.835 | 771.023 | 768.498 | 263.37 | GGB | 10856 | GGB | 9.85 | GGB | 1010.04 | GGB | 60.73 | GGB | 167846.62 | GGB | 136900.85 | GGB | 0 | 0 | 2782 | 3600 | 2766.63 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 153339.64 | GGB | 153341.38 | 2766.63 | 2760.5964 |  |  |  | 1 | 1 |  |  |  |  | 136900.85 | 2760.5964 | 136900.85 | 2760.5964 | 9.3802 | [5 empty] | 105.2094 | 2760.5964 |  | 104.98
24.02.2008 07:00 | 3600 | 2 | 763.29 | GGB | 767.033 | 773.203 | 770.696 | 262.91 | GGB | 10852.6 | GGB | 9.86 | GGB | 1009.66 | GGB | 60.9 | GGB | 167398.78 | GGB | 136417.7 | GGB | 0 | 0 | 2755 | 3600 | 2739.24 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 153378.56 | GGB | 153380.3 | 2739.24 | 2739.24 |  |  |  | 1 | 1 |  |  |  |  | 136417.7 | 2739.24 | 136417.7 | 2739.24 | 9.6013 | [5 empty] | 103.8002 |  |  | #VALUE!
24.02.2008 08:00 | 3600 | 2 | 763.57 | GGB | 764.835 | 771.984 | 768.498 | 262.02 | GGB | 10809.3 | GGB | 9.85 | GGB | 1009.69 | GGB | 61.26 | GGB | 166314.95 | GGB | 135392.5 | GGB | 0 | 0 | 2736 | 3600 | 2720.13 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 153418.98 | GGB | 153420.72 | 2720.13 | 2720.13 |  |  |  | 1 | 1 |  |  |  |  | 135392.5 | 2720.13 | 135392.5 | 2720.13 | 9.1115 | [5 empty] | 102.3014 |  |  | #VALUE!
24.02.2008 09:00 | 3600 | 2 | 763.83 | GGB | 765.934 | 773.086 | 769.597 | 261.68 | GGB | 10805.3 | GGB | 9.86 | GGB | 1009.15 | GGB | 61.44 | GGB | 165966.14 | GGB | 134959.5 | GGB | 0 | 0 | 2723 | 3600 | 2707.4 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 153458.65 | GGB | 153460.39 | 2707.4 | 2707.4 |  |  |  | 1 | 1 |  |  |  |  | 134959.5 | 2707.4 | 134959.5 | 2707.4 | 9.2107 | [5 empty] | 101.497 |  |  | #VALUE!
24.02.2008 10:00 | 3600 | 2 | 763.68 | GGB | 765.934 | 772.148 | 769.597 | 260.93 | GGB | 10800.9 | GGB | 9.86 | GGB | 1008.96 | GGB | 61.46 | GGB | 165544.71 | GGB | 134584.04 | GGB | 0 | 0 | 2719 | 3600 | 2703.48 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 153497.73 | GGB | 153499.47 | 2703.48 | 2703.48 |  |  |  | 1 | 1 |  |  |  |  | 134584.04 | 2703.48 | 134584.04 | 2703.48 | 9.3103 | [5 empty] | 101.0681 |  |  | #VALUE!
24.02.2008 11:00 | 3600 | 2 | 764.08 | GGB | 767.033 | 773.18 | 769.597 | 260.06 | GGB | 10796.2 | GGB | 9.86 | GGB | 1008.63 | GGB | 61.46 | GGB | 165260.83 | GGB | 134311.79 | GGB | 0 | 0 | 2704 | 3600 | 2688.68 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 153538.23 | GGB | 153539.97 | 2688.68 | 2688.68 |  |  |  | 1 | 1 |  |  |  |  | 134311.79 | 2688.68 | 134311.79 | 2688.68 | 8.9166 | [5 empty] | 100.3115 |  |  | #VALUE!
24.02.2008 12:00 | 3600 | 2 | 764.28 | GGB | 767.033 | 774.234 | 770.696 | 259.11 | GGB | 10783.3 | GGB | 9.86 | GGB | 1008.14 | GGB | 61.29 | GGB | 164533.5 | GGB | 133722.3 | GGB | 0 | 0 | 2683 | 3600 | 2668.07 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 153577.65 | GGB | 153579.39 | 2668.07 | 2668.07 |  |  |  | 1 | 1 |  |  |  |  | 133722.3 | 2668.07 | 133722.3 | 2668.07 | 9.0507 | [5 empty] | 99.1057 |  |  | #VALUE!
24.02.2008 13:00 | 3600 | 2 | 764.34 | GGB | 765.934 | 772.875 | 769.597 | 258.7 | GGB | 10758.9 | GGB | 9.85 | GGB | 1007.32 | GGB | 61.03 | GGB | 164365.15 | GGB | 133581.47 | GGB | 0 | 0 | 2663 | 3600 | 2647.83 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 153617.23 | GGB | 153618.97 | 2647.83 | 2647.83 |  |  |  | 1 | 1 |  |  |  |  | 133581.47 | 2647.83 | 133581.47 | 2647.83 | 8.9364 | [5 empty] | 98.2503 |  |  | #VALUE!
24.02.2008 14:00 | 3600 | 2 | 764.64 | GGB | 765.934 | 774.07 | 770.696 | 258.18 | GGB | 10736.7 | GGB | 9.86 | GGB | 1006.97 | GGB | 61.45 | GGB | 163400.16 | GGB | 132584.8 | GGB | 0 | 0 | 2643 | 3600 | 2628.1 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 153657.67 | GGB | 153659.41 | 2628.1 | 2628.1 |  |  |  | 1 | 1 |  |  |  |  | 132584.8 | 2628.1 | 132584.8 | 2628.1 | 8.6164 | [5 empty] | 96.7906 |  |  | #VALUE!
24.02.2008 15:00 | 3600 | 2 | 765.19 | GGB | 767.033 | 775.102 | 771.795 | 258.38 | GGB | 10715.5 | GGB | 9.86 | GGB | 1006.32 | GGB | 61.17 | GGB | 163977.83 | GGB | 133078.42 | GGB | 0 | 0 | 2607 | 3600 | 2591.76 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 153696.77 | GGB | 153698.51 | 2591.76 | 2591.76 |  |  |  | 1 | 1 |  |  |  |  | 133078.42 | 2591.76 | 133078.42 | 2591.76 | 8.8212 | [5 empty] | 95.8076 |  |  | #VALUE!
24.02.2008 16:00 | 3600 | 2 | 765.04 | GGB | 768.132 | 775.031 | 771.795 | 257.5 | GGB | 10698.1 | GGB | 9.85 | GGB | 1006.03 | GGB | 61.53 | GGB | 162978.73 | GGB | 132086.41 | GGB | 0 | 0 | 2607 | 3600 | 2591.49 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 153736.08 | GGB | 153737.83 | 2591.49 | 2591.49 |  |  |  | 1 | 1 |  |  |  |  | 132086.41 | 2591.49 | 132086.41 | 2591.49 | 8.7055 | [5 empty] | 95.0835 |  |  | #VALUE!
24.02.2008 17:00 | 3600 | 2 | 765.37 | GGB | 767.033 | 774.023 | 770.696 | 256.54 | GGB | 10695.1 | GGB | 9.86 | GGB | 1005.97 | GGB | 62.02 | GGB | 161627.51 | GGB | 130793.89 | GGB | 0 | 0 | 2586 | 3600 | 2570.52 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 153775.93 | GGB | 153777.68 | 2570.52 | 2570.52 |  |  |  | 1 | 1 |  |  |  |  | 130793.89 | 2570.52 | 130793.89 | 2570.52 | 8.4368 | [5 empty] | 93.3912 |  |  | #VALUE!
24.02.2008 18:00 | 3600 | 2 | 765.57 | GGB | 767.033 | 775.102 | 771.795 | 256.25 | GGB | 10684.7 | GGB | 9.86 | GGB | 1005.86 | GGB | 62.12 | GGB | 161339.22 | GGB | 130504.8 | GGB | 0 | 0 | 2578 | 3600 | 2562.73 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 153814.7 | GGB | 153816.45 | 2562.73 | 2562.73 |  |  |  | 1 | 1 |  |  |  |  | 130504.8 | 2562.73 | 130504.8 | 2562.73 | 8.6265 | [5 empty] | 92.9024 |  |  | #VALUE!
24.02.2008 19:00 | 3600 | 2 | 765.69 | GGB | 767.033 | 774.984 | 771.795 | 256.25 | GGB | 10683.4 | GGB | 9.85 | GGB | 1005.9 | GGB | 62.05 | GGB | 161257.8 | GGB | 130470.82 | GGB | 0 | 0 | 2575 | 3600 | 2559.26 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 153854.24 | GGB | 153855.99 | 2559.26 | 2559.26 |  |  |  | 1 | 1 |  |  |  |  | 130470.82 | 2559.26 | 130470.82 | 2559.26 | 8.4448 | [5 empty] | 92.7524 |  |  | #VALUE!
24.02.2008 20:00 | 3600 | 2 | 765.67 | GGB | 768.132 | 774.984 | 771.795 | 256.26 | GGB | 10681.7 | GGB | 9.85 | GGB | 1006.11 | GGB | 62.03 | GGB | 161364.53 | GGB | 130593.12 | GGB | 0 | 0 | 2567 | 3600 | 2551.42 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 153893.83 | GGB | 153895.58 | 2551.42 | 2551.42 |  |  |  | 1 | 1 |  |  |  |  | 130593.12 | 2551.42 | 130593.12 | 2551.42 | 8.4162 | [5 empty] | 92.555 |  |  | #VALUE!
24.02.2008 21:00 | 3600 | 2 | 765.56 | GGB | 767.033 | 775.102 | 771.795 | 255.79 | GGB | 10698.6 | GGB | 9.85 | GGB | 1006.24 | GGB | 61.73 | GGB | 162026.93 | GGB | 131264.57 | GGB | 0 | 0 | 2580 | 3600 | 2564.82 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 153932.47 | GGB | 153934.23 | 2564.82 | 2564.82 |  |  |  | 1 | 1 |  |  |  |  | 131264.57 | 2564.82 | 131264.57 | 2564.82 | 8.7107 | [5 empty] | 93.5194 |  |  | #VALUE!
24.02.2008 22:00 | 3600 | 2 | 765.91 | GGB | 767.033 | 775.102 | 771.795 | 256.41 | GGB | 10697.2 | GGB | 9.86 | GGB | 1005.76 | GGB | 61.98 | GGB | 161843.18 | GGB | 130956.9 | GGB | 0 | 0 | 2563 | 3600 | 2547.75 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 153972.7 | GGB | 153974.46 | 2547.75 | 2547.75 |  |  |  | 1 | 1 |  |  |  |  | 130956.9 | 2547.75 | 130956.9 | 2547.75 | 8.2934 | [5 empty] | 92.6793 |  |  | #VALUE!
24.02.2008 23:00 | 3600 | 2 | 765.78 | GGB | 767.033 | 775.102 | 771.795 | 256.13 | GGB | 10692 | GGB | 9.85 | GGB | 1005.34 | GGB | 61.89 | GGB | 161878.39 | GGB | 130964.78 | GGB | 0 | 0 | 2557 | 3600 | 2541.57 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 154012.11 | GGB | 154013.87 | 2541.57 | 2541.57 |  |  |  | 1 | 1 |  |  |  |  | 130964.78 | 2541.57 | 130964.78 | 2541.57 | 8.446 | [5 empty] | 92.46 |  |  | #VALUE!
24.02.2008 24:00 | 3600 | 2 | 765.8 | GGB | 767.033 | 775.102 | 770.696 | 256.15 | GGB | 10691.3 | GGB | 9.86 | GGB | 1004.88 | GGB | 61.83 | GGB | 162086.35 | GGB | 131097.48 | GGB | 0 | 0 | 2558 | 3600 | 2543.13 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 154050.56 | GGB | 154052.32 | 2543.13 | 2543.13 |  |  |  | 1 | 1 |  |  |  |  | 131097.48 | 2543.13 | 131097.48 | 2543.13 | 8.6709 | [5 empty] | 92.6105 |  |  | #VALUE!
25.02.2008 01:00 | 3600 | 2 | 765.45 | GGB | 767.033 | 774.023 | 771.795 | 256.32 | GGB | 10685.4 | GGB | 9.85 | GGB | 1004.51 | GGB | 61.85 | GGB | 162045.64 | GGB | 131007.17 | GGB | 0 | 0 | 2568 | 3600 | 2552.32 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 154090.8 | GGB | 154092.56 | 2552.32 | 2552.32 |  |  |  | 1 | 1 |  |  |  |  | 131007.17 | 2552.32 | 131007.17 | 2552.32 | 8.3094 | [5 empty] | 92.8812 |  |  | #VALUE!
25.02.2008 02:00 | 3600 | 2 | 765.5 | GGB | 768.132 | 774.914 | 771.795 | 256.27 | GGB | 10687.2 | GGB | 9.86 | GGB | 1003.9 | GGB | 61.84 | GGB | 162032.44 | GGB | 130920.23 | GGB | 0 | 0 | 2566 | 3600 | 2550.23 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 154129.88 | GGB | 154131.64 | 2550.23 | 2550.23 |  |  |  | 1 | 1 |  |  |  |  | 130920.23 | 2550.23 | 130920.23 | 2550.23 | 8.5434 | [5 empty] | 92.7435 |  |  | #VALUE!
25.02.2008 03:00 | 3600 | 2 | 765.3 | GGB | 767.033 | 773.859 | 770.696 | 256.29 | GGB | 10689.5 | GGB | 9.85 | GGB | 1003.49 | GGB | 61.79 | GGB | 162221.69 | GGB | 131039.27 | GGB | 0 | 0 | 2569 | 3600 | 2554.01 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 154168.67 | GGB | 154170.43 | 2554.01 | 2554.01 |  |  |  | 1 | 1 |  |  |  |  | 131039.27 | 2554.01 | 131039.27 | 2554.01 | 8.6279 | [5 empty] | 92.9654 |  |  | #VALUE!
25.02.2008 04:00 | 3600 | 2 | 765.02 | GGB | 767.033 | 773.859 | 770.696 | 256.42 | GGB | 10693.6 | GGB | 9.85 | GGB | 1002.97 | GGB | 61.63 | GGB | 162353.73 | GGB | 131140.95 | GGB | 0 | 0 | 2588 | 3600 | 2572.21 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 154209.07 | GGB | 154210.83 | 2572.21 | 2572.21 |  |  |  | 1 | 1 |  |  |  |  | 131140.95 | 2572.21 | 131140.95 | 2572.21 | 8.3496 | [5 empty] | 93.7006 |  |  | #VALUE!
25.02.2008 05:00 | 3600 | 2 | 764.87 | GGB | 765.934 | 773.859 | 770.696 | 256.39 | GGB | 10696.9 | GGB | 9.86 | GGB | 1002.53 | GGB | 61.53 | GGB | 162402.15 | GGB | 131160.39 | GGB | 0 | 0 | 2590 | 3600 | 2574.21 | GGB | 100 | GGB | 38.69 | GGB | 38.69 | GGB | 154247.76 | GGB | 154249.52 | 2574.21 | 2574.21 |  |  |  | 1 | 1 |  |  |  |  | 131160.39 | 2574.21 | 131160.39 | 2574.21 | 8.7267 | [5 empty] | 93.7873 |  |  | #VALUE!
25.02.2008 06:00 | 3600 | 2 | 764.89 | GGB | 767.033 | 773.859 | 770.33 | 256.25 | GGB | 10691.2 | GGB | 9.85 | GGB | 1002.18 | GGB | 61.49 | GGB | 162333.93 | GGB | 131076.4 | GGB | 0 | 0 | 2589 | 3600 | 2573.66 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 154286.85 | GGB | 154288.62 | 2573.66 | 2573.66 |  |  |  | 1 | 1 |  |  |  |  | 131076.4 | 2573.66 | 131076.4 | 2573.66 | 8.6278 | [5 empty] | 93.7072 |  |  | #VALUE!
25.02.2008 07:00 | 3600 | 2 | 764.87 | GGB | 767.033 | 773.859 | 770.696 | 256.31 | GGB | 10685 | GGB | 9.85 | GGB | 1001.75 | GGB | 61.6 | GGB | 162302.02 | GGB | 130951.49 | GGB | 0 | 0 | 2589 | 3600 | 2574.12 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 154326.98 | GGB | 154328.75 | 2574.12 | 2574.12 |  |  |  | 1 | 1 |  |  |  |  | 130951.49 | 2574.12 | 130951.49 | 2574.12 | 8.3998 | [5 empty] | 93.6347 |  |  | #VALUE!
25.02.2008 08:00 | 3600 | 2 | 764.69 | GGB | 767.033 | 773.859 | 770.33 | 257.52 | GGB | 10665.4 | GGB | 9.85 | GGB | 1001.49 | GGB | 61.16 | GGB | 163761.07 | GGB | 132268.13 | GGB | 0 | 0 | 2583 | 3600 | 2567.51 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 154365.53 | GGB | 154367.3 | 2567.51 | 2567.51 |  |  |  | 1 | 1 |  |  |  |  | 132268.13 | 2567.51 | 132268.13 | 2567.51 | 8.8093 | [5 empty] | 94.3333 |  |  | #VALUE!
25.02.2008 09:00 | 3600 | 2 | 765.07 | GGB | 765.934 | 773.836 | 770.696 | 256.25 | GGB | 10683.9 | GGB | 9.86 | GGB | 1001.26 | GGB | 61.56 | GGB | 162153.47 | GGB | 130781.88 | GGB | 0 | 0 | 2587 | 3600 | 2572.06 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 154404.73 | GGB | 154406.5 | 2572.06 | 2572.06 |  |  |  | 1 | 1 |  |  |  |  | 130781.88 | 2572.06 | 130781.88 | 2572.06 | 8.5811 | [5 empty] | 93.4386 |  |  | #VALUE!
25.02.2008 10:00 | 3600 | 2 | 764.72 | GGB | 767.033 | 774.117 | 770.696 | 256.25 | GGB | 10688.7 | GGB | 9.86 | GGB | 1001.45 | GGB | 61.49 | GGB | 162139.17 | GGB | 130823.25 | GGB | 0 | 0 | 2602 | 3600 | 2586.25 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 154445.15 | GGB | 154446.92 | 2586.25 | 2586.25 |  |  |  | 1 | 1 |  |  |  |  | 130823.25 | 2586.25 | 130823.25 | 2586.25 | 8.3706 | [5 empty] | 93.9838 |  |  | #VALUE!
25.02.2008 11:00 | 3600 | 2 | 764.97 | GGB | 767.033 | 774.258 | 770.696 | 257.4 | GGB | 10653.8 | GGB | 9.85 | GGB | 1001.21 | GGB | 60.95 | GGB | 163847.99 | GGB | 132383.92 | GGB | 0 | 0 | 2575 | 3600 | 2559.27 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 154483.95 | GGB | 154485.72 | 2559.27 | 2559.27 |  |  |  | 1 | 1 |  |  |  |  | 132383.92 | 2559.27 | 132383.92 | 2559.27 | 8.7321 | [5 empty] | 94.1128 |  |  | #VALUE!
25.02.2008 12:00 | 3600 | 2 | 765.17 | GGB | 767.033 | 774.258 | 769.597 | 256.61 | GGB | 10653.9 | GGB | 9.85 | GGB | 1000.7 | GGB | 60.89 | GGB | 162969.92 | GGB | 131632.19 | GGB | 0 | 0 | 2566 | 3600 | 2550.67 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 154522.9 | GGB | 154524.67 | 2550.67 | 2550.67 |  |  |  | 1 | 1 |  |  |  |  | 131632.19 | 2550.67 | 131632.19 | 2550.67 | 8.62 | [5 empty] | 93.264 |  |  | #VALUE!
25.02.2008 13:00 | 3600 | 2 | 764.27 | GGB | 767.033 | 774.234 | 770.696 | 256.63 | GGB | 10697.8 | GGB | 9.85 | GGB | 1000.73 | GGB | 61.26 | GGB | 162761.96 | GGB | 131321.11 | GGB | 0 | 0 | 2627 | 3600 | 2612.07 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 154562.81 | GGB | 154564.57 | 2612.07 | 2612.07 |  |  |  | 1 | 1 |  |  |  |  | 131321.11 | 2612.07 | 131321.11 | 2612.07 | 8.597 | [5 empty] | 95.2833 |  |  | #VALUE!
25.02.2008 14:00 | 3600 | 2 | 764.18 | GGB | 765.934 | 772.922 | 769.597 | 257.24 | GGB | 10708.8 | GGB | 9.85 | GGB | 1000.77 | GGB | 61.32 | GGB | 163301.13 | GGB | 131740.29 | GGB | 0 | 0 | 2636 | 3600 | 2620.31 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 154601.6 | GGB | 154603.36 | 2620.31 | 2620.31 |  |  |  | 1 | 1 |  |  |  |  | 131740.29 | 2620.31 | 131740.29 | 2620.31 | 8.8992 | [5 empty] | 95.889 |  |  | #VALUE!
25.02.2008 15:00 | 3600 | 2 | 763.54 | GGB | 764.835 | 771.797 | 768.864 | 257.92 | GGB | 10734.2 | GGB | 9.85 | GGB | 1000.61 | GGB | 60.67 | GGB | 164152.79 | GGB | 132661.16 | GGB | 0 | 0 | 2669 | 3600 | 2653.87 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 154641.02 | GGB | 154642.78 | 2653.87 | 2653.87 |  |  |  | 1 | 1 |  |  |  |  | 132661.16 | 2653.87 | 132661.16 | 2653.87 | 8.9311 | [5 empty] | 97.796 |  |  | #VALUE!
25.02.2008 16:00 | 3600 | 2 | 762.89 | GGB | 764.835 | 771.727 | 767.766 | 258.6 | GGB | 10769.8 | GGB | 9.85 | GGB | 1001.26 | GGB | 59.96 | GGB | 165127.69 | GGB | 133824.09 | GGB | 0 | 0 | 2708 | 3600 | 2692.53 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 154680.97 | GGB | 154682.73 | 2692.53 | 2692.53 |  |  |  | 1 | 1 |  |  |  |  | 133824.09 | 2692.53 | 133824.09 | 2692.53 | 9.0194 | [5 empty] | 100.0904 |  |  | #VALUE!
25.02.2008 17:00 | 3600 | 2 | 763.22 | GGB | 764.835 | 771.516 | 768.864 | 258.68 | GGB | 10769.9 | GGB | 9.86 | GGB | 1001.84 | GGB | 60.28 | GGB | 165193.71 | GGB | 133822.57 | GGB | 0 | 0 | 2697 | 3600 | 2681.86 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 154719.74 | GGB | 154721.5 | 2681.86 | 2681.86 |  |  |  | 1 | 1 |  |  |  |  | 133822.57 | 2681.86 | 133822.57 | 2681.86 | 9.257 | [5 empty] | 99.6926 |  |  | #VALUE!
25.02.2008 18:00 | 3600 | 2 | 763.1 | GGB | 764.835 | 771.516 | 767.766 | 258.78 | GGB | 10770.1 | GGB | 9.85 | GGB | 1002.39 | GGB | 60.32 | GGB | 165297.14 | GGB | 133964.25 | GGB | 0 | 0 | 2700 | 3600 | 2684.19 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 154759.9 | GGB | 154761.66 | 2684.19 | 2684.19 |  |  |  | 1 | 1 |  |  |  |  | 133964.25 | 2684.19 | 133964.25 | 2684.19 | 8.9538 | [5 empty] | 99.8849 |  |  | #VALUE!
25.02.2008 19:00 | 3600 | 2 | 763.27 | GGB | 764.835 | 772.547 | 768.864 | 259.16 | GGB | 10785.2 | GGB | 9.85 | GGB | 1003.37 | GGB | 60.37 | GGB | 165497.4 | GGB | 134240.51 | GGB | 0 | 0 | 2704 | 3600 | 2688.76 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 154799.35 | GGB | 154801.11 | 2688.76 | 2688.76 |  |  |  | 1 | 1 |  |  |  |  | 134240.51 | 2688.76 | 134240.51 | 2688.76 | 9.1493 | [5 empty] | 100.2613 |  |  | #VALUE!
25.02.2008 20:00 | 3600 | 2 | 763.16 | GGB | 764.835 | 771.492 | 767.766 | 259.65 | GGB | 10794.6 | GGB | 9.85 | GGB | 1004.66 | GGB | 60.32 | GGB | 165972.75 | GGB | 134819.42 | GGB | 0 | 0 | 2716 | 3600 | 2700.23 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 154838.77 | GGB | 154840.53 | 2700.23 | 2700.23 |  |  |  | 1 | 1 |  |  |  |  | 134819.42 | 2700.23 | 134819.42 | 2700.23 | 9.235 | [5 empty] | 101.1232 |  |  | #VALUE!
25.02.2008 21:00 | 3600 | 2 | 762.79 | GGB | 764.835 | 772.758 | 768.864 | 261.12 | GGB | 10805.7 | GGB | 9.85 | GGB | 1005.67 | GGB | 59.79 | GGB | 167611.15 | GGB | 136503.08 | GGB | 0 | 0 | 2726 | 3600 | 2710.49 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 154879.69 | GGB | 154881.45 | 2710.49 | 2710.49 |  |  |  | 1 | 1 |  |  |  |  | 136503.08 | 2710.49 | 136503.08 | 2710.49 | 9.0418 | [5 empty] | 102.7751 |  |  | #VALUE!
25.02.2008 22:00 | 3600 | 2 | 762.83 | GGB | 764.835 | 771.516 | 767.766 | 260.85 | GGB | 10831.7 | GGB | 9.85 | GGB | 1006.59 | GGB | 60.04 | GGB | 167127 | GGB | 136132.06 | GGB | 0 | 0 | 2748 | 3600 | 2732.87 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 154918.31 | GGB | 154920.07 | 2732.87 | 2732.87 |  |  |  | 1 | 1 |  |  |  |  | 136132.06 | 2732.87 | 136132.06 | 2732.87 | 9.6331 | [5 empty] | 103.342 |  |  | #VALUE!
25.02.2008 23:00 | 3600 | 2 | 762.21 | GGB | 765.934 | 771.516 | 768.864 | 261.96 | GGB | 10821 | GGB | 9.85 | GGB | 1007.08 | GGB | 59.55 | GGB | 168780.81 | GGB | 137747.09 | GGB | 0 | 0 | 2759 | 3600 | 2743.36 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 154956.35 | GGB | 154958.11 | 2743.36 | 2743.36 |  |  |  | 1 | 1 |  |  |  |  | 137747.09 | 2743.36 | 137747.09 | 2743.36 | 9.934 | [5 empty] | 104.9694 |  |  | #VALUE!
25.02.2008 24:00 | 3600 | 2 | 762.84 | GGB | 763.37 | 770.625 | 767.766 | 261.37 | GGB | 10866.3 | GGB | 9.86 | GGB | 1007.61 | GGB | 59.1 | GGB | 169039.39 | GGB | 138218.13 | GGB | 0 | 0 | 2747 | 3600 | 2731.64 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 154997.86 | GGB | 154999.62 | 2731.64 | 2731.64 |  |  |  | 0 | 1 | [14 empty] | 104.8784 |  |  | #VALUE!
26.02.2008 01:00 | 3600 | 2 | 762.24 | GGB | 764.469 | 771.703 | 768.864 | 261.05 | GGB | 10859 | GGB | 9.85 | GGB | 1008.1 | GGB | 59.63 | GGB | 167772.9 | GGB | 137030.89 | GGB | 0 | 0 | 2783 | 3600 | 2767.53 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 155037.68 | GGB | 155039.45 | 2767.53 | 2757.9767 |  |  |  | 1 | 1 |  |  |  |  | 137030.89 | 2757.9767 | 137030.89 | 2757.9767 | 9.4885 | [5 empty] | 105.3436 | 2757.9767 |  | 104.98
26.02.2008 02:00 | 3600 | 2 | 762.82 | GGB | 765.934 | 772.828 | 768.864 | 260.93 | GGB | 10857.7 | GGB | 9.86 | GGB | 1008.71 | GGB | 59.91 | GGB | 167407.59 | GGB | 136698.55 | GGB | 0 | 0 | 2765 | 3600 | 2749.86 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 155076.93 | GGB | 155078.69 | 2749.86 | 2749.86 |  |  |  | 1 | 1 |  |  |  |  | 136698.55 | 2749.86 | 136698.55 | 2749.86 | 9.5796 | [5 empty] | 104.4172 |  |  | #VALUE!
26.02.2008 03:00 | 3600 | 2 | 762.99 | GGB | 764.835 | 771.703 | 768.864 | 260.85 | GGB | 10842.8 | GGB | 9.85 | GGB | 1008.94 | GGB | 60.29 | GGB | 166934.44 | GGB | 136188.02 | GGB | 0 | 0 | 2757 | 3600 | 2741.08 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 155117.8 | GGB | 155119.56 | 2741.08 | 2741.08 |  |  |  | 1 | 1 |  |  |  |  | 136188.02 | 2741.08 | 136188.02 | 2741.08 | 9.1339 | [5 empty] | 103.6951 |  |  | #VALUE!
26.02.2008 04:00 | 3600 | 2 | 763.01 | GGB | 765.934 | 772.828 | 769.963 | 261.72 | GGB | 10819.5 | GGB | 9.85 | GGB | 1008.73 | GGB | 59.93 | GGB | 167908.24 | GGB | 137103.4 | GGB | 0 | 0 | 2738 | 3600 | 2722.79 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 155157.18 | GGB | 155158.94 | 2722.79 | 2722.79 |  |  |  | 1 | 1 |  |  |  |  | 137103.4 | 2722.79 | 137103.4 | 2722.79 | 9.4795 | [5 empty] | 103.6955 |  |  | #VALUE!
26.02.2008 05:00 | 3600 | 2 | 763.54 | GGB | 764.835 | 771.773 | 768.864 | 262.44 | GGB | 10818.2 | GGB | 9.85 | GGB | 1008.21 | GGB | 59.57 | GGB | 168970.07 | GGB | 138047.97 | GGB | 0 | 0 | 2720 | 3600 | 2705.03 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 155196.73 | GGB | 155198.49 | 2705.03 | 2705.03 |  |  |  | 1 | 1 |  |  |  |  | 138047.97 | 2705.03 | 138047.97 | 2705.03 | 9.4418 | [5 empty] | 103.7289 |  |  | #VALUE!
26.02.2008 06:00 | 3600 | 2 | 763.47 | GGB | 764.835 | 772.664 | 768.864 | 261.05 | GGB | 10840.2 | GGB | 9.86 | GGB | 1007.99 | GGB | 60.37 | GGB | 166922.34 | GGB | 136019.35 | GGB | 0 | 0 | 2740 | 3600 | 2724.31 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 155237.04 | GGB | 155238.8 | 2724.31 | 2724.31 |  |  |  | 1 | 1 |  |  |  |  | 136019.35 | 2724.31 | 136019.35 | 2724.31 | 9.1927 | [5 empty] | 102.933 |  |  | #VALUE!
26.02.2008 07:00 | 3600 | 2 | 763.35 | GGB | 765.934 | 773.648 | 769.963 | 261.89 | GGB | 10811.4 | GGB | 9.85 | GGB | 1008.34 | GGB | 59.88 | GGB | 168143.71 | GGB | 137263.6 | GGB | 0 | 0 | 2723 | 3600 | 2707.59 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 155276.74 | GGB | 155278.51 | 2707.59 | 2707.59 |  |  |  | 1 | 1 |  |  |  |  | 137263.6 | 2707.59 | 137263.6 | 2707.59 | 9.3592 | [5 empty] | 103.2371 |  |  | #VALUE!
26.02.2008 08:00 | 3600 | 2 | 763.81 | GGB | 765.934 | 772.383 | 768.864 | 261.45 | GGB | 10822.5 | GGB | 9.86 | GGB | 1008.96 | GGB | 59.96 | GGB | 167696.98 | GGB | 136949 | GGB | 0 | 0 | 2712 | 3600 | 2696.36 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 155316.5 | GGB | 155318.27 | 2696.36 | 2696.36 |  |  |  | 1 | 1 |  |  |  |  | 136949 | 2696.36 | 136949 | 2696.36 | 9.2873 | [5 empty] | 102.5733 |  |  | #VALUE!
26.02.2008 09:00 | 3600 | 2 | 763.35 | GGB | 764.835 | 772.383 | 768.864 | 261.09 | GGB | 10828.7 | GGB | 9.85 | GGB | 1009.4 | GGB | 60.62 | GGB | 166537.22 | GGB | 135793.57 | GGB | 0 | 0 | 2747 | 3600 | 2731.58 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 155356.24 | GGB | 155358.01 | 2731.58 | 2731.58 |  |  |  | 1 | 1 |  |  |  |  | 135793.57 | 2731.58 | 135793.57 | 2731.58 | 9.3339 | [5 empty] | 103.0364 |  |  | #VALUE!
26.02.2008 10:00 | 3600 | 2 | 764.15 | GGB | 765.934 | 773.531 | 768.864 | 261.57 | GGB | 10791.8 | GGB | 9.85 | GGB | 1008.99 | GGB | 60.28 | GGB | 167509.92 | GGB | 136668.07 | GGB | 0 | 0 | 2686 | 3600 | 2670.93 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 155396.36 | GGB | 155398.14 | 2670.93 | 2670.93 |  |  |  | 1 | 1 |  |  |  |  | 136668.07 | 2670.93 | 136668.07 | 2670.93 | 9.0962 | [5 empty] | 101.3975 |  |  | #VALUE!
26.02.2008 11:00 | 3600 | 2 | 764.29 | GGB | 765.934 | 773.531 | 768.864 | 261.49 | GGB | 10792.3 | GGB | 9.85 | GGB | 1008.46 | GGB | 59.98 | GGB | 167963.26 | GGB | 137089.79 | GGB | 0 | 0 | 2671 | 3600 | 2655.94 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 155435.86 | GGB | 155437.64 | 2655.94 | 2655.94 |  |  |  | 1 | 1 |  |  |  |  | 137089.79 | 2655.94 | 137089.79 | 2655.94 | 9.2178 | [5 empty] | 101.1395 |  |  | #VALUE!
26.02.2008 12:00 | 3600 | 2 | 764.55 | GGB | 767.033 | 774.539 | 771.429 | 261.52 | GGB | 10792.2 | GGB | 9.86 | GGB | 1008.29 | GGB | 60.03 | GGB | 168020.47 | GGB | 137093.37 | GGB | 0 | 0 | 2659 | 3600 | 2644.06 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 155475.36 | GGB | 155477.14 | 2644.06 | 2644.06 |  |  |  | 1 | 1 |  |  |  |  | 137093.37 | 2644.06 | 137093.37 | 2644.06 | 9.1768 | [5 empty] | 100.6897 |  |  | #VALUE!
26.02.2008 13:00 | 3600 | 2 | 765.53 | GGB | 768.132 | 774.633 | 772.527 | 260.03 | GGB | 10750.2 | GGB | 9.86 | GGB | 1007.63 | GGB | 60.51 | GGB | 166387.57 | GGB | 135477.15 | GGB | 0 | 0 | 2600 | 3600 | 2584.5 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 155515.11 | GGB | 155516.89 | 2584.5 | 2584.5 |  |  |  | 1 | 1 |  |  |  |  | 135477.15 | 2584.5 | 135477.15 | 2584.5 | 8.8086 | [5 empty] | 97.2613 |  |  | #VALUE!
26.02.2008 14:00 | 3600 | 2 | 766.06 | GGB | 767.033 | 774.68 | 771.429 | 257.87 | GGB | 10728.6 | GGB | 9.86 | GGB | 1006.21 | GGB | 61.36 | GGB | 163632.33 | GGB | 132707.11 | GGB | 0 | 0 | 2579 | 3600 | 2563.31 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 155554.03 | GGB | 155555.81 | 2563.31 | 2563.31 |  |  |  | 1 | 1 |  |  |  |  | 132707.11 | 2563.31 | 132707.11 | 2563.31 | 8.7402 | [5 empty] | 94.4915 |  |  | #VALUE!
26.02.2008 15:00 | 3600 | 2 | 765.62 | GGB | 768.132 | 775.055 | 771.429 | 258.3 | GGB | 10713 | GGB | 9.85 | GGB | 1005.57 | GGB | 61.53 | GGB | 164254.02 | GGB | 133059.95 | GGB | 0 | 0 | 2580 | 3600 | 2565.2 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 155593.88 | GGB | 155595.66 | 2565.2 | 2565.2 |  |  |  | 1 | 1 |  |  |  |  | 133059.95 | 2565.2 | 133059.95 | 2565.2 | 8.5653 | [5 empty] | 94.8126 |  |  | #VALUE!
26.02.2008 16:00 | 3600 | 2 | 765.79 | GGB | 768.132 | 775.055 | 771.429 | 259.15 | GGB | 10701.1 | GGB | 9.85 | GGB | 1005.02 | GGB | 61.1 | GGB | 165161.8 | GGB | 133892.21 | GGB | 0 | 0 | 2554 | 3600 | 2539.22 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 155633.54 | GGB | 155635.32 | 2539.22 | 2539.22 |  |  |  | 1 | 1 |  |  |  |  | 133892.21 | 2539.22 | 133892.21 | 2539.22 | 8.5724 | [5 empty] | 94.4394 |  |  | #VALUE!
26.02.2008 17:00 | 3600 | 2 | 765.88 | GGB | 768.132 | 774.891 | 771.429 | 258.9 | GGB | 10685.9 | GGB | 9.86 | GGB | 1003.87 | GGB | 61.18 | GGB | 164976.94 | GGB | 133559.01 | GGB | 0 | 0 | 2552 | 3600 | 2537.02 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 155672.16 | GGB | 155673.94 | 2537.02 | 2537.02 |  |  |  | 1 | 1 |  |  |  |  | 133559.01 | 2537.02 | 133559.01 | 2537.02 | 8.7737 | [5 empty] | 94.1227 |  |  | #VALUE!
26.02.2008 18:00 | 3600 | 2 | 765.89 | GGB | 767.033 | 775.195 | 771.795 | 258.85 | GGB | 10681.3 | GGB | 9.85 | GGB | 1002.62 | GGB | 61.21 | GGB | 164886.71 | GGB | 133307.71 | GGB | 0 | 0 | 2552 | 3600 | 2536.54 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 155712.29 | GGB | 155714.07 | 2536.54 | 2536.54 |  |  |  | 1 | 1 |  |  |  |  | 133307.71 | 2536.54 | 133307.71 | 2536.54 | 8.4261 | [5 empty] | 93.9279 |  |  | #VALUE!
26.02.2008 19:00 | 3600 | 2 | 765.5 | GGB | 767.033 | 774.141 | 771.429 | 257.17 | GGB | 10704.3 | GGB | 9.86 | GGB | 1001.54 | GGB | 61.7 | GGB | 163163.58 | GGB | 131580.99 | GGB | 0 | 0 | 2578 | 3600 | 2562.94 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 155751.22 | GGB | 155753 | 2562.94 | 2562.94 |  |  |  | 1 | 1 |  |  |  |  | 131580.99 | 2562.94 | 131580.99 | 2562.94 | 8.6626 | [5 empty] | 93.6762 |  |  | #VALUE!
26.02.2008 20:00 | 3600 | 2 | 765.36 | GGB | 767.033 | 775.172 | 771.429 | 256.48 | GGB | 10689.2 | GGB | 9.86 | GGB | 1000.39 | GGB | 61.77 | GGB | 162517.69 | GGB | 130881.13 | GGB | 0 | 0 | 2578 | 3600 | 2562.35 | GGB | 100 | GGB | 39.06 | GGB | 39.06 | GGB | 155790.28 | GGB | 155792.06 | 2562.35 | 2562.35 |  |  |  | 1 | 1 |  |  |  |  | 130881.13 | 2562.35 | 130881.13 | 2562.35 | 8.5858 | [5 empty] | 93.1565 |  |  | #VALUE!
26.02.2008 21:00 | 3600 | 2 | 765.24 | GGB | 767.033 | 775.219 | 771.429 | 256.2 | GGB | 10665.1 | GGB | 9.86 | GGB | 999.27 | GGB | 61.91 | GGB | 162223.9 | GGB | 130444.33 | GGB | 0 | 0 | 2571 | 3600 | 2556.06 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 155830.41 | GGB | 155832.19 | 2556.06 | 2556.06 |  |  |  | 1 | 1 |  |  |  |  | 130444.33 | 2556.06 | 130444.33 | 2556.06 | 8.3086 | [5 empty] | 92.6176 |  |  | #VALUE!
26.02.2008 22:00 | 3600 | 2 | 765.36 | GGB | 767.033 | 775.406 | 770.696 | 256.38 | GGB | 10643.2 | GGB | 9.86 | GGB | 997.84 | GGB | 61.01 | GGB | 163296.72 | GGB | 131472.29 | GGB | 0 | 0 | 2549 | 3600 | 2534.17 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 155869.21 | GGB | 155870.99 | 2534.17 | 2534.17 |  |  |  | 1 | 1 |  |  |  |  | 131472.29 | 2534.17 | 131472.29 | 2534.17 | 8.5869 | [5 empty] | 92.5481 |  |  | #VALUE!
26.02.2008 23:00 | 3600 | 2 | 764.92 | GGB | 767.033 | 775.266 | 770.696 | 256.65 | GGB | 10628.5 | GGB | 9.86 | GGB | 996.77 | GGB | 60.82 | GGB | 162990.83 | GGB | 131157.91 | GGB | 0 | 0 | 2572 | 3600 | 2557.12 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 155908.28 | GGB | 155910.06 | 2557.12 | 2557.12 |  |  |  | 1 | 1 |  |  |  |  | 131157.91 | 2557.12 | 131157.91 | 2557.12 | 8.5842 | [5 empty] | 93.1629 |  |  | #VALUE!
26.02.2008 24:00 | 3600 | 2 | 765.17 | GGB | 767.033 | 773.906 | 770.696 | 254.3 | GGB | 10613.1 | GGB | 9.86 | GGB | 995.63 | GGB | 61.94 | GGB | 159849.37 | GGB | 128055.76 | GGB | 0 | 0 | 2566 | 3600 | 2550.36 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 155948.1 | GGB | 155949.87 | 2550.36 | 2550.36 |  |  |  | 1 | 1 |  |  |  |  | 128055.76 | 2550.36 | 128055.76 | 2550.36 | 8.2037 | [5 empty] | 90.719 |  |  | #VALUE!
27.02.2008 01:00 | 3600 | 2 | 765.66 | GGB | 767.033 | 774.914 | 770.696 | 254.8 | GGB | 10557.5 | GGB | 9.86 | GGB | 994.72 | GGB | 61.82 | GGB | 160749.44 | GGB | 128705.81 | GGB | 0 | 0 | 2523 | 3600 | 2507.88 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 155986.6 | GGB | 155988.38 | 2507.88 | 2507.88 |  |  |  | 1 | 1 |  |  |  |  | 128705.81 | 2507.88 | 128705.81 | 2507.88 | 8.3817 | [5 empty] | 89.6608 |  |  | #VALUE!
27.02.2008 02:00 | 3600 | 2 | 765.92 | GGB | 767.033 | 774.938 | 770.696 | 252.79 | GGB | 10552.5 | GGB | 9.86 | GGB | 993.93 | GGB | 62.32 | GGB | 158385.92 | GGB | 126522.78 | GGB | 0 | 0 | 2521 | 3600 | 2506.08 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 156025.68 | GGB | 156027.46 | 2506.08 | 2506.08 |  |  |  | 1 | 1 |  |  |  |  | 126522.78 | 2506.08 | 126522.78 | 2506.08 | 8.1135 | [5 empty] | 88.0767 |  |  | #VALUE!
27.02.2008 03:00 | 3600 | 2 | 765.83 | GGB | 767.033 | 774.938 | 770.696 | 252.07 | GGB | 10533.4 | GGB | 9.86 | GGB | 993.28 | GGB | 62.8 | GGB | 157409.92 | GGB | 125481.23 | GGB | 0 | 0 | 2519 | 3600 | 2504.07 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 156065.03 | GGB | 156066.81 | 2504.07 | 2504.07 |  |  |  | 1 | 1 |  |  |  |  | 125481.23 | 2504.07 | 125481.23 | 2504.07 | 7.9851 | [5 empty] | 87.2816 |  |  | #VALUE!
27.02.2008 04:00 | 3600 | 2 | 766.34 | GGB | 768.132 | 776.25 | 773.26 | 253.16 | GGB | 10495 | GGB | 9.85 | GGB | 992.69 | GGB | 62.6 | GGB | 158454.14 | GGB | 126311.96 | GGB | 0 | 0 | 2495 | 3600 | 2479.64 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 156103.66 | GGB | 156105.44 | 2479.64 | 2479.64 |  |  |  | 1 | 1 |  |  |  |  | 126311.96 | 2479.64 | 126311.96 | 2479.64 | 8.1079 | [5 empty] | 87.0023 |  |  | #VALUE!
27.02.2008 05:00 | 3600 | 2 | 766.86 | GGB | 768.132 | 775.242 | 772.161 | 253.16 | GGB | 10472.7 | GGB | 9.85 | GGB | 992.28 | GGB | 62.85 | GGB | 158380.42 | GGB | 126108.58 | GGB | 0 | 0 | 2474 | 3600 | 2458.73 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 156142.32 | GGB | 156144.1 | 2458.73 | 2458.73 |  |  |  | 1 | 1 |  |  |  |  | 126108.58 | 2458.73 | 126108.58 | 2458.73 | 8.0204 | [5 empty] | 86.1297 |  |  | #VALUE!
27.02.2008 06:00 | 3600 | 2 | 766.35 | GGB | 767.033 | 775.336 | 772.161 | 252.34 | GGB | 10499.9 | GGB | 9.85 | GGB | 992.01 | GGB | 63 | GGB | 157601.38 | GGB | 125397.46 | GGB | 0 | 0 | 2496 | 3600 | 2481.06 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 156181.01 | GGB | 156182.8 | 2481.06 | 2481.06 |  |  |  | 1 | 1 |  |  |  |  | 125397.46 | 2481.06 |  | 2481.06 | 8.0392 | [5 empty] | 86.4218 |  |  | #VALUE!
27.02.2008 07:00 | 3600 | 2 | 765.61 | GGB | 767.033 | 774.328 | 770.696 | 253.11 | GGB | 10543.8 | GGB | 9.85 | GGB | 992.37 | GGB | 62.86 | GGB | 158865.66 | GGB | 126503.78 | GGB | 0 | 0 | 2534 | 3600 | 2518.78 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 156219.53 | GGB | 156221.32 | 2518.78 | 2518.78 |  |  |  | 1 | 1 |  |  |  |  | 126503.78 | 2518.78 | 126503.78 | 2518.78 | 8.2719 | [5 empty] | 88.5098 |  |  | #VALUE!
27.02.2008 08:00 | 3600 | 2 | 763.94 | GGB | 765.934 | 773.18 | 769.597 | 257.29 | GGB | 10626.3 | GGB | 9.84 | GGB | 993.64 | GGB | 61.1 | GGB | 164053.76 | GGB | 131489.57 | GGB | 0 | 0 | 2624 | 3600 | 2609.07 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 156259.19 | GGB | 156260.98 | 2609.07 | 2609.07 |  |  |  | 1 | 1 |  |  |  |  | 131489.57 | 2609.07 | 131489.57 | 2609.07 | 8.6502 | [5 empty] | 95.296 |  |  | #VALUE!
27.02.2008 09:00 | 3600 | 2 | 763.58 | GGB | 764.835 | 773.273 | 768.498 | 258.62 | GGB | 10677.1 | GGB | 9.85 | GGB | 994.3 | GGB | 60.01 | GGB | 166170.81 | GGB | 133709.36 | GGB | 0 | 0 | 2643 | 3600 | 2627.29 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 156297.94 | GGB | 156299.73 | 2627.29 | 2627.29 |  |  |  | 1 | 1 |  |  |  |  | 133709.36 | 2627.29 | 133709.36 | 2627.29 | 9.0656 | [5 empty] | 97.5815 |  |  | #VALUE!
27.02.2008 10:00 | 3600 | 2 | 763.58 | GGB | 765.934 | 772.242 | 768.498 | 256.56 | GGB | 10702.6 | GGB | 9.86 | GGB | 994.33 | GGB | 60.47 | GGB | 163911.81 | GGB | 131714.04 | GGB | 0 | 0 | 2658 | 3600 | 2642.38 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 156336.4 | GGB | 156338.19 | 2642.38 | 2642.38 |  |  |  | 1 | 1 |  |  |  |  | 131714.04 | 2642.38 | 131714.04 | 2642.38 | 9.0494 | [5 empty] | 96.6774 |  |  | #VALUE!
27.02.2008 11:00 | 3600 | 2 | 763.53 | GGB | 764.835 | 772.266 | 768.498 | 256.13 | GGB | 10696.9 | GGB | 9.86 | GGB | 994.54 | GGB | 60.53 | GGB | 163568.51 | GGB | 131443.45 | GGB | 0 | 0 | 2662 | 3600 | 2646.57 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 156376.16 | GGB | 156377.95 | 2646.57 | 2646.57 |  |  |  | 1 | 1 |  |  |  |  | 131443.45 | 2646.57 | 131443.45 | 2646.57 | 8.7494 | [5 empty] | 96.6317 |  |  | #VALUE!
27.02.2008 12:00 | 3600 | 2 | 764.09 | GGB | 765.934 | 773.461 | 770.696 | 256.14 | GGB | 10654.2 | GGB | 9.86 | GGB | 994.52 | GGB | 60.41 | GGB | 164008.64 | GGB | 131844.39 | GGB | 0 | 0 | 2617 | 3600 | 2602.12 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 156415.71 | GGB | 156417.5 | 2602.12 | 2602.12 |  |  |  | 1 | 1 |  |  |  |  | 131844.39 | 2602.12 | 131844.39 | 2602.12 | 8.6745 | [5 empty] | 95.2986 |  |  | #VALUE!
27.02.2008 13:00 | 3600 | 2 | 764.62 | GGB | 765.934 | 773.461 | 769.597 | 256.18 | GGB | 10624.3 | GGB | 9.85 | GGB | 994.13 | GGB | 60.35 | GGB | 163911.81 | GGB | 131738.22 | GGB | 0 | 0 | 2580 | 3600 | 2564.8 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 156454.66 | GGB | 156456.45 | 2564.8 | 2564.8 |  |  |  | 1 | 1 |  |  |  |  | 131738.22 | 2564.8 | 131738.22 | 2564.8 | 8.6748 | [5 empty] | 93.8562 |  |  | #VALUE!
27.02.2008 14:00 | 3600 | 2 | 764.56 | GGB | 765.934 | 773.414 | 769.597 | 254.54 | GGB | 10642.5 | GGB | 9.86 | GGB | 993.05 | GGB | 60.64 | GGB | 162384.54 | GGB | 130251.93 | GGB | 0 | 0 | 2588 | 3600 | 2573.02 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 156493.55 | GGB | 156495.33 | 2573.02 | 2573.02 |  |  |  | 1 | 1 |  |  |  |  | 130251.93 | 2573.02 | 130251.93 | 2573.02 | 8.6199 | [5 empty] | 93.0947 |  |  | #VALUE!
27.02.2008 15:00 | 3600 | 2 | 764.27 | GGB | 764.835 | 772.148 | 769.597 | 254.5 | GGB | 10626.4 | GGB | 9.85 | GGB | 992.33 | GGB | 60.58 | GGB | 162355.94 | GGB | 130159.04 | GGB | 0 | 0 | 2594 | 3600 | 2578.56 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 156532.94 | GGB | 156534.73 | 2578.56 | 2578.56 |  |  |  | 1 | 1 |  |  |  |  | 130159.04 | 2578.56 | 130159.04 | 2578.56 | 8.5183 | [5 empty] | 93.2286 |  |  | #VALUE!
27.02.2008 16:00 | 3600 | 2 | 764.11 | GGB | 765.934 | 773.344 | 769.597 | 256.1 | GGB | 10660.3 | GGB | 9.86 | GGB | 992.75 | GGB | 59.88 | GGB | 164058.16 | GGB | 131857.38 | GGB | 0 | 0 | 2620 | 3600 | 2604.56 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 156572.45 | GGB | 156574.24 | 2604.56 | 2604.56 |  |  |  | 1 | 1 |  |  |  |  | 131857.38 | 2604.56 | 131857.38 | 2604.56 | 8.6922 | [5 empty] | 95.3973 |  |  | #VALUE!
27.02.2008 17:00 | 3600 | 2 | 762.88 | GGB | 764.469 | 771.352 | 768.132 | 256.05 | GGB | 10691.7 | GGB | 9.85 | GGB | 992.88 | GGB | 60.12 | GGB | 163621.32 | GGB | 131427.57 | GGB | 0 | 0 | 2687 | 3600 | 2671.15 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 156611.27 | GGB | 156613.06 | 2671.15 | 2671.15 |  |  |  | 1 | 1 |  |  |  |  | 131427.57 | 2671.15 | 131427.57 | 2671.15 | 9.0433 | [5 empty] | 97.5174 |  |  | #VALUE!
27.02.2008 18:00 | 3600 | 2 | 763.09 | GGB | 764.835 | 772.453 | 768.498 | 257.58 | GGB | 10676.8 | GGB | 9.85 | GGB | 993.06 | GGB | 59.4 | GGB | 165652.55 | GGB | 133371.81 | GGB | 0 | 0 | 2668 | 3600 | 2652.45 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 156651.21 | GGB | 156653 | 2652.45 | 2652.45 |  |  |  | 1 | 1 |  |  |  |  | 133371.81 | 2652.45 | 133371.81 | 2652.45 | 8.8573 | [5 empty] | 98.2672 |  |  | #VALUE!
27.02.2008 19:00 | 3600 | 2 | 763 | GGB | 764.835 | 772.406 | 768.498 | 257.47 | GGB | 10709.3 | GGB | 9.86 | GGB | 993.4 | GGB | 59.48 | GGB | 165220.11 | GGB | 133039.49 | GGB | 0 | 0 | 2687 | 3600 | 2671.57 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 156689.85 | GGB | 156691.64 | 2671.57 | 2671.57 |  |  |  | 1 | 1 |  |  |  |  | 133039.49 | 2671.57 | 133039.49 | 2671.57 | 9.1984 | [5 empty] | 98.729 |  |  | #VALUE!
27.02.2008 20:00 | 3600 | 2 | 761.88 | GGB | 763.37 | 770.25 | 767.033 | 256.57 | GGB | 10723.1 | GGB | 9.85 | GGB | 993.62 | GGB | 59.43 | GGB | 164340.94 | GGB | 132379.84 | GGB | 0 | 0 | 2730 | 3600 | 2714.24 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 156729.03 | GGB | 156730.82 | 2714.24 | 2714.24 |  |  |  | 0 | 1 | [14 empty] | 99.8085 |  |  | #VALUE!
27.02.2008 21:00 | 3600 | 2 | 762.13 | GGB | 764.469 | 771.516 | 768.132 | 257.75 | GGB | 10712.3 | GGB | 9.85 | GGB | 993.54 | GGB | 59.16 | GGB | 166097.08 | GGB | 133891.91 | GGB | 0 | 0 | 2717 | 3600 | 2702.02 | GGB | 100 | GGB | 37.98 | GGB | 37.98 | GGB | 156767.01 | GGB | 156768.8 | 2702.02 | 2702.02 |  |  |  | 1 | 1 |  |  |  |  | 133891.91 | 2702.02 | 133891.91 | 2702.02 | 9.5255 | [5 empty] | 100.4941 |  |  | #VALUE!
27.02.2008 22:00 | 3600 | 2 | 763.19 | GGB | 763.37 | 770.438 | 767.033 | 256.73 | GGB | 10716.3 | GGB | 9.86 | GGB | 993.27 | GGB | 58.92 | GGB | 166364.47 | GGB | 134169.05 | GGB | 0 | 0 | 2673 | 3600 | 2657.34 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 156806.78 | GGB | 156808.57 | 2657.34 | 2657.34 |  |  |  | 0 | 1 | [14 empty] | 99.0369 |  |  | #VALUE!
27.02.2008 23:00 | 3600 | 2 | 761.96 | GGB | 763.37 | 770.414 | 767.033 | 255.87 | GGB | 10718.7 | GGB | 9.85 | GGB | 992.66 | GGB | 59.2 | GGB | 164278.23 | GGB | 132291.43 | GGB | 0 | 0 | 2717 | 3600 | 2701.75 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 156847.14 | GGB | 156848.93 | 2701.75 | 2701.75 |  |  |  | 0 | 1 | [14 empty] | 99.2829 |  |  | #VALUE!
27.02.2008 24:00 | 3600 | 2 | 761.63 | GGB | 763.37 | 770.227 | 767.033 | 256.69 | GGB | 10729.7 | GGB | 9.85 | GGB | 992.81 | GGB | 59.14 | GGB | 165148.59 | GGB | 133037.36 | GGB | 0 | 0 | 2743 | 3600 | 2727.18 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 156886.22 | GGB | 156888.01 | 2727.18 | 2727.18 |  |  |  | 0 | 1 | [14 empty] | 100.7825 |  |  | #VALUE!
28.02.2008 01:00 | 3600 | 2 | 761.32 | GGB | 763.37 | 770.273 | 766.667 | 256.83 | GGB | 10739.9 | GGB | 9.85 | GGB | 992.62 | GGB | 58.94 | GGB | 165224.52 | GGB | 133153.14 | GGB | 0 | 0 | 2759 | 3600 | 2743.56 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 156925.77 | GGB | 156927.55 | 2743.56 | 2743.56 |  |  |  | 0 | 1 | [14 empty] | 101.476 |  |  | #VALUE!
28.02.2008 02:00 | 3600 | 2 | 761.35 | GGB | 763.37 | 770.227 | 766.667 | 257.06 | GGB | 10745.2 | GGB | 9.85 | GGB | 992.09 | GGB | 58.93 | GGB | 165423.68 | GGB | 133247.92 | GGB | 0 | 0 | 2764 | 3600 | 2748.8 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 156965.65 | GGB | 156967.43 | 2748.8 | 2748.8 |  |  |  | 0 | 1 | [14 empty] | 101.7422 |  |  | #VALUE!
28.02.2008 03:00 | 3600 | 2 | 760.99 | GGB | 763.37 | 770.227 | 766.667 | 257.63 | GGB | 10753.7 | GGB | 9.85 | GGB | 992.02 | GGB | 58.72 | GGB | 166142.2 | GGB | 133901.03 | GGB | 0 | 0 | 2788 | 3600 | 2772.11 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 157004.43 | GGB | 157006.22 | 2772.11 | 2772.11 |  |  |  | 0 | 1 | [14 empty] | 103.1079 |  |  | #VALUE!
28.02.2008 04:00 | 3600 | 2 | 760.67 | GGB | 762.271 | 769.148 | 766.3 | 258.47 | GGB | 10781.8 | GGB | 9.85 | GGB | 992.19 | GGB | 58.4 | GGB | 167066.48 | GGB | 134799.53 | GGB | 0 | 0 | 2821 | 3600 | 2805.2 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 157044.25 | GGB | 157046.04 | 2805.2 | 2803.63 |  |  |  | 0 | 1 | [14 empty] | 105.0388 | 2803.63 |  | 104.98
28.02.2008 05:00 | 3600 | 2 | 760.15 | GGB | 762.271 | 769.289 | 765.201 | 258.86 | GGB | 10800.9 | GGB | 9.85 | GGB | 992.96 | GGB | 58.03 | GGB | 167734.39 | GGB | 135595.38 | GGB | 0 | 0 | 2851 | 3600 | 2835.93 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 157083.89 | GGB | 157085.69 | 2835.93 | 2787.1746 |  |  |  | 0 | 1 | [14 empty] | 106.8164 | 2787.1746 |  | 104.98
28.02.2008 06:00 | 3600 | 2 | 760.57 | GGB | 763.37 | 770.578 | 766.3 | 258.68 | GGB | 10806.1 | GGB | 9.86 | GGB | 994.01 | GGB | 58.4 | GGB | 167671.67 | GGB | 135534.57 | GGB | 0 | 0 | 2838 | 3600 | 2822.48 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 157123.06 | GGB | 157124.85 | 2822.48 | 2788.4251 |  |  |  | 0 | 1 | [14 empty] | 106.2621 | 2788.4251 |  | 104.98
28.02.2008 07:00 | 3600 | 2 | 760.79 | GGB | 762.271 | 769.547 | 766.667 | 259.27 | GGB | 10779.9 | GGB | 9.85 | GGB | 995.19 | GGB | 58.64 | GGB | 167926.95 | GGB | 135804.83 | GGB | 0 | 0 | 2816 | 3600 | 2800.46 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 157162.69 | GGB | 157164.48 | 2800.46 | 2782.876 |  |  |  | 0 | 1 | [14 empty] | 105.6433 | 2782.876 |  | 104.98
28.02.2008 08:00 | 3600 | 2 | 761.25 | GGB | 763.37 | 769.758 | 767.766 | 260.41 | GGB | 10792.1 | GGB | 9.85 | GGB | 996.21 | GGB | 58.31 | GGB | 169099.91 | GGB | 137031.03 | GGB | 0 | 0 | 2793 | 3600 | 2777.37 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 157202.68 | GGB | 157204.47 | 2777.37 | 2757.9739 |  |  |  | 0 | 1 | [14 empty] | 105.7183 | 2757.9739 |  | 104.98
28.02.2008 09:00 | 3600 | 2 | 760.64 | GGB | 762.271 | 769.781 | 766.667 | 259.94 | GGB | 10822.4 | GGB | 9.85 | GGB | 997.33 | GGB | 58.81 | GGB | 167955.55 | GGB | 136048.03 | GGB | 0 | 0 | 2853 | 3600 | 2837.04 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 157242.21 | GGB | 157244.01 | 2837.04 | 2777.9013 |  |  |  | 0 | 1 | [14 empty] | 107.2149 | 2777.9013 |  | 104.98
28.02.2008 10:00 | 3600 | 2 | 760.74 | GGB | 762.271 | 770.016 | 766.3 | 259.85 | GGB | 10828.7 | GGB | 9.86 | GGB | 998.5 | GGB | 58.94 | GGB | 167931.35 | GGB | 136135.61 | GGB | 0 | 0 | 2848 | 3600 | 2832.56 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 157281.85 | GGB | 157283.65 | 2832.56 | 2776.1142 |  |  |  | 0 | 1 | [14 empty] | 107.1145 | 2776.1142 |  | 104.98
28.02.2008 11:00 | 3600 | 2 | 760.4 | GGB | 763.37 | 770.203 | 766.667 | 259.72 | GGB | 10831.5 | GGB | 9.85 | GGB | 999.14 | GGB | 58.9 | GGB | 167875.23 | GGB | 136196.44 | GGB | 0 | 0 | 2846 | 3600 | 2830.27 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 157321.48 | GGB | 157323.27 | 2830.27 | 2774.8743 |  |  |  | 0 | 1 | [14 empty] | 107.0757 | 2774.8743 |  | 104.98
28.02.2008 12:00 | 3600 | 2 | 760.31 | GGB | 763.37 | 770.133 | 767.766 | 260.03 | GGB | 10849.1 | GGB | 9.85 | GGB | 1000.4 | GGB | 58.61 | GGB | 168246.04 | GGB | 136788.78 | GGB | 0 | 0 | 2859 | 3600 | 2843.57 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 157361.08 | GGB | 157362.87 | 2843.57 | 2762.8582 |  |  |  | 0 | 1 | [14 empty] | 108.0468 | 2762.8582 |  | 104.98
28.02.2008 13:00 | 3600 | 2 | 760.89 | GGB | 763.37 | 771.07 | 767.766 | 259.9 | GGB | 10847.8 | GGB | 9.86 | GGB | 1001.12 | GGB | 58.9 | GGB | 167867.53 | GGB | 136457.98 | GGB | 0 | 0 | 2832 | 3600 | 2816.04 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 157400.9 | GGB | 157402.69 | 2816.04 | 2769.5559 |  |  |  | 0 | 1 | [14 empty] | 106.742 | 2769.5559 |  | 104.98
28.02.2008 14:00 | 3600 | 2 | 761.41 | GGB | 764.469 | 771.07 | 768.864 | 259.28 | GGB | 10832.4 | GGB | 9.86 | GGB | 1001.91 | GGB | 59.05 | GGB | 167310.76 | GGB | 136048.85 | GGB | 0 | 0 | 2792 | 3600 | 2776.13 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 157440.49 | GGB | 157442.29 | 2776.13 | 2776.13 |  |  |  | 1 | 1 |  |  |  |  | 136048.85 | 2776.13 | 136048.85 | 2776.13 | 9.5376 | [5 empty] | 104.9137 |  |  | #VALUE!
28.02.2008 15:00 | 3600 | 2 | 762.45 | GGB | 764.835 | 772.055 | 768.864 | 258.55 | GGB | 10801.1 | GGB | 9.86 | GGB | 1002.12 | GGB | 59.49 | GGB | 166300.65 | GGB | 135081.47 | GGB | 0 | 0 | 2741 | 3600 | 2725.58 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 157480.04 | GGB | 157481.84 | 2725.58 | 2725.58 |  |  |  | 1 | 1 |  |  |  |  | 135081.47 | 2725.58 | 135081.47 | 2725.58 | 9.3091 | [5 empty] | 102.2709 |  |  | #VALUE!
28.02.2008 16:00 | 3600 | 2 | 763.51 | GGB | 765.934 | 773.391 | 769.963 | 258.61 | GGB | 10789.1 | GGB | 9.85 | GGB | 1002.73 | GGB | 59.71 | GGB | 166336.96 | GGB | 135101.27 | GGB | 0 | 0 | 2696 | 3600 | 2680.12 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 157519.68 | GGB | 157521.48 | 2680.12 | 2680.12 |  |  |  | 1 | 1 |  |  |  |  | 135101.27 | 2680.12 | 135101.27 | 2680.12 | 9.1344 | [5 empty] | 100.5799 |  |  | #VALUE!
28.02.2008 17:00 | 3600 | 2 | 763.75 | GGB | 765.934 | 773.297 | 770.33 | 260.33 | GGB | 10777.1 | GGB | 9.85 | GGB | 1003.2 | GGB | 59.15 | GGB | 168645.47 | GGB | 137272.08 | GGB | 0 | 0 | 2672 | 3600 | 2656.64 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 157559.69 | GGB | 157561.48 | 2656.64 | 2656.64 |  |  |  | 1 | 1 |  |  |  |  | 137272.08 | 2656.64 | 137272.08 | 2656.64 | 9.1171 | [5 empty] | 101.3007 |  |  | #VALUE!
28.02.2008 18:00 | 3600 | 2 | 762.9 | GGB | 763.37 | 771.117 | 767.766 | 260.31 | GGB | 10830.2 | GGB | 9.85 | GGB | 1004.11 | GGB | 59.34 | GGB | 168075.49 | GGB | 136853.7 | GGB | 0 | 0 | 2730 | 3600 | 2714.19 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 157599.21 | GGB | 157601 | 2714.19 | 2714.19 |  |  |  | 0 | 1 | [14 empty] | 103.1797 |  |  | #VALUE!
28.02.2008 19:00 | 3600 | 2 | 762.9 | GGB | 764.835 | 772.008 | 768.864 | 259.91 | GGB | 10854.8 | GGB | 9.86 | GGB | 1005.22 | GGB | 59.32 | GGB | 167781.7 | GGB | 136774.15 | GGB | 0 | 0 | 2748 | 3600 | 2732.26 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 157639.01 | GGB | 157640.8 | 2732.26 | 2732.26 |  |  |  | 1 | 1 |  |  |  |  | 136774.15 | 2732.26 | 136774.15 | 2732.26 | 9.3895 | [5 empty] | 103.8063 |  |  | #VALUE!
28.02.2008 20:00 | 3600 | 2 | 762.51 | GGB | 764.469 | 772.008 | 767.766 | 260.55 | GGB | 10838.5 | GGB | 9.85 | GGB | 1006.04 | GGB | 59.45 | GGB | 167755.29 | GGB | 136811.08 | GGB | 0 | 0 | 2753 | 3600 | 2737.17 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 157679.32 | GGB | 157681.11 | 2737.17 | 2737.17 |  |  |  | 1 | 1 |  |  |  |  | 136811.08 | 2737.17 | 136811.08 | 2737.17 | 9.2899 | [5 empty] | 104.0209 |  |  | #VALUE!
28.02.2008 21:00 | 3600 | 2 | 762.32 | GGB | 764.835 | 772.031 | 768.864 | 261.4 | GGB | 10852.9 | GGB | 9.85 | GGB | 1007.33 | GGB | 59.65 | GGB | 167845.52 | GGB | 136976.27 | GGB | 0 | 0 | 2772 | 3600 | 2756.28 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 157718.76 | GGB | 157720.56 | 2756.28 | 2756.28 |  |  |  | 1 | 1 |  |  |  |  | 136976.27 | 2756.28 | 136976.27 | 2756.28 | 9.5702 | [5 empty] | 104.8736 |  |  | #VALUE!
28.02.2008 22:00 | 3600 | 2 | 762.26 | GGB | 764.835 | 772.266 | 768.864 | 261.72 | GGB | 10869.8 | GGB | 9.85 | GGB | 1008.31 | GGB | 59.91 | GGB | 168175.62 | GGB | 137272.66 | GGB | 0 | 0 | 2786 | 3600 | 2770.88 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 157758.49 | GGB | 157760.29 | 2770.88 | 2753.1192 |  |  |  | 1 | 1 |  |  |  |  | 137272.66 | 2753.1192 | 137272.66 | 2753.1192 | 9.5124 | [5 empty] | 105.6572 | 2753.1192 |  | 104.98
28.02.2008 23:00 | 3600 | 2 | 762.28 | GGB | 764.469 | 771.117 | 767.766 | 262.36 | GGB | 10858.4 | GGB | 9.85 | GGB | 1008.43 | GGB | 60.22 | GGB | 167864.23 | GGB | 136908.8 | GGB | 0 | 0 | 2787 | 3600 | 2771.77 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 157798.99 | GGB | 157800.79 | 2771.77 | 2760.4361 |  |  |  | 1 | 1 |  |  |  |  | 136908.8 | 2760.4361 | 136908.8 | 2760.4361 | 9.3316 | [5 empty] | 105.411 | 2760.4361 |  | 104.98
28.02.2008 24:00 | 3600 | 2 | 762.23 | GGB | 764.835 | 772.148 | 768.864 | 262.95 | GGB | 10862.8 | GGB | 9.85 | GGB | 1008.66 | GGB | 60.38 | GGB | 168381.39 | GGB | 137295.73 | GGB | 0 | 0 | 2797 | 3600 | 2781.93 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 157837.96 | GGB | 157839.76 | 2781.93 | 2752.6566 |  |  |  | 1 | 1 |  |  |  |  | 137295.73 | 2752.6566 | 137295.73 | 2752.6566 | 9.6979 | [5 empty] | 106.0964 | 2752.6566 |  | 104.98
29.02.2008 01:00 | 3600 | 2 | 761.82 | GGB | 763.37 | 769.852 | 767.766 | 263.44 | GGB | 10869.5 | GGB | 9.85 | GGB | 1008.7 | GGB | 60.36 | GGB | 168896.34 | GGB | 137728.72 | GGB | 0 | 0 | 2822 | 3600 | 2806.5 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 157877.85 | GGB | 157879.65 | 2806.5 | 2744.0028 |  |  |  | 0 | 1 | [14 empty] | 107.371 | 2744.0028 |  | 104.98
29.02.2008 02:00 | 3600 | 2 | 762.35 | GGB | 764.835 | 771.164 | 767.766 | 263.49 | GGB | 10880.7 | GGB | 9.86 | GGB | 1008.8 | GGB | 60.38 | GGB | 168899.64 | GGB | 137737.37 | GGB | 0 | 0 | 2815 | 3600 | 2799.76 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 157918.27 | GGB | 157920.07 | 2799.76 | 2743.8305 |  |  |  | 1 | 1 |  |  |  |  | 137737.37 | 2743.8305 | 137737.37 | 2743.8305 | 9.35 | [5 empty] | 107.1199 | 2743.8305 |  | 104.98
29.02.2008 03:00 | 3600 | 2 | 762.91 | GGB | 764.835 | 772.313 | 768.864 | 262.89 | GGB | 10868.5 | GGB | 9.86 | GGB | 1008.75 | GGB | 60.39 | GGB | 168317.57 | GGB | 137250.66 | GGB | 0 | 0 | 2789 | 3600 | 2773.14 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 157957.22 | GGB | 157959.02 | 2773.14 | 2753.5605 |  |  |  | 1 | 1 |  |  |  |  | 137250.66 | 2753.5605 | 137250.66 | 2753.5605 | 9.7029 | [5 empty] | 105.7265 | 2753.5605 |  | 104.98
29.02.2008 04:00 | 3600 | 2 | 763.37 | GGB | 764.835 | 771.117 | 768.864 | 262.38 | GGB | 10844 | GGB | 9.85 | GGB | 1008.55 | GGB | 60.54 | GGB | 167606.75 | GGB | 136584.43 | GGB | 0 | 0 | 2761 | 3600 | 2745.81 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 157997.57 | GGB | 157999.36 | 2745.81 | 2745.81 |  |  |  | 1 | 1 |  |  |  |  | 136584.43 | 2745.81 | 136584.43 | 2745.81 | 9.2968 | [5 empty] | 104.1764 |  |  | #VALUE!
29.02.2008 05:00 | 3600 | 2 | 763.3 | GGB | 764.835 | 772.242 | 768.864 | 262.48 | GGB | 10845 | GGB | 9.86 | GGB | 1008.42 | GGB | 60.71 | GGB | 167253.54 | GGB | 136208.26 | GGB | 0 | 0 | 2766 | 3600 | 2750.6 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 158037.72 | GGB | 158039.51 | 2750.6 | 2750.6 |  |  |  | 1 | 1 |  |  |  |  | 136208.26 | 2750.6 | 136208.26 | 2750.6 | 9.3314 | [5 empty] | 104.0707 |  |  | #VALUE!
29.02.2008 06:00 | 3600 | 2 | 763.72 | GGB | 764.835 | 772.125 | 768.864 | 261.92 | GGB | 10834.1 | GGB | 9.86 | GGB | 1007.93 | GGB | 60.72 | GGB | 166920.14 | GGB | 135867.58 | GGB | 0 | 0 | 2741 | 3600 | 2725.93 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 158076.86 | GGB | 158078.66 | 2725.93 | 2725.93 |  |  |  | 1 | 1 |  |  |  |  | 135867.58 | 2725.93 | 135867.58 | 2725.93 | 9.4602 | [5 empty] | 102.8793 |  |  | #VALUE!
29.02.2008 07:00 | 3600 | 2 | 763.2 | GGB | 765.934 | 772.313 | 769.963 | 262.34 | GGB | 10836.4 | GGB | 9.85 | GGB | 1007.85 | GGB | 60.55 | GGB | 167272.24 | GGB | 136209.63 | GGB | 0 | 0 | 2765 | 3600 | 2749.52 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 158117.48 | GGB | 158119.28 | 2749.52 | 2749.52 |  |  |  | 1 | 1 |  |  |  |  | 136209.63 | 2749.52 | 136209.63 | 2749.52 | 9.2199 | [5 empty] | 104.0309 |  |  | #VALUE!
29.02.2008 08:00 | 3600 | 2 | 763.13 | GGB | 765.934 | 772.266 | 768.864 | 262.5 | GGB | 10843.3 | GGB | 9.85 | GGB | 1008.1 | GGB | 60.56 | GGB | 167453.8 | GGB | 136388.7 | GGB | 0 | 0 | 2756 | 3208 | 2740.84 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 158157.28 | GGB | 158159.08 | 2740.84 | 2740.84 |  |  |  | 1 | 1 |  |  |  |  | 136388.7 | 2740.84 | 136388.7 | 2740.84 | 9.3925 | [5 empty] | 103.8388 |  |  | #VALUE!
29.02.2008 09:00 | 3600 | 2 | 763.1 | GGB | 765.934 | 773.25 | 769.963 | 262.36 | GGB | 10847.2 | GGB | 9.86 | GGB | 1008.02 | GGB | 60.52 | GGB | 167636.46 | GGB | 136541.81 | GGB | 0 | 0 | 2764 | 3600 | 2748.92 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 158196.56 | GGB | 158198.36 | 2748.92 | 2748.92 |  |  |  | 1 | 1 |  |  |  |  | 136541.81 | 2748.92 | 136541.81 | 2748.92 | 9.5556 | [5 empty] | 104.2618 |  |  | #VALUE!
29.02.2008 10:00 | 3600 | 2 | 762.96 | GGB | 765.934 | 772.078 | 769.963 | 262.49 | GGB | 10842.3 | GGB | 9.85 | GGB | 1008.45 | GGB | 60.58 | GGB | 167462.6 | GGB | 136433.49 | GGB | 0 | 0 | 2773 | 3600 | 2757.87 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 158237.32 | GGB | 158239.12 | 2757.87 | 2757.87 |  |  |  | 1 | 1 |  |  |  |  | 136433.49 | 2757.87 | 136433.49 | 2757.87 | 9.2313 | [5 empty] | 104.5183 |  |  | #VALUE!
29.02.2008 11:00 | 3600 | 2 | 763.24 | GGB | 765.934 | 772.336 | 769.963 | 261.96 | GGB | 10839.4 | GGB | 9.86 | GGB | 1007.77 | GGB | 60.67 | GGB | 166762.79 | GGB | 135734.66 | GGB | 0 | 0 | 2751 | 3600 | 2735.54 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 158276.54 | GGB | 158278.34 | 2735.54 | 2735.54 |  |  |  | 1 | 1 |  |  |  |  | 135734.66 | 2735.54 | 135734.66 | 2735.54 | 9.4673 | [5 empty] | 103.141 |  |  | #VALUE!
29.02.2008 12:00 | 3600 | 2 | 763.88 | GGB | 767.033 | 773.344 | 769.963 | 260.7 | GGB | 10809.1 | GGB | 9.86 | GGB | 1006.67 | GGB | 60.93 | GGB | 165731.77 | GGB | 134647.08 | GGB | 0 | 0 | 2706 | 3600 | 2690.94 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 158315.85 | GGB | 158317.65 | 2690.94 | 2690.94 |  |  |  | 1 | 1 |  |  |  |  | 134647.08 | 2690.94 | 134647.08 | 2690.94 | 9.2172 | [5 empty] | 100.6464 |  |  | #VALUE!
29.02.2008 13:00 | 3600 | 2 | 764.26 | GGB | 765.934 | 773.391 | 770.33 | 259.82 | GGB | 10774.4 | GGB | 9.85 | GGB | 1005.57 | GGB | 60.99 | GGB | 164989.04 | GGB | 133872.45 | GGB | 0 | 0 | 2674 | 3600 | 2658.4 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 158356.31 | GGB | 158358.11 | 2658.4 | 2658.4 |  |  |  | 1 | 1 |  |  |  |  | 133872.45 | 2658.4 | 133872.45 | 2658.4 | 8.796 | [5 empty] | 98.8574 |  |  | #VALUE!
29.02.2008 14:00 | 3600 | 2 | 764.14 | GGB | 765.934 | 773.461 | 770.33 | 259.71 | GGB | 10770 | GGB | 9.86 | GGB | 1004.82 | GGB | 60.93 | GGB | 165071.57 | GGB | 133861.46 | GGB | 0 | 0 | 2672 | 3600 | 2656.94 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 158395.23 | GGB | 158397.03 | 2656.94 | 2656.94 |  |  |  | 1 | 1 |  |  |  |  | 133861.46 | 2656.94 | 133861.46 | 2656.94 | 9.1383 | [5 empty] | 98.795 |  |  | #VALUE!
29.02.2008 15:00 | 3600 | 2 | 764.2 | GGB | 765.934 | 773.508 | 770.33 | 259.74 | GGB | 10765.3 | GGB | 9.85 | GGB | 1004.28 | GGB | 61.01 | GGB | 164899.92 | GGB | 133619.13 | GGB | 0 | 0 | 2672 | 3600 | 2656.38 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 158435.1 | GGB | 158436.9 | 2656.38 | 2656.38 |  |  |  | 1 | 1 |  |  |  |  | 133619.13 | 2656.38 | 133619.13 | 2656.38 | 8.9025 | [5 empty] | 98.5953 |  |  | #VALUE!
29.02.2008 16:00 | 3600 | 2 | 763.9 | GGB | 765.934 | 772.43 | 768.864 | 259.99 | GGB | 10765.8 | GGB | 9.85 | GGB | 1003.79 | GGB | 60.97 | GGB | 165072.67 | GGB | 133708.25 | GGB | 0 | 0 | 2687 | 3600 | 2671.98 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 158475.27 | GGB | 158477.07 | 2671.98 | 2671.98 |  |  |  | 1 | 1 |  |  |  |  | 133708.25 | 2671.98 | 133708.25 | 2671.98 | 8.8938 | [5 empty] | 99.2405 |  |  | #VALUE!
29.02.2008 17:00 | 3600 | 2 | 763.83 | GGB | 764.835 | 772.477 | 769.963 | 260.32 | GGB | 10769.4 | GGB | 9.86 | GGB | 1003.48 | GGB | 61.06 | GGB | 165172.8 | GGB | 133714.4 | GGB | 0 | 0 | 2691 | 3600 | 2675.24 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 158514.09 | GGB | 158515.89 | 2675.24 | 2675.24 |  |  |  | 1 | 1 |  |  |  |  | 133714.4 | 2675.24 | 133714.4 | 2675.24 | 9.2148 | [5 empty] | 99.3661 |  |  | #VALUE!
29.02.2008 18:00 | 3600 | 2 | 763.73 | GGB | 764.835 | 771.539 | 768.864 | 260.33 | GGB | 10762 | GGB | 9.85 | GGB | 1003.04 | GGB | 61.02 | GGB | 165219.01 | GGB | 133707.35 | GGB | 0 | 0 | 2698 | 3600 | 2682.56 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 158554.19 | GGB | 158556 | 2682.56 | 2682.56 |  |  |  | 1 | 1 |  |  |  |  | 133707.35 | 2682.56 | 133707.35 | 2682.56 | 8.9424 | [5 empty] | 99.6328 |  |  | #VALUE!
29.02.2008 19:00 | 3600 | 2 | 763.74 | GGB | 765.934 | 772.383 | 769.963 | 260.47 | GGB | 10772.2 | GGB | 9.85 | GGB | 1002.92 | GGB | 61.03 | GGB | 165470.99 | GGB | 133893.26 | GGB | 0 | 0 | 2702 | 3600 | 2686.16 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 158593.52 | GGB | 158595.33 | 2686.16 | 2686.16 |  |  |  | 1 | 1 |  |  |  |  | 133893.26 | 2686.16 | 133893.26 | 2686.16 | 9.1446 | [5 empty] | 99.9052 |  |  | #VALUE!
29.02.2008 20:00 | 3600 | 2 | 763.7 | GGB | 764.835 | 772.359 | 769.963 | 260.59 | GGB | 10769.9 | GGB | 9.85 | GGB | 1002.77 | GGB | 61.24 | GGB | 165374.16 | GGB | 133711.14 | GGB | 0 | 0 | 2708 | 3600 | 2692.73 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 158632.47 | GGB | 158634.28 | 2692.73 | 2692.73 |  |  |  | 1 | 1 |  |  |  |  | 133711.14 | 2692.73 | 133711.14 | 2692.73 | 9.2439 | [5 empty] | 100.0133 |  |  | #VALUE!
29.02.2008 21:00 | 3600 | 2 | 763.54 | GGB | 764.835 | 772.359 | 769.963 | 260.52 | GGB | 10771.8 | GGB | 9.85 | GGB | 1002.25 | GGB | 61.06 | GGB | 165628.34 | GGB | 133917.12 | GGB | 0 | 0 | 2709 | 3600 | 2693.71 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 158672.24 | GGB | 158674.05 | 2693.71 | 2693.71 |  |  |  | 1 | 1 |  |  |  |  | 133917.12 | 2693.71 | 133917.12 | 2693.71 | 9.0705 | [5 empty] | 100.2039 |  |  | #VALUE!
29.02.2008 22:00 | 3600 | 2 | 763.5 | GGB | 764.835 | 772.359 | 769.963 | 260.59 | GGB | 10771.4 | GGB | 9.85 | GGB | 1001.82 | GGB | 61.02 | GGB | 165682.26 | GGB | 133920.38 | GGB | 0 | 0 | 2714 | 3600 | 2698.38 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 158711.96 | GGB | 158713.77 | 2698.38 | 2698.38 |  |  |  | 1 | 1 |  |  |  |  | 133920.38 | 2698.38 | 133920.38 | 2698.38 | 9.0979 | [5 empty] | 100.38 |  |  | #VALUE!
29.02.2008 23:00 | 3600 | 2 | 763.65 | GGB | 764.835 | 772.43 | 768.864 | 260.52 | GGB | 10767.5 | GGB | 9.85 | GGB | 1001.46 | GGB | 61.12 | GGB | 165486.4 | GGB | 133675.62 | GGB | 0 | 0 | 2711 | 3600 | 2695.53 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 158751.49 | GGB | 158753.3 | 2695.53 | 2695.53 |  |  |  | 1 | 1 |  |  |  |  | 133675.62 | 2695.53 | 133675.62 | 2695.53 | 9.1153 | [5 empty] | 100.0907 |  |  | #VALUE!
29.02.2008 24:00 | 3600 | 2 | 763.5 | GGB | 765.934 | 773.273 | 769.963 | 260.52 | GGB | 10767.8 | GGB | 9.86 | GGB | 1000.53 | GGB | 61.11 | GGB | 165575.52 | GGB | 133625.95 | GGB | 0 | 0 | 2718 | 3600 | 2702.96 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 158791.12 | GGB | 158792.93 | 2702.96 | 2702.96 |  |  |  | 1 | 1 |  |  |  |  | 133625.95 | 2702.96 | 133625.95 | 2702.96 | 9.1139 | [5 empty] | 100.3293 |  |  | #VALUE!
01.03.2008 01:00 | 3600 | 2 | 762.52 | GGB | 764.835 | 771.82 | 768.864 | 261.2 | GGB | 10762.1 | GGB | 9.85 | GGB | 999.38 | GGB | 61.06 | GGB | 166196.11 | GGB | 133991.15 | GGB | 0 | 0 | 2747 | 3600 | 2731.2 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 158830.84 | GGB | 158832.65 | 2731.2 | 2731.2 |  |  |  | 1 | 1 |  |  |  |  | 133991.15 | 2731.2 | 133991.15 | 2731.2 | 9.2134 | [5 empty] | 101.6546 |  |  | #VALUE!
01.03.2008 02:00 | 3600 | 2 | 762.64 | GGB | 764.835 | 771.891 | 767.766 | 261.42 | GGB | 10778.3 | GGB | 9.85 | GGB | 997.8 | GGB | 60.94 | GGB | 166703.37 | GGB | 134239.25 | GGB | 0 | 0 | 2752 | 3600 | 2736.43 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 158870.16 | GGB | 158871.97 | 2736.43 | 2736.43 |  |  |  | 1 | 1 |  |  |  |  | 134239.25 | 2736.43 | 134239.25 | 2736.43 | 9.3422 | [5 empty] | 102.0379 |  |  | #VALUE!
01.03.2008 03:00 | 3600 | 2 | 762.87 | GGB | 764.835 | 772.922 | 767.766 | 260.94 | GGB | 10770.7 | GGB | 9.86 | GGB | 996.17 | GGB | 60.85 | GGB | 166588.93 | GGB | 133960.73 | GGB | 0 | 0 | 2741 | 3600 | 2725.6 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 158909.53 | GGB | 158911.35 | 2725.6 | 2725.6 |  |  |  | 1 | 1 |  |  |  |  | 133960.73 | 2725.6 | 133960.73 | 2725.6 | 9.2718 | [5 empty] | 101.4232 |  |  | #VALUE!
01.03.2008 04:00 | 3600 | 2 | 762.37 | GGB | 764.469 | 772.922 | 768.864 | 260.26 | GGB | 10754.6 | GGB | 9.85 | GGB | 994.46 | GGB | 60.79 | GGB | 166408.48 | GGB | 133612.11 | GGB | 0 | 0 | 2744 | 3600 | 2728.69 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 158949.37 | GGB | 158951.19 | 2728.69 | 2728.69 |  |  |  | 1 | 1 |  |  |  |  | 133612.11 | 2728.69 | 133612.11 | 2728.69 | 9.1513 | [5 empty] | 101.2739 |  |  | #VALUE!
01.03.2008 05:00 | 3600 | 2 | 762.02 | GGB | 764.469 | 771.75 | 767.766 | 260.05 | GGB | 10762.9 | GGB | 9.86 | GGB | 992.6 | GGB | 60.56 | GGB | 166816.7 | GGB | 133779.43 | GGB | 0 | 0 | 2755 | 3600 | 2739.58 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 158988.58 | GGB | 158990.4 | 2739.58 | 2739.58 |  |  |  | 1 | 1 |  |  |  |  | 133779.43 | 2739.58 | 133779.43 | 2739.58 | 9.3471 | [5 empty] | 101.8054 |  |  | #VALUE!
01.03.2008 06:00 | 3600 | 2 | 761.7 | GGB | 764.469 | 771.75 | 768.864 | 259.05 | GGB | 10741.2 | GGB | 9.86 | GGB | 990.11 | GGB | 60.42 | GGB | 166349.06 | GGB | 133126.12 | GGB | 0 | 0 | 2750 | 3600 | 2734.64 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 159028.06 | GGB | 159029.88 | 2734.64 | 2734.64 |  |  |  | 1 | 1 |  |  |  |  | 133126.12 | 2734.64 | 133126.12 | 2734.64 | 9.2212 | [5 empty] | 101.1256 |  |  | #VALUE!
01.03.2008 07:00 | 3600 | 2 | 762.04 | GGB | 764.835 | 772.828 | 768.864 | 258.45 | GGB | 10717.3 | GGB | 9.86 | GGB | 988.4 | GGB | 60.53 | GGB | 165720.77 | GGB | 132351.05 | GGB | 0 | 0 | 2735 | 3600 | 2719.84 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 159067.74 | GGB | 159069.56 | 2719.84 | 2719.84 |  |  |  | 1 | 1 |  |  |  |  | 132351.05 | 2719.84 | 132351.05 | 2719.84 | 9.0719 | [5 empty] | 99.9927 |  |  | #VALUE!
01.03.2008 08:00 | 3600 | 2 | 762.11 | GGB | 763.37 | 771.75 | 767.766 | 257.38 | GGB | 10686.5 | GGB | 9.86 | GGB | 986.31 | GGB | 60.53 | GGB | 164894.41 | GGB | 131411.69 | GGB | 0 | 0 | 2718 | 3600 | 2702.9 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 159106.88 | GGB | 159108.7 | 2702.9 | 2702.9 |  |  |  | 0 | 1 | [14 empty] | 98.6646 |  |  | #VALUE!
01.03.2008 09:00 | 3600 | 2 | 762.61 | GGB | 764.835 | 772.898 | 768.864 | 256.53 | GGB | 10655.2 | GGB | 9.86 | GGB | 984.71 | GGB | 60.68 | GGB | 164137.38 | GGB | 130540.33 | GGB | 0 | 0 | 2692 | 3600 | 2676.75 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 159146.03 | GGB | 159147.85 | 2676.75 | 2676.75 |  |  |  | 1 | 1 |  |  |  |  | 130540.33 | 2676.75 | 130540.33 | 2676.75 | 8.9253 | [5 empty] | 97.0622 |  |  | #VALUE!
01.03.2008 10:00 | 3600 | 2 | 762.92 | GGB | 764.835 | 772.898 | 768.864 | 255.31 | GGB | 10631.1 | GGB | 9.86 | GGB | 982.72 | GGB | 60.57 | GGB | 163337.44 | GGB | 129684.71 | GGB | 0 | 0 | 2664 | 3600 | 2648.36 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 159185.41 | GGB | 159187.23 | 2648.36 | 2648.36 |  |  |  | 1 | 1 |  |  |  |  | 129684.71 | 2648.36 | 129684.71 | 2648.36 | 8.7215 | [5 empty] | 95.4033 |  |  | #VALUE!
01.03.2008 11:00 | 3600 | 2 | 762.21 | GGB | 764.469 | 772.031 | 768.864 | 254.9 | GGB | 10610.2 | GGB | 9.85 | GGB | 980.16 | GGB | 60.49 | GGB | 162955.62 | GGB | 129072.79 | GGB | 0 | 0 | 2678 | 3600 | 2662.63 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 159224.45 | GGB | 159226.28 | 2662.63 | 2662.63 |  |  |  | 1 | 1 |  |  |  |  | 129072.79 | 2662.63 | 129072.79 | 2662.63 | 8.8008 | [5 empty] | 95.4647 |  |  | #VALUE!
01.03.2008 12:00 | 3600 | 2 | 762.22 | GGB | 764.469 | 772.617 | 768.864 | 254.38 | GGB | 10598.5 | GGB | 9.86 | GGB | 977.93 | GGB | 60.25 | GGB | 162676.13 | GGB | 128651.3 | GGB | 0 | 0 | 2675 | 3600 | 2659.79 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 159263.27 | GGB | 159265.1 | 2659.79 | 2659.79 |  |  |  | 1 | 1 |  |  |  |  | 128651.3 | 2659.79 | 128651.3 | 2659.79 | 8.8147 | [5 empty] | 95.0515 |  |  | #VALUE!
01.03.2008 13:00 | 3600 | 2 | 762.16 | GGB | 763.37 | 771.422 | 767.766 | 253.66 | GGB | 10578.5 | GGB | 9.86 | GGB | 976.23 | GGB | 60.14 | GGB | 161963.12 | GGB | 127905.99 | GGB | 0 | 0 | 2668 | 3600 | 2652.45 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 159302.55 | GGB | 159304.38 | 2652.45 | 2652.45 |  |  |  | 0 | 1 | [14 empty] | 94.2401 |  |  | #VALUE!
01.03.2008 14:00 | 3600 | 2 | 762.23 | GGB | 764.469 | 772.406 | 768.864 | 253.62 | GGB | 10565.7 | GGB | 9.86 | GGB | 974.69 | GGB | 60.35 | GGB | 162147.97 | GGB | 127772.05 | GGB | 0 | 0 | 2661 | 3600 | 2646.07 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 159341.03 | GGB | 159342.86 | 2646.07 | 2646.07 |  |  |  | 1 | 1 |  |  |  |  | 127772.05 | 2646.07 | 127772.05 | 2646.07 | 8.7862 | [5 empty] | 93.9149 |  |  | #VALUE!
01.03.2008 15:00 | 3600 | 2 | 762.94 | GGB | 764.835 | 772.477 | 768.864 | 252.96 | GGB | 10538.8 | GGB | 9.86 | GGB | 972.89 | GGB | 60.74 | GGB | 161232.49 | GGB | 126666.4 | GGB | 0 | 0 | 2634 | 3600 | 2618.98 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 159379.4 | GGB | 159381.23 | 2618.98 | 2618.98 |  |  |  | 1 | 1 |  |  |  |  | 126666.4 | 2618.98 | 126666.4 | 2618.98 | 8.6457 | [5 empty] | 92.1491 |  |  | #VALUE!
01.03.2008 16:00 | 3600 | 2 | 763.22 | GGB | 764.835 | 772.289 | 768.864 | 252.39 | GGB | 10504.3 | GGB | 9.85 | GGB | 971.52 | GGB | 60.99 | GGB | 160473.26 | GGB | 125796.8 | GGB | 0 | 0 | 2612 | 3600 | 2596.54 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 159418.38 | GGB | 159420.2 | 2596.54 | 2596.54 |  |  |  | 1 | 1 |  |  |  |  | 125796.8 | 2596.54 | 125796.8 | 2596.54 | 8.3817 | [5 empty] | 90.7323 |  |  | #VALUE!
01.03.2008 17:00 | 3600 | 2 | 763.07 | GGB | 764.835 | 772.359 | 768.864 | 252.05 | GGB | 10489.4 | GGB | 9.85 | GGB | 970.5 | GGB | 61.06 | GGB | 160137.65 | GGB | 125376.73 | GGB | 0 | 0 | 2613 | 3600 | 2597.56 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 159456.82 | GGB | 159458.64 | 2597.56 | 2597.56 |  |  |  | 1 | 1 |  |  |  |  | 125376.73 | 2597.56 |  | 2597.56 | 8.4723 | [5 empty] | 90.4649 |  |  | #VALUE!
01.03.2008 18:00 | 3600 | 2 | 763.11 | GGB | 764.835 | 772.477 | 768.864 | 251.75 | GGB | 10481.4 | GGB | 9.86 | GGB | 969.78 | GGB | 61.06 | GGB | 159547.87 | GGB | 124821.87 | GGB | 0 | 0 | 2605 | 3600 | 2589.26 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 159495.22 | GGB | 159497.04 | 2589.26 | 2589.26 |  |  |  | 1 | 1 |  |  |  |  | 124821.87 | 2589.26 |  | 2589.26 | 8.4166 | [5 empty] | 89.7767 |  |  | #VALUE!
01.03.2008 19:00 | 3600 | 2 | 763.36 | GGB | 764.835 | 772.453 | 768.864 | 251.72 | GGB | 10472.6 | GGB | 9.86 | GGB | 969.58 | GGB | 61.26 | GGB | 159357.52 | GGB | 124573.57 | GGB | 0 | 0 | 2598 | 3600 | 2582.42 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 159533.98 | GGB | 159535.8 | 2582.42 | 2582.42 |  |  |  | 1 | 1 |  |  |  |  | 124573.57 | 2582.42 |  | 2582.42 | 8.2998 | [5 empty] | 89.3615 |  |  | #VALUE!
01.03.2008 20:00 | 3600 | 2 | 763.15 | GGB | 764.469 | 772.664 | 768.864 | 252.1 | GGB | 10466 | GGB | 9.85 | GGB | 969.52 | GGB | 61.23 | GGB | 159377.32 | GGB | 124592.94 | GGB | 0 | 0 | 2606 | 3600 | 2590.9 | GGB | 100 | GGB | 37.06 | GGB | 37.06 | GGB | 159571.04 | GGB | 159572.86 | 2590.9 | 2590.9 |  |  |  | 1 | 1 |  |  |  |  | 124592.94 | 2590.9 |  | 2590.9 | 8.7104 | [5 empty] | 89.6688 |  |  | #VALUE!
01.03.2008 21:00 | 3600 | 2 | 763.69 | GGB | 764.835 | 772.805 | 768.864 | 252.32 | GGB | 10480.9 | GGB | 9.86 | GGB | 969.73 | GGB | 61.16 | GGB | 159311.3 | GGB | 124594.25 | GGB | 0 | 0 | 2594 | 3600 | 2578.86 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 159609.7 | GGB | 159611.52 | 2578.86 | 2578.86 |  |  |  | 1 | 1 |  |  |  |  | 124594.25 | 2578.86 |  | 2578.86 | 8.3112 | [5 empty] | 89.2531 |  |  | #VALUE!
01.03.2008 22:00 | 3600 | 2 | 763.57 | GGB | 764.835 | 772.688 | 769.963 | 252.07 | GGB | 10477.6 | GGB | 9.85 | GGB | 969.58 | GGB | 61.19 | GGB | 159276.09 | GGB | 124535.28 | GGB | 0 | 0 | 2595 | 3600 | 2579.7 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 159648.74 | GGB | 159650.56 | 2579.7 | 2579.7 |  |  |  | 1 | 1 |  |  |  |  | 124535.28 | 2579.7 |  | 2579.7 | 8.2291 | [5 empty] | 89.2399 |  |  | #VALUE!
01.03.2008 23:00 | 3600 | 2 | 763.23 | GGB | 765.934 | 772.594 | 768.864 | 252.12 | GGB | 10503.4 | GGB | 9.86 | GGB | 969.68 | GGB | 61.01 | GGB | 160545.88 | GGB | 125610.76 | GGB | 0 | 0 | 2605 | 3600 | 2589.42 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 159687.16 | GGB | 159688.98 | 2589.42 | 2589.42 |  |  |  | 1 | 1 |  |  |  |  | 125610.76 | 2589.42 | 125610.76 | 2589.42 | 8.4659 | [5 empty] | 90.3497 |  |  | #VALUE!
01.03.2008 24:00 | 3600 | 2 | 763.11 | GGB | 765.934 | 773.625 | 769.963 | 252.88 | GGB | 10492.5 | GGB | 9.85 | GGB | 969.87 | GGB | 61.18 | GGB | 160188.27 | GGB | 125290.92 | GGB | 0 | 0 | 2608 | 3600 | 2593.02 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 159725.52 | GGB | 159727.35 | 2593.02 | 2593.02 |  |  |  | 1 | 1 |  |  |  |  | 125290.92 | 2593.02 |  | 2593.02 | 8.4671 | [5 empty] | 90.245 |  |  | #VALUE!
02.03.2008 01:00 | 3600 | 2 | 763.57 | GGB | 764.835 | 771.516 | 768.498 | 252.65 | GGB | 10482 | GGB | 9.85 | GGB | 969.76 | GGB | 61.52 | GGB | 159726.13 | GGB | 124787.45 | GGB | 0 | 0 | 2593 | 3600 | 2577.98 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 159764.17 | GGB | 159766 | 2577.98 | 2577.98 |  |  |  | 1 | 1 |  |  |  |  | 124787.45 | 2577.98 |  | 2577.98 | 8.3234 | [5 empty] | 89.361 |  |  | #VALUE!
02.03.2008 02:00 | 3600 | 2 | 763.4 | GGB | 764.835 | 771.563 | 768.132 | 252.42 | GGB | 10472.5 | GGB | 9.85 | GGB | 969.53 | GGB | 61.41 | GGB | 159569.88 | GGB | 124675.87 | GGB | 0 | 0 | 2595 | 3600 | 2579.89 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 159802.96 | GGB | 159804.79 | 2579.89 | 2579.89 |  |  |  | 1 | 1 |  |  |  |  | 124675.87 | 2579.89 |  | 2579.89 | 8.2921 | [5 empty] | 89.3472 |  |  | #VALUE!
02.03.2008 03:00 | 3600 | 2 | 763.48 | GGB | 764.835 | 772.359 | 768.498 | 252.68 | GGB | 10484 | GGB | 9.86 | GGB | 969.39 | GGB | 61.44 | GGB | 159860.37 | GGB | 124874.41 | GGB | 0 | 0 | 2596 | 3600 | 2580.55 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 159841.63 | GGB | 159843.46 | 2580.55 | 2580.55 |  |  |  | 1 | 1 |  |  |  |  | 124874.41 | 2580.55 |  | 2580.55 | 8.3332 | [5 empty] | 89.5124 |  |  | #VALUE!
02.03.2008 04:00 | 3600 | 2 | 762.91 | GGB | 763.37 | 771.117 | 768.498 | 253.42 | GGB | 10505 | GGB | 9.85 | GGB | 969.26 | GGB | 60.93 | GGB | 160739.54 | GGB | 125734.14 | GGB | 0 | 0 | 2626 | 3600 | 2610.57 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 159880.23 | GGB | 159882.05 | 2610.57 | 2610.57 |  |  |  | 0 | 1 | [14 empty] | 91.1772 |  |  | #VALUE!
02.03.2008 05:00 | 3600 | 2 | 762.88 | GGB | 764.469 | 772.148 | 768.498 | 253.52 | GGB | 10510.8 | GGB | 9.86 | GGB | 969.38 | GGB | 61.01 | GGB | 160993.72 | GGB | 125920.15 | GGB | 0 | 0 | 2623 | 3600 | 2607.19 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 159918.52 | GGB | 159920.35 | 2607.19 | 2607.19 |  |  |  | 1 | 1 |  |  |  |  | 125920.15 | 2607.19 | 125920.15 | 2607.19 | 8.5717 | [5 empty] | 91.1938 |  |  | #VALUE!
02.03.2008 06:00 | 3600 | 2 | 763.04 | GGB | 764.835 | 772.125 | 768.498 | 253.53 | GGB | 10516.7 | GGB | 9.86 | GGB | 969.7 | GGB | 60.88 | GGB | 160901.29 | GGB | 125940.86 | GGB | 0 | 0 | 2621 | 3600 | 2605.57 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 159957.18 | GGB | 159959.01 | 2605.57 | 2605.57 |  |  |  | 1 | 1 |  |  |  |  | 125940.86 | 2605.57 | 125940.86 | 2605.57 | 8.488 | [5 empty] | 91.1521 |  |  | #VALUE!
02.03.2008 07:00 | 3600 | 2 | 762.56 | GGB | 763.37 | 771.117 | 768.498 | 253.44 | GGB | 10516.2 | GGB | 9.85 | GGB | 969.82 | GGB | 60.76 | GGB | 161078.44 | GGB | 126138.61 | GGB | 0 | 0 | 2629 | 3600 | 2613.29 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 159995.99 | GGB | 159997.82 | 2613.29 | 2613.29 |  |  |  | 0 | 1 | [14 empty] | 91.5658 |  |  | #VALUE!
02.03.2008 08:00 | 3600 | 2 | 762.46 | GGB | 764.469 | 771.117 | 768.498 | 253.73 | GGB | 10530.8 | GGB | 9.85 | GGB | 970.21 | GGB | 60.57 | GGB | 161566.99 | GGB | 126643.62 | GGB | 0 | 0 | 2640 | 3600 | 2624.33 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 160034.3 | GGB | 160036.12 | 2624.33 | 2624.33 |  |  |  | 1 | 1 |  |  |  |  | 126643.62 | 2624.33 | 126643.62 | 2624.33 | 8.6777 | [5 empty] | 92.3207 |  |  | #VALUE!
02.03.2008 09:00 | 3600 | 2 | 762.52 | GGB | 764.469 | 772.219 | 768.498 | 253.97 | GGB | 10546.7 | GGB | 9.86 | GGB | 970.96 | GGB | 60.37 | GGB | 161946.61 | GGB | 127115.02 | GGB | 0 | 0 | 2641 | 3600 | 2626.08 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 160073.04 | GGB | 160074.87 | 2626.08 | 2626.08 |  |  |  | 1 | 1 |  |  |  |  | 127115.02 | 2626.08 | 127115.02 | 2626.08 | 8.6146 | [5 empty] | 92.7262 |  |  | #VALUE!
02.03.2008 10:00 | 3600 | 2 | 761.94 | GGB | 764.469 | 771.445 | 768.132 | 255 | GGB | 10537.4 | GGB | 9.85 | GGB | 971.3 | GGB | 59.85 | GGB | 163569.61 | GGB | 128636.36 | GGB | 0 | 0 | 2646 | 3600 | 2630.71 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 160112.02 | GGB | 160113.85 | 2630.71 | 2630.71 |  |  |  | 1 | 1 |  |  |  |  | 128636.36 | 2630.71 | 128636.36 | 2630.71 | 8.6815 | [5 empty] | 94.0014 |  |  | #VALUE!
02.03.2008 11:00 | 3600 | 2 | 763.15 | GGB | 764.469 | 771.492 | 768.498 | 254.39 | GGB | 10560 | GGB | 9.86 | GGB | 971.71 | GGB | 60 | GGB | 163027.14 | GGB | 128206.94 | GGB | 0 | 0 | 2626 | 3600 | 2610.76 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 160149.58 | GGB | 160151.4 | 2610.76 | 2610.76 |  |  |  | 1 | 1 |  |  |  |  | 128206.94 | 2610.76 | 128206.94 | 2610.76 | 8.9139 | [5 empty] | 92.9771 |  |  | #VALUE!
02.03.2008 12:00 | 3600 | 2 | 762.4 | GGB | 764.469 | 771.516 | 768.132 | 253.93 | GGB | 10557.6 | GGB | 9.85 | GGB | 972.01 | GGB | 60.28 | GGB | 162160.08 | GGB | 127455.07 | GGB | 0 | 0 | 2645 | 3600 | 2629.91 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 160188.82 | GGB | 160190.65 | 2629.91 | 2629.91 |  |  |  | 1 | 1 |  |  |  |  | 127455.07 | 2629.91 | 127455.07 | 2629.91 | 8.54 | [5 empty] | 93.1098 |  |  | #VALUE!
02.03.2008 13:00 | 3600 | 2 | 762.2 | GGB | 763.37 | 770.344 | 767.033 | 253.87 | GGB | 10555.8 | GGB | 9.85 | GGB | 972.11 | GGB | 60.24 | GGB | 162077.55 | GGB | 127417.25 | GGB | 0 | 0 | 2650 | 3600 | 2634.8 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 160227.82 | GGB | 160229.64 | 2634.8 | 2634.8 |  |  |  | 0 | 1 | [14 empty] | 93.2553 |  |  | #VALUE!
02.03.2008 14:00 | 3600 | 2 | 761.71 | GGB | 763.37 | 770.508 | 768.132 | 254.53 | GGB | 10578.3 | GGB | 9.85 | GGB | 972.53 | GGB | 59.92 | GGB | 162867.59 | GGB | 128219.48 | GGB | 0 | 0 | 2672 | 3600 | 2657.11 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 160266.28 | GGB | 160268.11 | 2657.11 | 2657.11 |  |  |  | 0 | 1 | [14 empty] | 94.637 |  |  | #VALUE!
02.03.2008 15:00 | 3600 | 2 | 761.58 | GGB | 764.469 | 771.516 | 768.132 | 254.85 | GGB | 10603.9 | GGB | 9.86 | GGB | 973.57 | GGB | 59.56 | GGB | 163417.76 | GGB | 128928.2 | GGB | 0 | 0 | 2687 | 3600 | 2671.37 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 160305.61 | GGB | 160307.44 | 2671.37 | 2671.37 |  |  |  | 1 | 1 |  |  |  |  | 128928.2 | 2671.37 | 128928.2 | 2671.37 | 8.7571 | [5 empty] | 95.6708 |  |  | #VALUE!
02.03.2008 16:00 | 3600 | 2 | 762.46 | GGB | 764.835 | 772.781 | 768.132 | 254.21 | GGB | 10579.8 | GGB | 9.86 | GGB | 974.46 | GGB | 60.08 | GGB | 162581.5 | GGB | 128185.22 | GGB | 0 | 0 | 2659 | 3600 | 2643.33 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 160343.95 | GGB | 160345.78 | 2643.33 | 2643.33 |  |  |  | 1 | 1 |  |  |  |  | 128185.22 | 2643.33 | 128185.22 | 2643.33 | 8.8377 | [5 empty] | 94.1211 |  |  | #VALUE!
02.03.2008 17:00 | 3600 | 2 | 763.26 | GGB | 764.835 | 772.641 | 768.498 | 254.08 | GGB | 10567.1 | GGB | 9.86 | GGB | 975.43 | GGB | 60.38 | GGB | 162075.35 | GGB | 127796.92 | GGB | 0 | 0 | 2629 | 3600 | 2613.56 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 160382.56 | GGB | 160384.39 | 2613.56 | 2613.56 |  |  |  | 1 | 1 |  |  |  |  | 127796.92 | 2613.56 | 127796.92 | 2613.56 | 8.6507 | [5 empty] | 92.7791 |  |  | #VALUE!
02.03.2008 18:00 | 3600 | 2 | 762.74 | GGB | 764.835 | 771.586 | 768.498 | 254.66 | GGB | 10573 | GGB | 9.85 | GGB | 976.12 | GGB | 60.35 | GGB | 162531.99 | GGB | 128263.41 | GGB | 0 | 0 | 2647 | 3600 | 2631.39 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 160421.89 | GGB | 160423.73 | 2631.39 | 2631.39 |  |  |  | 1 | 1 |  |  |  |  | 128263.41 | 2631.39 | 128263.41 | 2631.39 | 8.5793 | [5 empty] | 93.7531 |  |  | #VALUE!
02.03.2008 19:00 | 3600 | 2 | 762.23 | GGB | 764.469 | 771.703 | 768.498 | 255.55 | GGB | 10601.4 | GGB | 9.85 | GGB | 977.42 | GGB | 60.22 | GGB | 163351.74 | GGB | 129129.02 | GGB | 0 | 0 | 2673 | 3600 | 2657.43 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 160460.31 | GGB | 160462.15 | 2657.43 | 2657.43 |  |  |  | 1 | 1 |  |  |  |  | 129129.02 | 2657.43 | 129129.02 | 2657.43 | 8.9316 | [5 empty] | 95.3198 |  |  | #VALUE!
02.03.2008 20:00 | 3600 | 2 | 762.53 | GGB | 764.469 | 771.609 | 768.498 | 255.93 | GGB | 10609.8 | GGB | 9.85 | GGB | 978.66 | GGB | 60.37 | GGB | 163264.81 | GGB | 129168.75 | GGB | 0 | 0 | 2672 | 3600 | 2656.43 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 160499.33 | GGB | 160501.16 | 2656.43 | 2656.43 |  |  |  | 1 | 1 |  |  |  |  | 129168.75 | 2656.43 | 129168.75 | 2656.43 | 8.7959 | [5 empty] | 95.3133 |  |  | #VALUE!
02.03.2008 21:00 | 3600 | 2 | 762.3 | GGB | 763.37 | 771.516 | 768.132 | 255.56 | GGB | 10618.8 | GGB | 9.85 | GGB | 979.08 | GGB | 60.15 | GGB | 163707.15 | GGB | 129656.31 | GGB | 0 | 0 | 2676 | 3600 | 2660.31 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 160538.46 | GGB | 160540.29 | 2660.31 | 2660.31 |  |  |  | 0 | 1 | [14 empty] | 95.8128 |  |  | #VALUE!
02.03.2008 22:00 | 3600 | 2 | 762.3 | GGB | 764.469 | 771.422 | 768.132 | 256.37 | GGB | 10627.1 | GGB | 9.85 | GGB | 979.29 | GGB | 60.24 | GGB | 163905.21 | GGB | 129807.24 | GGB | 0 | 0 | 2687 | 3600 | 2671.35 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 160576.95 | GGB | 160578.78 | 2671.35 | 2671.35 |  |  |  | 1 | 1 |  |  |  |  | 129807.24 | 2671.35 | 129807.24 | 2671.35 | 9.0091 | [5 empty] | 96.3224 |  |  | #VALUE!
02.03.2008 23:00 | 3600 | 2 | 762 | GGB | 764.469 | 771.469 | 768.132 | 256.8 | GGB | 10636.3 | GGB | 9.85 | GGB | 979.38 | GGB | 60.27 | GGB | 164522.5 | GGB | 130295.56 | GGB | 0 | 0 | 2699 | 3600 | 2683.91 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 160616.71 | GGB | 160618.54 | 2683.91 | 2683.91 |  |  |  | 1 | 1 |  |  |  |  | 130295.56 | 2683.91 | 130295.56 | 2683.91 | 8.7953 | [5 empty] | 97.1393 |  |  | #VALUE!
02.03.2008 24:00 | 3600 | 2 | 762.14 | GGB | 764.469 | 771.469 | 768.132 | 257.01 | GGB | 10643.7 | GGB | 9.86 | GGB | 979.85 | GGB | 60.33 | GGB | 164634.74 | GGB | 130425.33 | GGB | 0 | 0 | 2703 | 3600 | 2687.78 | GGB | 100 | GGB | 38.41 | GGB | 38.41 | GGB | 160655.12 | GGB | 160656.95 | 2687.78 | 2687.78 |  |  |  | 1 | 1 |  |  |  |  | 130425.33 | 2687.78 | 130425.33 | 2687.78 | 9.1266 | [5 empty] | 97.3763 |  |  | #VALUE!
03.03.2008 01:00 | 3600 | 2 | 761.89 | GGB | 764.469 | 771.492 | 768.498 | 257 | GGB | 10644.3 | GGB | 9.85 | GGB | 980.34 | GGB | 60.29 | GGB | 164498.29 | GGB | 130398.28 | GGB | 0 | 0 | 2708 | 3600 | 2692.85 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 160694.05 | GGB | 160695.88 | 2692.85 | 2692.85 |  |  |  | 1 | 1 |  |  |  |  | 130398.28 | 2692.85 | 130398.28 | 2692.85 | 9.0199 | [5 empty] | 97.5397 |  |  | #VALUE!
03.03.2008 02:00 | 3600 | 2 | 762.29 | GGB | 764.469 | 772.359 | 768.498 | 258.36 | GGB | 10646.4 | GGB | 9.85 | GGB | 981.05 | GGB | 59.52 | GGB | 166252.23 | GGB | 132187.88 | GGB | 0 | 0 | 2693 | 3600 | 2677.98 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 160733.7 | GGB | 160735.53 | 2677.98 | 2677.98 |  |  |  | 1 | 1 |  |  |  |  | 132187.88 | 2677.98 | 132187.88 | 2677.98 | 8.928 | [5 empty] | 98.3324 |  |  | #VALUE!
03.03.2008 03:00 | 3600 | 2 | 761.19 | GGB | 763.37 | 770.18 | 767.033 | 258.28 | GGB | 10699.5 | GGB | 9.85 | GGB | 981.52 | GGB | 59.36 | GGB | 166038.77 | GGB | 132147.98 | GGB | 0 | 0 | 2755 | 3600 | 2739.8 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 160771.81 | GGB | 160773.64 | 2739.8 | 2739.8 |  |  |  | 0 | 1 | [14 empty] | 100.572 |  |  | #VALUE!
03.03.2008 04:00 | 3600 | 2 | 761.48 | GGB | 764.469 | 771.211 | 768.132 | 257.94 | GGB | 10709.3 | GGB | 9.86 | GGB | 982.45 | GGB | 59.45 | GGB | 165656.95 | GGB | 131931.02 | GGB | 0 | 0 | 2746 | 3600 | 2731.01 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 160811.63 | GGB | 160813.46 | 2731.01 | 2731.01 |  |  |  | 1 | 1 |  |  |  |  | 131931.02 | 2731.01 | 131931.02 | 2731.01 | 9.0483 | [5 empty] | 100.0847 |  |  | #VALUE!
03.03.2008 05:00 | 3600 | 2 | 762.1 | GGB | 764.469 | 772.359 | 768.132 | 257.37 | GGB | 10700.6 | GGB | 9.86 | GGB | 983.57 | GGB | 59.57 | GGB | 165269.63 | GGB | 131724.16 | GGB | 0 | 0 | 2723 | 3600 | 2707.09 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 160850.82 | GGB | 160852.65 | 2707.09 | 2707.09 |  |  |  | 1 | 1 |  |  |  |  | 131724.16 | 2707.09 | 131724.16 | 2707.09 | 9.099 | [5 empty] | 99.0525 |  |  | #VALUE!
03.03.2008 06:00 | 3600 | 2 | 761.95 | GGB | 764.835 | 772.383 | 768.498 | 257.51 | GGB | 10685.3 | GGB | 9.85 | GGB | 984.65 | GGB | 59.45 | GGB | 165579.93 | GGB | 132164.32 | GGB | 0 | 0 | 2716 | 3600 | 2700.28 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 160889.38 | GGB | 160891.21 | 2700.28 | 2700.28 |  |  |  | 1 | 1 |  |  |  |  | 132164.32 | 2700.28 | 132164.32 | 2700.28 | 9.2552 | [5 empty] | 99.1335 |  |  | #VALUE!
03.03.2008 07:00 | 3600 | 2 | 762.56 | GGB | 765.934 | 772.383 | 768.498 | 258.48 | GGB | 10677.9 | GGB | 9.85 | GGB | 985.46 | GGB | 59.3 | GGB | 166498.71 | GGB | 133067.11 | GGB | 0 | 0 | 2695 | 3600 | 2679.54 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 160929.44 | GGB | 160931.27 | 2679.54 | 2679.54 |  |  |  | 1 | 1 |  |  |  |  | 133067.11 | 2679.54 | 133067.11 | 2679.54 | 8.9006 | [5 empty] | 99.0441 |  |  | #VALUE!
03.03.2008 08:00 | 3600 | 2 | 762.15 | GGB | 764.835 | 772.383 | 768.498 | 258.99 | GGB | 10685.6 | GGB | 9.85 | GGB | 986.14 | GGB | 59.3 | GGB | 166980.66 | GGB | 133544.39 | GGB | 0 | 0 | 2708 | 3600 | 2692.24 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 160968.16 | GGB | 160969.98 | 2692.24 | 2692.24 |  |  |  | 1 | 1 |  |  |  |  | 133544.39 | 2692.24 | 133544.39 | 2692.24 | 9.2879 | [5 empty] | 99.8704 |  |  | #VALUE!
03.03.2008 09:00 | 3600 | 2 | 762.78 | GGB | 764.835 | 771.281 | 768.498 | 259.1 | GGB | 10707.8 | GGB | 9.86 | GGB | 987.11 | GGB | 59.5 | GGB | 166684.66 | GGB | 133359.99 | GGB | 0 | 0 | 2701 | 3600 | 2686 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 161007.16 | GGB | 161008.99 | 2686 | 2686 |  |  |  | 1 | 1 |  |  |  |  | 133359.99 | 2686 | 133359.99 | 2686 | 9.1824 | [5 empty] | 99.5014 |  |  | #VALUE!
03.03.2008 10:00 | 3600 | 2 | 762.65 | GGB | 764.835 | 772.242 | 768.498 | 258.48 | GGB | 10716.7 | GGB | 9.86 | GGB | 987.97 | GGB | 59.83 | GGB | 165445.68 | GGB | 132351.76 | GGB | 0 | 0 | 2720 | 3600 | 2704.91 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 161046.8 | GGB | 161048.63 | 2704.91 | 2704.91 |  |  |  | 1 | 1 |  |  |  |  | 132351.76 | 2704.91 | 132351.76 | 2704.91 | 9.0313 | [5 empty] | 99.4443 |  |  | #VALUE!
03.03.2008 11:00 | 3600 | 2 | 762.9 | GGB | 764.835 | 772.383 | 768.498 | 259.13 | GGB | 10693.2 | GGB | 9.85 | GGB | 988.69 | GGB | 59.79 | GGB | 166342.46 | GGB | 133181.86 | GGB | 0 | 0 | 2705 | 3600 | 2689.62 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 161085.91 | GGB | 161087.74 | 2689.62 | 2689.62 |  |  |  | 1 | 1 |  |  |  |  | 133181.86 | 2689.62 | 133181.86 | 2689.62 | 9.159 | [5 empty] | 99.5024 |  |  | #VALUE!
03.03.2008 12:00 | 3600 | 2 | 763.85 | GGB | 765.934 | 773.273 | 769.597 | 257.74 | GGB | 10698.1 | GGB | 9.86 | GGB | 988.96 | GGB | 60.24 | GGB | 164708.46 | GGB | 131732.38 | GGB | 0 | 0 | 2666 | 3600 | 2650.47 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 161124.88 | GGB | 161126.71 | 2650.47 | 2650.47 |  |  |  | 1 | 1 |  |  |  |  | 131732.38 | 2650.47 | 131732.38 | 2650.47 | 8.9595 | [5 empty] | 96.9869 |  |  | #VALUE!
03.03.2008 13:00 | 3600 | 2 | 764.05 | GGB | 765.934 | 774.211 | 770.696 | 257.11 | GGB | 10680.5 | GGB | 9.86 | GGB | 989.01 | GGB | 60.56 | GGB | 163961.33 | GGB | 131013.46 | GGB | 0 | 0 | 2654 | 3600 | 2638.56 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 161164.32 | GGB | 161166.15 | 2638.56 | 2638.56 |  |  |  | 1 | 1 |  |  |  |  | 131013.46 | 2638.56 | 131013.46 | 2638.56 | 8.7649 | [5 empty] | 96.0241 |  |  | #VALUE!
03.03.2008 14:00 | 3600 | 2 | 764.01 | GGB | 764.835 | 772.031 | 768.498 | 258.22 | GGB | 10651.5 | GGB | 9.85 | GGB | 988.89 | GGB | 60.47 | GGB | 165040.76 | GGB | 131895.86 | GGB | 0 | 0 | 2644 | 3600 | 2628.49 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 161203.79 | GGB | 161205.62 | 2628.49 | 2628.49 |  |  |  | 1 | 1 |  |  |  |  | 131895.86 | 2628.49 | 131895.86 | 2628.49 | 8.7836 | [5 empty] | 96.3019 |  |  | #VALUE!
03.03.2008 15:00 | 3600 | 2 | 761.07 | GGB | 763.37 | 770.906 | 765.934 | 260.38 | GGB | 10754.9 | GGB | 9.84 | GGB | 989.26 | GGB | 59 | GGB | 167416.39 | GGB | 134439.83 | GGB | 0 | 0 | 2805 | 3600 | 2789.06 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 161242.96 | GGB | 161244.79 | 2789.06 | 2789.06 |  |  |  | 0 | 1 | [14 empty] | 104.1558 |  |  | #VALUE!
03.03.2008 16:00 | 3600 | 2 | 761.04 | GGB | 762.271 | 770.016 | 765.934 | 261.12 | GGB | 10789 | GGB | 9.85 | GGB | 990.25 | GGB | 58.14 | GGB | 169011.88 | GGB | 136209.24 | GGB | 0 | 0 | 2817 | 3600 | 2801.17 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 161282.79 | GGB | 161284.62 | 2801.17 | 2774.6135 |  |  |  | 0 | 1 | [14 empty] | 105.9848 | 2774.6135 |  | 104.98
03.03.2008 17:00 | 3600 | 2 | 763.22 | GGB | 765.934 | 773.25 | 769.597 | 260.96 | GGB | 10750.2 | GGB | 9.87 | GGB | 991.15 | GGB | 59.09 | GGB | 168635.56 | GGB | 135637.06 | GGB | 0 | 0 | 2722 | 3600 | 2706.14 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 161321.8 | GGB | 161323.63 | 2706.14 | 2706.14 |  |  |  | 1 | 1 |  |  |  |  | 135637.06 | 2706.14 | 135637.06 | 2706.14 | 9.4092 | [5 empty] | 101.9591 |  |  | #VALUE!
03.03.2008 18:00 | 3600 | 2 | 763.19 | GGB | 764.835 | 772.148 | 768.498 | 258.99 | GGB | 10721 | GGB | 9.86 | GGB | 990.94 | GGB | 59.68 | GGB | 166024.46 | GGB | 133275.63 | GGB | 0 | 0 | 2706 | 3600 | 2690.54 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 161360.68 | GGB | 161362.51 | 2690.54 | 2690.54 |  |  |  | 1 | 1 |  |  |  |  | 133275.63 | 2690.54 | 133275.63 | 2690.54 | 9.2228 | [5 empty] | 99.6065 |  |  | #VALUE!
03.03.2008 19:00 | 3600 | 2 | 762.35 | GGB | 764.469 | 772.078 | 768.498 | 258.93 | GGB | 10726.1 | GGB | 9.85 | GGB | 991.36 | GGB | 60.13 | GGB | 165662.45 | GGB | 132861.08 | GGB | 0 | 0 | 2731 | 3600 | 2715.3 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 161400.87 | GGB | 161402.7 | 2715.3 | 2715.3 |  |  |  | 1 | 1 |  |  |  |  | 132861.08 | 2715.3 | 132861.08 | 2715.3 | 8.9763 | [5 empty] | 100.2105 |  |  | #VALUE!
03.03.2008 20:00 | 3600 | 2 | 762.38 | GGB | 764.835 | 772.078 | 768.132 | 259.7 | GGB | 10742 | GGB | 9.85 | GGB | 992.36 | GGB | 60.24 | GGB | 166213.72 | GGB | 133392.34 | GGB | 0 | 0 | 2742 | 3600 | 2726.96 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 161439.92 | GGB | 161441.75 | 2726.96 | 2726.96 |  |  |  | 1 | 1 |  |  |  |  | 133392.34 | 2726.96 | 133392.34 | 2726.96 | 9.3151 | [5 empty] | 101.0432 |  |  | #VALUE!
03.03.2008 21:00 | 3600 | 2 | 762.5 | GGB | 764.469 | 772.195 | 768.132 | 259.97 | GGB | 10750.7 | GGB | 9.85 | GGB | 992.54 | GGB | 60.07 | GGB | 166521.81 | GGB | 133734.98 | GGB | 0 | 0 | 2752 | 3600 | 2736.49 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 161479.28 | GGB | 161481.11 | 2736.49 | 2736.49 |  |  |  | 1 | 1 |  |  |  |  | 133734.98 | 2736.49 | 133734.98 | 2736.49 | 9.2979 | [5 empty] | 101.6568 |  |  | #VALUE!
03.03.2008 22:00 | 3600 | 2 | 762.17 | GGB | 764.835 | 771.281 | 768.132 | 259.49 | GGB | 10761.5 | GGB | 9.85 | GGB | 993.02 | GGB | 59.92 | GGB | 166876.12 | GGB | 134140.25 | GGB | 0 | 0 | 2759 | 3600 | 2743.28 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 161519.34 | GGB | 161521.18 | 2743.28 | 2743.28 |  |  |  | 1 | 1 |  |  |  |  | 134140.25 | 2743.28 | 134140.25 | 2743.28 | 9.1835 | [5 empty] | 102.2179 |  |  | #VALUE!
03.03.2008 23:00 | 3600 | 2 | 762.46 | GGB | 763.37 | 771.211 | 767.033 | 261.05 | GGB | 10738.7 | GGB | 9.85 | GGB | 993 | GGB | 59.64 | GGB | 167776.2 | GGB | 134977.54 | GGB | 0 | 0 | 2745 | 3600 | 2729.81 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 161558.46 | GGB | 161560.3 | 2729.81 | 2729.81 |  |  |  | 0 | 1 | [14 empty] | 102.3508 |  |  | #VALUE!
03.03.2008 24:00 | 3600 | 2 | 762.2 | GGB | 763.37 | 770.156 | 767.033 | 260.64 | GGB | 10766.4 | GGB | 9.85 | GGB | 993.54 | GGB | 60.1 | GGB | 166873.92 | GGB | 134138.97 | GGB | 0 | 0 | 2770 | 3600 | 2754.58 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 161596.57 | GGB | 161598.41 | 2754.58 | 2754.58 |  |  |  | 0 | 1 | [14 empty] | 102.6379 |  |  | #VALUE!
04.03.2008 01:00 | 3600 | 2 | 761.7 | GGB | 764.469 | 771.844 | 768.132 | 262.18 | GGB | 10770 | GGB | 9.85 | GGB | 993.48 | GGB | 59.86 | GGB | 168780.81 | GGB | 135762.38 | GGB | 0 | 0 | 2793 | 3600 | 2777.34 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 161636.32 | GGB | 161638.16 | 2777.34 | 2777.34 |  |  |  | 1 | 1 |  |  |  |  | 135762.38 | 2777.34 | 135762.38 | 2777.34 | 9.4857 | [5 empty] | 104.7384 |  |  | #VALUE!
04.03.2008 02:00 | 3600 | 2 | 762.93 | GGB | 764.835 | 772.688 | 768.498 | 262.33 | GGB | 10778.9 | GGB | 9.86 | GGB | 993.53 | GGB | 59.55 | GGB | 169042.69 | GGB | 136105.77 | GGB | 0 | 0 | 2750 | 3600 | 2735.03 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 161676.95 | GGB | 161678.79 | 2735.03 | 2735.03 |  |  |  | 1 | 1 |  |  |  |  | 136105.77 | 2735.03 | 136105.77 | 2735.03 | 9.162 | [5 empty] | 103.4037 |  |  | #VALUE!
04.03.2008 03:00 | 3600 | 2 | 761.16 | GGB | 764.469 | 771.633 | 767.033 | 261.62 | GGB | 10796.6 | GGB | 9.85 | GGB | 993.48 | GGB | 59.65 | GGB | 168286.76 | GGB | 135451.06 | GGB | 0 | 0 | 2826 | 3600 | 2810.89 | GGB | 100 | GGB | 37.94 | GGB | 37.94 | GGB | 161714.89 | GGB | 161716.73 | 2810.89 | 2790.1443 |  |  |  | 1 | 1 |  |  |  |  | 135451.06 | 2790.1443 | 135451.06 | 2790.1443 | 9.9612 | [5 empty] | 105.7606 | 2790.1443 |  | 104.98
04.03.2008 04:00 | 3600 | 2 | 760.98 | GGB | 764.469 | 770.672 | 767.766 | 262.35 | GGB | 10822.6 | GGB | 9.85 | GGB | 993.45 | GGB | 59.28 | GGB | 169093.3 | GGB | 136245.65 | GGB | 0 | 0 | 2855 | 3600 | 2839.27 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 161756 | GGB | 161757.84 | 2839.27 | 2773.872 |  |  |  | 1 | 1 |  |  |  |  | 136245.65 | 2773.872 | 136245.65 | 2773.872 | 9.1931 | [5 empty] | 107.4551 | 2773.872 |  | 104.98
04.03.2008 05:00 | 3600 | 2 | 761.03 | GGB | 763.37 | 770.813 | 766.667 | 262.39 | GGB | 10819.3 | GGB | 9.85 | GGB | 993.58 | GGB | 59.6 | GGB | 169253.95 | GGB | 136259.99 | GGB | 0 | 0 | 2849 | 3600 | 2833.07 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 161794.89 | GGB | 161796.73 | 2833.07 | 2773.5801 |  |  |  | 0 | 1 | [14 empty] | 107.2317 | 2773.5801 |  | 104.98
04.03.2008 06:00 | 3600 | 2 | 760.66 | GGB | 763.37 | 770.695 | 766.667 | 263.03 | GGB | 10841 | GGB | 9.85 | GGB | 993.8 | GGB | 59.34 | GGB | 170249.76 | GGB | 137201.78 | GGB | 0 | 0 | 2873 | 3600 | 2856.96 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 161834.19 | GGB | 161836.02 | 2856.96 | 2754.5415 |  |  |  | 0 | 1 | [14 empty] | 108.8833 | 2754.5415 |  | 104.98
04.03.2008 07:00 | 3600 | 2 | 761.24 | GGB | 762.271 | 769.711 | 765.201 | 263.31 | GGB | 10849.1 | GGB | 9.86 | GGB | 993.86 | GGB | 59.04 | GGB | 170960.58 | GGB | 137904.47 | GGB | 0 | 0 | 2844 | 3600 | 2828.05 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 161875.48 | GGB | 161877.32 | 2828.05 | 2740.5058 |  |  |  | 0 | 1 | [14 empty] | 108.3335 | 2740.5058 |  | 104.98
04.03.2008 08:00 | 3600 | 2 | 761.1 | GGB | 763.37 | 770.789 | 767.033 | 262.78 | GGB | 10865.9 | GGB | 9.86 | GGB | 994.55 | GGB | 59.1 | GGB | 170373 | GGB | 137504.44 | GGB | 0 | 0 | 2863 | 3600 | 2847.82 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 161913.58 | GGB | 161915.42 | 2847.82 | 2748.4785 |  |  |  | 0 | 1 | [14 empty] | 108.7744 | 2748.4785 |  | 104.98
04.03.2008 09:00 | 3600 | 2 | 760.84 | GGB | 764.469 | 771.938 | 767.033 | 262.54 | GGB | 10860.2 | GGB | 9.86 | GGB | 995.36 | GGB | 59.16 | GGB | 169975.77 | GGB | 137270.83 | GGB | 0 | 0 | 2871 | 3600 | 2855.51 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 161954.44 | GGB | 161956.28 | 2855.51 | 2753.1559 |  |  |  | 1 | 1 |  |  |  |  | 137270.83 | 2753.1559 | 137270.83 | 2753.1559 | 9.2493 | [5 empty] | 108.8828 | 2753.1559 |  | 104.98
04.03.2008 10:00 | 3600 | 2 | 761.13 | GGB | 763.37 | 770.227 | 765.934 | 263.48 | GGB | 10827.4 | GGB | 9.85 | GGB | 996.27 | GGB | 59.03 | GGB | 171005.69 | GGB | 138282.74 | GGB | 0 | 0 | 2846 | 3600 | 2830.06 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 161994.39 | GGB | 161996.23 | 2830.06 | 2733.0092 |  |  |  | 0 | 1 | [14 empty] | 108.7079 | 2733.0092 |  | 104.98
04.03.2008 11:00 | 3600 | 2 | 762.69 | GGB | 764.469 | 771.492 | 768.132 | 262.28 | GGB | 10846.2 | GGB | 9.87 | GGB | 996.77 | GGB | 59.17 | GGB | 169696.29 | GGB | 137232.07 | GGB | 0 | 0 | 2792 | 3600 | 2776.18 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 162032.68 | GGB | 162034.52 | 2776.18 | 2753.9335 |  |  |  | 1 | 1 |  |  |  |  | 137232.07 | 2753.9335 | 137232.07 | 2753.9335 | 9.8701 | [5 empty] | 105.828 | 2753.9335 |  | 104.98
04.03.2008 12:00 | 3600 | 2 | 761.82 | GGB | 764.469 | 771.586 | 768.498 | 260.36 | GGB | 10817.5 | GGB | 9.86 | GGB | 996.78 | GGB | 59.71 | GGB | 167607.85 | GGB | 135326.7 | GGB | 0 | 0 | 2770 | 3600 | 2754.21 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 162073.69 | GGB | 162075.53 | 2754.21 | 2754.21 |  |  |  | 1 | 1 |  |  |  |  | 135326.7 | 2754.21 | 135326.7 | 2754.21 | 9.0885 | [5 empty] | 103.5328 |  |  | #VALUE!
04.03.2008 13:00 | 3600 | 2 | 761.87 | GGB | 764.835 | 771.609 | 768.498 | 260 | GGB | 10807.3 | GGB | 9.86 | GGB | 997.42 | GGB | 59.58 | GGB | 167537.43 | GGB | 135408.8 | GGB | 0 | 0 | 2753 | 3600 | 2737.76 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 162113.03 | GGB | 162114.87 | 2737.76 | 2737.76 |  |  |  | 1 | 1 |  |  |  |  | 135408.8 | 2737.76 | 135408.8 | 2737.76 | 9.4234 | [5 empty] | 102.9769 |  |  | #VALUE!
04.03.2008 14:00 | 3600 | 2 | 762.16 | GGB | 764.835 | 771.75 | 768.498 | 259.57 | GGB | 10788.1 | GGB | 9.86 | GGB | 997.73 | GGB | 59.78 | GGB | 166872.82 | GGB | 134833.02 | GGB | 0 | 0 | 2730 | 3600 | 2714.82 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 162152.37 | GGB | 162154.21 | 2714.82 | 2714.82 |  |  |  | 1 | 1 |  |  |  |  | 134833.02 | 2714.82 | 134833.02 | 2714.82 | 9.3047 | [5 empty] | 101.6798 |  |  | #VALUE!
04.03.2008 15:00 | 3600 | 2 | 763.13 | GGB | 764.835 | 773.531 | 770.696 | 260.23 | GGB | 10760.9 | GGB | 9.85 | GGB | 998.34 | GGB | 60.5 | GGB | 166168.61 | GGB | 134057.14 | GGB | 0 | 0 | 2705 | 3600 | 2689.97 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 162192.92 | GGB | 162194.76 | 2689.97 | 2689.97 |  |  |  | 1 | 1 |  |  |  |  | 134057.14 | 2689.97 | 134057.14 | 2689.97 | 8.893 | [5 empty] | 100.1694 |  |  | #VALUE!
04.03.2008 16:00 | 3600 | 2 | 762.7 | GGB | 763.37 | 771.328 | 767.033 | 262.09 | GGB | 10735.2 | GGB | 9.84 | GGB | 998.78 | GGB | 60.55 | GGB | 167755.29 | GGB | 135376.74 | GGB | 0 | 0 | 2714 | 3600 | 2698.46 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 162231.26 | GGB | 162233.1 | 2698.46 | 2698.46 |  |  |  | 0 | 1 | [14 empty] | 101.4746 |  |  | #VALUE!
04.03.2008 17:00 | 3600 | 2 | 763.34 | GGB | 764.835 | 772.453 | 769.597 | 263.9 | GGB | 10763.2 | GGB | 9.85 | GGB | 999.34 | GGB | 60.06 | GGB | 169380.49 | GGB | 136963.33 | GGB | 0 | 0 | 2694 | 3600 | 2678.72 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 162271.39 | GGB | 162273.23 | 2678.72 | 2678.72 |  |  |  | 1 | 1 |  |  |  |  | 136963.33 | 2678.72 | 136963.33 | 2678.72 | 9.1424 | [5 empty] | 101.9129 |  |  | #VALUE!
04.03.2008 18:00 | 3600 | 2 | 762.87 | GGB | 763.37 | 771.352 | 767.766 | 262.99 | GGB | 10799.8 | GGB | 9.86 | GGB | 1000.1 | GGB | 60.57 | GGB | 167823.51 | GGB | 135601.99 | GGB | 0 | 0 | 2729 | 3600 | 2713.4 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 162310.39 | GGB | 162312.23 | 2713.4 | 2713.4 |  |  |  | 0 | 1 | [14 empty] | 102.2062 |  |  | #VALUE!
04.03.2008 19:00 | 3600 | 2 | 762.4 | GGB | 764.835 | 772.43 | 768.864 | 263.54 | GGB | 10821 | GGB | 9.86 | GGB | 1001.18 | GGB | 60.52 | GGB | 168402.29 | GGB | 136234.83 | GGB | 0 | 0 | 2762 | 3600 | 2746.14 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 162349.59 | GGB | 162351.43 | 2746.14 | 2746.14 |  |  |  | 1 | 1 |  |  |  |  | 136234.83 | 2746.14 | 136234.83 | 2746.14 | 9.5439 | [5 empty] | 103.9222 |  |  | #VALUE!
04.03.2008 20:00 | 3600 | 2 | 760.93 | GGB | 763.37 | 770.133 | 766.667 | 264.4 | GGB | 10860.8 | GGB | 9.85 | GGB | 1002.57 | GGB | 59.98 | GGB | 169913.06 | GGB | 137872.84 | GGB | 0 | 0 | 2834 | 3600 | 2818.52 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 162390.27 | GGB | 162392.11 | 2818.52 | 2741.1345 |  |  |  | 0 | 1 | [14 empty] | 107.9437 | 2741.1345 |  | 104.98
04.03.2008 21:00 | 3600 | 2 | 760.62 | GGB | 761.172 | 769.031 | 765.201 | 266.11 | GGB | 10862.8 | GGB | 9.84 | GGB | 1003.57 | GGB | 59.69 | GGB | 171104.72 | GGB | 139100.41 | GGB | 0 | 0 | 2865 | 3600 | 2849.04 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 162429.03 | GGB | 162430.88 | 2849.04 | 2716.9438 |  |  |  | 0 | 1 | [14 empty] | 110.0841 | 2716.9438 |  | 104.98
04.03.2008 22:00 | 3600 | 2 | 761.37 | GGB | 763.37 | 770.25 | 767.033 | 267.47 | GGB | 10904 | GGB | 9.86 | GGB | 1004.43 | GGB | 59.35 | GGB | 172236.97 | GGB | 140284.75 | GGB | 0 | 0 | 2854 | 3600 | 2838.42 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 162469.3 | GGB | 162471.14 | 2838.42 | 2694.0063 |  |  |  | 0 | 1 | [14 empty] | 110.6075 | 2694.0063 |  | 104.98
04.03.2008 23:00 | 3600 | 2 | 760.65 | GGB | 763.37 | 770.273 | 767.033 | 266.81 | GGB | 10917.1 | GGB | 9.85 | GGB | 1005.7 | GGB | 59.67 | GGB | 171352.3 | GGB | 139603.61 | GGB | 0 | 0 | 2890 | 3600 | 2874.28 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 162509.02 | GGB | 162510.86 | 2874.28 | 2707.1506 |  |  |  | 0 | 1 | [14 empty] | 111.4611 | 2707.1506 |  | 104.98
04.03.2008 24:00 | 3600 | 2 | 760.55 | GGB | 763.37 | 770.344 | 767.033 | 267.33 | GGB | 10939.1 | GGB | 9.85 | GGB | 1006.83 | GGB | 59.54 | GGB | 171900.27 | GGB | 140262.22 | GGB | 0 | 0 | 2910 | 3600 | 2894.04 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 162548.93 | GGB | 162550.77 | 2894.04 | 2694.439 |  |  |  | 0 | 1 | [14 empty] | 112.7568 | 2694.439 |  | 104.98
05.03.2008 01:00 | 3600 | 2 | 760.5 | GGB | 762.271 | 769.219 | 765.934 | 267.84 | GGB | 10948.2 | GGB | 9.85 | GGB | 1007.81 | GGB | 59.42 | GGB | 172429.53 | GGB | 140881.7 | GGB | 0 | 0 | 2926 | 3600 | 2910.12 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 162589.59 | GGB | 162591.43 | 2910.12 | 2682.5911 |  |  |  | 0 | 1 | [14 empty] | 113.8841 | 2682.5911 |  | 104.98
05.03.2008 02:00 | 3600 | 2 | 760.35 | GGB | 763.37 | 770.344 | 767.033 | 268.61 | GGB | 10967.8 | GGB | 9.85 | GGB | 1008.84 | GGB | 59.33 | GGB | 173047.92 | GGB | 141568.76 | GGB | 0 | 0 | 2945 | 3600 | 2929.17 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 162629.11 | GGB | 162630.95 | 2929.17 | 2669.572 |  |  |  | 0 | 1 | [14 empty] | 115.1886 | 2669.572 |  | 104.98
05.03.2008 03:00 | 3600 | 2 | 760.16 | GGB | 763.37 | 770.531 | 767.033 | 269.42 | GGB | 10974.4 | GGB | 9.85 | GGB | 1009.49 | GGB | 59.48 | GGB | 173444.04 | GGB | 141922.19 | GGB | 0 | 0 | 2965 | 3600 | 2949.09 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 162669.41 | GGB | 162671.25 | 2949.09 | 2662.924 |  |  |  | 0 | 1 | [14 empty] | 116.2615 | 2662.924 |  | 104.98
05.03.2008 04:00 | 3600 | 2 | 760.24 | GGB | 762.271 | 769.148 | 765.934 | 269.74 | GGB | 10986.1 | GGB | 9.85 | GGB | 1009.91 | GGB | 59.38 | GGB | 173701.52 | GGB | 142233.18 | GGB | 0 | 0 | 2975 | 3600 | 2959.23 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 162709.76 | GGB | 162711.6 | 2959.23 | 2657.1015 |  |  |  | 0 | 1 | [14 empty] | 116.9169 | 2657.1015 |  | 104.98
05.03.2008 05:00 | 3600 | 2 | 759.38 | GGB | 762.271 | 768.727 | 765.201 | 270.45 | GGB | 10992.4 | GGB | 9.84 | GGB | 1010.67 | GGB | 59.26 | GGB | 174675.32 | GGB | 143193.29 | GGB | 0 | 0 | 3024 | 3600 | 3007.87 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 162749.78 | GGB | 162751.62 | 3007.87 | 2639.2857 |  |  |  | 0 | 1 | [14 empty] | 119.6408 | 2639.2857 |  | 104.98
05.03.2008 06:00 | 3600 | 2 | 761.37 | GGB | 762.271 | 769.969 | 766.667 | 269.88 | GGB | 11021.7 | GGB | 9.88 | GGB | 1011.42 | GGB | 59.57 | GGB | 173799.45 | GGB | 142446.28 | GGB | 0 | 0 | 2943 | 3600 | 2926.91 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 162790.34 | GGB | 162792.18 | 2926.91 | 2653.1265 |  |  |  | 0 | 1 | [14 empty] | 115.8132 | 2653.1265 |  | 104.98
05.03.2008 07:00 | 3600 | 2 | 760.62 | GGB | 763.37 | 770.063 | 766.667 | 269.02 | GGB | 10984.6 | GGB | 9.85 | GGB | 1012.11 | GGB | 59.61 | GGB | 173409.93 | GGB | 142206.31 | GGB | 0 | 0 | 2955 | 3600 | 2939.83 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 162830.46 | GGB | 162832.3 | 2939.83 | 2657.6036 |  |  |  | 0 | 1 | [14 empty] | 116.1284 | 2657.6036 |  | 104.98
05.03.2008 08:00 | 3600 | 2 | 760.37 | GGB | 763.37 | 770.367 | 766.667 | 270.55 | GGB | 10960.1 | GGB | 9.84 | GGB | 1012.26 | GGB | 59.03 | GGB | 175278.3 | GGB | 144012.84 | GGB | 0 | 0 | 2957 | 3600 | 2941.53 | GGB | 100 | GGB | 41.02 | GGB | 41.02 | GGB | 162871.48 | GGB | 162873.32 | 2941.53 | 2624.266 |  |  |  | 0 | 1 | [14 empty] | 117.6717 | 2624.266 |  | 104.98
05.03.2008 09:00 | 3600 | 2 | 762.19 | GGB | 767.033 | 773.602 | 769.963 | 270.24 | GGB | 10975.6 | GGB | 9.87 | GGB | 1012.93 | GGB | 59.08 | GGB | 174887.68 | GGB | 143762.83 | GGB | 0 | 0 | 2866 | 3600 | 2850.89 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 162911.39 | GGB | 162913.23 | 2850.89 | 2628.8297 |  |  |  | 1 | 1 |  |  |  |  | 143762.83 | 2628.8297 | 143762.83 | 2628.8297 | 9.4695 | [5 empty] | 113.8478 | 2628.8297 |  | 104.98
05.03.2008 10:00 | 3600 | 2 | 763.98 | GGB | 767.033 | 774.328 | 770.33 | 266.53 | GGB | 10950.3 | GGB | 9.88 | GGB | 1013.78 | GGB | 60.31 | GGB | 170333.38 | GGB | 139621.73 | GGB | 0 | 0 | 2789 | 3600 | 2773.55 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 162951.14 | GGB | 162952.99 | 2773.55 | 2706.7993 |  |  |  | 1 | 1 |  |  |  |  | 139621.73 | 2706.7993 | 139621.73 | 2706.7993 | 9.5052 | [5 empty] | 107.5688 | 2706.7993 |  | 104.98
05.03.2008 11:00 | 3600 | 2 | 764.37 | GGB | 765.934 | 773.227 | 770.33 | 264.35 | GGB | 10878.4 | GGB | 9.86 | GGB | 1013.71 | GGB | 61.05 | GGB | 168008.37 | GGB | 137402.12 | GGB | 0 | 0 | 2732 | 3600 | 2716.76 | GGB | 100 | GGB | 41.14 | GGB | 41.14 | GGB | 162992.28 | GGB | 162994.13 | 2716.76 | 2716.76 |  |  |  | 1 | 1 |  |  |  |  | 137402.12 | 2716.76 | 137402.12 | 2716.76 | 9.0736 | [5 empty] | 103.6913 |  |  | #VALUE!
05.03.2008 12:00 | 3600 | 2 | 764.24 | GGB | 765.934 | 773.086 | 769.963 | 264.75 | GGB | 10843 | GGB | 9.85 | GGB | 1013.46 | GGB | 60.92 | GGB | 168965.66 | GGB | 138201.51 | GGB | 0 | 0 | 2724 | 3600 | 2708.96 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 163031.79 | GGB | 163033.64 | 2708.96 | 2708.96 |  |  |  | 1 | 1 |  |  |  |  | 138201.51 | 2708.96 | 138201.51 | 2708.96 | 9.4756 | [5 empty] | 103.9951 |  |  | #VALUE!
05.03.2008 13:00 | 3600 | 2 | 765.55 | GGB | 767.033 | 775.359 | 771.429 | 264.77 | GGB | 10830.8 | GGB | 9.86 | GGB | 1012.75 | GGB | 60.62 | GGB | 169187.93 | GGB | 138410.33 | GGB | 0 | 0 | 2644 | 3600 | 2628.6 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 163071.75 | GGB | 163073.6 | 2628.6 | 2628.6 |  |  |  | 1 | 1 |  |  |  |  | 138410.33 | 2628.6 | 138410.33 | 2628.6 | 9.1047 | [5 empty] | 101.0626 |  |  | #VALUE!
05.03.2008 14:00 | 3600 | 2 | 765.67 | GGB | 768.132 | 775.383 | 771.429 | 263.29 | GGB | 10833.8 | GGB | 9.86 | GGB | 1012.27 | GGB | 61.64 | GGB | 166917.94 | GGB | 136074.28 | GGB | 0 | 0 | 2637 | 3600 | 2621.55 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 163111.48 | GGB | 163113.33 | 2621.55 | 2621.55 |  |  |  | 1 | 1 |  |  |  |  | 136074.28 | 2621.55 | 136074.28 | 2621.55 | 8.9787 | [5 empty] | 99.0904 |  |  | #VALUE!
05.03.2008 15:00 | 3600 | 2 | 765.47 | GGB | 768.498 | 776.484 | 772.527 | 264.12 | GGB | 10791.4 | GGB | 9.85 | GGB | 1011.99 | GGB | 61.14 | GGB | 168075.49 | GGB | 137183.55 | GGB | 0 | 0 | 2630 | 3600 | 2614.94 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 163151.1 | GGB | 163152.95 | 2614.94 | 2614.94 |  |  |  | 1 | 1 |  |  |  |  | 137183.55 | 2614.94 | 137183.55 | 2614.94 | 9.0542 | [5 empty] | 99.6463 |  |  | #VALUE!
05.03.2008 16:00 | 3600 | 2 | 766.08 | GGB | 764.835 | 773.25 | 768.864 | 264.04 | GGB | 10779.1 | GGB | 9.85 | GGB | 1011.52 | GGB | 61.14 | GGB | 168466.11 | GGB | 137438.61 | GGB | 0 | 0 | 2597 | 3600 | 2581.45 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 163191.24 | GGB | 163193.09 | 2581.45 | 2581.45 |  |  |  | 1 | 1 |  |  |  |  | 137438.61 | 2581.45 | 137438.61 | 2581.45 | 8.8388 | [5 empty] | 98.553 |  |  | #VALUE!
05.03.2008 17:00 | 3600 | 2 | 764.25 | GGB | 764.835 | 772.359 | 768.864 | 265.64 | GGB | 10850.2 | GGB | 9.85 | GGB | 1012.03 | GGB | 60.73 | GGB | 169421.2 | GGB | 138456.43 | GGB | 0 | 0 | 2705 | 3600 | 2689.82 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 163230.41 | GGB | 163232.26 | 2689.82 | 2689.82 |  |  |  | 1 | 1 |  |  |  |  | 138456.43 | 2689.82 | 138456.43 | 2689.82 | 9.5079 | [5 empty] | 103.4508 |  |  | #VALUE!
05.03.2008 18:00 | 3600 | 2 | 763.57 | GGB | 764.835 | 772.359 | 768.864 | 265.7 | GGB | 10876.5 | GGB | 9.85 | GGB | 1012.35 | GGB | 61.41 | GGB | 168910.65 | GGB | 137805.03 | GGB | 0 | 0 | 2770 | 3600 | 2754.07 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 163270.65 | GGB | 163272.51 | 2754.07 | 2742.4833 |  |  |  | 1 | 1 |  |  |  |  | 137805.03 | 2742.4833 | 137805.03 | 2742.4833 | 9.3895 | [5 empty] | 105.4235 | 2742.4833 |  | 104.98
05.03.2008 19:00 | 3600 | 2 | 763.73 | GGB | 765.934 | 772.289 | 768.864 | 265.73 | GGB | 10876.2 | GGB | 9.85 | GGB | 1012.43 | GGB | 61.01 | GGB | 169042.69 | GGB | 138085.46 | GGB | 0 | 0 | 2757 | 3600 | 2741.28 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 163310.96 | GGB | 163312.82 | 2741.28 | 2736.9138 |  |  |  | 1 | 1 |  |  |  |  | 138085.46 | 2736.9138 | 138085.46 | 2736.9138 | 9.3755 | [5 empty] | 105.1475 | 2736.9138 |  | 104.98
05.03.2008 20:00 | 3600 | 2 | 763.31 | GGB | 764.835 | 772.43 | 768.864 | 267.33 | GGB | 10885.3 | GGB | 9.85 | GGB | 1012.83 | GGB | 60.86 | GGB | 170378.5 | GGB | 139297.4 | GGB | 0 | 0 | 2779 | 3600 | 2763.88 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 163350.38 | GGB | 163352.24 | 2763.88 | 2713.1016 |  |  |  | 1 | 1 |  |  |  |  | 139297.4 | 2713.1016 | 139297.4 | 2713.1016 | 9.5872 | [5 empty] | 106.9448 | 2713.1016 |  | 104.98
05.03.2008 21:00 | 3600 | 2 | 762.9 | GGB | 764.469 | 771.352 | 767.766 | 266.82 | GGB | 10904.8 | GGB | 9.85 | GGB | 1012.64 | GGB | 60.66 | GGB | 169998.88 | GGB | 139042.43 | GGB | 0 | 0 | 2801 | 3600 | 2785.87 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 163389.73 | GGB | 163391.59 | 2785.87 | 2718.0768 |  |  |  | 1 | 1 |  |  |  |  | 139042.43 | 2718.0768 | 139042.43 | 2718.0768 | 9.6043 | [5 empty] | 107.5984 | 2718.0768 |  | 104.98
05.03.2008 22:00 | 3600 | 2 | 763.48 | GGB | 767.033 | 773.531 | 770.33 | 266.64 | GGB | 10947 | GGB | 9.87 | GGB | 1012.6 | GGB | 60.59 | GGB | 170650.28 | GGB | 139599.34 | GGB | 0 | 0 | 2796 | 3600 | 2780.65 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 163430.06 | GGB | 163431.92 | 2780.65 | 2707.2334 |  |  |  | 1 | 1 |  |  |  |  | 139599.34 | 2707.2334 | 139599.34 | 2707.2334 | 9.3709 | [5 empty] | 107.8269 | 2707.2334 |  | 104.98
05.03.2008 23:00 | 3600 | 2 | 762.13 | GGB | 765.934 | 773.297 | 768.864 | 267.5 | GGB | 10918.6 | GGB | 9.84 | GGB | 1013 | GGB | 60.61 | GGB | 170746.01 | GGB | 139723.5 | GGB | 0 | 0 | 2846 | 3600 | 2830.93 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 163470.5 | GGB | 163472.36 | 2830.93 | 2704.8277 |  |  |  | 1 | 1 |  |  |  |  | 139723.5 | 2704.8277 | 139723.5 | 2704.8277 | 9.3454 | [5 empty] | 109.8743 | 2704.8277 |  | 104.98
05.03.2008 24:00 | 3600 | 2 | 762.53 | GGB | 763.37 | 770.063 | 766.667 | 267.6 | GGB | 10930.5 | GGB | 9.85 | GGB | 1012.95 | GGB | 60.6 | GGB | 170992.49 | GGB | 139925.65 | GGB | 0 | 0 | 2843 | 3600 | 2827.26 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 163510.28 | GGB | 163512.14 | 2827.26 | 2700.9201 |  |  |  | 0 | 1 | [14 empty] | 109.8906 | 2700.9201 |  | 104.98
06.03.2008 01:00 | 3600 | 2 | 762.22 | GGB | 765.934 | 772.242 | 768.864 | 268.58 | GGB | 10928.5 | GGB | 9.85 | GGB | 1013.06 | GGB | 60 | GGB | 172490.05 | GGB | 141419.8 | GGB | 0 | 0 | 2850 | 3600 | 2834.15 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 163550.93 | GGB | 163552.79 | 2834.15 | 2672.3839 |  |  |  | 1 | 1 |  |  |  |  | 141419.8 | 2672.3839 | 141419.8 | 2672.3839 | 9.2971 | [5 empty] | 111.3347 | 2672.3839 |  | 104.98
06.03.2008 02:00 | 3600 | 2 | 763.22 | GGB | 765.934 | 773.367 | 769.963 | 268.6 | GGB | 10930.6 | GGB | 9.86 | GGB | 1012.93 | GGB | 59.93 | GGB | 172678.2 | GGB | 141584.28 | GGB | 0 | 0 | 2817 | 3600 | 2801.65 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 163590.29 | GGB | 163592.15 | 2801.65 | 2669.2794 |  |  |  | 1 | 1 |  |  |  |  | 141584.28 | 2669.2794 | 141584.28 | 2669.2794 | 9.6018 | [5 empty] | 110.186 | 2669.2794 |  | 104.98
06.03.2008 03:00 | 3600 | 2 | 762.41 | GGB | 763.37 | 771.164 | 767.766 | 267.16 | GGB | 10943.3 | GGB | 9.86 | GGB | 1012.62 | GGB | 60.33 | GGB | 171013.39 | GGB | 140010.99 | GGB | 0 | 0 | 2844 | 3600 | 2828.1 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 163630.24 | GGB | 163632.1 | 2828.1 | 2699.2738 |  |  |  | 0 | 1 | [14 empty] | 109.9903 | 2699.2738 |  | 104.98
06.03.2008 04:00 | 3600 | 2 | 762.1 | GGB | 764.835 | 771.984 | 767.766 | 267.29 | GGB | 10948.9 | GGB | 9.86 | GGB | 1012.31 | GGB | 60.3 | GGB | 171138.83 | GGB | 140080.66 | GGB | 0 | 0 | 2864 | 3600 | 2848.1 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 163671.53 | GGB | 163673.39 | 2848.1 | 2697.9313 |  |  |  | 1 | 1 |  |  |  |  | 140080.66 | 2697.9313 | 140080.66 | 2697.9313 | 9.153 | [5 empty] | 110.8233 | 2697.9313 |  | 104.98
06.03.2008 05:00 | 3600 | 2 | 762.39 | GGB | 765.934 | 773.133 | 768.864 | 267.27 | GGB | 10940.6 | GGB | 9.86 | GGB | 1011.73 | GGB | 60.46 | GGB | 171171.84 | GGB | 139963.29 | GGB | 0 | 0 | 2857 | 3600 | 2841.74 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 163710.81 | GGB | 163712.67 | 2841.74 | 2700.1937 |  |  |  | 1 | 1 |  |  |  |  | 139963.29 | 2700.1937 | 139963.29 | 2700.1937 | 9.6214 | [5 empty] | 110.4831 | 2700.1937 |  | 104.98
06.03.2008 06:00 | 3600 | 2 | 763.08 | GGB | 764.835 | 771.961 | 768.864 | 266.23 | GGB | 10928.8 | GGB | 9.86 | GGB | 1011.15 | GGB | 60.46 | GGB | 170167.23 | GGB | 139060.53 | GGB | 0 | 0 | 2828 | 3600 | 2812.34 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 163751.29 | GGB | 163753.16 | 2812.34 | 2717.723 |  |  |  | 1 | 1 |  |  |  |  | 139060.53 | 2717.723 | 139060.53 | 2717.723 | 9.3339 | [5 empty] | 108.6349 | 2717.723 |  | 104.98
06.03.2008 07:00 | 3600 | 2 | 763.49 | GGB | 765.934 | 772.922 | 769.963 | 265.15 | GGB | 10900.9 | GGB | 9.86 | GGB | 1010.13 | GGB | 60.65 | GGB | 169139.52 | GGB | 138000.81 | GGB | 0 | 0 | 2791 | 3600 | 2775.69 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 163791.33 | GGB | 163793.19 | 2775.69 | 2738.5926 |  |  |  | 1 | 1 |  |  |  |  | 138000.81 | 2738.5926 | 138000.81 | 2738.5926 | 9.4411 | [5 empty] | 106.4021 | 2738.5926 |  | 104.98
06.03.2008 08:00 | 3600 | 2 | 763.43 | GGB | 765.934 | 772.734 | 768.864 | 264.79 | GGB | 10877.2 | GGB | 9.86 | GGB | 1009.8 | GGB | 60.94 | GGB | 168592.65 | GGB | 137391.34 | GGB | 0 | 0 | 2795 | 3600 | 2779.61 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 163831.57 | GGB | 163833.44 | 2779.61 | 2750.7411 |  |  |  | 1 | 1 |  |  |  |  | 137391.34 | 2750.7411 | 137391.34 | 2750.7411 | 9.3895 | [5 empty] | 106.0818 | 2750.7411 |  | 104.98
06.03.2008 09:00 | 3600 | 2 | 763.36 | GGB | 764.835 | 772.43 | 768.864 | 265.48 | GGB | 10854.9 | GGB | 9.85 | GGB | 1009.12 | GGB | 60.72 | GGB | 169468.52 | GGB | 138100.69 | GGB | 0 | 0 | 2778 | 3600 | 2762.44 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 163871.4 | GGB | 163873.27 | 2762.44 | 2736.612 |  |  |  | 1 | 1 |  |  |  |  | 138100.69 | 2736.612 | 138100.69 | 2736.612 | 9.4885 | [5 empty] | 105.9708 | 2736.612 |  | 104.98
06.03.2008 10:00 | 3600 | 2 | 764.28 | GGB | 765.934 | 773.391 | 769.597 | 264.26 | GGB | 10862.5 | GGB | 9.87 | GGB | 1007.63 | GGB | 60.68 | GGB | 168351.68 | GGB | 137006.11 | GGB | 0 | 0 | 2730 | 3600 | 2714.95 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 163911.16 | GGB | 163913.03 | 2714.95 | 2714.95 |  |  |  | 1 | 1 |  |  |  |  | 137006.11 | 2714.95 | 137006.11 | 2714.95 | 9.3552 | [5 empty] | 103.3235 |  |  | #VALUE!
06.03.2008 11:00 | 3600 | 2 | 763.9 | GGB | 765.934 | 772.336 | 769.597 | 263.41 | GGB | 10838.3 | GGB | 9.86 | GGB | 1006.3 | GGB | 60.84 | GGB | 167465.9 | GGB | 136042.77 | GGB | 0 | 0 | 2729 | 3600 | 2714.05 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 163950.83 | GGB | 163952.71 | 2714.05 | 2714.05 |  |  |  | 1 | 1 |  |  |  |  | 136042.77 | 2714.05 | 136042.77 | 2714.05 | 9.3051 | [5 empty] | 102.563 |  |  | #VALUE!
06.03.2008 12:00 | 3600 | 2 | 763.15 | GGB | 764.835 | 772.594 | 769.597 | 263.8 | GGB | 10844.9 | GGB | 9.85 | GGB | 1005.11 | GGB | 60.72 | GGB | 168252.65 | GGB | 136568.91 | GGB | 0 | 0 | 2769 | 3600 | 2753.28 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 163991.02 | GGB | 163992.89 | 2753.28 | 2753.28 |  |  |  | 1 | 1 |  |  |  |  | 136568.91 | 2753.28 | 136568.91 | 2753.28 | 9.3582 | [5 empty] | 104.4479 |  |  | #VALUE!
06.03.2008 13:00 | 3600 | 2 | 763.31 | GGB | 765.934 | 773.625 | 769.597 | 263.52 | GGB | 10851.5 | GGB | 9.86 | GGB | 1004.19 | GGB | 60.52 | GGB | 167995.17 | GGB | 136316.74 | GGB | 0 | 0 | 2772 | 3600 | 2756.23 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 164031.01 | GGB | 164032.88 | 2756.23 | 2756.23 |  |  |  | 1 | 1 |  |  |  |  | 136316.74 | 2756.23 | 136316.74 | 2756.23 | 9.3954 | [5 empty] | 104.3667 |  |  | #VALUE!
06.03.2008 14:00 | 3600 | 2 | 763.02 | GGB | 765.934 | 772.453 | 769.597 | 263.18 | GGB | 10847.8 | GGB | 9.86 | GGB | 1003.36 | GGB | 60.2 | GGB | 168072.19 | GGB | 136396.54 | GGB | 0 | 0 | 2779 | 3600 | 2763.74 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 164070.69 | GGB | 164072.56 | 2763.74 | 2763.74 |  |  |  | 1 | 1 |  |  |  |  | 136396.54 | 2763.74 | 136396.54 | 2763.74 | 9.5001 | [5 empty] | 104.7124 |  |  | #VALUE!
06.03.2008 15:00 | 3600 | 2 | 763.31 | GGB | 765.934 | 772.5 | 769.597 | 262.63 | GGB | 10840.8 | GGB | 9.86 | GGB | 1002.99 | GGB | 60.13 | GGB | 167472.51 | GGB | 135889.31 | GGB | 0 | 0 | 2762 | 3600 | 2746.6 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 164110.78 | GGB | 164112.65 | 2746.6 | 2746.6 |  |  |  | 1 | 1 |  |  |  |  | 135889.31 | 2746.6 | 135889.31 | 2746.6 | 9.3099 | [5 empty] | 103.676 |  |  | #VALUE!
06.03.2008 16:00 | 3600 | 2 | 763.23 | GGB | 765.934 | 772.453 | 769.597 | 262.37 | GGB | 10826 | GGB | 9.85 | GGB | 1002.34 | GGB | 60.13 | GGB | 167158.91 | GGB | 135544.21 | GGB | 0 | 0 | 2760 | 3600 | 2744.61 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 164150.49 | GGB | 164152.37 | 2744.61 | 2744.61 |  |  |  | 1 | 1 |  |  |  |  | 135544.21 | 2744.61 | 135544.21 | 2744.61 | 9.366 | [5 empty] | 103.3378 |  |  | #VALUE!
06.03.2008 17:00 | 3600 | 2 | 763.46 | GGB | 765.934 | 773.531 | 770.696 | 262.34 | GGB | 10822.9 | GGB | 9.86 | GGB | 1001.98 | GGB | 60.05 | GGB | 167036.77 | GGB | 135428.97 | GGB | 0 | 0 | 2758 | 3600 | 2742.14 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 164190.33 | GGB | 164192.21 | 2742.14 | 2742.14 |  |  |  | 1 | 1 |  |  |  |  | 135428.97 | 2742.14 | 135428.97 | 2742.14 | 9.3214 | [5 empty] | 103.157 |  |  | #VALUE!
06.03.2008 18:00 | 3600 | 2 | 763.46 | GGB | 765.934 | 773.391 | 769.597 | 262.29 | GGB | 10803.6 | GGB | 9.85 | GGB | 1001.69 | GGB | 60.47 | GGB | 166671.46 | GGB | 134924.27 | GGB | 0 | 0 | 2743 | 3600 | 2727.43 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 164230.17 | GGB | 164232.04 | 2727.43 | 2727.43 |  |  |  | 1 | 1 |  |  |  |  | 134924.27 | 2727.43 | 134924.27 | 2727.43 | 9.2392 | [5 empty] | 102.2213 |  |  | #VALUE!
06.03.2008 19:00 | 3600 | 2 | 763.91 | GGB | 765.934 | 773.297 | 769.597 | 261.76 | GGB | 10792.5 | GGB | 9.86 | GGB | 1001.95 | GGB | 60.55 | GGB | 166090.48 | GGB | 134458.9 | GGB | 0 | 0 | 2720 | 3600 | 2704.53 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 164269.58 | GGB | 164271.46 | 2704.53 | 2704.53 |  |  |  | 1 | 1 |  |  |  |  | 134458.9 | 2704.53 | 134458.9 | 2704.53 | 9.225 | [5 empty] | 101.0134 |  |  | #VALUE!
06.03.2008 20:00 | 3600 | 2 | 763.49 | GGB | 764.835 | 772.008 | 768.498 | 261.21 | GGB | 10808.1 | GGB | 9.85 | GGB | 1002.19 | GGB | 60.33 | GGB | 166408.48 | GGB | 134834.22 | GGB | 0 | 0 | 2734 | 3600 | 2718.57 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 164309.36 | GGB | 164311.24 | 2718.57 | 2718.57 |  |  |  | 1 | 1 |  |  |  |  | 134834.22 | 2718.57 | 134834.22 | 2718.57 | 9.2146 | [5 empty] | 101.8212 |  |  | #VALUE!
06.03.2008 21:00 | 3600 | 2 | 763.7 | GGB | 765.934 | 773.156 | 769.597 | 260.58 | GGB | 10816.7 | GGB | 9.86 | GGB | 1002.31 | GGB | 60.1 | GGB | 166440.39 | GGB | 134969.26 | GGB | 0 | 0 | 2728 | 3600 | 2712.12 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 164349.78 | GGB | 164351.66 | 2712.12 | 2712.12 |  |  |  | 1 | 1 |  |  |  |  | 134969.26 | 2712.12 | 134969.26 | 2712.12 | 9.0562 | [5 empty] | 101.6813 |  |  | #VALUE!
06.03.2008 22:00 | 3600 | 2 | 763.57 | GGB | 765.934 | 773.156 | 769.597 | 260.18 | GGB | 10805.3 | GGB | 9.85 | GGB | 1002.38 | GGB | 60.03 | GGB | 166239.03 | GGB | 134843.43 | GGB | 0 | 0 | 2725 | 3600 | 2709.72 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 164389.44 | GGB | 164391.33 | 2709.72 | 2709.72 |  |  |  | 1 | 1 |  |  |  |  | 134843.43 | 2709.72 | 134843.43 | 2709.72 | 9.2107 | [5 empty] | 101.4966 |  |  | #VALUE!
06.03.2008 23:00 | 3600 | 2 | 763.05 | GGB | 765.934 | 773.039 | 769.597 | 259.46 | GGB | 10813.7 | GGB | 9.86 | GGB | 1002.31 | GGB | 59.66 | GGB | 166494.31 | GGB | 135191.94 | GGB | 0 | 0 | 2735 | 3600 | 2719.62 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 164428.71 | GGB | 164430.6 | 2719.62 | 2719.62 |  |  |  | 1 | 1 |  |  |  |  | 135191.94 | 2719.62 | 135191.94 | 2719.62 | 9.3626 | [5 empty] | 102.1308 |  |  | #VALUE!
06.03.2008 24:00 | 3600 | 2 | 763.62 | GGB | 764.835 | 772.898 | 769.597 | 259.91 | GGB | 10802.2 | GGB | 9.85 | GGB | 1002.51 | GGB | 60.05 | GGB | 166045.37 | GGB | 134697.76 | GGB | 0 | 0 | 2724 | 3600 | 2709.08 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 164466.89 | GGB | 164468.79 | 2709.08 | 2709.08 |  |  |  | 1 | 1 |  |  |  |  | 134697.76 | 2709.08 | 134697.76 | 2709.08 | 9.555 | [5 empty] | 101.3631 |  |  | #VALUE!
07.03.2008 01:00 | 3600 | 2 | 763.85 | GGB | 765.934 | 774 | 770.696 | 259.46 | GGB | 10792.2 | GGB | 9.86 | GGB | 1002.56 | GGB | 60.38 | GGB | 165506.2 | GGB | 134134.85 | GGB | 0 | 0 | 2712 | 3600 | 2696.59 | GGB | 100 | GGB | 41.49 | GGB | 41.49 | GGB | 164508.38 | GGB | 164510.28 | 2696.59 | 2696.59 |  |  |  | 1 | 1 |  |  |  |  | 134134.85 | 2696.59 | 134134.85 | 2696.59 | 8.7179 | [5 empty] | 100.4741 |  |  | #VALUE!
07.03.2008 02:00 | 3600 | 2 | 764.14 | GGB | 765.934 | 774.047 | 769.597 | 259.02 | GGB | 10778.2 | GGB | 9.86 | GGB | 1002.28 | GGB | 60.49 | GGB | 165128.79 | GGB | 133747.38 | GGB | 0 | 0 | 2695 | 3600 | 2679.69 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 164547.8 | GGB | 164549.7 | 2679.69 | 2679.69 |  |  |  | 1 | 1 |  |  |  |  | 133747.38 | 2679.69 | 133747.38 | 2679.69 | 9.0919 | [5 empty] | 99.556 |  |  | #VALUE!
07.03.2008 03:00 | 3600 | 2 | 764.28 | GGB | 767.033 | 774.047 | 770.696 | 259.31 | GGB | 10763.7 | GGB | 9.86 | GGB | 1002.33 | GGB | 60.35 | GGB | 165188.2 | GGB | 133859.49 | GGB | 0 | 0 | 2674 | 3600 | 2659 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 164587.15 | GGB | 164589.05 | 2659 | 2659 |  |  |  | 1 | 1 |  |  |  |  | 133859.49 | 2659 | 133859.49 | 2659 | 9.0453 | [5 empty] | 98.8701 |  |  | #VALUE!
07.03.2008 04:00 | 3600 | 2 | 764.37 | GGB | 765.934 | 774.047 | 770.696 | 258.71 | GGB | 10761.6 | GGB | 9.85 | GGB | 1001.91 | GGB | 60.53 | GGB | 164390.46 | GGB | 133083.97 | GGB | 0 | 0 | 2677 | 3600 | 2661.25 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 164627.12 | GGB | 164629.02 | 2661.25 | 2661.25 |  |  |  | 1 | 1 |  |  |  |  | 133083.97 | 2661.25 | 133083.97 | 2661.25 | 8.8609 | [5 empty] | 98.3805 |  |  | #VALUE!
07.03.2008 05:00 | 3600 | 2 | 764.32 | GGB | 765.934 | 774.094 | 770.696 | 258.64 | GGB | 10760.5 | GGB | 9.85 | GGB | 1001.99 | GGB | 60.57 | GGB | 164447.68 | GGB | 133124.86 | GGB | 0 | 0 | 2676 | 3600 | 2660.73 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 164666.99 | GGB | 164668.89 | 2660.73 | 2660.73 |  |  |  | 1 | 1 |  |  |  |  | 133124.86 | 2660.73 | 133124.86 | 2660.73 | 8.8841 | [5 empty] | 98.3915 |  |  | #VALUE!
07.03.2008 06:00 | 3600 | 2 | 764.35 | GGB | 765.934 | 774.094 | 769.597 | 258.65 | GGB | 10760.7 | GGB | 9.85 | GGB | 1002.38 | GGB | 60.63 | GGB | 164391.56 | GGB | 133105.12 | GGB | 0 | 0 | 2674 | 3600 | 2658.19 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 164706.74 | GGB | 164708.64 | 2658.19 | 2658.19 |  |  |  | 1 | 1 |  |  |  |  | 133105.12 | 2658.19 | 133105.12 | 2658.19 | 8.9011 | [5 empty] | 98.283 |  |  | #VALUE!
07.03.2008 07:00 | 3600 | 2 | 764.54 | GGB | 765.934 | 774.07 | 770.696 | 258.78 | GGB | 10764.4 | GGB | 9.86 | GGB | 1003.15 | GGB | 60.75 | GGB | 164344.25 | GGB | 133123.09 | GGB | 0 | 0 | 2668 | 3600 | 2652.33 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 164746.15 | GGB | 164748.05 | 2652.33 | 2652.33 |  |  |  | 1 | 1 |  |  |  |  | 133123.09 | 2652.33 | 133123.09 | 2652.33 | 8.9593 | [5 empty] | 98.0795 |  |  | #VALUE!
07.03.2008 08:00 | 3600 | 2 | 764.3 | GGB | 765.934 | 774.164 | 769.597 | 259.24 | GGB | 10764.7 | GGB | 9.85 | GGB | 1004.19 | GGB | 60.87 | GGB | 164683.15 | GGB | 133488 | GGB | 0 | 0 | 2688 | 3208 | 2672.2 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 164785.65 | GGB | 164787.55 | 2672.2 | 2672.2 |  |  |  | 1 | 1 |  |  |  |  | 133488 | 2672.2 | 133488 | 2672.2 | 9.0305 | [5 empty] | 99.0852 |  |  | #VALUE!
07.03.2008 09:00 | 3600 | 2 | 764.6 | GGB | 767.033 | 774.188 | 770.696 | 259.77 | GGB | 10767.6 | GGB | 9.85 | GGB | 1004.95 | GGB | 60.91 | GGB | 165230.02 | GGB | 134014.8 | GGB | 0 | 0 | 2672 | 3600 | 2656.12 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 164825.62 | GGB | 164827.52 | 2656.12 | 2656.12 |  |  |  | 1 | 1 |  |  |  |  | 134014.8 | 2656.12 | 134014.8 | 2656.12 | 8.9057 | [5 empty] | 98.8776 |  |  | #VALUE!
07.03.2008 10:00 | 3600 | 2 | 765.33 | GGB | 768.132 | 776.18 | 772.161 | 260.09 | GGB | 10755.8 | GGB | 9.86 | GGB | 1005.52 | GGB | 60.66 | GGB | 165666.85 | GGB | 134548.01 | GGB | 0 | 0 | 2624 | 3600 | 2608.88 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 164865.4 | GGB | 164867.29 | 2608.88 | 2608.88 |  |  |  | 1 | 1 |  |  |  |  | 134548.01 | 2608.88 | 134548.01 | 2608.88 | 8.8262 | [5 empty] | 97.5054 |  |  | #VALUE!
07.03.2008 11:00 | 3600 | 2 | 765.09 | GGB | 767.033 | 775.289 | 771.795 | 258.38 | GGB | 10760.7 | GGB | 9.86 | GGB | 1005.16 | GGB | 61.1 | GGB | 163929.42 | GGB | 132913.97 | GGB | 0 | 0 | 2643 | 3600 | 2627.47 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 164904.67 | GGB | 164906.57 | 2627.47 | 2627.47 |  |  |  | 1 | 1 |  |  |  |  | 132913.97 | 2627.47 | 132913.97 | 2627.47 | 8.8907 | [5 empty] | 97.0076 |  |  | #VALUE!
07.03.2008 12:00 | 3600 | 2 | 765.33 | GGB | 767.033 | 775.125 | 771.795 | 257.67 | GGB | 10745.2 | GGB | 9.86 | GGB | 1005.64 | GGB | 61.42 | GGB | 163264.81 | GGB | 132309.42 | GGB | 0 | 0 | 2618 | 3600 | 2602.82 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 164944.25 | GGB | 164946.15 | 2602.82 | 2602.82 |  |  |  | 1 | 1 |  |  |  |  | 132309.42 | 2602.82 | 132309.42 | 2602.82 | 8.7008 | [5 empty] | 95.6604 |  |  | #VALUE!
07.03.2008 13:00 | 3600 | 2 | 766.14 | GGB | 768.132 | 776.039 | 772.161 | 257.03 | GGB | 10727.3 | GGB | 9.86 | GGB | 1005.97 | GGB | 61.69 | GGB | 162794.97 | GGB | 131867.08 | GGB | 0 | 0 | 2582 | 3600 | 2566.97 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 164983.91 | GGB | 164985.81 | 2566.97 | 2566.97 |  |  |  | 1 | 1 |  |  |  |  | 131867.08 | 2566.97 | 131867.08 | 2566.97 | 8.535 | [5 empty] | 94.0275 |  |  | #VALUE!
07.03.2008 14:00 | 3600 | 2 | 766.87 | GGB | 769.597 | 777.047 | 773.26 | 256.46 | GGB | 10703.2 | GGB | 9.86 | GGB | 1005.17 | GGB | 62.11 | GGB | 161817.87 | GGB | 130806.05 | GGB | 0 | 0 | 2545 | 3600 | 2529.28 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 165023.2 | GGB | 165025.1 | 2529.28 | 2529.28 |  |  |  | 1 | 1 |  |  |  |  | 130806.05 | 2529.28 | 130806.05 | 2529.28 | 8.4206 | [5 empty] | 91.9014 |  |  | #VALUE!
07.03.2008 15:00 | 3600 | 2 | 766.76 | GGB | 767.033 | 774.75 | 770.696 | 256.92 | GGB | 10695 | GGB | 9.84 | GGB | 1004.88 | GGB | 62.26 | GGB | 162359.24 | GGB | 131148.25 | GGB | 0 | 0 | 2546 | 3600 | 2530.88 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 165062.55 | GGB | 165064.46 | 2530.88 | 2530.88 |  |  |  | 1 | 1 |  |  |  |  | 131148.25 | 2530.88 | 131148.25 | 2530.88 | 8.4329 | [5 empty] | 92.2001 |  |  | #VALUE!
07.03.2008 16:00 | 3600 | 2 | 766.7 | GGB | 767.033 | 775.711 | 772.161 | 258.45 | GGB | 10722.5 | GGB | 9.86 | GGB | 1005.6 | GGB | 62.09 | GGB | 163728.06 | GGB | 132416.36 | GGB | 0 | 0 | 2556 | 3600 | 2541.22 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 165102.48 | GGB | 165104.39 | 2541.22 | 2541.22 |  |  |  | 1 | 1 |  |  |  |  | 132416.36 | 2541.22 | 132416.36 | 2541.22 | 8.4272 | [5 empty] | 93.472 |  |  | #VALUE!
07.03.2008 17:00 | 3600 | 2 | 767.15 | GGB | 768.498 | 776.672 | 773.26 | 259.78 | GGB | 10702.5 | GGB | 9.85 | GGB | 1006.06 | GGB | 61.75 | GGB | 165437.98 | GGB | 133996.68 | GGB | 0 | 0 | 2527 | 3600 | 2511.45 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 165141.94 | GGB | 165143.85 | 2511.45 | 2511.45 |  |  |  | 1 | 1 |  |  |  |  | 133996.68 | 2511.45 | 133996.68 | 2511.45 | 8.5283 | [5 empty] | 93.4794 |  |  | #VALUE!
07.03.2008 18:00 | 3600 | 2 | 766.63 | GGB | 767.033 | 775.148 | 772.161 | 258.93 | GGB | 10743.8 | GGB | 9.85 | GGB | 1006.1 | GGB | 61.99 | GGB | 164080.16 | GGB | 132806.59 | GGB | 0 | 0 | 2568 | 3600 | 2552.85 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 165180.2 | GGB | 165182.12 | 2552.85 | 2552.85 |  |  |  | 1 | 1 |  |  |  |  | 132806.59 | 2552.85 | 132806.59 | 2552.85 | 8.859 | [5 empty] | 94.1765 |  |  | #VALUE!
07.03.2008 19:00 | 3600 | 2 | 765.38 | GGB | 767.033 | 775.148 | 772.161 | 260.45 | GGB | 10776.1 | GGB | 9.85 | GGB | 1007.42 | GGB | 61.83 | GGB | 165210.21 | GGB | 133962.51 | GGB | 0 | 0 | 2632 | 3600 | 2617.08 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 165220.44 | GGB | 165222.36 | 2617.08 | 2617.08 |  |  |  | 1 | 1 |  |  |  |  | 133962.51 | 2617.08 | 133962.51 | 2617.08 | 8.7125 | [5 empty] | 97.3863 |  |  | #VALUE!
07.03.2008 20:00 | 3600 | 2 | 764.64 | GGB | 765.934 | 773.813 | 770.696 | 262.9 | GGB | 10793.4 | GGB | 9.84 | GGB | 1008.31 | GGB | 61.14 | GGB | 167797.11 | GGB | 136456.79 | GGB | 0 | 0 | 2685 | 3600 | 2669.57 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 165259.7 | GGB | 165261.62 | 2669.57 | 2669.57 |  |  |  | 1 | 1 |  |  |  |  | 136456.79 | 2669.57 | 136456.79 | 2669.57 | 9.2787 | [5 empty] | 101.1892 |  |  | #VALUE!
07.03.2008 21:00 | 3600 | 2 | 764.62 | GGB | 765.934 | 774.258 | 770.696 | 264.14 | GGB | 10851.7 | GGB | 9.86 | GGB | 1009.28 | GGB | 60.53 | GGB | 169222.04 | GGB | 138001.56 | GGB | 0 | 0 | 2699 | 3600 | 2683.13 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 165298.22 | GGB | 165300.14 | 2683.13 | 2683.13 |  |  |  | 1 | 1 |  |  |  |  | 138001.56 | 2683.13 | 138001.56 | 2683.13 | 9.6126 | [5 empty] | 102.8545 |  |  | #VALUE!
07.03.2008 22:00 | 3600 | 2 | 763.16 | GGB | 764.469 | 772.336 | 768.132 | 263.19 | GGB | 10889.9 | GGB | 9.85 | GGB | 1010.08 | GGB | 60.75 | GGB | 169008.58 | GGB | 137846.47 | GGB | 0 | 0 | 2787 | 3600 | 2771.84 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 165338.04 | GGB | 165339.96 | 2771.84 | 2741.6589 |  |  |  | 1 | 1 |  |  |  |  | 137846.47 | 2741.6589 | 137846.47 | 2741.6589 | 9.4909 | [5 empty] | 106.1357 | 2741.6589 |  | 104.98
07.03.2008 23:00 | 3600 | 2 | 761.84 | GGB | 764.469 | 772.289 | 768.132 | 264.89 | GGB | 10898.3 | GGB | 9.84 | GGB | 1010.5 | GGB | 60.46 | GGB | 169779.91 | GGB | 138656.24 | GGB | 0 | 0 | 2849 | 3600 | 2833.42 | GGB | 100 | GGB | 41.12 | GGB | 41.12 | GGB | 165379.16 | GGB | 165381.08 | 2833.42 | 2725.6473 |  |  |  | 1 | 1 |  |  |  |  | 138656.24 | 2725.6473 | 138656.24 | 2725.6473 | 9.1909 | [5 empty] | 109.1309 | 2725.6473 |  | 104.98
07.03.2008 24:00 | 3600 | 2 | 761.39 | GGB | 763.37 | 771 | 767.033 | 266.28 | GGB | 10945 | GGB | 9.85 | GGB | 1011.33 | GGB | 60.09 | GGB | 171207.05 | GGB | 140090.06 | GGB | 0 | 0 | 2892 | 3600 | 2876.73 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 165419.31 | GGB | 165421.23 | 2876.73 | 2697.7503 |  |  |  | 0 | 1 | [14 empty] | 111.9448 | 2697.7503 |  | 104.98
08.03.2008 01:00 | 3600 | 2 | 761.34 | GGB | 763.37 | 770.836 | 767.033 | 266.54 | GGB | 10962.7 | GGB | 9.85 | GGB | 1011.91 | GGB | 59.88 | GGB | 171610.88 | GGB | 140591.14 | GGB | 0 | 0 | 2913 | 3600 | 2897.72 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 165458.83 | GGB | 165460.75 | 2897.72 | 2688.1353 |  |  |  | 0 | 1 | [14 empty] | 113.1649 | 2688.1353 |  | 104.98
08.03.2008 02:00 | 3600 | 2 | 761.3 | GGB | 763.37 | 770.742 | 767.033 | 267.39 | GGB | 10961.8 | GGB | 9.85 | GGB | 1012.55 | GGB | 60.06 | GGB | 171814.44 | GGB | 140769.53 | GGB | 0 | 0 | 2928 | 3600 | 2911.93 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 165499.17 | GGB | 165501.1 | 2911.93 | 2684.7287 |  |  |  | 0 | 1 | [14 empty] | 113.8642 | 2684.7287 |  | 104.98
08.03.2008 03:00 | 3600 | 2 | 761.54 | GGB | 764.469 | 772.758 | 768.132 | 268.2 | GGB | 10963.9 | GGB | 9.85 | GGB | 1012.59 | GGB | 60.46 | GGB | 171945.38 | GGB | 140711.85 | GGB | 0 | 0 | 2938 | 3600 | 2922.89 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 165538.8 | GGB | 165540.73 | 2922.89 | 2685.8292 |  |  |  | 1 | 1 |  |  |  |  | 140711.85 | 2685.8292 | 140711.85 | 2685.8292 | 9.5364 | [5 empty] | 114.2459 | 2685.8292 |  | 104.98
08.03.2008 04:00 | 3600 | 2 | 761.57 | GGB | 765.934 | 773.227 | 768.132 | 268.55 | GGB | 10968.1 | GGB | 9.85 | GGB | 1012.44 | GGB | 60.73 | GGB | 172164.35 | GGB | 140757.2 | GGB | 0 | 0 | 2945 | 3600 | 2929.64 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 165578.58 | GGB | 165580.51 | 2929.64 | 2684.9639 |  |  |  | 1 | 1 |  |  |  |  | 140757.2 | 2684.9639 | 140757.2 | 2684.9639 | 9.5005 | [5 empty] | 114.5466 | 2684.9639 |  | 104.98
08.03.2008 05:00 | 3600 | 2 | 762.19 | GGB | 765.934 | 773.18 | 769.597 | 269.64 | GGB | 10945.5 | GGB | 9.85 | GGB | 1012.28 | GGB | 60.16 | GGB | 173720.22 | GGB | 142250.07 | GGB | 0 | 0 | 2904 | 3600 | 2888.62 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 165619.71 | GGB | 165621.64 | 2888.62 | 2656.786 |  |  |  | 1 | 1 |  |  |  |  | 142250.07 | 2656.786 | 142250.07 | 2656.786 | 9.1886 | [5 empty] | 114.1407 | 2656.786 |  | 104.98
08.03.2008 06:00 | 3600 | 2 | 763.21 | GGB | 764.835 | 772.359 | 769.597 | 268.07 | GGB | 10947.3 | GGB | 9.87 | GGB | 1012.16 | GGB | 60.27 | GGB | 172222.66 | GGB | 140960.5 | GGB | 0 | 0 | 2857 | 3600 | 2841.95 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 165658.92 | GGB | 165660.85 | 2841.95 | 2681.0915 |  |  |  | 1 | 1 |  |  |  |  | 140960.5 | 2681.0915 | 140960.5 | 2681.0915 | 9.6386 | [5 empty] | 111.2785 | 2681.0915 |  | 104.98
08.03.2008 07:00 | 3600 | 2 | 761.63 | GGB | 763.37 | 771.281 | 767.766 | 267.53 | GGB | 10935.4 | GGB | 9.85 | GGB | 1011.54 | GGB | 60.73 | GGB | 171181.74 | GGB | 139829.71 | GGB | 0 | 0 | 2917 | 3600 | 2901.81 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 165699.71 | GGB | 165701.64 | 2901.81 | 2702.7733 |  |  |  | 0 | 1 | [14 empty] | 112.7109 | 2702.7733 |  | 104.98
08.03.2008 08:00 | 3600 | 2 | 762.42 | GGB | 764.469 | 772.219 | 768.864 | 267.11 | GGB | 10937.6 | GGB | 9.86 | GGB | 1011.57 | GGB | 60.89 | GGB | 170695.4 | GGB | 139369.4 | GGB | 0 | 0 | 2897 | 3600 | 2881.87 | GGB | 100 | GGB | 41.04 | GGB | 41.04 | GGB | 165740.75 | GGB | 165742.68 | 2881.87 | 2711.7 |  |  |  | 1 | 1 |  |  |  |  | 139369.4 | 2711.7 | 139369.4 | 2711.7 | 9.2088 | [5 empty] | 111.5679 | 2711.7 |  | 104.98
08.03.2008 09:00 | 3600 | 2 | 762.69 | GGB | 765.934 | 773.297 | 769.963 | 266.8 | GGB | 10927 | GGB | 9.86 | GGB | 1011.53 | GGB | 60.96 | GGB | 170325.68 | GGB | 139035.22 | GGB | 0 | 0 | 2879 | 3600 | 2863.57 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 165779.66 | GGB | 165781.59 | 2863.57 | 2718.2177 |  |  |  | 1 | 1 |  |  |  |  | 139035.22 | 2718.2177 | 139035.22 | 2718.2177 | 9.7129 | [5 empty] | 110.5936 | 2718.2177 |  | 104.98
08.03.2008 10:00 | 3600 | 2 | 763.88 | GGB | 767.033 | 774.398 | 771.429 | 264.98 | GGB | 10899.1 | GGB | 9.87 | GGB | 1011.82 | GGB | 61.48 | GGB | 168664.17 | GGB | 137500.59 | GGB | 0 | 0 | 2810 | 3600 | 2794.98 | GGB | 100 | GGB | 41.53 | GGB | 41.53 | GGB | 165821.18 | GGB | 165823.12 | 2794.98 | 2748.5555 |  |  |  | 1 | 1 |  |  |  |  | 137500.59 | 2748.5555 | 137500.59 | 2748.5555 | 9.1001 | [5 empty] | 106.7532 | 2748.5555 |  | 104.98
08.03.2008 11:00 | 3600 | 2 | 764.67 | GGB | 767.033 | 775.664 | 772.527 | 263.07 | GGB | 10846.3 | GGB | 9.87 | GGB | 1012.26 | GGB | 62.16 | GGB | 166278.64 | GGB | 135340.26 | GGB | 0 | 0 | 2733 | 3600 | 2717.26 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 165861.04 | GGB | 165862.98 | 2717.26 | 2717.26 |  |  |  | 1 | 1 |  |  |  |  | 135340.26 | 2717.26 | 135340.26 | 2717.26 | 9.2262 | [5 empty] | 102.1541 |  |  | #VALUE!
08.03.2008 12:00 | 3600 | 2 | 765.76 | GGB | 768.498 | 776.836 | 772.527 | 261.11 | GGB | 10778.7 | GGB | 9.87 | GGB | 1011.38 | GGB | 62.88 | GGB | 163843.59 | GGB | 132955.49 | GGB | 0 | 0 | 2647 | 3600 | 2631.5 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 165899.95 | GGB | 165901.89 | 2631.5 | 2631.5 |  |  |  | 1 | 1 |  |  |  |  | 132955.49 | 2631.5 | 132955.49 | 2631.5 | 8.9918 | [5 empty] | 97.1868 |  |  | #VALUE!
08.03.2008 13:00 | 3600 | 2 | 766.48 | GGB | 767.033 | 775.781 | 772.527 | 260.77 | GGB | 10684.1 | GGB | 9.85 | GGB | 1010.32 | GGB | 63.39 | GGB | 163447.47 | GGB | 132295.96 | GGB | 0 | 0 | 2588 | 3600 | 2572.83 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 165941.14 | GGB | 165943.08 | 2572.83 | 2572.83 |  |  |  | 1 | 1 |  |  |  |  | 132295.96 | 2572.83 | 132295.96 | 2572.83 | 8.2635 | [5 empty] | 94.5486 |  |  | #VALUE!
08.03.2008 14:00 | 3600 | 2 | 767.11 | GGB | 769.597 | 777.867 | 773.26 | 258.7 | GGB | 10703.9 | GGB | 9.86 | GGB | 1009.57 | GGB | 63.97 | GGB | 161576.9 | GGB | 130461.7 | GGB | 0 | 0 | 2563 | 3600 | 2547.92 | GGB | 100 | GGB | 38.09 | GGB | 38.09 | GGB | 165979.23 | GGB | 165981.17 | 2547.92 | 2547.92 |  |  |  | 1 | 1 |  |  |  |  | 130461.7 | 2547.92 | 130461.7 | 2547.92 | 8.7269 | [5 empty] | 92.335 |  |  | #VALUE!
08.03.2008 15:00 | 3600 | 2 | 767.22 | GGB | 769.597 | 777.844 | 774.359 | 257.91 | GGB | 10689.6 | GGB | 9.86 | GGB | 1009.09 | GGB | 64.01 | GGB | 161149.97 | GGB | 130037.28 | GGB | 0 | 0 | 2554 | 3600 | 2538.34 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 166019.61 | GGB | 166021.55 | 2538.34 | 2538.34 |  |  |  | 1 | 1 |  |  |  |  | 130037.28 | 2538.34 | 130037.28 | 2538.34 | 8.1743 | [5 empty] | 91.6886 |  |  | #VALUE!
08.03.2008 16:00 | 3600 | 2 | 767.54 | GGB | 768.498 | 776.648 | 773.26 | 257.04 | GGB | 10658.3 | GGB | 9.86 | GGB | 1008.49 | GGB | 64.2 | GGB | 160472.16 | GGB | 129342.11 | GGB | 0 | 0 | 2528 | 3600 | 2512.98 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 166059.88 | GGB | 166061.82 | 2512.98 | 2512.98 |  |  |  | 1 | 1 |  |  |  |  | 129342.11 | 2512.98 | 129342.11 | 2512.98 | 8.0714 | [5 empty] | 90.2873 |  |  | #VALUE!
08.03.2008 17:00 | 3600 | 2 | 767.27 | GGB | 769.597 | 777.328 | 773.26 | 256.65 | GGB | 10639.4 | GGB | 9.85 | GGB | 1007.84 | GGB | 64.15 | GGB | 160380.83 | GGB | 129202.6 | GGB | 0 | 0 | 2535 | 3600 | 2520.05 | GGB | 100 | GGB | 38.07 | GGB | 38.07 | GGB | 166097.95 | GGB | 166099.89 | 2520.05 | 2520.05 |  |  |  | 1 | 1 |  |  |  |  | 129202.6 | 2520.05 | 129202.6 | 2520.05 | 8.5526 | [5 empty] | 90.4436 |  |  | #VALUE!
08.03.2008 18:00 | 3600 | 2 | 767.83 | GGB | 769.597 | 778.5 | 774.359 | 257.82 | GGB | 10626.9 | GGB | 9.85 | GGB | 1007.54 | GGB | 63.54 | GGB | 161839.88 | GGB | 130575.53 | GGB | 0 | 0 | 2504 | 3600 | 2488.39 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 166138.92 | GGB | 166140.86 | 2488.39 | 2488.39 |  |  |  | 1 | 1 |  |  |  |  | 130575.53 | 2488.39 | 130575.53 | 2488.39 | 7.9308 | [5 empty] | 90.2563 |  |  | #VALUE!
08.03.2008 19:00 | 3600 | 2 | 767.26 | GGB | 768.498 | 777.188 | 773.26 | 256.81 | GGB | 10663.3 | GGB | 9.86 | GGB | 1007.49 | GGB | 63.56 | GGB | 160530.48 | GGB | 129504.42 | GGB | 0 | 0 | 2534 | 3600 | 2518.44 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 166177.3 | GGB | 166179.24 | 2518.44 | 2518.44 |  |  |  | 1 | 1 |  |  |  |  | 129504.42 | 2518.44 | 129504.42 | 2518.44 | 8.4979 | [5 empty] | 90.597 |  |  | #VALUE!
08.03.2008 20:00 | 3600 | 2 | 766.56 | GGB | 768.498 | 775.945 | 772.161 | 258.05 | GGB | 10675.5 | GGB | 9.85 | GGB | 1007.73 | GGB | 63.42 | GGB | 161498.77 | GGB | 130372.31 | GGB | 0 | 0 | 2572 | 3600 | 2557.16 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 166217.41 | GGB | 166219.34 | 2557.16 | 2557.16 |  |  |  | 1 | 1 |  |  |  |  | 130372.31 | 2557.16 | 130372.31 | 2557.16 | 8.3138 | [5 empty] | 92.6063 |  |  | #VALUE!
08.03.2008 21:00 | 3600 | 2 | 766.18 | GGB | 769.597 | 776.977 | 773.26 | 258.84 | GGB | 10698.4 | GGB | 9.85 | GGB | 1007.92 | GGB | 63.3 | GGB | 161993.92 | GGB | 130845.01 | GGB | 0 | 0 | 2592 | 3600 | 2576.5 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 166256.44 | GGB | 166258.38 | 2576.5 | 2576.5 |  |  |  | 1 | 1 |  |  |  |  | 130845.01 | 2576.5 | 130845.01 | 2576.5 | 8.6353 | [5 empty] | 93.645 |  |  | #VALUE!
08.03.2008 22:00 | 3600 | 2 | 766.16 | GGB | 768.498 | 776.859 | 772.161 | 259.13 | GGB | 10704.1 | GGB | 9.86 | GGB | 1008.5 | GGB | 63.3 | GGB | 162384.54 | GGB | 131234.57 | GGB | 0 | 0 | 2592 | 3600 | 2577.1 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 166295.69 | GGB | 166297.62 | 2577.1 | 2577.1 |  |  |  | 1 | 1 |  |  |  |  | 131234.57 | 2577.1 | 131234.57 | 2577.1 | 8.6189 | [5 empty] | 93.9457 |  |  | #VALUE!
08.03.2008 23:00 | 3600 | 2 | 765.83 | GGB | 768.132 | 776.836 | 773.26 | 259.89 | GGB | 10693.5 | GGB | 9.85 | GGB | 1007.96 | GGB | 62.94 | GGB | 163367.15 | GGB | 132096.94 | GGB | 0 | 0 | 2597 | 3600 | 2581.7 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 166335.08 | GGB | 166337.01 | 2581.7 | 2581.7 |  |  |  | 1 | 1 |  |  |  |  | 132096.94 | 2581.7 | 132096.94 | 2581.7 | 8.6579 | [5 empty] | 94.7319 |  |  | #VALUE!
08.03.2008 24:00 | 3600 | 2 | 765.48 | GGB | 768.132 | 776.016 | 773.26 | 259.72 | GGB | 10721.4 | GGB | 9.85 | GGB | 1007.59 | GGB | 63.1 | GGB | 162870.89 | GGB | 131585.41 | GGB | 0 | 0 | 2629 | 3600 | 2614 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 166374.63 | GGB | 166376.56 | 2614 | 2614 |  |  |  | 1 | 1 |  |  |  |  | 131585.41 | 2614 | 131585.41 | 2614 | 8.6969 | [5 empty] | 95.5456 |  |  | #VALUE!
09.03.2008 01:00 | 3600 | 2 | 765.22 | GGB | 767.033 | 774.867 | 771.795 | 259.57 | GGB | 10727.3 | GGB | 9.85 | GGB | 1007.5 | GGB | 63.17 | GGB | 163123.97 | GGB | 131751.69 | GGB | 0 | 0 | 2639 | 3600 | 2623.82 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 166413.94 | GGB | 166415.87 | 2623.82 | 2623.82 |  |  |  | 1 | 1 |  |  |  |  | 131751.69 | 2623.82 | 131751.69 | 2623.82 | 8.794 | [5 empty] | 96.0258 |  |  | #VALUE!
09.03.2008 02:00 | 3600 | 2 | 764.91 | GGB | 767.033 | 774.867 | 770.696 | 259.98 | GGB | 10744.1 | GGB | 9.85 | GGB | 1007.53 | GGB | 62.91 | GGB | 163996.54 | GGB | 132563.03 | GGB | 0 | 0 | 2659 | 3600 | 2644.08 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 166453.27 | GGB | 166455.2 | 2644.08 | 2644.08 |  |  |  | 1 | 1 |  |  |  |  | 132563.03 | 2644.08 | 132563.03 | 2644.08 | 8.912 | [5 empty] | 97.3631 |  |  | #VALUE!
09.03.2008 03:00 | 3600 | 2 | 764.95 | GGB | 767.033 | 774.773 | 770.696 | 260.21 | GGB | 10761.8 | GGB | 9.85 | GGB | 1007.58 | GGB | 62.71 | GGB | 164438.87 | GGB | 133005.58 | GGB | 0 | 0 | 2667 | 3600 | 2651.17 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 166492.96 | GGB | 166494.89 | 2651.17 | 2651.17 |  |  |  | 1 | 1 |  |  |  |  | 133005.58 | 2651.17 | 133005.58 | 2651.17 | 8.8844 | [5 empty] | 97.9501 |  |  | #VALUE!
09.03.2008 04:00 | 3600 | 2 | 764.55 | GGB | 767.033 | 774.727 | 770.696 | 260.51 | GGB | 10765.7 | GGB | 9.85 | GGB | 1007.23 | GGB | 62.52 | GGB | 164942.83 | GGB | 133442.46 | GGB | 0 | 0 | 2687 | 3600 | 2671.63 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 166532.18 | GGB | 166534.11 | 2671.63 | 2671.63 |  |  |  | 1 | 1 |  |  |  |  | 133442.46 | 2671.63 | 133442.46 | 2671.63 | 9.09 | [5 empty] | 99.0302 |  |  | #VALUE!
09.03.2008 05:00 | 3600 | 2 | 764.72 | GGB | 765.934 | 773.625 | 769.597 | 260.51 | GGB | 10765 | GGB | 9.85 | GGB | 1006.82 | GGB | 62.48 | GGB | 164735.97 | GGB | 133238.91 | GGB | 0 | 0 | 2682 | 3600 | 2666.18 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 166571.85 | GGB | 166573.78 | 2666.18 | 2666.18 |  |  |  | 1 | 1 |  |  |  |  | 133238.91 | 2666.18 | 133238.91 | 2666.18 | 8.9549 | [5 empty] | 98.6775 |  |  | #VALUE!
09.03.2008 06:00 | 3600 | 2 | 764.67 | GGB | 765.934 | 774.539 | 770.696 | 260.61 | GGB | 10772.7 | GGB | 9.86 | GGB | 1006.93 | GGB | 62.38 | GGB | 164879.01 | GGB | 133407.9 | GGB | 0 | 0 | 2687 | 3600 | 2672 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 166611.61 | GGB | 166613.55 | 2672 | 2672 |  |  |  | 1 | 1 |  |  |  |  | 133407.9 | 2672 | 133407.9 | 2672 | 8.9632 | [5 empty] | 99.0183 |  |  | #VALUE!
09.03.2008 07:00 | 3600 | 2 | 764.27 | GGB | 767.033 | 774.727 | 770.696 | 260.58 | GGB | 10771.6 | GGB | 9.85 | GGB | 1006.76 | GGB | 62.32 | GGB | 164899.92 | GGB | 133427.17 | GGB | 0 | 0 | 2707 | 3600 | 2691.4 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 166651.2 | GGB | 166653.13 | 2691.4 | 2691.4 |  |  |  | 1 | 1 |  |  |  |  | 133427.17 | 2691.4 | 133427.17 | 2691.4 | 9.0729 | [5 empty] | 99.7516 |  |  | #VALUE!
09.03.2008 08:00 | 3600 | 2 | 764.57 | GGB | 767.033 | 774.914 | 770.696 | 260.27 | GGB | 10764.6 | GGB | 9.86 | GGB | 1006.92 | GGB | 62.46 | GGB | 164718.36 | GGB | 133242.96 | GGB | 0 | 0 | 2690 | 3600 | 2674.58 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 166690.89 | GGB | 166692.82 | 2674.58 | 2674.58 |  |  |  | 1 | 1 |  |  |  |  | 133242.96 | 2674.58 | 133242.96 | 2674.58 | 8.9788 | [5 empty] | 98.9914 |  |  | #VALUE!
09.03.2008 09:00 | 3600 | 2 | 764.96 | GGB | 767.033 | 774.727 | 770.696 | 260.07 | GGB | 10759.3 | GGB | 9.86 | GGB | 1007.03 | GGB | 62.52 | GGB | 164391.56 | GGB | 132971.59 | GGB | 0 | 0 | 2674 | 3600 | 2658.74 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 166730.37 | GGB | 166732.31 | 2658.74 | 2658.74 |  |  |  | 1 | 1 |  |  |  |  | 132971.59 | 2658.74 | 132971.59 | 2658.74 | 8.9526 | [5 empty] | 98.2047 |  |  | #VALUE!
09.03.2008 10:00 | 3600 | 2 | 765.13 | GGB | 767.033 | 774.609 | 770.696 | 259.69 | GGB | 10741 | GGB | 9.85 | GGB | 1007.48 | GGB | 62.7 | GGB | 163961.33 | GGB | 132609.96 | GGB | 0 | 0 | 2667 | 3600 | 2651.55 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 166769.81 | GGB | 166771.75 | 2651.55 | 2651.55 |  |  |  | 1 | 1 |  |  |  |  | 132609.96 | 2651.55 | 132609.96 | 2651.55 | 8.9154 | [5 empty] | 97.6728 |  |  | #VALUE!
09.03.2008 11:00 | 3600 | 2 | 765.5 | GGB | 768.132 | 775.688 | 771.795 | 258.8 | GGB | 10735.1 | GGB | 9.86 | GGB | 1007.4 | GGB | 62.86 | GGB | 163189.99 | GGB | 131914.07 | GGB | 0 | 0 | 2640 | 3600 | 2624.86 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 166809.64 | GGB | 166811.57 | 2624.86 | 2624.86 |  |  |  | 1 | 1 |  |  |  |  | 131914.07 | 2624.86 | 131914.07 | 2624.86 | 8.6955 | [5 empty] | 96.1822 |  |  | #VALUE!
09.03.2008 12:00 | 3600 | 2 | 765.7 | GGB | 768.132 | 775.688 | 771.795 | 257.49 | GGB | 10708 | GGB | 9.86 | GGB | 1007.13 | GGB | 63.15 | GGB | 162003.83 | GGB | 130805.28 | GGB | 0 | 0 | 2606 | 3600 | 2590.81 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 166849.5 | GGB | 166851.43 | 2590.81 | 2590.81 |  |  |  | 1 | 1 |  |  |  |  | 130805.28 | 2590.81 | 130805.28 | 2590.81 | 8.502 | [5 empty] | 94.1366 |  |  | #VALUE!
09.03.2008 13:00 | 3600 | 2 | 766.85 | GGB | 769.597 | 777.938 | 773.26 | 256.37 | GGB | 10655.5 | GGB | 9.86 | GGB | 1006.71 | GGB | 63.49 | GGB | 160730.74 | GGB | 129594.58 | GGB | 0 | 0 | 2552 | 3600 | 2536.75 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 166887.72 | GGB | 166889.65 | 2536.75 | 2536.75 |  |  |  | 1 | 1 |  |  |  |  | 129594.58 | 2536.75 | 129594.58 | 2536.75 | 8.6015 | [5 empty] | 91.3192 |  |  | #VALUE!
09.03.2008 14:00 | 3600 | 2 | 767.17 | GGB | 769.597 | 778.852 | 774.359 | 255.8 | GGB | 10632.6 | GGB | 9.86 | GGB | 1006.29 | GGB | 63.68 | GGB | 160198.17 | GGB | 129037.78 | GGB | 0 | 0 | 2524 | 3600 | 2508.86 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 166928.27 | GGB | 166930.2 | 2508.86 | 2508.86 |  |  |  | 0 | 1 | [14 empty] | 89.9271 |  |  | #VALUE!
09.03.2008 15:00 | 3600 | 2 | 767.76 | GGB | 769.597 | 777.75 | 773.26 | 255.77 | GGB | 10607.5 | GGB | 9.85 | GGB | 1005.79 | GGB | 63.76 | GGB | 160341.22 | GGB | 129057.94 | GGB | 0 | 0 | 2492 | 3600 | 2476.77 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 166967.08 | GGB | 166969.01 | 2476.77 | 2476.77 |  |  |  | 1 | 1 |  |  |  |  | 129057.94 | 2476.77 | 129057.94 | 2476.77 | 8.2362 | [5 empty] | 88.7908 |  |  | #VALUE!
09.03.2008 16:00 | 3600 | 2 | 767.97 | GGB | 769.597 | 778.758 | 774.359 | 255.36 | GGB | 10607 | GGB | 9.86 | GGB | 1005.51 | GGB | 64.07 | GGB | 159754.74 | GGB | 128432.83 | GGB | 0 | 0 | 2482 | 3600 | 2466.65 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 167005.27 | GGB | 167007.2 | 2466.65 | 2466.65 |  |  |  | 0 | 1 | [14 empty] | 87.9997 |  |  | #VALUE!
09.03.2008 17:00 | 3600 | 2 | 768.35 | GGB | 769.597 | 778.57 | 774.359 | 255.82 | GGB | 10592.2 | GGB | 9.86 | GGB | 1005.35 | GGB | 63.99 | GGB | 160205.88 | GGB | 128804.82 | GGB | 0 | 0 | 2466 | 3600 | 2450.72 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 167045.98 | GGB | 167047.92 | 2450.72 | 2450.72 |  |  |  | 1 | 1 |  |  |  |  | 128804.82 | 2450.72 | 128804.82 | 2450.72 | 7.7521 | [5 empty] | 87.6846 |  |  | #VALUE!
09.03.2008 18:00 | 3600 | 2 | 767.78 | GGB | 768.498 | 777.492 | 773.26 | 255.37 | GGB | 10595.2 | GGB | 9.85 | GGB | 1005.51 | GGB | 64.21 | GGB | 159732.73 | GGB | 128362.13 | GGB | 0 | 0 | 2483 | 3600 | 2467.88 | GGB | 100 | GGB | 37.65 | GGB | 37.65 | GGB | 167083.63 | GGB | 167085.57 | 2467.88 | 2467.88 |  |  |  | 1 | 1 |  |  |  |  | 128362.13 | 2467.88 | 128362.13 | 2467.88 | 8.4139 | [5 empty] | 87.9951 |  |  | #VALUE!
09.03.2008 19:00 | 3600 | 2 | 768.13 | GGB | 768.498 | 777.75 | 773.26 | 256.1 | GGB | 10585.6 | GGB | 9.85 | GGB | 1005.34 | GGB | 63.8 | GGB | 160784.65 | GGB | 129343.7 | GGB | 0 | 0 | 2466 | 3600 | 2450.37 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 167122.66 | GGB | 167124.6 | 2450.37 | 2450.37 |  |  |  | 1 | 1 |  |  |  |  | 129343.7 | 2450.37 | 129343.7 | 2450.37 | 8.1204 | [5 empty] | 88.0389 |  |  | #VALUE!
09.03.2008 20:00 | 3600 | 2 | 767.67 | GGB | 770.696 | 779.742 | 774.359 | 255.89 | GGB | 10627.3 | GGB | 9.86 | GGB | 1005.69 | GGB | 64.16 | GGB | 160332.41 | GGB | 128883.48 | GGB | 0 | 0 | 2502 | 3600 | 2487.09 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 167161.32 | GGB | 167163.26 | 2487.09 | 2487.09 |  |  |  | 0 | 1 | [14 empty] | 89.0402 |  |  | #VALUE!
09.03.2008 21:00 | 3600 | 2 | 767.02 | GGB | 769.597 | 777.609 | 773.26 | 256.49 | GGB | 10633.9 | GGB | 9.85 | GGB | 1006.31 | GGB | 63.87 | GGB | 160751.64 | GGB | 129412.03 | GGB | 0 | 0 | 2533 | 3600 | 2517.96 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 167201.18 | GGB | 167203.12 | 2517.96 | 2517.96 |  |  |  | 1 | 1 |  |  |  |  | 129412.03 | 2517.96 | 129412.03 | 2517.96 | 8.175 | [5 empty] | 90.5151 |  |  | #VALUE!
09.03.2008 22:00 | 3600 | 2 | 766.95 | GGB | 768.498 | 777.609 | 772.527 | 256.63 | GGB | 10650.7 | GGB | 9.85 | GGB | 1006.25 | GGB | 63.67 | GGB | 161171.97 | GGB | 129821.03 | GGB | 0 | 0 | 2536 | 3600 | 2520.63 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 167240.32 | GGB | 167242.26 | 2520.63 | 2520.63 |  |  |  | 1 | 1 |  |  |  |  | 129821.03 | 2520.63 | 129821.03 | 2520.63 | 8.3605 | [5 empty] | 90.8974 |  |  | #VALUE!
09.03.2008 23:00 | 3600 | 2 | 766.89 | GGB | 768.498 | 777.586 | 772.161 | 256.72 | GGB | 10665.7 | GGB | 9.86 | GGB | 1005.76 | GGB | 63.44 | GGB | 161627.51 | GGB | 130212.17 | GGB | 0 | 0 | 2543 | 3600 | 2527.99 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 167279.64 | GGB | 167281.58 | 2527.99 | 2527.99 |  |  |  | 1 | 1 |  |  |  |  | 130212.17 | 2527.99 | 130212.17 | 2527.99 | 8.3717 | [5 empty] | 91.4375 |  |  | #VALUE!
09.03.2008 24:00 | 3600 | 2 | 766.64 | GGB | 768.132 | 777.492 | 773.26 | 256.94 | GGB | 10676 | GGB | 9.85 | GGB | 1005.77 | GGB | 63.26 | GGB | 162059.94 | GGB | 130632.54 | GGB | 0 | 0 | 2560 | 3600 | 2544.38 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 167319.34 | GGB | 167321.28 | 2544.38 | 2544.38 |  |  |  | 1 | 1 |  |  |  |  | 130632.54 | 2544.38 | 130632.54 | 2544.38 | 8.3723 | [5 empty] | 92.3275 |  |  | #VALUE!
10.03.2008 01:00 | 3600 | 2 | 766.44 | GGB | 768.132 | 776.531 | 772.161 | 257.03 | GGB | 10678.1 | GGB | 9.85 | GGB | 1005.44 | GGB | 63.13 | GGB | 162098.46 | GGB | 130671.62 | GGB | 0 | 0 | 2566 | 3600 | 2551.01 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 167358.63 | GGB | 167360.57 | 2551.01 | 2551.01 |  |  |  | 1 | 1 |  |  |  |  | 130671.62 | 2551.01 | 130671.62 | 2551.01 | 8.4842 | [5 empty] | 92.5957 |  |  | #VALUE!
10.03.2008 02:00 | 3600 | 2 | 766.28 | GGB | 768.498 | 777.539 | 773.26 | 257.31 | GGB | 10693.6 | GGB | 9.86 | GGB | 1005.46 | GGB | 62.98 | GGB | 162394.45 | GGB | 130970.75 | GGB | 0 | 0 | 2572 | 3600 | 2557.06 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 167397.67 | GGB | 167399.61 | 2557.06 | 2557.06 |  |  |  | 1 | 1 |  |  |  |  | 130970.75 | 2557.06 | 130970.75 | 2557.06 | 8.5784 | [5 empty] | 93.0278 |  |  | #VALUE!
10.03.2008 03:00 | 3600 | 2 | 766.12 | GGB | 768.132 | 776.414 | 772.161 | 257.41 | GGB | 10692.4 | GGB | 9.85 | GGB | 1005.54 | GGB | 62.97 | GGB | 162431.86 | GGB | 131017.29 | GGB | 0 | 0 | 2580 | 3600 | 2564.94 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 167437.07 | GGB | 167439.02 | 2564.94 | 2564.94 |  |  |  | 1 | 1 |  |  |  |  | 131017.29 | 2564.94 | 131017.29 | 2564.94 | 8.5271 | [5 empty] | 93.3476 |  |  | #VALUE!
10.03.2008 04:00 | 3600 | 2 | 765.85 | GGB | 767.033 | 775.336 | 771.795 | 257.69 | GGB | 10698.7 | GGB | 9.85 | GGB | 1005.28 | GGB | 62.87 | GGB | 162713.55 | GGB | 131248.5 | GGB | 0 | 0 | 2597 | 3600 | 2581.9 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 167476.84 | GGB | 167478.79 | 2581.9 | 2581.9 |  |  |  | 1 | 1 |  |  |  |  | 131248.5 | 2581.9 | 131248.5 | 2581.9 | 8.5208 | [5 empty] | 94.1307 |  |  | #VALUE!
10.03.2008 05:00 | 3600 | 2 | 766.03 | GGB | 767.033 | 776.484 | 772.161 | 257.67 | GGB | 10703.6 | GGB | 9.86 | GGB | 1005.04 | GGB | 62.89 | GGB | 162777.36 | GGB | 131261.54 | GGB | 0 | 0 | 2592 | 3600 | 2576.99 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 167516.14 | GGB | 167518.09 | 2576.99 | 2576.99 |  |  |  | 1 | 1 |  |  |  |  | 131261.54 | 2576.99 | 131261.54 | 2576.99 | 8.6071 | [5 empty] | 93.961 |  |  | #VALUE!
10.03.2008 06:00 | 3600 | 2 | 766.02 | GGB | 768.132 | 776.484 | 772.161 | 257.27 | GGB | 10696.1 | GGB | 9.86 | GGB | 1004.84 | GGB | 62.89 | GGB | 162623.32 | GGB | 131108.38 | GGB | 0 | 0 | 2592 | 3600 | 2577.06 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 167555.75 | GGB | 167557.7 | 2577.06 | 2577.06 |  |  |  | 1 | 1 |  |  |  |  | 131108.38 | 2577.06 | 131108.38 | 2577.06 | 8.53 | [5 empty] | 93.8539 |  |  | #VALUE!
10.03.2008 07:00 | 3600 | 2 | 766.15 | GGB | 768.132 | 776.344 | 771.795 | 257.08 | GGB | 10689 | GGB | 9.85 | GGB | 1004.81 | GGB | 62.91 | GGB | 162316.32 | GGB | 130851.85 | GGB | 0 | 0 | 2586 | 3600 | 2570.55 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 167595.4 | GGB | 167597.35 | 2570.55 | 2570.55 |  |  |  | 1 | 1 |  |  |  |  | 130851.85 | 2570.55 | 130851.85 | 2570.55 | 8.4833 | [5 empty] | 93.4337 |  |  | #VALUE!
10.03.2008 08:00 | 3600 | 2 | 766.09 | GGB | 768.132 | 776.391 | 772.161 | 257.12 | GGB | 10693.6 | GGB | 9.85 | GGB | 1004.92 | GGB | 62.81 | GGB | 162429.66 | GGB | 130994.81 | GGB | 0 | 0 | 2590 | 3600 | 2574.43 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 167634.49 | GGB | 167636.44 | 2574.43 | 2574.43 |  |  |  | 1 | 1 |  |  |  |  | 130994.81 | 2574.43 | 130994.81 | 2574.43 | 8.6272 | [5 empty] | 93.6769 |  |  | #VALUE!
10.03.2008 09:00 | 3600 | 2 | 766.24 | GGB | 768.132 | 776.227 | 772.161 | 257.05 | GGB | 10692.9 | GGB | 9.86 | GGB | 1005.26 | GGB | 62.82 | GGB | 162266.81 | GGB | 130905.4 | GGB | 0 | 0 | 2586 | 3600 | 2571.16 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 167674.39 | GGB | 167676.34 | 2571.16 | 2571.16 |  |  |  | 1 | 1 |  |  |  |  | 130905.4 | 2571.16 | 130905.4 | 2571.16 | 8.4356 | [5 empty] | 93.4941 |  |  | #VALUE!
10.03.2008 10:00 | 3600 | 2 | 767.37 | GGB | 769.597 | 778.383 | 773.993 | 255.38 | GGB | 10648.9 | GGB | 9.87 | GGB | 1005.17 | GGB | 63.22 | GGB | 160603.1 | GGB | 129395.67 | GGB | 0 | 0 | 2520 | 3600 | 2505.21 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 167713.41 | GGB | 167715.36 | 2505.21 | 2505.21 |  |  |  | 1 | 1 |  |  |  |  | 129395.67 | 2505.21 | 129395.67 | 2505.21 | 8.3076 | [5 empty] | 90.0454 |  |  | #VALUE!
10.03.2008 11:00 | 3600 | 2 | 768.57 | GGB | 770.696 | 779.484 | 775.091 | 253.93 | GGB | 10586 | GGB | 9.86 | GGB | 1004.74 | GGB | 63.87 | GGB | 158857.96 | GGB | 127688.76 | GGB | 0 | 0 | 2454 | 3600 | 2438.37 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 167751.69 | GGB | 167753.65 | 2438.37 | 2438.37 |  |  |  | 0 | 1 | [14 empty] | 86.4868 |  |  | #VALUE!
10.03.2008 12:00 | 3600 | 2 | 769.99 | GGB | 771.795 | 780.633 | 776.19 | 252.54 | GGB | 10549.7 | GGB | 9.86 | GGB | 1003.79 | GGB | 64.35 | GGB | 157539.76 | GGB | 126331.03 | GGB | 0 | 0 | 2413 | 3600 | 2397.76 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 167791.8 | GGB | 167793.75 | 2397.76 | 2397.76 |  |  |  | 0 | 1 | [14 empty] | 84.1421 |  |  | #VALUE!
10.03.2008 13:00 | 3600 | 2 | 770.76 | GGB | 773.26 | 782.883 | 777.656 | 251.76 | GGB | 10514 | GGB | 9.86 | GGB | 1002.96 | GGB | 64.82 | GGB | 156767.32 | GGB | 125429.79 | GGB | 0 | 0 | 2373 | 3600 | 2357.59 | GGB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 167829.98 | GGB | 167831.93 | 2357.59 | 2357.59 |  |  |  | 0 | 1 | [14 empty] | 82.1422 |  |  | #VALUE!
10.03.2008 14:00 | 3600 | 2 | 771.05 | GGB | 771.795 | 780.773 | 776.19 | 251.2 | GGB | 10480 | GGB | 9.86 | GGB | 1001.81 | GGB | 65.22 | GGB | 156078.51 | GGB | 124589.86 | GGB | 0 | 0 | 2350 | 3600 | 2334.42 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 167868.59 | GGB | 167870.54 | 2334.42 | 2334.42 |  |  |  | 0 | 1 | [14 empty] | 80.7903 |  |  | #VALUE!
10.03.2008 15:00 | 3600 | 2 | 771.62 | GGB | 772.161 | 781.195 | 777.656 | 250.84 | GGB | 10453.5 | GGB | 9.86 | GGB | 1000.83 | GGB | 65.39 | GGB | 155822.13 | GGB | 124199.87 | GGB | 0 | 0 | 2320 | 3600 | 2305.39 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 167908.17 | GGB | 167910.13 | 2305.39 | 2305.39 |  |  |  | 0 | 1 | [14 empty] | 79.5359 |  |  | #VALUE!
10.03.2008 16:00 | 3600 | 2 | 771.57 | GGB | 772.161 | 781.266 | 777.289 | 251.27 | GGB | 10440 | GGB | 9.85 | GGB | 999.98 | GGB | 65.23 | GGB | 156518.64 | GGB | 124708.89 | GGB | 0 | 0 | 2314 | 3600 | 2298.71 | GGB | 100 | GGB | 37.86 | GGB | 37.86 | GGB | 167946.03 | GGB | 167947.99 | 2298.71 | 2298.71 |  |  |  | 0 | 1 | [14 empty] | 79.6304 |  |  | #VALUE!
10.03.2008 17:00 | 3600 | 2 | 770.74 | GGB | 770.696 | 780.141 | 775.091 | 251.39 | GGB | 10445.5 | GGB | 9.85 | GGB | 999.67 | GGB | 65.29 | GGB | 156653.99 | GGB | 124757.04 | GGB | 0 | 0 | 2341 | 3600 | 2326.33 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 167985.05 | GGB | 167987.01 | 2326.33 | 2326.33 |  |  |  | 0 | 1 | [14 empty] | 80.6183 |  |  | #VALUE!
10.03.2008 18:00 | 3600 | 2 | 770.41 | GGB | 770.696 | 780.094 | 775.091 | 251.79 | GGB | 10491.8 | GGB | 9.86 | GGB | 999.79 | GGB | 65.24 | GGB | 156582.46 | GGB | 124733 | GGB | 0 | 0 | 2371 | 3600 | 2355.61 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 168024.34 | GGB | 168026.31 | 2355.61 | 2355.61 |  |  |  | 0 | 1 | [14 empty] | 81.6173 |  |  | #VALUE!
10.03.2008 19:00 | 3600 | 2 | 768.44 | GGB | 769.597 | 779.086 | 773.993 | 253.2 | GGB | 10517.4 | GGB | 9.85 | GGB | 1000.12 | GGB | 64.83 | GGB | 157884.16 | GGB | 125964.81 | GGB | 0 | 0 | 2426 | 3600 | 2410.45 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 168062.3 | GGB | 168064.26 | 2410.45 | 2410.45 |  |  |  | 0 | 1 | [14 empty] | 84.3422 |  |  | #VALUE!
10.03.2008 20:00 | 3600 | 2 | 767.83 | GGB | 770.696 | 779.156 | 775.091 | 254.82 | GGB | 10546.8 | GGB | 9.85 | GGB | 1000.64 | GGB | 64.22 | GGB | 159565.48 | GGB | 127602.04 | GGB | 0 | 0 | 2460 | 3600 | 2444.56 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 168101.95 | GGB | 168103.91 | 2444.56 | 2444.56 |  |  |  | 0 | 1 | [14 empty] | 86.6475 |  |  | #VALUE!
10.03.2008 21:00 | 3600 | 2 | 767.16 | GGB | 768.498 | 778.031 | 772.527 | 255.71 | GGB | 10588 | GGB | 9.85 | GGB | 1001.18 | GGB | 63.41 | GGB | 160626.2 | GGB | 128827.47 | GGB | 0 | 0 | 2497 | 3600 | 2481.75 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 168140.72 | GGB | 168142.69 | 2481.75 | 2481.75 |  |  |  | 1 | 1 |  |  |  |  | 128827.47 | 2481.75 | 128827.47 | 2481.75 | 8.2444 | [5 empty] | 88.8104 |  |  | #VALUE!
10.03.2008 22:00 | 3600 | 2 | 765.66 | GGB | 767.033 | 775.852 | 770.696 | 255.95 | GGB | 10642.9 | GGB | 9.85 | GGB | 1001.68 | GGB | 62.92 | GGB | 161680.33 | GGB | 129927.38 | GGB | 0 | 0 | 2573 | 3600 | 2557.85 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 168179.33 | GGB | 168181.3 | 2557.85 | 2557.85 |  |  |  | 1 | 1 |  |  |  |  | 129927.38 | 2557.85 | 129927.38 | 2557.85 | 8.6075 | [5 empty] | 92.3152 |  |  | #VALUE!
10.03.2008 23:00 | 3600 | 2 | 765.14 | GGB | 767.033 | 775.852 | 770.696 | 257.26 | GGB | 10678.9 | GGB | 9.85 | GGB | 1002.14 | GGB | 62.8 | GGB | 162739.95 | GGB | 130887.58 | GGB | 0 | 0 | 2613 | 3600 | 2597.46 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 168219.09 | GGB | 168221.06 | 2597.46 | 2597.46 |  |  |  | 1 | 1 |  |  |  |  | 130887.58 | 2597.46 | 130887.58 | 2597.46 | 8.5507 | [5 empty] | 94.4376 |  |  | #VALUE!
10.03.2008 24:00 | 3600 | 2 | 764.88 | GGB | 767.033 | 776.156 | 770.696 | 257.92 | GGB | 10703.9 | GGB | 9.85 | GGB | 1002.69 | GGB | 62.56 | GGB | 163516.79 | GGB | 131678.8 | GGB | 0 | 0 | 2633 | 3600 | 2617.64 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 168258.02 | GGB | 168259.99 | 2617.64 | 2617.64 |  |  |  | 1 | 1 |  |  |  |  | 131678.8 | 2617.64 | 131678.8 | 2617.64 | 8.854 | [5 empty] | 95.7466 |  |  | #VALUE!
11.03.2008 01:00 | 3600 | 2 | 764.44 | GGB | 765.201 | 774.047 | 769.597 | 258.47 | GGB | 10715.5 | GGB | 9.85 | GGB | 1002.92 | GGB | 62.37 | GGB | 163996.54 | GGB | 132169.74 | GGB | 0 | 0 | 2661 | 3600 | 2645.53 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 168297.41 | GGB | 168299.38 | 2645.53 | 2645.53 |  |  |  | 1 | 1 |  |  |  |  | 132169.74 | 2645.53 | 132169.74 | 2645.53 | 8.8768 | [5 empty] | 97.1275 |  |  | #VALUE!
11.03.2008 02:00 | 3600 | 2 | 764.07 | GGB | 766.3 | 774 | 770.696 | 259.88 | GGB | 10725.6 | GGB | 9.85 | GGB | 1002.02 | GGB | 61.57 | GGB | 166017.86 | GGB | 133997.08 | GGB | 0 | 0 | 2686 | 3600 | 2671.06 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 168337.54 | GGB | 168339.51 | 2671.06 | 2671.06 |  |  |  | 1 | 1 |  |  |  |  | 133997.08 | 2671.06 | 133997.08 | 2671.06 | 8.9189 | [5 empty] | 99.4206 |  |  | #VALUE!
11.03.2008 03:00 | 3600 | 2 | 764.37 | GGB | 765.201 | 774.07 | 769.597 | 259.62 | GGB | 10747.4 | GGB | 9.86 | GGB | 1001.78 | GGB | 60.97 | GGB | 166214.82 | GGB | 134366.9 | GGB | 0 | 0 | 2675 | 3600 | 2659.82 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 168376.1 | GGB | 168378.07 | 2659.82 | 2659.82 |  |  |  | 1 | 1 |  |  |  |  | 134366.9 | 2659.82 | 134366.9 | 2659.82 | 9.2685 | [5 empty] | 99.2755 |  |  | #VALUE!
11.03.2008 04:00 | 3600 | 2 | 763.44 | GGB | 766.3 | 774.891 | 769.597 | 259.21 | GGB | 10758.9 | GGB | 9.85 | GGB | 1001.36 | GGB | 61.08 | GGB | 165484.2 | GGB | 133676.48 | GGB | 0 | 0 | 2726 | 3600 | 2710.11 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 168415.82 | GGB | 168417.79 | 2710.11 | 2710.11 |  |  |  | 1 | 1 |  |  |  |  | 133676.48 | 2710.11 | 133676.48 | 2710.11 | 9.1208 | [5 empty] | 100.6328 |  |  | #VALUE!
11.03.2008 05:00 | 3600 | 2 | 763.14 | GGB | 766.3 | 775.219 | 769.597 | 259.07 | GGB | 10772 | GGB | 9.86 | GGB | 1000.89 | GGB | 60.93 | GGB | 166048.67 | GGB | 134128.25 | GGB | 0 | 0 | 2739 | 3600 | 2723.99 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 168456.64 | GGB | 168458.61 | 2723.99 | 2723.99 |  |  |  | 1 | 1 |  |  |  |  | 134128.25 | 2723.99 | 134128.25 | 2723.99 | 8.9506 | [5 empty] | 101.49 |  |  | #VALUE!
11.03.2008 06:00 | 3600 | 2 | 762.98 | GGB | 765.201 | 773.109 | 768.498 | 259.09 | GGB | 10772 | GGB | 9.85 | GGB | 1001.24 | GGB | 60.87 | GGB | 166136.7 | GGB | 134270.78 | GGB | 0 | 0 | 2753 | 3600 | 2737.71 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 168494.84 | GGB | 168496.81 | 2737.71 | 2737.71 |  |  |  | 1 | 1 |  |  |  |  | 134270.78 | 2737.71 | 134270.78 | 2737.71 | 9.6229 | [5 empty] | 102.1096 |  |  | #VALUE!
11.03.2008 07:00 | 3600 | 2 | 763.16 | GGB | 765.201 | 774.141 | 768.498 | 258.85 | GGB | 10768 | GGB | 9.86 | GGB | 1001.3 | GGB | 60.99 | GGB | 165771.38 | GGB | 133936.74 | GGB | 0 | 0 | 2742 | 3600 | 2726.32 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 168534.94 | GGB | 168536.9 | 2726.32 | 2726.32 |  |  |  | 1 | 1 |  |  |  |  | 133936.74 | 2726.32 | 133936.74 | 2726.32 | 9.1084 | [5 empty] | 101.4318 |  |  | #VALUE!
11.03.2008 08:00 | 3600 | 2 | 764.49 | GGB | 766.667 | 775.383 | 770.696 | 258.63 | GGB | 10729 | GGB | 9.86 | GGB | 1001.43 | GGB | 61.08 | GGB | 165508.4 | GGB | 133702.54 | GGB | 0 | 0 | 2672 | 3600 | 2657.1 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 168575.68 | GGB | 168577.64 | 2657.1 | 2657.1 |  |  |  | 1 | 1 |  |  |  |  | 133702.54 | 2657.1 | 133702.54 | 2657.1 | 8.7202 | [5 empty] | 98.6836 |  |  | #VALUE!
11.03.2008 09:00 | 3600 | 2 | 764.77 | GGB | 766.667 | 775.711 | 770.696 | 256.55 | GGB | 10707.2 | GGB | 9.86 | GGB | 1000.78 | GGB | 61.71 | GGB | 163098.66 | GGB | 131424.68 | GGB | 0 | 0 | 2650 | 3600 | 2634.68 | GGB | 100 | GGB | 37.34 | GGB | 37.34 | GGB | 168613.02 | GGB | 168614.98 | 2634.68 | 2634.68 |  |  |  | 1 | 1 |  |  |  |  | 131424.68 | 2634.68 | 131424.68 | 2634.68 | 9.2732 | [5 empty] | 96.1839 |  |  | #VALUE!
11.03.2008 10:00 | 3600 | 2 | 765.31 | GGB | 767.766 | 776.789 | 773.26 | 256.3 | GGB | 10654.2 | GGB | 9.85 | GGB | 1001.12 | GGB | 61.93 | GGB | 162793.87 | GGB | 131135.75 | GGB | 0 | 0 | 2605 | 3600 | 2590.01 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 168653.86 | GGB | 168655.82 | 2590.01 | 2590.01 |  |  |  | 1 | 1 |  |  |  |  | 131135.75 | 2590.01 | 131135.75 | 2590.01 | 8.3164 | [5 empty] | 94.3453 |  |  | #VALUE!
11.03.2008 11:00 | 3600 | 2 | 766.88 | GGB | 767.766 | 776.672 | 772.161 | 255.61 | GGB | 10631.9 | GGB | 9.86 | GGB | 1000.43 | GGB | 62.37 | GGB | 161818.97 | GGB | 130089.15 | GGB | 0 | 0 | 2537 | 3600 | 2521.38 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 168693.36 | GGB | 168695.32 | 2521.38 | 2521.38 |  |  |  | 1 | 1 |  |  |  |  | 130089.15 | 2521.38 | 130089.15 | 2521.38 | 8.3039 | [5 empty] | 91.1123 |  |  | #VALUE!
11.03.2008 12:00 | 3600 | 2 | 766.76 | GGB | 767.766 | 776.672 | 773.26 | 254.02 | GGB | 10609.7 | GGB | 9.86 | GGB | 999.86 | GGB | 62.8 | GGB | 160146.46 | GGB | 128507.02 | GGB | 0 | 0 | 2532 | 3600 | 2517.06 | GGB | 100 | GGB | 37.44 | GGB | 37.44 | GGB | 168730.81 | GGB | 168732.76 | 2517.06 | 2517.06 |  |  |  | 1 | 1 |  |  |  |  | 128507.02 | 2517.06 | 128507.02 | 2517.06 | 8.6394 | [5 empty] | 89.85 |  |  | #VALUE!
11.03.2008 13:00 | 3600 | 2 | 766.8 | GGB | 767.766 | 776.813 | 772.161 | 254 | GGB | 10598.2 | GGB | 9.85 | GGB | 998.85 | GGB | 62.9 | GGB | 160062.83 | GGB | 128275.06 | GGB | 0 | 0 | 2522 | 3600 | 2506.47 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 168772.04 | GGB | 168773.99 | 2506.47 | 2506.47 |  |  |  | 1 | 1 |  |  |  |  | 128275.06 | 2506.47 | 128275.06 | 2506.47 | 7.7981 | [5 empty] | 89.3104 |  |  | #VALUE!
11.03.2008 14:00 | 3600 | 2 | 767.25 | GGB | 767.766 | 776.883 | 772.161 | 253.79 | GGB | 10594.4 | GGB | 9.86 | GGB | 998.41 | GGB | 62.99 | GGB | 159989.11 | GGB | 128120.97 | GGB | 0 | 0 | 2505 | 3600 | 2489.96 | GGB | 100 | GGB | 37.93 | GGB | 37.93 | GGB | 168809.97 | GGB | 168811.92 | 2489.96 | 2489.96 |  |  |  | 1 | 1 |  |  |  |  | 128120.97 | 2489.96 | 128120.97 | 2489.96 | 8.4107 | [5 empty] | 88.6156 |  |  | #VALUE!
11.03.2008 15:00 | 3600 | 2 | 767.77 | GGB | 769.963 | 779.016 | 774.359 | 252.65 | GGB | 10565.6 | GGB | 9.86 | GGB | 997.46 | GGB | 63.19 | GGB | 159106.64 | GGB | 127217.3 | GGB | 0 | 0 | 2475 | 3600 | 2459.3 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 168848.73 | GGB | 168850.68 | 2459.3 | 2459.3 |  |  |  | 0 | 1 | [14 empty] | 86.9071 |  |  | #VALUE!
11.03.2008 16:00 | 3600 | 2 | 768.47 | GGB | 769.963 | 779.016 | 774.359 | 251.74 | GGB | 10531.8 | GGB | 9.86 | GGB | 996.66 | GGB | 63.69 | GGB | 158030.51 | GGB | 126071.83 | GGB | 0 | 0 | 2424 | 3600 | 2409 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 168889.2 | GGB | 168891.16 | 2409 | 2409 |  |  |  | 0 | 1 | [14 empty] | 84.3631 |  |  | #VALUE!
11.03.2008 17:00 | 3600 | 2 | 768.12 | GGB | 769.963 | 779.063 | 774.359 | 252.12 | GGB | 10523.7 | GGB | 9.85 | GGB | 996.29 | GGB | 63.63 | GGB | 158513.56 | GGB | 126430.27 | GGB | 0 | 0 | 2437 | 3600 | 2422.05 | GGB | 100 | GGB | 37.04 | GGB | 37.04 | GGB | 168926.25 | GGB | 168928.2 | 2422.05 | 2422.05 |  |  |  | 0 | 1 | [14 empty] | 85.0612 |  |  | #VALUE!
11.03.2008 18:00 | 3600 | 2 | 768.1 | GGB | 768.864 | 778.852 | 773.26 | 252.2 | GGB | 10541 | GGB | 9.86 | GGB | 995.85 | GGB | 63.6 | GGB | 158372.71 | GGB | 126275.57 | GGB | 0 | 0 | 2439 | 3600 | 2423.97 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 168966.23 | GGB | 168968.18 | 2423.97 | 2423.97 |  |  |  | 0 | 1 | [14 empty] | 85.0245 |  |  | #VALUE!
11.03.2008 19:00 | 3600 | 2 | 767.08 | GGB | 768.864 | 777.844 | 773.26 | 253.74 | GGB | 10558.1 | GGB | 9.85 | GGB | 996.12 | GGB | 63.42 | GGB | 159272.79 | GGB | 127094.26 | GGB | 0 | 0 | 2492 | 3600 | 2476.96 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 169005.61 | GGB | 169007.56 | 2476.96 | 2476.96 |  |  |  | 1 | 1 |  |  |  |  | 127094.26 | 2476.96 | 127094.26 | 2476.96 | 7.9941 | [5 empty] | 87.4465 |  |  | #VALUE!
11.03.2008 20:00 | 3600 | 2 | 766.43 | GGB | 767.766 | 776.859 | 773.26 | 254.93 | GGB | 10585.7 | GGB | 9.85 | GGB | 996.42 | GGB | 63.21 | GGB | 160517.27 | GGB | 128206.92 | GGB | 0 | 0 | 2527 | 3600 | 2511.26 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 169043.64 | GGB | 169045.59 | 2511.26 | 2511.26 |  |  |  | 1 | 1 |  |  |  |  | 128206.92 | 2511.26 | 128206.92 | 2511.26 | 8.466 | [5 empty] | 89.4336 |  |  | #VALUE!
11.03.2008 21:00 | 3600 | 2 | 765.83 | GGB | 765.201 | 774.961 | 770.696 | 255.36 | GGB | 10630.1 | GGB | 9.85 | GGB | 996.58 | GGB | 62.73 | GGB | 161652.82 | GGB | 129316.29 | GGB | 0 | 0 | 2563 | 3600 | 2547.68 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 169084.05 | GGB | 169086 | 2547.68 | 2547.68 |  |  |  | 1 | 1 |  |  |  |  | 129316.29 | 2547.68 | 129316.29 | 2547.68 | 8.1528 | [5 empty] | 91.5157 |  |  | #VALUE!
11.03.2008 22:00 | 3600 | 2 | 765.65 | GGB | 767.766 | 776.016 | 771.795 | 256.04 | GGB | 10640.9 | GGB | 9.86 | GGB | 996.74 | GGB | 62.65 | GGB | 161915.8 | GGB | 129579.79 | GGB | 0 | 0 | 2580 | 3600 | 2564.78 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 169122.21 | GGB | 169124.16 | 2564.78 | 2564.78 |  |  |  | 1 | 1 |  |  |  |  | 129579.79 | 2564.78 | 129579.79 | 2564.78 | 8.7092 | [5 empty] | 92.3177 |  |  | #VALUE!
11.03.2008 23:00 | 3600 | 2 | 765.04 | GGB | 766.3 | 776.016 | 771.795 | 256.42 | GGB | 10645.9 | GGB | 9.85 | GGB | 996.1 | GGB | 62.53 | GGB | 162277.81 | GGB | 129833.34 | GGB | 0 | 0 | 2609 | 3600 | 2593.59 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 169162.1 | GGB | 169164.05 | 2593.59 | 2593.59 |  |  |  | 1 | 1 |  |  |  |  | 129833.34 | 2593.59 | 129833.34 | 2593.59 | 8.4416 | [5 empty] | 93.5373 |  |  | #VALUE!
11.03.2008 24:00 | 3600 | 2 | 765.2 | GGB | 766.667 | 776.016 | 770.696 | 256.39 | GGB | 10640.7 | GGB | 9.86 | GGB | 995.64 | GGB | 62.36 | GGB | 161909.2 | GGB | 129543.22 | GGB | 0 | 0 | 2604 | 3600 | 2588.3 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 169201.24 | GGB | 169203.19 | 2588.3 | 2588.3 |  |  |  | 1 | 1 |  |  |  |  | 129543.22 | 2588.3 | 129543.22 | 2588.3 | 8.5666 | [5 empty] | 93.138 |  |  | #VALUE!
12.03.2008 01:00 | 3600 | 2 | 764.7 | GGB | 766.667 | 775.008 | 770.696 | 256.61 | GGB | 10648.4 | GGB | 9.85 | GGB | 994.95 | GGB | 62.17 | GGB | 162309.72 | GGB | 129845.99 | GGB | 0 | 0 | 2628 | 3600 | 2612.91 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 169239.8 | GGB | 169241.76 | 2612.91 | 2612.91 |  |  |  | 1 | 1 |  |  |  |  | 129845.99 | 2612.91 | 129845.99 | 2612.91 | 8.7964 | [5 empty] | 94.2433 |  |  | #VALUE!
12.03.2008 02:00 | 3600 | 2 | 765.2 | GGB | 766.667 | 776.109 | 771.795 | 255.59 | GGB | 10638.6 | GGB | 9.86 | GGB | 994.39 | GGB | 62.29 | GGB | 161783.76 | GGB | 129305.92 | GGB | 0 | 0 | 2606 | 3600 | 2591.01 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 169280.12 | GGB | 169282.08 | 2591.01 | 2591.01 |  |  |  | 1 | 1 |  |  |  |  | 129305.92 | 2591.01 | 129305.92 | 2591.01 | 8.3093 | [5 empty] | 93.0647 |  |  | #VALUE!
12.03.2008 03:00 | 3600 | 2 | 765.34 | GGB | 767.766 | 776.109 | 771.795 | 254.78 | GGB | 10609.8 | GGB | 9.86 | GGB | 993.63 | GGB | 62.37 | GGB | 160978.31 | GGB | 128536.59 | GGB | 0 | 0 | 2582 | 3600 | 2566.32 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 169318.29 | GGB | 169320.24 | 2566.32 | 2566.32 |  |  |  | 1 | 1 |  |  |  |  | 128536.59 | 2566.32 | 128536.59 | 2566.32 | 8.6443 | [5 empty] | 91.6295 |  |  | #VALUE!
12.03.2008 04:00 | 3600 | 2 | 765.53 | GGB | 766.667 | 776.109 | 771.795 | 254.46 | GGB | 10590.6 | GGB | 9.85 | GGB | 992.71 | GGB | 62.45 | GGB | 160716.43 | GGB | 128177.87 | GGB | 0 | 0 | 2571 | 3600 | 2555.25 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 169357.34 | GGB | 169359.29 | 2555.25 | 2555.25 |  |  |  | 1 | 1 |  |  |  |  | 128177.87 | 2555.25 | 128177.87 | 2555.25 | 8.3874 | [5 empty] | 90.9796 |  |  | #VALUE!
12.03.2008 05:00 | 3600 | 2 | 765.72 | GGB | 767.766 | 776.109 | 771.795 | 254.33 | GGB | 10585.4 | GGB | 9.86 | GGB | 992.09 | GGB | 62.59 | GGB | 160390.73 | GGB | 127784.97 | GGB | 0 | 0 | 2568 | 3600 | 2552.64 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 169397.11 | GGB | 169399.06 | 2552.64 | 2552.64 |  |  |  | 1 | 1 |  |  |  |  | 127784.97 | 2552.64 | 127784.97 | 2552.64 | 8.2019 | [5 empty] | 90.6081 |  |  | #VALUE!
12.03.2008 06:00 | 3600 | 2 | 765.78 | GGB | 766.667 | 775.805 | 771.795 | 254.49 | GGB | 10572.1 | GGB | 9.85 | GGB | 991.47 | GGB | 62.59 | GGB | 160687.82 | GGB | 127938.97 | GGB | 0 | 0 | 2560 | 3600 | 2544.78 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 169435.08 | GGB | 169437.03 | 2544.78 | 2544.78 |  |  |  | 1 | 1 |  |  |  |  | 127938.97 | 2544.78 | 127938.97 | 2544.78 | 8.5746 | [5 empty] | 90.4379 |  |  | #VALUE!
12.03.2008 07:00 | 3600 | 2 | 765.76 | GGB | 767.766 | 775.781 | 772.161 | 255.93 | GGB | 10557.3 | GGB | 9.85 | GGB | 990.71 | GGB | 61.97 | GGB | 162388.95 | GGB | 129434.29 | GGB | 0 | 0 | 2546 | 3600 | 2531.14 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 169475.02 | GGB | 169476.97 | 2531.14 | 2531.14 |  |  |  | 1 | 1 |  |  |  |  | 129434.29 | 2531.14 | 129434.29 | 2531.14 | 8.2027 | [5 empty] | 91.0045 |  |  | #VALUE!
12.03.2008 08:00 | 3600 | 2 | 764.6 | GGB | 766.3 | 774.563 | 770.696 | 257.63 | GGB | 10606.4 | GGB | 9.85 | GGB | 990.36 | GGB | 61.45 | GGB | 163929.42 | GGB | 130821.2 | GGB | 0 | 0 | 2625 | 3600 | 2609.29 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 169514.12 | GGB | 169516.07 | 2609.29 | 2609.29 |  |  |  | 1 | 1 |  |  |  |  | 130821.2 | 2609.29 | 130821.2 | 2609.29 | 8.7302 | [5 empty] | 94.8196 |  |  | #VALUE!
12.03.2008 09:00 | 3600 | 2 | 764.4 | GGB | 765.201 | 774.75 | 769.597 | 256.58 | GGB | 10634.3 | GGB | 9.86 | GGB | 989.58 | GGB | 61.98 | GGB | 162478.07 | GGB | 129353.44 | GGB | 0 | 0 | 2662 | 3600 | 2646.5 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 169552.43 | GGB | 169554.38 | 2646.5 | 2646.5 |  |  |  | 1 | 1 |  |  |  |  | 129353.44 | 2646.5 | 129353.44 | 2646.5 | 8.9359 | [5 empty] | 95.0927 |  |  | #VALUE!
12.03.2008 10:00 | 3600 | 2 | 764.51 | GGB | 766.667 | 775.805 | 770.696 | 256.7 | GGB | 10669 | GGB | 9.85 | GGB | 989.29 | GGB | 61.93 | GGB | 163239.51 | GGB | 129943.26 | GGB | 0 | 0 | 2657 | 3600 | 2641.62 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 169593.45 | GGB | 169595.41 | 2641.62 | 2641.62 |  |  |  | 1 | 1 |  |  |  |  | 129943.26 | 2641.62 | 129943.26 | 2641.62 | 8.3661 | [5 empty] | 95.3502 |  |  | #VALUE!
12.03.2008 11:00 | 3600 | 2 | 765.47 | GGB | 766.667 | 775.805 | 771.429 | 257.88 | GGB | 10641 | GGB | 9.85 | GGB | 988.31 | GGB | 61.41 | GGB | 165034.16 | GGB | 131444.62 | GGB | 0 | 0 | 2605 | 3600 | 2589.4 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 169632.71 | GGB | 169634.67 | 2589.4 | 2589.4 |  |  |  | 1 | 1 |  |  |  |  | 131444.62 | 2589.4 | 131444.62 | 2589.4 | 8.6695 | [5 empty] | 94.5452 |  |  | #VALUE!
12.03.2008 12:00 | 3600 | 2 | 766.07 | GGB | 768.864 | 777.07 | 772.527 | 256.86 | GGB | 10615.2 | GGB | 9.86 | GGB | 987.72 | GGB | 61.7 | GGB | 164014.14 | GGB | 130440.02 | GGB | 0 | 0 | 2568 | 3600 | 2552.39 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 169672.58 | GGB | 169674.54 | 2552.39 | 2552.39 |  |  |  | 1 | 1 |  |  |  |  | 130440.02 | 2552.39 | 130440.02 | 2552.39 | 8.3505 | [5 empty] | 92.4816 |  |  | #VALUE!
12.03.2008 13:00 | 3600 | 2 | 767.05 | GGB | 768.864 | 778.313 | 773.993 | 253.21 | GGB | 10584.9 | GGB | 9.87 | GGB | 986.27 | GGB | 62.95 | GGB | 159706.32 | GGB | 126355.12 | GGB | 0 | 0 | 2529 | 3600 | 2513.5 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 169712.24 | GGB | 169714.2 | 2513.5 | 2513.5 |  |  |  | 1 | 1 |  |  |  |  | 126355.12 | 2513.5 | 126355.12 | 2513.5 | 8.0079 | [5 empty] | 88.2204 |  |  | #VALUE!
12.03.2008 14:00 | 3600 | 2 | 767.51 | GGB | 768.864 | 778.242 | 772.527 | 252.12 | GGB | 10527.9 | GGB | 9.86 | GGB | 984.5 | GGB | 63.57 | GGB | 158565.27 | GGB | 124998.49 | GGB | 0 | 0 | 2489 | 3600 | 2474.07 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 169751.47 | GGB | 169753.43 | 2474.07 | 2474.07 |  |  |  | 1 | 1 |  |  |  |  | 124998.49 | 2474.07 |  | 2474.07 | 7.8831 | [5 empty] | 85.9042 |  |  | #VALUE!
12.03.2008 15:00 | 3600 | 2 | 767.74 | GGB | 768.864 | 778.383 | 772.527 | 251.94 | GGB | 10512.7 | GGB | 9.85 | GGB | 983.5 | GGB | 63.62 | GGB | 158191.16 | GGB | 124556.63 | GGB | 0 | 0 | 2478 | 3600 | 2462.3 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 169790.7 | GGB | 169792.66 | 2462.3 | 2462.3 |  |  |  | 1 | 1 |  |  |  |  | 124556.63 | 2462.3 |  | 2462.3 | 7.8179 | [5 empty] | 85.1933 |  |  | #VALUE!
12.03.2008 16:00 | 3600 | 2 | 766.69 | GGB | 767.766 | 777.281 | 772.527 | 254.42 | GGB | 10527.9 | GGB | 9.85 | GGB | 983.35 | GGB | 62.51 | GGB | 160947.5 | GGB | 127127.94 | GGB | 0 | 0 | 2520 | 3600 | 2504.58 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 169830.83 | GGB | 169832.8 | 2504.58 | 2504.58 |  |  |  | 1 | 1 |  |  |  |  | 127127.94 | 2504.58 | 127127.94 | 2504.58 | 7.9323 | [5 empty] | 88.445 |  |  | #VALUE!
12.03.2008 17:00 | 3600 | 2 | 766.55 | GGB | 767.766 | 776.273 | 772.527 | 255.71 | GGB | 10540.9 | GGB | 9.85 | GGB | 982.91 | GGB | 62.26 | GGB | 162141.37 | GGB | 128106.71 | GGB | 0 | 0 | 2523 | 3600 | 2507.27 | GGB | 100 | GGB | 38.45 | GGB | 38.45 | GGB | 169869.28 | GGB | 169871.25 | 2507.27 | 2507.27 |  |  |  | 1 | 1 |  |  |  |  | 128106.71 | 2507.27 | 128106.71 | 2507.27 | 8.3537 | [5 empty] | 89.2217 |  |  | #VALUE!
12.03.2008 18:00 | 3600 | 2 | 766.53 | GGB | 767.766 | 777.375 | 772.527 | 256.04 | GGB | 10548.6 | GGB | 9.86 | GGB | 982.71 | GGB | 62.15 | GGB | 162271.21 | GGB | 128229.12 | GGB | 0 | 0 | 2526 | 3600 | 2510.53 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 169908.95 | GGB | 169910.92 | 2510.53 | 2510.53 |  |  |  | 1 | 1 |  |  |  |  | 128229.12 | 2510.53 | 128229.12 | 2510.53 | 8.115 | [5 empty] | 89.4231 |  |  | #VALUE!
12.03.2008 19:00 | 3600 | 2 | 766.42 | GGB | 767.766 | 776.602 | 772.527 | 255.29 | GGB | 10559.1 | GGB | 9.86 | GGB | 982.63 | GGB | 62.55 | GGB | 161288.61 | GGB | 127288.97 | GGB | 0 | 0 | 2535 | 3600 | 2519.5 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 169948.7 | GGB | 169950.67 | 2519.5 | 2519.5 |  |  |  | 1 | 1 |  |  |  |  | 127288.97 | 2519.5 | 127288.97 | 2519.5 | 8.068 | [5 empty] | 89.0846 |  |  | #VALUE!
12.03.2008 20:00 | 3600 | 2 | 765.64 | GGB | 766.667 | 775.57 | 771.429 | 254.61 | GGB | 10560.6 | GGB | 9.85 | GGB | 982.58 | GGB | 63.13 | GGB | 160438.05 | GGB | 126394 | GGB | 0 | 0 | 2572 | 3600 | 2556.35 | GGB | 100 | GGB | 37.72 | GGB | 37.72 | GGB | 169986.42 | GGB | 169988.39 | 2556.35 | 2556.35 |  |  |  | 1 | 1 |  |  |  |  | 126394 | 2556.35 | 126394 | 2556.35 | 8.5659 | [5 empty] | 89.752 |  |  | #VALUE!
12.03.2008 21:00 | 3600 | 2 | 766.02 | GGB | 768.864 | 777.891 | 773.626 | 254.54 | GGB | 10583.1 | GGB | 9.86 | GGB | 982.32 | GGB | 62.95 | GGB | 160555.78 | GGB | 126517.77 | GGB | 0 | 0 | 2568 | 3600 | 2552.8 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 170027.2 | GGB | 170029.18 | 2552.8 | 2552.8 |  |  |  | 1 | 1 |  |  |  |  | 126517.77 | 2552.8 | 126517.77 | 2552.8 | 7.918 | [5 empty] | 89.7152 |  |  | #VALUE!
12.03.2008 22:00 | 3600 | 2 | 765.29 | GGB | 767.766 | 775.594 | 771.429 | 254.91 | GGB | 10584 | GGB | 9.85 | GGB | 982.49 | GGB | 61.89 | GGB | 161345.83 | GGB | 127565.56 | GGB | 0 | 0 | 2591 | 3600 | 2575.55 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 170066.83 | GGB | 170068.8 | 2575.55 | 2575.55 |  |  |  | 1 | 1 |  |  |  |  | 127565.56 | 2575.55 | 127565.56 | 2575.55 | 8.2926 | [5 empty] | 91.2643 |  |  | #VALUE!
12.03.2008 23:00 | 3600 | 2 | 764.87 | GGB | 766.667 | 774.375 | 770.33 | 257.88 | GGB | 10598.6 | GGB | 9.84 | GGB | 983.5 | GGB | 61.37 | GGB | 164876.81 | GGB | 130693.61 | GGB | 0 | 0 | 2611 | 3600 | 2595.77 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 170104.87 | GGB | 170106.84 | 2595.77 | 2595.77 |  |  |  | 1 | 1 |  |  |  |  | 130693.61 | 2595.77 | 130693.61 | 2595.77 | 8.9183 | [5 empty] | 94.2363 |  |  | #VALUE!
12.03.2008 24:00 | 3600 | 2 | 764.81 | GGB | 765.201 | 774.164 | 770.33 | 258.44 | GGB | 10655.5 | GGB | 9.85 | GGB | 984.72 | GGB | 60.78 | GGB | 166299.55 | GGB | 132218.96 | GGB | 0 | 0 | 2626 | 3600 | 2610.51 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 170145.8 | GGB | 170147.77 | 2610.51 | 2610.51 |  |  |  | 1 | 1 |  |  |  |  | 132218.96 | 2610.51 | 132218.96 | 2610.51 | 8.4329 | [5 empty] | 95.8775 |  |  | #VALUE!
13.03.2008 01:00 | 3600 | 2 | 764.52 | GGB | 765.201 | 774.164 | 769.963 | 259.51 | GGB | 10673.9 | GGB | 9.85 | GGB | 985.42 | GGB | 60.65 | GGB | 167023.57 | GGB | 132943.52 | GGB | 0 | 0 | 2651 | 3600 | 2635.95 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 170184.1 | GGB | 170186.06 | 2635.95 | 2635.95 |  |  |  | 1 | 1 |  |  |  |  | 132943.52 | 2635.95 | 132943.52 | 2635.95 | 9.1521 | [5 empty] | 97.3424 |  |  | #VALUE!
13.03.2008 02:00 | 3600 | 2 | 763.87 | GGB | 765.201 | 774.164 | 768.864 | 258.9 | GGB | 10718.6 | GGB | 9.85 | GGB | 985.56 | GGB | 61.22 | GGB | 165543.61 | GGB | 131557.72 | GGB | 0 | 0 | 2697 | 3600 | 2681.99 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 170223.74 | GGB | 170225.7 | 2681.99 | 2681.99 |  |  |  | 1 | 1 |  |  |  |  | 131557.72 | 2681.99 | 131557.72 | 2681.99 | 8.901 | [5 empty] | 98.0101 |  |  | #VALUE!
13.03.2008 03:00 | 3600 | 2 | 763.06 | GGB | 765.201 | 773.016 | 768.864 | 259.88 | GGB | 10740.3 | GGB | 9.85 | GGB | 985.55 | GGB | 61.04 | GGB | 166752.89 | GGB | 132586.87 | GGB | 0 | 0 | 2743 | 3600 | 2727.39 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 170264.02 | GGB | 170265.99 | 2727.39 | 2727.39 |  |  |  | 1 | 1 |  |  |  |  | 132586.87 | 2727.39 | 132586.87 | 2727.39 | 8.9753 | [5 empty] | 100.4489 |  |  | #VALUE!
13.03.2008 04:00 | 3600 | 2 | 762.92 | GGB | 765.201 | 773.156 | 768.864 | 262 | GGB | 10723.6 | GGB | 9.85 | GGB | 985.61 | GGB | 60.36 | GGB | 169496.03 | GGB | 135051.5 | GGB | 0 | 0 | 2742 | 3600 | 2726.27 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 170302.8 | GGB | 170304.77 | 2726.27 | 2726.27 |  |  |  | 1 | 1 |  |  |  |  | 135051.5 | 2726.27 | 135051.5 | 2726.27 | 9.4942 | [5 empty] | 102.2741 |  |  | #VALUE!
13.03.2008 05:00 | 3600 | 2 | 763.4 | GGB | 766.3 | 774.117 | 769.963 | 261.31 | GGB | 10756.5 | GGB | 9.86 | GGB | 985.62 | GGB | 60.25 | GGB | 168806.12 | GGB | 134546.74 | GGB | 0 | 0 | 2730 | 3600 | 2715.02 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 170342.96 | GGB | 170344.93 | 2715.02 | 2715.02 |  |  |  | 1 | 1 |  |  |  |  | 134546.74 | 2715.02 | 134546.74 | 2715.02 | 9.096 | [5 empty] | 101.4714 |  |  | #VALUE!
13.03.2008 06:00 | 3600 | 2 | 762.62 | GGB | 765.201 | 773.883 | 768.864 | 259.81 | GGB | 10765 | GGB | 9.86 | GGB | 985.62 | GGB | 60.69 | GGB | 167476.91 | GGB | 133315.29 | GGB | 0 | 0 | 2763 | 3600 | 2747.81 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 170382.79 | GGB | 170384.76 | 2747.81 | 2747.81 |  |  |  | 1 | 1 |  |  |  |  | 133315.29 | 2747.81 | 133315.29 | 2747.81 | 9.1972 | [5 empty] | 101.757 |  |  | #VALUE!
13.03.2008 07:00 | 3600 | 2 | 762.85 | GGB | 764.102 | 772.828 | 767.766 | 259.44 | GGB | 10741.3 | GGB | 9.85 | GGB | 985.37 | GGB | 60.47 | GGB | 167573.74 | GGB | 133444.76 | GGB | 0 | 0 | 2757 | 3600 | 2741.56 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 170422.04 | GGB | 170424.01 | 2741.56 | 2741.56 |  |  |  | 1 | 1 |  |  |  |  | 133444.76 | 2741.56 | 133444.76 | 2741.56 | 9.3209 | [5 empty] | 101.6241 |  |  | #VALUE!
13.03.2008 08:00 | 3600 | 2 | 763.85 | GGB | 765.201 | 773.906 | 768.864 | 259.7 | GGB | 10714.3 | GGB | 9.86 | GGB | 985.25 | GGB | 59.87 | GGB | 167891.73 | GGB | 133924.34 | GGB | 0 | 0 | 2694 | 3600 | 2678.62 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 170462.81 | GGB | 170464.78 | 2678.62 | 2678.62 |  |  |  | 1 | 1 |  |  |  |  | 133924.34 | 2678.62 | 133924.34 | 2678.62 | 8.7989 | [5 empty] | 99.6479 |  |  | #VALUE!
13.03.2008 09:00 | 3600 | 2 | 763.95 | GGB | 766.3 | 774.047 | 769.963 | 259.59 | GGB | 10702.6 | GGB | 9.86 | GGB | 985.38 | GGB | 60.04 | GGB | 167754.19 | GGB | 133763.27 | GGB | 0 | 0 | 2689 | 3600 | 2673.53 | GGB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 170500.93 | GGB | 170502.9 | 2673.53 | 2673.53 |  |  |  | 1 | 1 |  |  |  |  | 133763.27 | 2673.53 | 133763.27 | 2673.53 | 9.3814 | [5 empty] | 99.3389 |  |  | #VALUE!
13.03.2008 10:00 | 3600 | 2 | 763.86 | GGB | 765.201 | 772.805 | 768.864 | 258.46 | GGB | 10721.7 | GGB | 9.86 | GGB | 985.57 | GGB | 60.31 | GGB | 166385.37 | GGB | 132589.17 | GGB | 0 | 0 | 2701 | 3600 | 2685.58 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 170541.19 | GGB | 170543.16 | 2685.58 | 2685.58 |  |  |  | 1 | 1 |  |  |  |  | 132589.17 | 2685.58 | 132589.17 | 2685.58 | 8.8445 | [5 empty] | 98.9108 |  |  | #VALUE!
13.03.2008 11:00 | 3600 | 2 | 763.31 | GGB | 765.201 | 773.016 | 768.864 | 258.55 | GGB | 10737.8 | GGB | 9.85 | GGB | 986.41 | GGB | 60.55 | GGB | 166134.5 | GGB | 132405.84 | GGB | 0 | 0 | 2741 | 3600 | 2725.32 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 170581.73 | GGB | 170583.7 | 2725.32 | 2725.32 |  |  |  | 1 | 1 |  |  |  |  | 132405.84 | 2725.32 | 132405.84 | 2725.32 | 8.901 | [5 empty] | 100.2356 |  |  | #VALUE!
13.03.2008 12:00 | 3600 | 2 | 763.45 | GGB | 766.3 | 773.93 | 769.963 | 259.82 | GGB | 10723.9 | GGB | 9.85 | GGB | 987.47 | GGB | 60.13 | GGB | 167791.6 | GGB | 134041.15 | GGB | 0 | 0 | 2723 | 3600 | 2708.02 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 170620.56 | GGB | 170622.53 | 2708.02 | 2708.02 |  |  |  | 1 | 1 |  |  |  |  | 134041.15 | 2708.02 | 134041.15 | 2708.02 | 9.3481 | [5 empty] | 100.8295 |  |  | #VALUE!
13.03.2008 13:00 | 3600 | 2 | 765.41 | GGB | 767.766 | 776.133 | 772.527 | 258.3 | GGB | 10671.9 | GGB | 9.86 | GGB | 987.84 | GGB | 60.53 | GGB | 165822 | GGB | 132355.73 | GGB | 0 | 0 | 2608 | 3600 | 2592.24 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 170659.73 | GGB | 170661.7 | 2592.24 | 2592.24 |  |  |  | 1 | 1 |  |  |  |  | 132355.73 | 2592.24 | 132355.73 | 2592.24 | 8.7592 | [5 empty] | 95.3049 |  |  | #VALUE!
13.03.2008 14:00 | 3600 | 2 | 766.22 | GGB | 767.766 | 777.211 | 772.527 | 257.12 | GGB | 10627.6 | GGB | 9.86 | GGB | 987.68 | GGB | 61.38 | GGB | 164601.72 | GGB | 131029.31 | GGB | 0 | 0 | 2566 | 3600 | 2551.18 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 170699.83 | GGB | 170701.8 | 2551.18 | 2551.18 |  |  |  | 1 | 1 |  |  |  |  | 131029.31 | 2551.18 | 131029.31 | 2551.18 | 8.3361 | [5 empty] | 92.8554 |  |  | #VALUE!
13.03.2008 15:00 | 3600 | 2 | 766.01 | GGB | 766.667 | 776.18 | 771.429 | 257.76 | GGB | 10639.8 | GGB | 9.85 | GGB | 987.02 | GGB | 60.85 | GGB | 165223.42 | GGB | 131645.59 | GGB | 0 | 0 | 2586 | 3600 | 2570.36 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 170738.72 | GGB | 170740.69 | 2570.36 | 2570.36 |  |  |  | 1 | 1 |  |  |  |  | 131645.59 | 2570.36 | 131645.59 | 2570.36 | 8.7009 | [5 empty] | 93.9935 |  |  | #VALUE!
13.03.2008 16:00 | 3600 | 2 | 765.28 | GGB | 766.667 | 775.031 | 771.429 | 257.44 | GGB | 10667.1 | GGB | 9.86 | GGB | 987.25 | GGB | 61.19 | GGB | 164558.81 | GGB | 131013.18 | GGB | 0 | 0 | 2614 | 3600 | 2598.74 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 170778.46 | GGB | 170780.43 | 2598.74 | 2598.74 |  |  |  | 1 | 1 |  |  |  |  | 131013.18 | 2598.74 | 131013.18 | 2598.74 | 8.5674 | [5 empty] | 94.5748 |  |  | #VALUE!
13.03.2008 17:00 | 3600 | 2 | 765.12 | GGB | 766.667 | 775.031 | 770.33 | 256.43 | GGB | 10668.3 | GGB | 9.86 | GGB | 987.06 | GGB | 61.91 | GGB | 163030.44 | GGB | 129488.35 | GGB | 0 | 0 | 2626 | 3600 | 2610.96 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 170817.5 | GGB | 170819.47 | 2610.96 | 2610.96 |  |  |  | 1 | 1 |  |  |  |  | 129488.35 | 2610.96 | 129488.35 | 2610.96 | 8.6601 | [5 empty] | 93.9136 |  |  | #VALUE!
13.03.2008 18:00 | 3600 | 2 | 764.55 | GGB | 766.3 | 774.844 | 771.429 | 257.13 | GGB | 10696.1 | GGB | 9.85 | GGB | 987.51 | GGB | 61.13 | GGB | 163993.24 | GGB | 130618.02 | GGB | 0 | 0 | 2664 | 3600 | 2648.61 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 170857.49 | GGB | 170859.46 | 2648.61 | 2648.61 |  |  |  | 1 | 1 |  |  |  |  | 130618.02 | 2648.61 | 130618.02 | 2648.61 | 8.6511 | [5 empty] | 96.0989 |  |  | #VALUE!
13.03.2008 19:00 | 3600 | 2 | 764.67 | GGB | 766.3 | 774.469 | 771.429 | 257.56 | GGB | 10702.1 | GGB | 9.86 | GGB | 988.1 | GGB | 61.77 | GGB | 164000.94 | GGB | 130453.94 | GGB | 0 | 0 | 2662 | 3600 | 2646.26 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 170897.04 | GGB | 170899.01 | 2646.26 | 2646.26 |  |  |  | 1 | 1 |  |  |  |  | 130453.94 | 2646.26 | 130453.94 | 2646.26 | 8.7286 | [5 empty] | 95.8931 |  |  | #VALUE!
13.03.2008 20:00 | 3600 | 2 | 764.94 | GGB | 766.667 | 774.586 | 770.33 | 258.75 | GGB | 10673.2 | GGB | 9.85 | GGB | 988.42 | GGB | 60.88 | GGB | 166047.57 | GGB | 132476.66 | GGB | 0 | 0 | 2632 | 3600 | 2617.14 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 170935.36 | GGB | 170937.33 | 2617.14 | 2617.14 |  |  |  | 1 | 1 |  |  |  |  | 132476.66 | 2617.14 | 132476.66 | 2617.14 | 9.0478 | [5 empty] | 96.3083 |  |  | #VALUE!
13.03.2008 21:00 | 3600 | 2 | 764.47 | GGB | 766.3 | 774.586 | 769.963 | 258.97 | GGB | 10699.1 | GGB | 9.85 | GGB | 988.46 | GGB | 60.41 | GGB | 167065.38 | GGB | 133479.9 | GGB | 0 | 0 | 2656 | 3600 | 2640.4 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 170975.81 | GGB | 170977.79 | 2640.4 | 2640.4 |  |  |  | 1 | 1 |  |  |  |  | 133479.9 | 2640.4 | 133479.9 | 2640.4 | 8.7108 | [5 empty] | 97.9001 |  |  | #VALUE!
13.03.2008 22:00 | 3600 | 2 | 764.7 | GGB | 766.3 | 774.516 | 770.33 | 258.06 | GGB | 10728.4 | GGB | 9.86 | GGB | 988.43 | GGB | 61.18 | GGB | 164986.84 | GGB | 131512.51 | GGB | 0 | 0 | 2670 | 3600 | 2654.68 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 171014.9 | GGB | 171016.88 | 2654.68 | 2654.68 |  |  |  | 1 | 1 |  |  |  |  | 131512.51 | 2654.68 | 131512.51 | 2654.68 | 8.9313 | [5 empty] | 96.9788 |  |  | #VALUE!
13.03.2008 23:00 | 3600 | 2 | 764.49 | GGB | 766.3 | 775.383 | 771.429 | 257.85 | GGB | 10721.9 | GGB | 9.86 | GGB | 988.32 | GGB | 61.13 | GGB | 164905.42 | GGB | 131452.43 | GGB | 0 | 0 | 2676 | 3600 | 2660.42 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 171054.43 | GGB | 171056.41 | 2660.42 | 2660.42 |  |  |  | 1 | 1 |  |  |  |  | 131452.43 | 2660.42 | 131452.43 | 2660.42 | 8.8469 | [5 empty] | 97.1441 |  |  | #VALUE!
13.03.2008 24:00 | 3600 | 2 | 764.54 | GGB | 767.766 | 775.336 | 772.527 | 258.78 | GGB | 10705.4 | GGB | 9.85 | GGB | 988.62 | GGB | 60.83 | GGB | 166268.74 | GGB | 132697.13 | GGB | 0 | 0 | 2667 | 3600 | 2651.19 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 171094.81 | GGB | 171096.79 | 2651.19 | 2651.19 |  |  |  | 1 | 1 |  |  |  |  | 132697.13 | 2651.19 | 132697.13 | 2651.19 | 8.7124 | [5 empty] | 97.7237 |  |  | #VALUE!
14.03.2008 01:00 | 3600 | 2 | 764.28 | GGB | 766.3 | 774.188 | 769.963 | 258.1 | GGB | 10728 | GGB | 9.85 | GGB | 988.74 | GGB | 60.83 | GGB | 165322.45 | GGB | 131959.6 | GGB | 0 | 0 | 2685 | 3600 | 2669.91 | GGB | 100 | GGB | 37.94 | GGB | 37.94 | GGB | 171132.75 | GGB | 171134.73 | 2669.91 | 2669.91 |  |  |  | 1 | 1 |  |  |  |  | 131959.6 | 2669.91 | 131959.6 | 2669.91 | 9.2862 | [5 empty] | 97.8667 |  |  | #VALUE!
14.03.2008 02:00 | 3600 | 2 | 764.08 | GGB | 766.3 | 774.516 | 770.33 | 258.47 | GGB | 10739.3 | GGB | 9.85 | GGB | 988.63 | GGB | 60.73 | GGB | 165691.06 | GGB | 132277.63 | GGB | 0 | 0 | 2701 | 3600 | 2685.68 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 171173.43 | GGB | 171175.4 | 2685.68 | 2685.68 |  |  |  | 1 | 1 |  |  |  |  | 132277.63 | 2685.68 | 132277.63 | 2685.68 | 8.7351 | [5 empty] | 98.6821 |  |  | #VALUE!
14.03.2008 03:00 | 3600 | 2 | 763.45 | GGB | 765.201 | 773.508 | 768.864 | 258.85 | GGB | 10749.7 | GGB | 9.85 | GGB | 988.81 | GGB | 60.4 | GGB | 166274.24 | GGB | 132899.85 | GGB | 0 | 0 | 2734 | 3600 | 2718.16 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 171213.12 | GGB | 171215.1 | 2718.16 | 2718.16 |  |  |  | 1 | 1 |  |  |  |  | 132899.85 | 2718.16 | 132899.85 | 2718.16 | 9.0993 | [5 empty] | 100.3453 |  |  | #VALUE!
14.03.2008 04:00 | 3600 | 2 | 763.63 | GGB | 765.201 | 772.313 | 768.864 | 259.15 | GGB | 10761.6 | GGB | 9.85 | GGB | 989.3 | GGB | 60.58 | GGB | 166393.07 | GGB | 132987.51 | GGB | 0 | 0 | 2734 | 3600 | 2718.17 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 171252.41 | GGB | 171254.39 | 2718.17 | 2718.17 |  |  |  | 1 | 1 |  |  |  |  | 132987.51 | 2718.17 | 132987.51 | 2718.17 | 9.2004 | [5 empty] | 100.4119 |  |  | #VALUE!
14.03.2008 05:00 | 3600 | 2 | 763.51 | GGB | 765.201 | 773.484 | 768.864 | 259.35 | GGB | 10774.1 | GGB | 9.85 | GGB | 990.2 | GGB | 60 | GGB | 166734.18 | GGB | 133613.66 | GGB | 0 | 0 | 2748 | 3600 | 2732.18 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 171293.34 | GGB | 171295.32 | 2732.18 | 2732.18 |  |  |  | 1 | 1 |  |  |  |  | 133613.66 | 2732.18 | 133613.66 | 2732.18 | 8.919 | [5 empty] | 101.4046 |  |  | #VALUE!
14.03.2008 06:00 | 3600 | 2 | 763.57 | GGB | 765.201 | 774.492 | 768.864 | 259.7 | GGB | 10770.9 | GGB | 9.85 | GGB | 990.59 | GGB | 60.45 | GGB | 166882.73 | GGB | 133608.39 | GGB | 0 | 0 | 2742 | 3600 | 2726.3 | GGB | 100 | GGB | 38.41 | GGB | 38.41 | GGB | 171331.75 | GGB | 171333.73 | 2726.3 | 2726.3 |  |  |  | 1 | 1 |  |  |  |  | 133608.39 | 2726.3 | 133608.39 | 2726.3 | 9.4834 | [5 empty] | 101.1824 |  |  | #VALUE!
14.03.2008 07:00 | 3600 | 2 | 763.85 | GGB | 765.201 | 774.539 | 768.864 | 259.9 | GGB | 10776.6 | GGB | 9.85 | GGB | 991.59 | GGB | 60.66 | GGB | 166707.77 | GGB | 133517.46 | GGB | 0 | 0 | 2737 | 3600 | 2721.95 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 171371.22 | GGB | 171373.2 | 2721.95 | 2721.95 |  |  |  | 1 | 1 |  |  |  |  | 133517.46 | 2721.95 | 133517.46 | 2721.95 | 9.2077 | [5 empty] | 100.9522 |  |  | #VALUE!
14.03.2008 08:00 | 3600 | 2 | 763.88 | GGB | 765.201 | 773.484 | 768.864 | 260.04 | GGB | 10780.6 | GGB | 9.85 | GGB | 992.51 | GGB | 60.77 | GGB | 166854.12 | GGB | 133714.37 | GGB | 0 | 0 | 2741 | 3208 | 2725.07 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 171412.12 | GGB | 171414.1 | 2725.07 | 2725.07 |  |  |  | 1 | 1 |  |  |  |  | 133714.37 | 2725.07 | 133714.37 | 2725.07 | 8.9091 | [5 empty] | 101.2169 |  |  | #VALUE!
14.03.2008 09:00 | 3600 | 2 | 764.19 | GGB | 766.3 | 774.539 | 769.963 | 260.14 | GGB | 10785.6 | GGB | 9.86 | GGB | 993.73 | GGB | 60.93 | GGB | 166925.64 | GGB | 133872.18 | GGB | 0 | 0 | 2729 | 3600 | 2713.2 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 171451.61 | GGB | 171453.6 | 2713.2 | 2713.2 |  |  |  | 1 | 1 |  |  |  |  | 133872.18 | 2713.2 | 133872.18 | 2713.2 | 9.1955 | [5 empty] | 100.895 |  |  | #VALUE!
14.03.2008 10:00 | 3600 | 2 | 764.59 | GGB | 766.3 | 774.633 | 770.33 | 259.66 | GGB | 10772 | GGB | 9.86 | GGB | 994.38 | GGB | 61.17 | GGB | 166335.86 | GGB | 133390.75 | GGB | 0 | 0 | 2706 | 3600 | 2690.63 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 171490.79 | GGB | 171492.78 | 2690.63 | 2690.63 |  |  |  | 1 | 1 |  |  |  |  | 133390.75 | 2690.63 | 133390.75 | 2690.63 | 9.1604 | [5 empty] | 99.6959 |  |  | #VALUE!
14.03.2008 11:00 | 3600 | 2 | 764.45 | GGB | 765.201 | 773.789 | 770.33 | 260.93 | GGB | 10738.4 | GGB | 9.84 | GGB | 994.91 | GGB | 60.87 | GGB | 167568.24 | GGB | 134571.39 | GGB | 0 | 0 | 2695 | 3600 | 2679.98 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 171530.65 | GGB | 171532.64 | 2679.98 | 2679.98 |  |  |  | 1 | 1 |  |  |  |  | 134571.39 | 2679.98 | 134571.39 | 2679.98 | 9.0479 | [5 empty] | 100.1802 |  |  | #VALUE!
14.03.2008 12:00 | 3600 | 2 | 764.92 | GGB | 766.3 | 775.008 | 771.429 | 259.76 | GGB | 10775.3 | GGB | 9.86 | GGB | 995.32 | GGB | 61.13 | GGB | 166202.72 | GGB | 133426.08 | GGB | 0 | 0 | 2690 | 3600 | 2674.91 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 171569.88 | GGB | 171571.87 | 2674.91 | 2674.91 |  |  |  | 1 | 1 |  |  |  |  | 133426.08 | 2674.91 | 133426.08 | 2674.91 | 9.0977 | [5 empty] | 99.1397 |  |  | #VALUE!
14.03.2008 13:00 | 3600 | 2 | 764.89 | GGB | 766.3 | 775.008 | 770.33 | 259.03 | GGB | 10763.5 | GGB | 9.86 | GGB | 995.18 | GGB | 61.5 | GGB | 165414.87 | GGB | 132627.26 | GGB | 0 | 0 | 2688 | 3600 | 2672.82 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 171609.57 | GGB | 171611.56 | 2672.82 | 2672.82 |  |  |  | 1 | 1 |  |  |  |  | 132627.26 | 2672.82 | 132627.26 | 2672.82 | 8.9314 | [5 empty] | 98.4691 |  |  | #VALUE!
14.03.2008 14:00 | 3600 | 2 | 765.13 | GGB | 766.3 | 775.078 | 770.33 | 259.11 | GGB | 10758.3 | GGB | 9.85 | GGB | 994.84 | GGB | 61.47 | GGB | 165463.29 | GGB | 132634.89 | GGB | 0 | 0 | 2680 | 3600 | 2664.23 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 171649.36 | GGB | 171651.35 | 2664.23 | 2664.23 |  |  |  | 1 | 1 |  |  |  |  | 132634.89 | 2664.23 | 132634.89 | 2664.23 | 8.8809 | [5 empty] | 98.1583 |  |  | #VALUE!
14.03.2008 15:00 | 3600 | 2 | 764.5 | GGB | 766.3 | 774.727 | 770.33 | 259.53 | GGB | 10769.8 | GGB | 9.85 | GGB | 995.14 | GGB | 60.97 | GGB | 166018.96 | GGB | 133317.17 | GGB | 0 | 0 | 2710 | 3600 | 2694.66 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 171688.86 | GGB | 171690.85 | 2694.66 | 2694.66 |  |  |  | 1 | 1 |  |  |  |  | 133317.17 | 2694.66 | 133317.17 | 2694.66 | 9.0948 | [5 empty] | 99.7901 |  |  | #VALUE!
14.03.2008 16:00 | 3600 | 2 | 763.47 | GGB | 765.201 | 773.906 | 768.864 | 260.23 | GGB | 10794.8 | GGB | 9.84 | GGB | 995.86 | GGB | 60.3 | GGB | 166876.12 | GGB | 134372.08 | GGB | 0 | 0 | 2761 | 3600 | 2745.4 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 171729.86 | GGB | 171731.85 | 2745.4 | 2745.4 |  |  |  | 1 | 1 |  |  |  |  | 134372.08 | 2745.4 | 134372.08 | 2745.4 | 8.9977 | [5 empty] | 102.4736 |  |  | #VALUE!
14.03.2008 17:00 | 3600 | 2 | 764.21 | GGB | 766.3 | 774.938 | 770.33 | 261.05 | GGB | 10797.6 | GGB | 9.86 | GGB | 996.62 | GGB | 60.7 | GGB | 167699.18 | GGB | 134975.17 | GGB | 0 | 0 | 2742 | 3600 | 2726.82 | GGB | 100 | GGB | 26.73 | GGB | 26.73 | GGB | 171756.59 | GGB | 171758.58 | 2726.82 | 2726.82 |  |  |  | 1 | 1 |  |  |  |  | 134975.17 | 2726.82 | 134975.17 | 2726.82 | 13.7693 | [5 empty] | 102.2369 |  |  | #VALUE!
14.03.2008 18:00 | 3600 | 2 | 764.38 | GGB | 766.3 | 775.031 | 769.963 | 260.85 | GGB | 10801.9 | GGB | 9.85 | GGB | 997.17 | GGB | 60.94 | GGB | 167041.17 | GGB | 134425.39 | GGB | 0 | 0 | 2732 | 3600 | 2716.61 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 171796.8 | GGB | 171798.79 | 2716.61 | 2716.61 |  |  |  | 1 | 1 |  |  |  |  | 134425.39 | 2716.61 | 134425.39 | 2716.61 | 9.0819 | [5 empty] | 101.4393 |  |  | #VALUE!
14.03.2008 19:00 | 3600 | 2 | 764.21 | GGB | 765.201 | 774 | 769.963 | 261.14 | GGB | 10806.2 | GGB | 9.85 | GGB | 997.66 | GGB | 60.93 | GGB | 167320.66 | GGB | 134720.26 | GGB | 0 | 0 | 2741 | 3600 | 2725.57 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 171837.12 | GGB | 171839.11 | 2725.57 | 2725.57 |  |  |  | 1 | 1 |  |  |  |  | 134720.26 | 2725.57 | 134720.26 | 2725.57 | 9.1069 | [5 empty] | 101.9971 |  |  | #VALUE!
14.03.2008 20:00 | 3600 | 2 | 764.22 | GGB | 765.201 | 773.953 | 769.963 | 261.46 | GGB | 10822.5 | GGB | 9.85 | GGB | 998.11 | GGB | 60.82 | GGB | 167823.51 | GGB | 135231.39 | GGB | 0 | 0 | 2750 | 3600 | 2734.23 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 171877.29 | GGB | 171879.28 | 2734.23 | 2734.23 |  |  |  | 1 | 1 |  |  |  |  | 135231.39 | 2734.23 | 135231.39 | 2734.23 | 9.2047 | [5 empty] | 102.7094 |  |  | #VALUE!
14.03.2008 21:00 | 3600 | 2 | 764 | GGB | 765.201 | 772.758 | 768.864 | 261.94 | GGB | 10834.3 | GGB | 9.85 | GGB | 998.44 | GGB | 60.92 | GGB | 168047.98 | GGB | 135415.47 | GGB | 0 | 0 | 2771 | 3600 | 2755.05 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 171916.63 | GGB | 171918.62 | 2755.05 | 2755.05 |  |  |  | 1 | 1 |  |  |  |  | 135415.47 | 2755.05 | 135415.47 | 2755.05 | 9.4834 | [5 empty] | 103.6323 |  |  | #VALUE!
14.03.2008 22:00 | 3600 | 2 | 763.75 | GGB | 764.102 | 772.781 | 767.766 | 262.1 | GGB | 10858.2 | GGB | 9.86 | GGB | 998.97 | GGB | 60.71 | GGB | 169114.21 | GGB | 136434.05 | GGB | 0 | 0 | 2783 | 3600 | 2767.18 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 171956.76 | GGB | 171958.76 | 2767.18 | 2767.18 |  |  |  | 1 | 1 |  |  |  |  | 136434.05 | 2767.18 | 136434.05 | 2767.18 | 9.4055 | [5 empty] | 104.8715 |  |  | #VALUE!
14.03.2008 23:00 | 3600 | 2 | 763.48 | GGB | 765.201 | 772.734 | 768.864 | 263.09 | GGB | 10853.7 | GGB | 9.85 | GGB | 999.33 | GGB | 60.87 | GGB | 169217.64 | GGB | 136497.96 | GGB | 0 | 0 | 2810 | 3600 | 2794.67 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 171996.31 | GGB | 171998.31 | 2794.67 | 2768.7447 |  |  |  | 1 | 1 |  |  |  |  | 136497.96 | 2768.7447 | 136497.96 | 2768.7447 | 9.5557 | [5 empty] | 105.963 | 2768.7447 |  | 104.98
14.03.2008 24:00 | 3600 | 2 | 763.79 | GGB | 766.3 | 774.891 | 769.963 | 262.8 | GGB | 10854.6 | GGB | 9.86 | GGB | 999.31 | GGB | 60.97 | GGB | 168835.82 | GGB | 136146.06 | GGB | 0 | 0 | 2796 | 3600 | 2780.59 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 172037.21 | GGB | 172039.21 | 2780.59 | 2775.9011 |  |  |  | 1 | 1 |  |  |  |  | 136146.06 | 2775.9011 | 136146.06 | 2775.9011 | 9.2403 | [5 empty] | 105.1573 | 2775.9011 |  | 104.98
15.03.2008 01:00 | 3600 | 2 | 764.05 | GGB | 765.201 | 773.883 | 768.864 | 262.59 | GGB | 10856.3 | GGB | 9.86 | GGB | 999.52 | GGB | 61.01 | GGB | 168821.52 | GGB | 136147.9 | GGB | 0 | 0 | 2788 | 3600 | 2772.65 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 172076.77 | GGB | 172078.78 | 2772.65 | 2772.65 |  |  |  | 1 | 1 |  |  |  |  | 136147.9 | 2772.65 | 136147.9 | 2772.65 | 9.5398 | [5 empty] | 104.8585 |  |  | #VALUE!
15.03.2008 02:00 | 3600 | 2 | 763.58 | GGB | 765.201 | 772.945 | 768.864 | 262.67 | GGB | 10850.7 | GGB | 9.85 | GGB | 999.64 | GGB | 60.98 | GGB | 168966.76 | GGB | 136295.85 | GGB | 0 | 0 | 2807 | 3600 | 2791.52 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 172116.48 | GGB | 172118.48 | 2791.52 | 2772.8504 |  |  |  | 1 | 1 |  |  |  |  | 136295.85 | 2772.8504 | 136295.85 | 2772.8504 | 9.5196 | [5 empty] | 105.6868 | 2772.8504 |  | 104.98
15.03.2008 03:00 | 3600 | 2 | 763.94 | GGB | 765.201 | 773.977 | 769.963 | 262.61 | GGB | 10859.7 | GGB | 9.86 | GGB | 999.94 | GGB | 60.9 | GGB | 168801.71 | GGB | 136235.58 | GGB | 0 | 0 | 2788 | 3600 | 2772.52 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 172157.4 | GGB | 172159.4 | 2772.52 | 2772.52 |  |  |  | 1 | 1 |  |  |  |  | 136235.58 | 2772.52 | 136235.58 | 2772.52 | 9.2306 | [5 empty] | 104.9211 |  |  | #VALUE!
15.03.2008 04:00 | 3600 | 2 | 763.79 | GGB | 765.201 | 773.906 | 768.864 | 262.86 | GGB | 10861 | GGB | 9.85 | GGB | 1000.01 | GGB | 60.71 | GGB | 169168.13 | GGB | 136618.05 | GGB | 0 | 0 | 2796 | 3600 | 2780.89 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 172196.87 | GGB | 172198.87 | 2780.89 | 2766.3109 |  |  |  | 1 | 1 |  |  |  |  | 136618.05 | 2766.3109 | 136618.05 | 2766.3109 | 9.5751 | [5 empty] | 105.5333 | 2766.3109 |  | 104.98
15.03.2008 05:00 | 3600 | 2 | 763.55 | GGB | 765.201 | 774.023 | 769.963 | 263.57 | GGB | 10879.5 | GGB | 9.85 | GGB | 1000.75 | GGB | 60.46 | GGB | 169927.36 | GGB | 137434.7 | GGB | 0 | 0 | 2818 | 3600 | 2802.44 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 172236.06 | GGB | 172238.06 | 2802.44 | 2749.8732 |  |  |  | 1 | 1 |  |  |  |  | 137434.7 | 2749.8732 | 137434.7 | 2749.8732 | 9.6435 | [5 empty] | 106.9868 | 2749.8732 |  | 104.98
15.03.2008 06:00 | 3600 | 2 | 763.38 | GGB | 765.201 | 774.047 | 768.864 | 263.81 | GGB | 10889.8 | GGB | 9.85 | GGB | 1001.09 | GGB | 60.21 | GGB | 170187.04 | GGB | 137795.8 | GGB | 0 | 0 | 2828 | 3600 | 2812.11 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 172277.13 | GGB | 172279.13 | 2812.11 | 2742.667 |  |  |  | 1 | 1 |  |  |  |  | 137795.8 | 2742.667 | 137795.8 | 2742.667 | 9.202 | [5 empty] | 107.638 | 2742.667 |  | 104.98
15.03.2008 07:00 | 3600 | 2 | 763.47 | GGB | 765.201 | 773.953 | 769.963 | 263.96 | GGB | 10896.5 | GGB | 9.86 | GGB | 1001.48 | GGB | 60.37 | GGB | 170240.96 | GGB | 137828.09 | GGB | 0 | 0 | 2830 | 3600 | 2814.89 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 172317.43 | GGB | 172319.44 | 2814.89 | 2742.0245 |  |  |  | 1 | 1 |  |  |  |  | 137828.09 | 2742.0245 | 137828.09 | 2742.0245 | 9.3755 | [5 empty] | 107.7697 | 2742.0245 |  | 104.98
15.03.2008 08:00 | 3600 | 2 | 763.42 | GGB | 765.201 | 772.688 | 768.864 | 263.94 | GGB | 10895.3 | GGB | 9.85 | GGB | 1002.13 | GGB | 60.45 | GGB | 170273.97 | GGB | 137908.28 | GGB | 0 | 0 | 2834 | 3600 | 2818.51 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 172357.36 | GGB | 172359.36 | 2818.51 | 2740.4301 |  |  |  | 1 | 1 |  |  |  |  | 137908.28 | 2740.4301 | 137908.28 | 2740.4301 | 9.4671 | [5 empty] | 107.9711 | 2740.4301 |  | 104.98
15.03.2008 09:00 | 3600 | 2 | 763.59 | GGB | 765.201 | 773.789 | 769.963 | 263.65 | GGB | 10898.6 | GGB | 9.86 | GGB | 1002.75 | GGB | 60.54 | GGB | 170047.3 | GGB | 137774.8 | GGB | 0 | 0 | 2826 | 3600 | 2810.15 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 172397.81 | GGB | 172399.82 | 2810.15 | 2743.0851 |  |  |  | 1 | 1 |  |  |  |  | 137774.8 | 2743.0851 | 137774.8 | 2743.0851 | 9.3408 | [5 empty] | 107.5466 | 2743.0851 |  | 104.98
15.03.2008 10:00 | 3600 | 2 | 764.02 | GGB | 766.3 | 774.891 | 770.696 | 263.36 | GGB | 10890.9 | GGB | 9.86 | GGB | 1003.39 | GGB | 60.57 | GGB | 169585.15 | GGB | 137474.43 | GGB | 0 | 0 | 2810 | 3600 | 2794.03 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 172438.42 | GGB | 172440.42 | 2794.03 | 2749.0785 |  |  |  | 1 | 1 |  |  |  |  | 137474.43 | 2749.0785 | 137474.43 | 2749.0785 | 9.3086 | [5 empty] | 106.6966 | 2749.0785 |  | 104.98
15.03.2008 11:00 | 3600 | 2 | 764.32 | GGB | 766.3 | 774.914 | 769.597 | 262.52 | GGB | 10873.8 | GGB | 9.86 | GGB | 1003.96 | GGB | 60.73 | GGB | 168761 | GGB | 136817.06 | GGB | 0 | 0 | 2780 | 3600 | 2764.42 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 172478.82 | GGB | 172480.83 | 2764.42 | 2762.2871 |  |  |  | 1 | 1 |  |  |  |  | 136817.06 | 2762.2871 | 136817.06 | 2762.2871 | 9.3523 | [5 empty] | 105.0611 | 2762.2871 |  | 104.98
15.03.2008 12:00 | 3600 | 2 | 764.28 | GGB | 766.3 | 774.75 | 770.696 | 262.55 | GGB | 10869.8 | GGB | 9.85 | GGB | 1004.31 | GGB | 60.8 | GGB | 168606.95 | GGB | 136714.7 | GGB | 0 | 0 | 2775 | 3600 | 2759.72 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 172519.08 | GGB | 172521.09 | 2759.72 | 2759.72 |  |  |  | 1 | 1 |  |  |  |  | 136714.7 | 2759.72 | 136714.7 | 2759.72 | 9.3714 | [5 empty] | 104.804 |  |  | #VALUE!
15.03.2008 13:00 | 3600 | 2 | 764.72 | GGB | 765.201 | 773.883 | 770.696 | 261.86 | GGB | 10851.5 | GGB | 9.86 | GGB | 1004.42 | GGB | 60.98 | GGB | 167846.62 | GGB | 136037.55 | GGB | 0 | 0 | 2746 | 3600 | 2730.27 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 172557.86 | GGB | 172559.87 | 2730.27 | 2730.27 |  |  |  | 1 | 1 |  |  |  |  | 136037.55 | 2730.27 | 136037.55 | 2730.27 | 9.5776 | [5 empty] | 103.172 |  |  | #VALUE!
15.03.2008 14:00 | 3600 | 2 | 765.22 | GGB | 766.667 | 776.109 | 771.795 | 261.9 | GGB | 10855.2 | GGB | 9.86 | GGB | 1003.82 | GGB | 61.15 | GGB | 167761.89 | GGB | 135820.02 | GGB | 0 | 0 | 2728 | 3600 | 2712.19 | GGB | 100 | GGB | 41.76 | GGB | 41.76 | GGB | 172599.61 | GGB | 172601.63 | 2712.19 | 2712.19 |  |  |  | 1 | 1 |  |  |  |  | 135820.02 | 2712.19 | 135820.02 | 2712.19 | 8.8211 | [5 empty] | 102.3249 |  |  | #VALUE!
15.03.2008 15:00 | 3600 | 2 | 764.87 | GGB | 767.766 | 776.25 | 773.26 | 261.66 | GGB | 10840.4 | GGB | 9.85 | GGB | 1003.44 | GGB | 60.99 | GGB | 167948.95 | GGB | 135984.85 | GGB | 0 | 0 | 2724 | 3600 | 2709 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 172639.97 | GGB | 172641.98 | 2709 | 2709 |  |  |  | 1 | 1 |  |  |  |  | 135984.85 | 2709 | 135984.85 | 2709 | 9.1297 | [5 empty] | 102.3286 |  |  | #VALUE!
15.03.2008 16:00 | 3600 | 2 | 765.41 | GGB | 767.766 | 776.32 | 771.795 | 261.37 | GGB | 10830.8 | GGB | 9.86 | GGB | 1003.5 | GGB | 61.3 | GGB | 167248.04 | GGB | 135298.2 | GGB | 0 | 0 | 2702 | 3600 | 2686.46 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 172680.09 | GGB | 172682.1 | 2686.46 | 2686.46 |  |  |  | 1 | 1 |  |  |  |  | 135298.2 | 2686.46 | 135298.2 | 2686.46 | 9.0597 | [5 empty] | 100.9648 |  |  | #VALUE!
15.03.2008 17:00 | 3600 | 2 | 765.45 | GGB | 767.766 | 776.344 | 772.161 | 261.06 | GGB | 10805.5 | GGB | 9.85 | GGB | 1003.09 | GGB | 61.65 | GGB | 166745.18 | GGB | 134695.82 | GGB | 0 | 0 | 2682 | 3600 | 2666.98 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 172720.94 | GGB | 172722.95 | 2666.98 | 2666.98 |  |  |  | 1 | 1 |  |  |  |  | 134695.82 | 2666.98 | 134695.82 | 2666.98 | 8.7939 | [5 empty] | 99.7864 |  |  | #VALUE!
15.03.2008 18:00 | 3600 | 2 | 765.71 | GGB | 767.766 | 775.219 | 771.795 | 261.31 | GGB | 10807.1 | GGB | 9.85 | GGB | 1003.07 | GGB | 61.84 | GGB | 166812.3 | GGB | 134672.68 | GGB | 0 | 0 | 2678 | 3600 | 2662.83 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 172760.61 | GGB | 172762.62 | 2662.83 | 2662.83 |  |  |  | 1 | 1 |  |  |  |  | 134672.68 | 2662.83 | 134672.68 | 2662.83 | 9.0398 | [5 empty] | 99.614 |  |  | #VALUE!
15.03.2008 19:00 | 3600 | 2 | 765.02 | GGB | 766.667 | 774.914 | 770.696 | 261.92 | GGB | 10828.3 | GGB | 9.85 | GGB | 1003.3 | GGB | 61.6 | GGB | 167344.87 | GGB | 135228.68 | GGB | 0 | 0 | 2726 | 3600 | 2710.5 | GGB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 172802.18 | GGB | 172804.19 | 2710.5 | 2710.5 |  |  |  | 1 | 1 |  |  |  |  | 135228.68 | 2710.5 | 135228.68 | 2710.5 | 8.8174 | [5 empty] | 101.8159 |  |  | #VALUE!
15.03.2008 20:00 | 3600 | 2 | 764.93 | GGB | 766.667 | 774.914 | 771.795 | 261.6 | GGB | 10826.4 | GGB | 9.85 | GGB | 1003.53 | GGB | 61.45 | GGB | 167190.82 | GGB | 135197.99 | GGB | 0 | 0 | 2722 | 3600 | 2706.74 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 172842.17 | GGB | 172844.18 | 2706.74 | 2706.74 |  |  |  | 1 | 1 |  |  |  |  | 135197.99 | 2706.74 | 135197.99 | 2706.74 | 9.1509 | [5 empty] | 101.6516 |  |  | #VALUE!
15.03.2008 21:00 | 3600 | 2 | 765.02 | GGB | 766.667 | 774.117 | 770.696 | 261.15 | GGB | 10822.9 | GGB | 9.86 | GGB | 1003.23 | GGB | 61.18 | GGB | 166983.96 | GGB | 135099.49 | GGB | 0 | 0 | 2712 | 3600 | 2696.55 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 172881.78 | GGB | 172883.79 | 2696.55 | 2696.55 |  |  |  | 1 | 1 |  |  |  |  | 135099.49 | 2696.55 | 135099.49 | 2696.55 | 9.1972 | [5 empty] | 101.1951 |  |  | #VALUE!
15.03.2008 22:00 | 3600 | 2 | 764.31 | GGB | 764.102 | 772.945 | 768.498 | 261.12 | GGB | 10836 | GGB | 9.85 | GGB | 1004.05 | GGB | 60.98 | GGB | 168003.97 | GGB | 136115.86 | GGB | 0 | 0 | 2749 | 3600 | 2733.93 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 172921.75 | GGB | 172923.76 | 2733.93 | 2733.93 |  |  |  | 1 | 1 |  |  |  |  | 136115.86 | 2733.93 | 136115.86 | 2733.93 | 9.3103 | [5 empty] | 103.3698 |  |  | #VALUE!
15.03.2008 23:00 | 3600 | 2 | 764.02 | GGB | 765.201 | 774.023 | 768.498 | 262.61 | GGB | 10853.6 | GGB | 9.85 | GGB | 1004.11 | GGB | 60.85 | GGB | 168440.8 | GGB | 136532.55 | GGB | 0 | 0 | 2781 | 3600 | 2765.07 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 172962.07 | GGB | 172964.08 | 2765.07 | 2765.07 |  |  |  | 1 | 1 |  |  |  |  | 136532.55 | 2765.07 | 136532.55 | 2765.07 | 9.3631 | [5 empty] | 104.8672 |  |  | #VALUE!
15.03.2008 24:00 | 3600 | 2 | 764.23 | GGB | 765.201 | 774.023 | 769.597 | 262.84 | GGB | 10866 | GGB | 9.86 | GGB | 1004.16 | GGB | 60.64 | GGB | 168692.78 | GGB | 136828.25 | GGB | 0 | 0 | 2778 | 3600 | 2763.03 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 173002.77 | GGB | 173004.78 | 2763.03 | 2762.0612 |  |  |  | 1 | 1 |  |  |  |  | 136828.25 | 2762.0612 | 136828.25 | 2762.0612 | 9.2857 | [5 empty] | 105.0168 | 2762.0612 |  | 104.98
16.03.2008 01:00 | 3600 | 2 | 764 | GGB | 766.3 | 774.023 | 770.696 | 262.96 | GGB | 10860.8 | GGB | 9.85 | GGB | 1004.23 | GGB | 60.79 | GGB | 168841.33 | GGB | 136895.81 | GGB | 0 | 0 | 2784 | 3600 | 2768.88 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 173041.77 | GGB | 173043.78 | 2768.88 | 2760.6981 |  |  |  | 1 | 1 |  |  |  |  | 136895.81 | 2760.6981 | 136895.81 | 2760.6981 | 9.6905 | [5 empty] | 105.2911 | 2760.6981 |  | 104.98
16.03.2008 02:00 | 3600 | 2 | 763.97 | GGB | 765.201 | 774.023 | 768.498 | 262.8 | GGB | 10860.9 | GGB | 9.85 | GGB | 1003.94 | GGB | 60.69 | GGB | 168636.66 | GGB | 136729.97 | GGB | 0 | 0 | 2785 | 3600 | 2769.82 | GGB | 100 | GGB | 41.71 | GGB | 41.71 | GGB | 173083.48 | GGB | 173085.49 | 2769.82 | 2764.0465 |  |  |  | 1 | 1 |  |  |  |  | 136729.97 | 2764.0465 | 136729.97 | 2764.0465 | 9.0608 | [5 empty] | 105.1993 | 2764.0465 |  | 104.98
16.03.2008 03:00 | 3600 | 2 | 763.9 | GGB | 764.102 | 772.922 | 768.498 | 262.77 | GGB | 10853.3 | GGB | 9.85 | GGB | 1004.27 | GGB | 60.78 | GGB | 168558.54 | GGB | 136675.73 | GGB | 0 | 0 | 2788 | 3600 | 2772.58 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 173123.78 | GGB | 173125.79 | 2772.58 | 2765.1435 |  |  |  | 1 | 1 |  |  |  |  | 136675.73 | 2765.1435 | 136675.73 | 2765.1435 | 9.3779 | [5 empty] | 105.2623 | 2765.1435 |  | 104.98
16.03.2008 04:00 | 3600 | 2 | 763.77 | GGB | 764.102 | 772.875 | 768.132 | 263.19 | GGB | 10861 | GGB | 9.85 | GGB | 1003.74 | GGB | 60.68 | GGB | 169010.78 | GGB | 137011.15 | GGB | 0 | 0 | 2800 | 3600 | 2784.32 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 173162.78 | GGB | 173164.79 | 2784.32 | 2758.374 |  |  |  | 1 | 1 |  |  |  |  | 137011.15 | 2758.374 | 137011.15 | 2758.374 | 9.6905 | [5 empty] | 105.9675 | 2758.374 |  | 104.98
16.03.2008 05:00 | 3600 | 2 | 763.95 | GGB | 765.201 | 773.672 | 769.597 | 263.03 | GGB | 10868.5 | GGB | 9.86 | GGB | 1003.68 | GGB | 60.71 | GGB | 168957.96 | GGB | 136949.85 | GGB | 0 | 0 | 2795 | 3600 | 2779.9 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 173203.57 | GGB | 173205.58 | 2779.9 | 2759.6087 |  |  |  | 1 | 1 |  |  |  |  | 136949.85 | 2759.6087 | 136949.85 | 2759.6087 | 9.2652 | [5 empty] | 105.7519 | 2759.6087 |  | 104.98
16.03.2008 06:00 | 3600 | 2 | 763.54 | GGB | 765.201 | 773.648 | 769.597 | 262.99 | GGB | 10861.5 | GGB | 9.85 | GGB | 1003.57 | GGB | 60.69 | GGB | 169237.45 | GGB | 137166.69 | GGB | 0 | 0 | 2813 | 3600 | 2797.53 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 173243.79 | GGB | 173245.8 | 2797.53 | 2755.2462 |  |  |  | 1 | 1 |  |  |  |  | 137166.69 | 2755.2462 | 137166.69 | 2755.2462 | 9.3965 | [5 empty] | 106.5911 | 2755.2462 |  | 104.98
16.03.2008 07:00 | 3600 | 2 | 763.92 | GGB | 765.201 | 773.578 | 768.498 | 262.98 | GGB | 10870.3 | GGB | 9.86 | GGB | 1003.06 | GGB | 60.57 | GGB | 169123.01 | GGB | 137057.32 | GGB | 0 | 0 | 2792 | 3600 | 2776.83 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 173282.94 | GGB | 173284.95 | 2776.83 | 2757.4448 |  |  |  | 1 | 1 |  |  |  |  | 137057.32 | 2757.4448 | 137057.32 | 2757.4448 | 9.6533 | [5 empty] | 105.718 | 2757.4448 |  | 104.98
16.03.2008 08:00 | 3600 | 2 | 763.6 | GGB | 765.201 | 773.578 | 769.597 | 262.95 | GGB | 10849.5 | GGB | 9.85 | GGB | 1002.82 | GGB | 60.69 | GGB | 169128.51 | GGB | 136977.26 | GGB | 0 | 0 | 2803 | 3600 | 2787.8 | GGB | 100 | GGB | 41.96 | GGB | 41.96 | GGB | 173324.9 | GGB | 173326.91 | 2787.8 | 2759.0565 |  |  |  | 1 | 1 |  |  |  |  | 136977.26 | 2759.0565 | 136977.26 | 2759.0565 | 9.0069 | [5 empty] | 106.0737 | 2759.0565 |  | 104.98
16.03.2008 09:00 | 3600 | 2 | 764.21 | GGB | 765.201 | 773.625 | 769.597 | 262.55 | GGB | 10856.7 | GGB | 9.86 | GGB | 1003.14 | GGB | 60.76 | GGB | 168613.56 | GGB | 136577.35 | GGB | 0 | 0 | 2777 | 3600 | 2761.32 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 173364.9 | GGB | 173366.91 | 2761.32 | 2761.32 |  |  |  | 1 | 1 |  |  |  |  | 136577.35 | 2761.32 | 136577.35 | 2761.32 | 9.4283 | [5 empty] | 104.7594 |  |  | #VALUE!
16.03.2008 10:00 | 3600 | 2 | 764.12 | GGB | 767.766 | 774.914 | 771.795 | 262.24 | GGB | 10835.8 | GGB | 9.86 | GGB | 1002.95 | GGB | 60.89 | GGB | 168334.07 | GGB | 136271.7 | GGB | 0 | 0 | 2774 | 3600 | 2758.97 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 173404.14 | GGB | 173406.15 | 2758.97 | 2758.97 |  |  |  | 1 | 1 |  |  |  |  | 136271.7 | 2758.97 | 136271.7 | 2758.97 | 9.5813 | [5 empty] | 104.436 |  |  | #VALUE!
16.03.2008 11:00 | 3600 | 2 | 764.56 | GGB | 766.667 | 774.938 | 770.696 | 261.42 | GGB | 10814 | GGB | 9.86 | GGB | 1002.58 | GGB | 61.03 | GGB | 167427.39 | GGB | 135429.75 | GGB | 0 | 0 | 2743 | 3600 | 2727.1 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 173444.5 | GGB | 173446.52 | 2727.1 | 2727.1 |  |  |  | 1 | 1 |  |  |  |  | 135429.75 | 2727.1 | 135429.75 | 2727.1 | 9.1486 | [5 empty] | 102.5918 |  |  | #VALUE!
16.03.2008 12:00 | 3600 | 2 | 765.3 | GGB | 767.766 | 776.086 | 771.795 | 260.85 | GGB | 10796.5 | GGB | 9.86 | GGB | 1002.31 | GGB | 61.42 | GGB | 166675.86 | GGB | 134628.13 | GGB | 0 | 0 | 2705 | 3600 | 2689.18 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 173484.22 | GGB | 173486.24 | 2689.18 | 2689.18 |  |  |  | 1 | 1 |  |  |  |  | 134628.13 | 2689.18 | 134628.13 | 2689.18 | 9.1148 | [5 empty] | 100.5665 |  |  | #VALUE!
16.03.2008 13:00 | 3600 | 2 | 765.63 | GGB | 767.766 | 777.141 | 773.26 | 260.01 | GGB | 10765.8 | GGB | 9.86 | GGB | 1001.39 | GGB | 61.67 | GGB | 165781.29 | GGB | 133683.8 | GGB | 0 | 0 | 2670 | 3600 | 2654.58 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 173523.04 | GGB | 173525.06 | 2654.58 | 2654.58 |  |  |  | 1 | 1 |  |  |  |  | 133683.8 | 2654.58 | 133683.8 | 2654.58 | 9.1415 | [5 empty] | 98.5762 |  |  | #VALUE!
16.03.2008 14:00 | 3600 | 2 | 766.42 | GGB | 767.766 | 776.156 | 772.161 | 258.95 | GGB | 10713.9 | GGB | 9.85 | GGB | 1000.6 | GGB | 62.28 | GGB | 164634.74 | GGB | 132412.13 | GGB | 0 | 0 | 2622 | 3600 | 2606.65 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 173563.23 | GGB | 173565.25 | 2606.65 | 2606.65 |  |  |  | 1 | 1 |  |  |  |  | 132412.13 | 2606.65 | 132412.13 | 2606.65 | 8.588 | [5 empty] | 95.8756 |  |  | #VALUE!
16.03.2008 15:00 | 3600 | 2 | 767.31 | GGB | 767.766 | 776.18 | 772.161 | 257.76 | GGB | 10681.4 | GGB | 9.86 | GGB | 999.44 | GGB | 62.5 | GGB | 163758.87 | GGB | 131466.86 | GGB | 0 | 0 | 2572 | 3600 | 2557.05 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 173602.5 | GGB | 173604.52 | 2557.05 | 2557.05 |  |  |  | 1 | 1 |  |  |  |  | 131466.86 | 2557.05 | 131466.86 | 2557.05 | 8.5604 | [5 empty] | 93.3798 |  |  | #VALUE!
16.03.2008 16:00 | 3600 | 2 | 766.9 | GGB | 767.766 | 776.086 | 772.161 | 257.75 | GGB | 10683.2 | GGB | 9.86 | GGB | 998.57 | GGB | 62.4 | GGB | 163959.13 | GGB | 131552.2 | GGB | 0 | 0 | 2584 | 3600 | 2568.51 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 173641.3 | GGB | 173643.32 | 2568.51 | 2568.51 |  |  |  | 1 | 1 |  |  |  |  | 131552.2 | 2568.51 | 131552.2 | 2568.51 | 8.7086 | [5 empty] | 93.8592 |  |  | #VALUE!
16.03.2008 17:00 | 3600 | 2 | 766.49 | GGB | 767.766 | 776.156 | 772.161 | 257.75 | GGB | 10680.6 | GGB | 9.86 | GGB | 998.39 | GGB | 62.39 | GGB | 163881 | GGB | 131469.64 | GGB | 0 | 0 | 2595 | 3600 | 2579.9 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 173681.72 | GGB | 173683.75 | 2579.9 | 2579.9 |  |  |  | 1 | 1 |  |  |  |  | 131469.64 | 2579.9 | 131469.64 | 2579.9 | 8.3893 | [5 empty] | 94.2163 |  |  | #VALUE!
16.03.2008 18:00 | 3600 | 2 | 765.36 | GGB | 766.3 | 775.969 | 770.696 | 259.07 | GGB | 10700.6 | GGB | 9.85 | GGB | 998.76 | GGB | 62.1 | GGB | 164962.64 | GGB | 132502.32 | GGB | 0 | 0 | 2662 | 3600 | 2647.12 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 173722.35 | GGB | 173724.38 | 2647.12 | 2647.12 |  |  |  | 1 | 1 |  |  |  |  | 132502.32 | 2647.12 | 132502.32 | 2647.12 | 8.6328 | [5 empty] | 97.4304 |  |  | #VALUE!
16.03.2008 19:00 | 3600 | 2 | 765.07 | GGB | 766.667 | 775.711 | 771.795 | 260.11 | GGB | 10730.3 | GGB | 9.85 | GGB | 998.98 | GGB | 62.06 | GGB | 165683.36 | GGB | 133129.07 | GGB | 0 | 0 | 2681 | 3600 | 2666.09 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 173761.63 | GGB | 173763.65 | 2666.09 | 2666.09 |  |  |  | 1 | 1 |  |  |  |  | 133129.07 | 2666.09 | 133129.07 | 2666.09 | 9.0383 | [5 empty] | 98.5928 |  |  | #VALUE!
16.03.2008 20:00 | 3600 | 2 | 764.35 | GGB | 766.3 | 774.398 | 770.696 | 260.73 | GGB | 10747.3 | GGB | 9.85 | GGB | 999.57 | GGB | 61.9 | GGB | 166234.63 | GGB | 133713.88 | GGB | 0 | 0 | 2727 | 3600 | 2712 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 173801.3 | GGB | 173803.33 | 2712 | 2712 |  |  |  | 1 | 1 |  |  |  |  | 133713.88 | 2712 | 133713.88 | 2712 | 9.1389 | [5 empty] | 100.7311 |  |  | #VALUE!
16.03.2008 21:00 | 3600 | 2 | 764.23 | GGB | 766.667 | 775.453 | 770.696 | 260.59 | GGB | 10779.3 | GGB | 9.86 | GGB | 999.65 | GGB | 61.67 | GGB | 167284.35 | GGB | 134660.15 | GGB | 0 | 0 | 2742 | 3600 | 2726.97 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 173840.82 | GGB | 173842.85 | 2726.97 | 2726.97 |  |  |  | 1 | 1 |  |  |  |  | 134660.15 | 2726.97 | 134660.15 | 2726.97 | 9.2919 | [5 empty] | 102.0039 |  |  | #VALUE!
16.03.2008 22:00 | 3600 | 2 | 763.61 | GGB | 765.201 | 774.609 | 770.696 | 261.2 | GGB | 10754.5 | GGB | 9.85 | GGB | 999.51 | GGB | 61.61 | GGB | 166910.23 | GGB | 134365.37 | GGB | 0 | 0 | 2763 | 3600 | 2747.84 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 173879.75 | GGB | 173881.78 | 2747.84 | 2747.84 |  |  |  | 1 | 1 |  |  |  |  | 134365.37 | 2747.84 | 134365.37 | 2747.84 | 9.4841 | [5 empty] | 102.5596 |  |  | #VALUE!
16.03.2008 23:00 | 3600 | 2 | 763.83 | GGB | 765.201 | 773.391 | 769.597 | 261.62 | GGB | 10761.5 | GGB | 9.85 | GGB | 999.2 | GGB | 61.67 | GGB | 167135.8 | GGB | 134480.25 | GGB | 0 | 0 | 2764 | 3600 | 2748.49 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 173919.5 | GGB | 173921.53 | 2748.49 | 2748.49 |  |  |  | 1 | 1 |  |  |  |  | 134480.25 | 2748.49 | 134480.25 | 2748.49 | 9.2986 | [5 empty] | 102.6716 |  |  | #VALUE!
16.03.2008 24:00 | 3600 | 2 | 763.42 | GGB | 764.102 | 772.313 | 768.498 | 262.27 | GGB | 10778.8 | GGB | 9.85 | GGB | 998.96 | GGB | 61.48 | GGB | 167979.76 | GGB | 135202.59 | GGB | 0 | 0 | 2800 | 3600 | 2784.57 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 173959.47 | GGB | 173961.5 | 2784.57 | 2784.57 |  |  |  | 1 | 1 |  |  |  |  | 135202.59 | 2784.57 | 135202.59 | 2784.57 | 9.4191 | [5 empty] | 104.5781 |  |  | #VALUE!
17.03.2008 01:00 | 3600 | 2 | 763.06 | GGB | 764.102 | 772.336 | 768.498 | 262.44 | GGB | 10789.4 | GGB | 9.85 | GGB | 998.53 | GGB | 61.27 | GGB | 168371.48 | GGB | 135546.84 | GGB | 0 | 0 | 2809 | 3600 | 2793.53 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 173998.79 | GGB | 174000.82 | 2793.53 | 2788.1727 |  |  |  | 1 | 1 |  |  |  |  | 135546.84 | 2788.1727 | 135546.84 | 2788.1727 | 9.6116 | [5 empty] | 105.1817 | 2788.1727 |  | 104.98
17.03.2008 02:00 | 3600 | 2 | 762.64 | GGB | 765.201 | 772.383 | 768.498 | 262.66 | GGB | 10803.7 | GGB | 9.86 | GGB | 998.17 | GGB | 61 | GGB | 169020.68 | GGB | 136130.75 | GGB | 0 | 0 | 2833 | 3600 | 2817.58 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 174038.36 | GGB | 174040.39 | 2817.58 | 2776.2133 |  |  |  | 1 | 1 |  |  |  |  | 136130.75 | 2776.2133 | 136130.75 | 2776.2133 | 9.5509 | [5 empty] | 106.5442 | 2776.2133 |  | 104.98
17.03.2008 03:00 | 3600 | 2 | 762.48 | GGB | 763.004 | 771.281 | 767.033 | 262.22 | GGB | 10797.8 | GGB | 9.85 | GGB | 997.57 | GGB | 60.84 | GGB | 168857.83 | GGB | 135982.24 | GGB | 0 | 0 | 2835 | 3600 | 2819.92 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 174078.18 | GGB | 174080.21 | 2819.92 | 2779.2453 |  |  |  | 0 | 1 | [14 empty] | 106.5164 | 2779.2453 |  | 104.98
17.03.2008 04:00 | 3600 | 2 | 761.96 | GGB | 764.102 | 772.266 | 768.132 | 262.52 | GGB | 10806.2 | GGB | 9.85 | GGB | 997.15 | GGB | 60.67 | GGB | 169314.47 | GGB | 136361.73 | GGB | 0 | 0 | 2863 | 3600 | 2847.84 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 174118.17 | GGB | 174120.2 | 2847.84 | 2771.5107 |  |  |  | 1 | 1 |  |  |  |  | 136361.73 | 2771.5107 | 136361.73 | 2771.5107 | 9.4506 | [5 empty] | 107.8712 | 2771.5107 |  | 104.98
17.03.2008 05:00 | 3600 | 2 | 761.35 | GGB | 763.004 | 771.117 | 766.667 | 262.61 | GGB | 10807.8 | GGB | 9.85 | GGB | 996.76 | GGB | 60.45 | GGB | 169743.6 | GGB | 136744.05 | GGB | 0 | 0 | 2880 | 3600 | 2864.39 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 174157.64 | GGB | 174159.67 | 2864.39 | 2763.7619 |  |  |  | 0 | 1 | [14 empty] | 108.8023 | 2763.7619 |  | 104.98
17.03.2008 06:00 | 3600 | 2 | 761.82 | GGB | 763.004 | 771 | 767.766 | 262.22 | GGB | 10816.2 | GGB | 9.86 | GGB | 996.42 | GGB | 60.45 | GGB | 169606.06 | GGB | 136583.81 | GGB | 0 | 0 | 2867 | 3600 | 2851.94 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 174197.23 | GGB | 174199.26 | 2851.94 | 2767.0044 |  |  |  | 0 | 1 | [14 empty] | 108.2025 | 2767.0044 |  | 104.98
17.03.2008 07:00 | 3600 | 2 | 761.5 | GGB | 763.004 | 772.289 | 767.766 | 262.41 | GGB | 10808 | GGB | 9.85 | GGB | 996.41 | GGB | 60.42 | GGB | 169673.18 | GGB | 136651.01 | GGB | 0 | 0 | 2881 | 3600 | 2864.98 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 174237.31 | GGB | 174239.35 | 2864.98 | 2765.6437 |  |  |  | 0 | 1 | [14 empty] | 108.7507 | 2765.6437 |  | 104.98
17.03.2008 08:00 | 3600 | 2 | 761.39 | GGB | 764.102 | 772.313 | 768.132 | 262.42 | GGB | 10816 | GGB | 9.86 | GGB | 996.59 | GGB | 60.32 | GGB | 169732.6 | GGB | 136767.39 | GGB | 0 | 0 | 2884 | 3600 | 2868.35 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 174278.02 | GGB | 174280.06 | 2868.35 | 2763.2903 |  |  |  | 1 | 1 |  |  |  |  | 136767.39 | 2763.2903 | 136767.39 | 2763.2903 | 9.2834 | [5 empty] | 108.9713 | 2763.2903 |  | 104.98
17.03.2008 09:00 | 3600 | 2 | 761.78 | GGB | 764.102 | 772.219 | 768.132 | 261.85 | GGB | 10801.6 | GGB | 9.86 | GGB | 996.86 | GGB | 60.4 | GGB | 169151.62 | GGB | 136300.42 | GGB | 0 | 0 | 2872 | 3600 | 2856.3 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 174317.4 | GGB | 174319.44 | 2856.3 | 2772.7574 |  |  |  | 1 | 1 |  |  |  |  | 136300.42 | 2772.7574 | 136300.42 | 2772.7574 | 9.597 | [5 empty] | 108.143 | 2772.7574 |  | 104.98
17.03.2008 10:00 | 3600 | 2 | 763.02 | GGB | 765.201 | 773.602 | 769.597 | 260.78 | GGB | 10782.2 | GGB | 9.86 | GGB | 996.51 | GGB | 60.73 | GGB | 168013.87 | GGB | 135203.02 | GGB | 0 | 0 | 2820 | 3600 | 2804.51 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 174357.31 | GGB | 174359.35 | 2804.51 | 2795.263 |  |  |  | 1 | 1 |  |  |  |  | 135203.02 | 2795.263 | 135203.02 | 2795.263 | 9.4695 | [5 empty] | 105.3273 | 2795.263 |  | 104.98
17.03.2008 11:00 | 3600 | 2 | 764 | GGB | 765.201 | 773.719 | 769.597 | 261.11 | GGB | 10709.6 | GGB | 9.85 | GGB | 995.53 | GGB | 60.69 | GGB | 168346.17 | GGB | 135352.28 | GGB | 0 | 0 | 2735 | 3600 | 2719.32 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 174396.7 | GGB | 174398.74 | 2719.32 | 2719.32 |  |  |  | 1 | 1 |  |  |  |  | 135352.28 | 2719.32 | 135352.28 | 2719.32 | 9.3442 | [5 empty] | 102.2406 |  |  | #VALUE!
17.03.2008 12:00 | 3600 | 2 | 765.05 | GGB | 765.201 | 774.773 | 770.33 | 258.97 | GGB | 10690.5 | GGB | 9.86 | GGB | 994.61 | GGB | 61.41 | GGB | 165983.75 | GGB | 133042.1 | GGB | 0 | 0 | 2672 | 3600 | 2656.69 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 174435.48 | GGB | 174437.53 | 2656.69 | 2656.69 |  |  |  | 1 | 1 |  |  |  |  | 133042.1 | 2656.69 | 133042.1 | 2656.69 | 9.1119 | [5 empty] | 98.181 |  |  | #VALUE!
17.03.2008 13:00 | 3600 | 2 | 765.8 | GGB | 766.667 | 775.758 | 771.429 | 257.02 | GGB | 10642.5 | GGB | 9.86 | GGB | 993.84 | GGB | 62.2 | GGB | 164074.66 | GGB | 131101.97 | GGB | 0 | 0 | 2623 | 3600 | 2607.69 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 174475.2 | GGB | 174477.25 | 2607.69 | 2607.69 |  |  |  | 1 | 1 |  |  |  |  | 131101.97 | 2607.69 | 131101.97 | 2607.69 | 8.6071 | [5 empty] | 94.9648 |  |  | #VALUE!
17.03.2008 14:00 | 3600 | 2 | 765.89 | GGB | 766.667 | 775.805 | 771.429 | 256.67 | GGB | 10625.6 | GGB | 9.85 | GGB | 993.47 | GGB | 62.45 | GGB | 163557.5 | GGB | 130544.45 | GGB | 0 | 0 | 2611 | 3600 | 2595.93 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 174514.48 | GGB | 174516.54 | 2595.93 | 2595.93 |  |  |  | 1 | 1 |  |  |  |  | 130544.45 | 2595.93 | 130544.45 | 2595.93 | 8.6252 | [5 empty] | 94.1345 |  |  | #VALUE!
17.03.2008 15:00 | 3600 | 2 | 765.11 | GGB | 766.667 | 774.82 | 770.696 | 257.66 | GGB | 10634 | GGB | 9.85 | GGB | 992.97 | GGB | 62.23 | GGB | 164062.56 | GGB | 130963.35 | GGB | 0 | 0 | 2643 | 3600 | 2627.4 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 174553.03 | GGB | 174555.08 | 2627.4 | 2627.4 |  |  |  | 1 | 1 |  |  |  |  | 130963.35 | 2627.4 | 130963.35 | 2627.4 | 8.9282 | [5 empty] | 95.5814 |  |  | #VALUE!
17.03.2008 16:00 | 3600 | 2 | 764.6 | GGB | 765.201 | 773.695 | 769.597 | 258.51 | GGB | 10660.6 | GGB | 9.85 | GGB | 993.03 | GGB | 62.22 | GGB | 164682.05 | GGB | 131470.77 | GGB | 0 | 0 | 2683 | 3600 | 2667.66 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 174592.93 | GGB | 174594.98 | 2667.66 | 2667.66 |  |  |  | 1 | 1 |  |  |  |  | 131470.77 | 2667.66 | 131470.77 | 2667.66 | 8.79 | [5 empty] | 97.422 |  |  | #VALUE!
17.03.2008 17:00 | 3600 | 2 | 764.38 | GGB | 765.201 | 773.719 | 769.597 | 258.57 | GGB | 10661.6 | GGB | 9.85 | GGB | 992.56 | GGB | 62.29 | GGB | 165046.26 | GGB | 131674.91 | GGB | 0 | 0 | 2704 | 3600 | 2688.42 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 174632.42 | GGB | 174634.47 | 2688.42 | 2688.42 |  |  |  | 1 | 1 |  |  |  |  | 131674.91 | 2688.42 | 131674.91 | 2688.42 | 8.9642 | [5 empty] | 98.3326 |  |  | #VALUE!
17.03.2008 18:00 | 3600 | 2 | 763.79 | GGB | 765.201 | 773.719 | 770.696 | 259.15 | GGB | 10685.5 | GGB | 9.85 | GGB | 992.28 | GGB | 61.82 | GGB | 165831.9 | GGB | 132445.23 | GGB | 0 | 0 | 2732 | 3600 | 2716.47 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 174670.94 | GGB | 174672.99 | 2716.47 | 2716.47 |  |  |  | 1 | 1 |  |  |  |  | 132445.23 | 2716.47 | 132445.23 | 2716.47 | 9.3402 | [5 empty] | 99.9399 |  |  | #VALUE!
17.03.2008 19:00 | 3600 | 2 | 763.37 | GGB | 765.201 | 773.555 | 769.597 | 259.6 | GGB | 10708.1 | GGB | 9.85 | GGB | 992.22 | GGB | 61.35 | GGB | 166225.82 | GGB | 132939.18 | GGB | 0 | 0 | 2752 | 3600 | 2736.34 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 174710.77 | GGB | 174712.82 | 2736.34 | 2736.34 |  |  |  | 1 | 1 |  |  |  |  | 132939.18 | 2736.34 | 132939.18 | 2736.34 | 9.133 | [5 empty] | 101.0463 |  |  | #VALUE!
17.03.2008 20:00 | 3600 | 2 | 761.79 | GGB | 761.538 | 770.461 | 767.033 | 259.97 | GGB | 10744.9 | GGB | 9.85 | GGB | 992.87 | GGB | 60.64 | GGB | 167937.95 | GGB | 134686 | GGB | 0 | 0 | 2815 | 3600 | 2799.33 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 174750.32 | GGB | 174752.37 | 2799.33 | 2799.33 |  |  |  | 0 | 1 | [14 empty] | 104.7307 |  |  | #VALUE!
17.03.2008 21:00 | 3600 | 2 | 761.76 | GGB | 762.637 | 771.703 | 767.033 | 261.68 | GGB | 10767 | GGB | 9.86 | GGB | 992.88 | GGB | 60.51 | GGB | 168591.55 | GGB | 135261.28 | GGB | 0 | 0 | 2850 | 3600 | 2834.24 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 174789.56 | GGB | 174791.61 | 2834.24 | 2794.059 |  |  |  | 0 | 1 | [14 empty] | 106.4897 | 2794.059 |  | 104.98
17.03.2008 22:00 | 3600 | 2 | 761.93 | GGB | 764.102 | 772.031 | 768.498 | 260.91 | GGB | 10763.5 | GGB | 9.86 | GGB | 992.8 | GGB | 60.7 | GGB | 168021.57 | GGB | 134716.98 | GGB | 0 | 0 | 2836 | 3600 | 2820.9 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 174829.11 | GGB | 174831.15 | 2820.9 | 2805.3479 |  |  |  | 1 | 1 |  |  |  |  | 134716.98 | 2805.3479 | 134716.98 | 2805.3479 | 9.5581 | [5 empty] | 105.562 | 2805.3479 |  | 104.98
17.03.2008 23:00 | 3600 | 2 | 762.34 | GGB | 765.201 | 773.156 | 768.864 | 259.8 | GGB | 10738.3 | GGB | 9.86 | GGB | 992.88 | GGB | 60.73 | GGB | 166894.83 | GGB | 133813.22 | GGB | 0 | 0 | 2811 | 3600 | 2795.13 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 174867.87 | GGB | 174869.92 | 2795.13 | 2795.13 |  |  |  | 1 | 1 |  |  |  |  | 133813.22 | 2795.13 | 133813.22 | 2795.13 | 9.6473 | [5 empty] | 103.8959 |  |  | #VALUE!
17.03.2008 24:00 | 3600 | 2 | 762.71 | GGB | 764.102 | 772.172 | 768.132 | 259.47 | GGB | 10726.6 | GGB | 9.86 | GGB | 992.11 | GGB | 60.8 | GGB | 166855.22 | GGB | 133648.62 | GGB | 0 | 0 | 2790 | 3600 | 2774.68 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 174907.02 | GGB | 174909.07 | 2774.68 | 2774.68 |  |  |  | 1 | 1 |  |  |  |  | 133648.62 | 2774.68 | 133648.62 | 2774.68 | 9.4721 | [5 empty] | 103.0089 |  |  | #VALUE!
18.03.2008 01:00 | 3600 | 2 | 762 | GGB | 762.637 | 771.07 | 767.766 | 260.16 | GGB | 10730.9 | GGB | 9.85 | GGB | 991.78 | GGB | 60.58 | GGB | 167450.5 | GGB | 134170.6 | GGB | 0 | 0 | 2819 | 3600 | 2803.65 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 174946.7 | GGB | 174948.75 | 2803.65 | 2803.65 |  |  |  | 0 | 1 | [14 empty] | 104.4909 |  |  | #VALUE!
18.03.2008 02:00 | 3600 | 2 | 760.54 | GGB | 761.538 | 770.156 | 766.3 | 262.17 | GGB | 10794.6 | GGB | 9.85 | GGB | 991.93 | GGB | 59.46 | GGB | 169764.51 | GGB | 136501.89 | GGB | 0 | 0 | 2920 | 3600 | 2904.52 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 174986.48 | GGB | 174988.53 | 2904.52 | 2768.665 |  |  |  | 0 | 1 | [14 empty] | 110.1312 | 2768.665 |  | 104.98
18.03.2008 03:00 | 3600 | 2 | 760.23 | GGB | 761.538 | 769.711 | 765.934 | 262.88 | GGB | 10833 | GGB | 9.85 | GGB | 992.25 | GGB | 58.73 | GGB | 171049.7 | GGB | 137884.37 | GGB | 0 | 0 | 2955 | 3600 | 2939.5 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 175026.07 | GGB | 175028.12 | 2939.5 | 2740.9053 |  |  |  | 0 | 1 | [14 empty] | 112.5864 | 2740.9053 |  | 104.98
18.03.2008 04:00 | 3600 | 2 | 760.27 | GGB | 759.341 | 767.742 | 763.004 | 263.03 | GGB | 10834.2 | GGB | 9.85 | GGB | 992.64 | GGB | 59.21 | GGB | 170982.58 | GGB | 137684.28 | GGB | 0 | 0 | 2953 | 3600 | 2937.53 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 175065.4 | GGB | 175067.45 | 2937.53 | 2744.8885 |  |  |  | 0 | 1 | [14 empty] | 112.3477 | 2744.8885 |  | 104.98
18.03.2008 05:00 | 3600 | 2 | 760.3 | GGB | 761.538 | 769.711 | 765.201 | 263.35 | GGB | 10840.9 | GGB | 9.86 | GGB | 992.22 | GGB | 59.25 | GGB | 171247.76 | GGB | 137822.98 | GGB | 0 | 0 | 2960 | 3600 | 2944.43 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 175104.79 | GGB | 175106.84 | 2944.43 | 2742.1262 |  |  |  | 0 | 1 | [14 empty] | 112.725 | 2742.1262 |  | 104.98
18.03.2008 06:00 | 3600 | 2 | 760.1 | GGB | 762.637 | 770.953 | 766.667 | 263.39 | GGB | 10852.7 | GGB | 9.86 | GGB | 991.85 | GGB | 59.02 | GGB | 171807.84 | GGB | 138318.25 | GGB | 0 | 0 | 2967 | 3600 | 2951.23 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 175144.44 | GGB | 175146.5 | 2951.23 | 2732.3076 |  |  |  | 0 | 1 | [14 empty] | 113.3914 | 2732.3076 |  | 104.98
18.03.2008 07:00 | 3600 | 2 | 759.76 | GGB | 760.44 | 768.539 | 765.201 | 263.65 | GGB | 10830.9 | GGB | 9.85 | GGB | 991.91 | GGB | 59.26 | GGB | 171680.2 | GGB | 138121.85 | GGB | 0 | 0 | 2987 | 3600 | 2971.26 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 175184.61 | GGB | 175186.66 | 2971.26 | 2736.1927 |  |  |  | 0 | 1 | [14 empty] | 113.9989 | 2736.1927 |  | 104.98
18.03.2008 08:00 | 3600 | 2 | 759.6 | GGB | 762.637 | 770.461 | 766.3 | 263.7 | GGB | 10862.4 | GGB | 9.85 | GGB | 991.83 | GGB | 59.03 | GGB | 172432.83 | GGB | 138812.47 | GGB | 0 | 0 | 3000 | 3600 | 2984.27 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 175224.51 | GGB | 175226.56 | 2984.27 | 2722.5796 |  |  |  | 0 | 1 | [14 empty] | 115.0705 | 2722.5796 |  | 104.98
18.03.2008 09:00 | 3600 | 2 | 760.33 | GGB | 763.004 | 772.078 | 767.033 | 263.15 | GGB | 10879 | GGB | 9.86 | GGB | 992.02 | GGB | 59.05 | GGB | 172154.44 | GGB | 138607.91 | GGB | 0 | 0 | 2967 | 3600 | 2951.81 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 175264.75 | GGB | 175266.8 | 2951.81 | 2726.5976 |  |  |  | 0 | 1 | [14 empty] | 113.6512 | 2726.5976 |  | 104.98
18.03.2008 10:00 | 3600 | 2 | 760.45 | GGB | 762.637 | 771.328 | 767.033 | 262.59 | GGB | 10852.1 | GGB | 9.86 | GGB | 991.8 | GGB | 59.11 | GGB | 171310.48 | GGB | 137874.79 | GGB | 0 | 0 | 2946 | 3600 | 2930.33 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 175303.52 | GGB | 175305.57 | 2930.33 | 2741.0957 |  |  |  | 0 | 1 | [14 empty] | 112.2274 | 2741.0957 |  | 104.98
18.03.2008 11:00 | 3600 | 2 | 760.35 | GGB | 762.637 | 770.32 | 767.033 | 261.87 | GGB | 10833.1 | GGB | 9.86 | GGB | 991.87 | GGB | 59.49 | GGB | 170517.14 | GGB | 137086.21 | GGB | 0 | 0 | 2921 | 3600 | 2904.94 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 175343.43 | GGB | 175345.49 | 2904.94 | 2756.8637 |  |  |  | 0 | 1 | [14 empty] | 110.6187 | 2756.8637 |  | 104.98
18.03.2008 12:00 | 3600 | 2 | 760.72 | GGB | 763.004 | 771.188 | 768.132 | 260.61 | GGB | 10809.6 | GGB | 9.86 | GGB | 991.9 | GGB | 59.82 | GGB | 169294.67 | GGB | 135975.18 | GGB | 0 | 0 | 2878 | 3600 | 2861.96 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 175383.98 | GGB | 175386.04 | 2861.96 | 2779.3896 |  |  |  | 0 | 1 | [14 empty] | 108.0988 | 2779.3896 |  | 104.98
18.03.2008 13:00 | 3600 | 2 | 761.17 | GGB | 764.102 | 772.242 | 768.498 | 259.93 | GGB | 10773.2 | GGB | 9.86 | GGB | 991.92 | GGB | 60 | GGB | 168312.06 | GGB | 135112.94 | GGB | 0 | 0 | 2842 | 3600 | 2826.25 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 175422.59 | GGB | 175424.65 | 2826.25 | 2797.1266 |  |  |  | 1 | 1 |  |  |  |  | 135112.94 | 2797.1266 | 135112.94 | 2797.1266 | 9.7883 | [5 empty] | 106.073 | 2797.1266 |  | 104.98
18.03.2008 14:00 | 3600 | 2 | 760.89 | GGB | 762.637 | 770.672 | 768.132 | 260.58 | GGB | 10773.3 | GGB | 9.85 | GGB | 991.78 | GGB | 59.81 | GGB | 168692.78 | GGB | 135479.67 | GGB | 0 | 0 | 2861 | 3600 | 2845.58 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 175462.37 | GGB | 175464.43 | 2845.58 | 2789.5551 |  |  |  | 0 | 1 | [14 empty] | 107.0884 | 2789.5551 |  | 104.98
18.03.2008 15:00 | 3600 | 2 | 760.22 | GGB | 761.538 | 769.828 | 767.033 | 261.19 | GGB | 10800.2 | GGB | 9.85 | GGB | 991.83 | GGB | 59.43 | GGB | 169500.43 | GGB | 136287.14 | GGB | 0 | 0 | 2905 | 3600 | 2889.71 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 175503.34 | GGB | 175505.4 | 2889.71 | 2773.0276 |  |  |  | 0 | 1 | [14 empty] | 109.3973 | 2773.0276 |  | 104.98
18.03.2008 16:00 | 3600 | 2 | 760.4 | GGB | 761.538 | 769.969 | 765.934 | 261.17 | GGB | 10800.4 | GGB | 9.86 | GGB | 991.15 | GGB | 59.53 | GGB | 169526.84 | GGB | 136177.18 | GGB | 0 | 0 | 2896 | 3600 | 2880.5 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 175542.15 | GGB | 175544.21 | 2880.5 | 2775.2668 |  |  |  | 0 | 1 | [14 empty] | 108.9607 | 2775.2668 |  | 104.98
18.03.2008 17:00 | 3600 | 2 | 760.11 | GGB | 761.538 | 769.734 | 765.934 | 261.41 | GGB | 10808.6 | GGB | 9.86 | GGB | 991.2 | GGB | 59.48 | GGB | 170005.48 | GGB | 136588.47 | GGB | 0 | 0 | 2924 | 3600 | 2907.95 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 175581.99 | GGB | 175584.05 | 2907.95 | 2766.91 |  |  |  | 0 | 1 | [14 empty] | 110.3312 | 2766.91 |  | 104.98
18.03.2008 18:00 | 3600 | 2 | 760.44 | GGB | 764.102 | 772.266 | 768.498 | 261.02 | GGB | 10801 | GGB | 9.86 | GGB | 991.01 | GGB | 59.7 | GGB | 169533.44 | GGB | 136092.87 | GGB | 0 | 0 | 2901 | 3600 | 2885.5 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 175621.97 | GGB | 175624.03 | 2885.5 | 2776.986 |  |  |  | 1 | 1 |  |  |  |  | 136092.87 | 2776.986 | 136092.87 | 2776.986 | 9.4529 | [5 empty] | 109.0822 | 2776.986 |  | 104.98
18.03.2008 19:00 | 3600 | 2 | 760.06 | GGB | 761.538 | 770.109 | 765.934 | 261.67 | GGB | 10804.6 | GGB | 9.85 | GGB | 991.18 | GGB | 59.51 | GGB | 170056.1 | GGB | 136611.94 | GGB | 0 | 0 | 2925 | 3600 | 2909.88 | GGB | 100 | GGB | 38.25 | GGB | 38.25 | GGB | 175660.22 | GGB | 175662.28 | 2909.88 | 2766.4346 |  |  |  | 0 | 1 | [14 empty] | 110.4234 | 2766.4346 |  | 104.98
18.03.2008 20:00 | 3600 | 2 | 759.79 | GGB | 760.44 | 769.125 | 765.934 | 261.83 | GGB | 10816.2 | GGB | 9.85 | GGB | 991.18 | GGB | 59.46 | GGB | 170387.3 | GGB | 136899.33 | GGB | 0 | 0 | 2940 | 3600 | 2924.24 | GGB | 100 | GGB | 41.08 | GGB | 41.08 | GGB | 175701.3 | GGB | 175703.36 | 2924.24 | 2760.6271 |  |  |  | 0 | 1 | [14 empty] | 111.2018 | 2760.6271 |  | 104.98
18.03.2008 21:00 | 3600 | 2 | 759.78 | GGB | 762.637 | 769.594 | 765.934 | 262.36 | GGB | 10844.7 | GGB | 9.85 | GGB | 991.79 | GGB | 59.3 | GGB | 171233.46 | GGB | 137731.96 | GGB | 0 | 0 | 2955 | 3600 | 2939.7 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 175740.99 | GGB | 175743.05 | 2939.7 | 2743.9383 |  |  |  | 0 | 1 | [14 empty] | 112.4696 | 2743.9383 |  | 104.98
18.03.2008 22:00 | 3600 | 2 | 760.13 | GGB | 762.637 | 770.859 | 767.033 | 262.98 | GGB | 10816.3 | GGB | 9.86 | GGB | 991.81 | GGB | 59.47 | GGB | 170572.16 | GGB | 137129.73 | GGB | 0 | 0 | 2947 | 3600 | 2931.36 | GGB | 100 | GGB | 38.13 | GGB | 38.13 | GGB | 175779.12 | GGB | 175781.18 | 2931.36 | 2755.9888 |  |  |  | 0 | 1 | [14 empty] | 111.6602 | 2755.9888 |  | 104.98
18.03.2008 23:00 | 3600 | 2 | 759.7 | GGB | 761.538 | 769.102 | 765.934 | 262.76 | GGB | 10795.4 | GGB | 9.85 | GGB | 991.82 | GGB | 59.66 | GGB | 170308.08 | GGB | 136843.3 | GGB | 0 | 0 | 2951 | 3600 | 2935.68 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 175819.52 | GGB | 175821.58 | 2935.68 | 2761.7574 |  |  |  | 0 | 1 | [14 empty] | 111.5911 | 2761.7574 |  | 104.98
18.03.2008 24:00 | 3600 | 2 | 759.99 | GGB | 762.637 | 769.945 | 767.033 | 264.48 | GGB | 10816.7 | GGB | 9.85 | GGB | 992.3 | GGB | 59.66 | GGB | 171420.52 | GGB | 137802.77 | GGB | 0 | 0 | 2953 | 3600 | 2937.61 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 175859.32 | GGB | 175861.39 | 2937.61 | 2742.5283 |  |  |  | 0 | 1 | [14 empty] | 112.4474 | 2742.5283 |  | 104.98
19.03.2008 01:00 | 3600 | 2 | 760.75 | GGB | 764.102 | 770.813 | 768.132 | 263.72 | GGB | 10824.1 | GGB | 9.86 | GGB | 992.46 | GGB | 59.66 | GGB | 170561.15 | GGB | 137133.3 | GGB | 0 | 0 | 2915 | 3600 | 2899.03 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 175897.78 | GGB | 175899.85 | 2899.03 | 2755.9171 |  |  |  | 1 | 1 |  |  |  |  | 137133.3 | 2755.9171 | 137133.3 | 2755.9171 | 9.8265 | [5 empty] | 110.4315 | 2755.9171 |  | 104.98
19.03.2008 02:00 | 3600 | 2 | 761.2 | GGB | 762.637 | 770.766 | 768.132 | 263.06 | GGB | 10797.4 | GGB | 9.86 | GGB | 992.63 | GGB | 60.04 | GGB | 169524.64 | GGB | 136168.97 | GGB | 0 | 0 | 2883 | 3600 | 2867.44 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 175938 | GGB | 175940.06 | 2867.44 | 2775.4341 |  |  |  | 0 | 1 | [14 empty] | 108.4601 | 2775.4341 |  | 104.98
19.03.2008 03:00 | 3600 | 2 | 761.13 | GGB | 762.637 | 770.719 | 767.033 | 262.37 | GGB | 10781.6 | GGB | 9.85 | GGB | 992.57 | GGB | 60.29 | GGB | 168974.47 | GGB | 135615.41 | GGB | 0 | 0 | 2870 | 3600 | 2854.91 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 175978 | GGB | 175980.07 | 2854.91 | 2786.7629 |  |  |  | 0 | 1 | [14 empty] | 107.5472 | 2786.7629 |  | 104.98
19.03.2008 04:00 | 3600 | 2 | 761.07 | GGB | 764.102 | 772.219 | 768.132 | 262.54 | GGB | 10789.6 | GGB | 9.86 | GGB | 992.97 | GGB | 60.11 | GGB | 169128.51 | GGB | 135867.01 | GGB | 0 | 0 | 2880 | 3600 | 2864.27 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 176016.73 | GGB | 176018.8 | 2864.27 | 2781.6024 |  |  |  | 1 | 1 |  |  |  |  | 135867.01 | 2781.6024 | 135867.01 | 2781.6024 | 9.758 | [5 empty] | 108.0999 | 2781.6024 |  | 104.98
19.03.2008 05:00 | 3600 | 2 | 760.84 | GGB | 764.102 | 771.469 | 768.132 | 262.96 | GGB | 10796.6 | GGB | 9.85 | GGB | 993.22 | GGB | 60.08 | GGB | 169590.66 | GGB | 136286.03 | GGB | 0 | 0 | 2899 | 3600 | 2883.14 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 176056.82 | GGB | 176058.88 | 2883.14 | 2773.0502 |  |  |  | 1 | 1 |  |  |  |  | 136286.03 | 2773.0502 | 136286.03 | 2773.0502 | 9.4293 | [5 empty] | 109.1477 | 2773.0502 |  | 104.98
19.03.2008 06:00 | 3600 | 2 | 760.71 | GGB | 764.102 | 772.172 | 768.132 | 263.44 | GGB | 10809.1 | GGB | 9.85 | GGB | 993.45 | GGB | 59.98 | GGB | 170103.41 | GGB | 136771.03 | GGB | 0 | 0 | 2911 | 3600 | 2895.78 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 176096.74 | GGB | 176098.8 | 2895.78 | 2763.2167 |  |  |  | 1 | 1 |  |  |  |  | 136771.03 | 2763.2167 | 136771.03 | 2763.2167 | 9.4671 | [5 empty] | 110.0163 | 2763.2167 |  | 104.98
19.03.2008 07:00 | 3600 | 2 | 760.54 | GGB | 762.637 | 771.211 | 767.033 | 263.81 | GGB | 10821 | GGB | 9.85 | GGB | 993.66 | GGB | 59.66 | GGB | 170446.72 | GGB | 137206.98 | GGB | 0 | 0 | 2927 | 3600 | 2910.95 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 176135.25 | GGB | 176137.31 | 2910.95 | 2754.4371 |  |  |  | 0 | 1 | [14 empty] | 110.9452 | 2754.4371 |  | 104.98
19.03.2008 08:00 | 3600 | 2 | 761.23 | GGB | 763.004 | 771.023 | 768.132 | 263.12 | GGB | 10814.9 | GGB | 9.86 | GGB | 994.04 | GGB | 59.74 | GGB | 169606.06 | GGB | 136550.35 | GGB | 0 | 0 | 2891 | 3600 | 2874.98 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 176175.33 | GGB | 176177.4 | 2874.98 | 2767.6824 |  |  |  | 0 | 1 | [14 empty] | 109.0499 | 2767.6824 |  | 104.98
19.03.2008 09:00 | 3600 | 2 | 761.38 | GGB | 764.102 | 772.383 | 767.033 | 262.56 | GGB | 10789.6 | GGB | 9.85 | GGB | 994.35 | GGB | 60.15 | GGB | 168943.66 | GGB | 135889.93 | GGB | 0 | 0 | 2873 | 3600 | 2857.49 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 176215.17 | GGB | 176217.24 | 2857.49 | 2781.1332 |  |  |  | 1 | 1 |  |  |  |  | 135889.93 | 2781.1332 | 135889.93 | 2781.1332 | 9.4861 | [5 empty] | 107.8623 | 2781.1332 |  | 104.98
19.03.2008 10:00 | 3600 | 2 | 761.96 | GGB | 763.004 | 771.023 | 767.033 | 262.08 | GGB | 10790.2 | GGB | 9.86 | GGB | 995.23 | GGB | 60.38 | GGB | 168390.19 | GGB | 135474.72 | GGB | 0 | 0 | 2842 | 3600 | 2826.32 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 176253.78 | GGB | 176255.85 | 2826.32 | 2789.657 |  |  |  | 0 | 1 | [14 empty] | 106.3597 | 2789.657 |  | 104.98
19.03.2008 11:00 | 3600 | 2 | 761.4 | GGB | 764.102 | 772.172 | 767.033 | 262.21 | GGB | 10780.2 | GGB | 9.85 | GGB | 995.58 | GGB | 60.36 | GGB | 168428.7 | GGB | 135561.18 | GGB | 0 | 0 | 2846 | 3600 | 2830.6 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 176294.1 | GGB | 176296.17 | 2830.6 | 2787.8778 |  |  |  | 1 | 1 |  |  |  |  | 135561.18 | 2787.8778 | 135561.18 | 2787.8778 | 9.3732 | [5 empty] | 106.5887 | 2787.8778 |  | 104.98
19.03.2008 12:00 | 3600 | 2 | 762.01 | GGB | 765.201 | 773.648 | 769.597 | 262.66 | GGB | 10808 | GGB | 9.86 | GGB | 996.07 | GGB | 60.22 | GGB | 168950.26 | GGB | 136102.73 | GGB | 0 | 0 | 2836 | 3600 | 2820.86 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 176334.03 | GGB | 176336.1 | 2820.86 | 2776.7849 |  |  |  | 1 | 1 |  |  |  |  | 136102.73 | 2776.7849 | 136102.73 | 2776.7849 | 9.4648 | [5 empty] | 106.6463 | 2776.7849 |  | 104.98
19.03.2008 13:00 | 3600 | 2 | 762.13 | GGB | 764.102 | 772.547 | 768.498 | 262.12 | GGB | 10781 | GGB | 9.85 | GGB | 996.34 | GGB | 60.37 | GGB | 168436.4 | GGB | 135665.46 | GGB | 0 | 0 | 2834 | 3600 | 2818.6 | GGB | 100 | GGB | 38.62 | GGB | 38.62 | GGB | 176372.65 | GGB | 176374.72 | 2818.6 | 2785.7349 |  |  |  | 1 | 1 |  |  |  |  | 135665.46 | 2785.7349 | 135665.46 | 2785.7349 | 9.7858 | [5 empty] | 106.2185 | 2785.7349 |  | 104.98
19.03.2008 14:00 | 3600 | 2 | 762.15 | GGB | 764.102 | 772.477 | 768.498 | 262.38 | GGB | 10779.3 | GGB | 9.85 | GGB | 996.5 | GGB | 60.53 | GGB | 168317.57 | GGB | 135528.31 | GGB | 0 | 0 | 2827 | 3600 | 2811.26 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 176412.77 | GGB | 176414.84 | 2811.26 | 2788.5539 |  |  |  | 1 | 1 |  |  |  |  | 135528.31 | 2788.5539 | 135528.31 | 2788.5539 | 9.4199 | [5 empty] | 105.8348 | 2788.5539 |  | 104.98
19.03.2008 15:00 | 3600 | 2 | 763.24 | GGB | 765.201 | 773.742 | 770.696 | 262.26 | GGB | 10780.7 | GGB | 9.86 | GGB | 996.87 | GGB | 60.77 | GGB | 167994.07 | GGB | 135219.02 | GGB | 0 | 0 | 2788 | 3600 | 2772.91 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 176452.44 | GGB | 176454.52 | 2772.91 | 2772.91 |  |  |  | 1 | 1 |  |  |  |  | 135219.02 | 2772.91 | 135219.02 | 2772.91 | 9.4493 | [5 empty] | 104.1528 |  |  | #VALUE!
19.03.2008 16:00 | 3600 | 2 | 763.5 | GGB | 764.102 | 772.758 | 769.597 | 262.24 | GGB | 10723.2 | GGB | 9.85 | GGB | 996.75 | GGB | 60.67 | GGB | 168304.36 | GGB | 135493.61 | GGB | 0 | 0 | 2752 | 3600 | 2736.3 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 176491.53 | GGB | 176493.61 | 2736.3 | 2736.3 |  |  |  | 1 | 1 |  |  |  |  | 135493.61 | 2736.3 | 135493.61 | 2736.3 | 9.4846 | [5 empty] | 102.9864 |  |  | #VALUE!
19.03.2008 17:00 | 3600 | 2 | 764.88 | GGB | 766.667 | 774.961 | 770.696 | 262.37 | GGB | 10716 | GGB | 9.86 | GGB | 996.38 | GGB | 60.74 | GGB | 168740.1 | GGB | 135765.55 | GGB | 0 | 0 | 2671 | 3600 | 2655.28 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 176531.12 | GGB | 176533.2 | 2655.28 | 2655.28 |  |  |  | 1 | 1 |  |  |  |  | 135765.55 | 2655.28 | 135765.55 | 2655.28 | 9.1057 | [5 empty] | 100.1377 |  |  | #VALUE!
19.03.2008 18:00 | 3600 | 2 | 764.1 | GGB | 765.201 | 772.852 | 769.597 | 261.14 | GGB | 10723 | GGB | 9.85 | GGB | 996.41 | GGB | 61.01 | GGB | 167040.07 | GGB | 134292.9 | GGB | 0 | 0 | 2712 | 3600 | 2696.18 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 176569.76 | GGB | 176571.85 | 2696.18 | 2696.18 |  |  |  | 1 | 1 |  |  |  |  | 134292.9 | 2696.18 | 134292.9 | 2696.18 | 9.3681 | [5 empty] | 100.5772 |  |  | #VALUE!
19.03.2008 19:00 | 3600 | 2 | 763.65 | GGB | 763.004 | 771.117 | 767.033 | 261.63 | GGB | 10749.5 | GGB | 9.85 | GGB | 997.13 | GGB | 61.37 | GGB | 167131.4 | GGB | 134318.87 | GGB | 0 | 0 | 2748 | 3600 | 2732.34 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 176609.02 | GGB | 176611.11 | 2732.34 | 2732.34 |  |  |  | 0 | 1 | [14 empty] | 101.9458 |  |  | #VALUE!
19.03.2008 20:00 | 3600 | 2 | 763.08 | GGB | 767.766 | 776.367 | 771.795 | 262.56 | GGB | 10778.3 | GGB | 9.86 | GGB | 997.97 | GGB | 61.21 | GGB | 167918.14 | GGB | 135131.14 | GGB | 0 | 0 | 2796 | 3600 | 2780.5 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 176649.18 | GGB | 176651.27 | 2780.5 | 2780.5 |  |  |  | 1 | 1 |  |  |  |  | 135131.14 | 2780.5 | 135131.14 | 2780.5 | 9.3559 | [5 empty] | 104.37 |  |  | #VALUE!
19.03.2008 21:00 | 3600 | 2 | 762.39 | GGB | 764.102 | 772.336 | 768.864 | 263.19 | GGB | 10771.2 | GGB | 9.84 | GGB | 998.73 | GGB | 61.2 | GGB | 168288.96 | GGB | 135535.99 | GGB | 0 | 0 | 2827 | 3600 | 2811.31 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 176687.85 | GGB | 176689.94 | 2811.31 | 2788.3959 |  |  |  | 1 | 1 |  |  |  |  | 135535.99 | 2788.3959 | 135535.99 | 2788.3959 | 9.7732 | [5 empty] | 105.8427 | 2788.3959 |  | 104.98
19.03.2008 22:00 | 3600 | 2 | 762.83 | GGB | 765.201 | 773.859 | 769.963 | 262.79 | GGB | 10820.8 | GGB | 9.86 | GGB | 998.78 | GGB | 61.01 | GGB | 169058.09 | GGB | 136239.67 | GGB | 0 | 0 | 2821 | 3600 | 2805.09 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 176727.53 | GGB | 176729.62 | 2805.09 | 2773.9938 |  |  |  | 1 | 1 |  |  |  |  | 136239.67 | 2773.9938 | 136239.67 | 2773.9938 | 9.5244 | [5 empty] | 106.1568 | 2773.9938 |  | 104.98
19.03.2008 23:00 | 3600 | 2 | 761.85 | GGB | 764.102 | 772.523 | 768.864 | 263.72 | GGB | 10804.8 | GGB | 9.85 | GGB | 998.95 | GGB | 60.88 | GGB | 169090 | GGB | 136342.3 | GGB | 0 | 0 | 2867 | 3600 | 2851.79 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 176767.59 | GGB | 176769.68 | 2851.79 | 2771.9057 |  |  |  | 1 | 1 |  |  |  |  | 136342.3 | 2771.9057 | 136342.3 | 2771.9057 | 9.434 | [5 empty] | 108.0054 | 2771.9057 |  | 104.98
19.03.2008 24:00 | 3600 | 2 | 762.18 | GGB | 763.004 | 771.445 | 766.667 | 263.9 | GGB | 10821.2 | GGB | 9.86 | GGB | 999.41 | GGB | 60.86 | GGB | 169302.37 | GGB | 136581.98 | GGB | 0 | 0 | 2858 | 3600 | 2842.1 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 176807.01 | GGB | 176809.11 | 2842.1 | 2767.0415 |  |  |  | 0 | 1 | [14 empty] | 107.8277 | 2767.0415 |  | 104.98
20.03.2008 01:00 | 3600 | 2 | 762.02 | GGB | 763.004 | 771.422 | 766.667 | 264.2 | GGB | 10829.8 | GGB | 9.85 | GGB | 999.34 | GGB | 60.7 | GGB | 169598.36 | GGB | 136878.7 | GGB | 0 | 0 | 2865 | 3600 | 2849.29 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 176846.6 | GGB | 176848.7 | 2849.29 | 2761.0432 |  |  |  | 0 | 1 | [14 empty] | 108.3353 | 2761.0432 |  | 104.98
20.03.2008 02:00 | 3600 | 2 | 762.04 | GGB | 764.102 | 772.664 | 767.766 | 263.99 | GGB | 10834 | GGB | 9.86 | GGB | 999.79 | GGB | 60.73 | GGB | 169729.3 | GGB | 137031.31 | GGB | 0 | 0 | 2869 | 3600 | 2853.72 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 176886.98 | GGB | 176889.08 | 2853.72 | 2757.9682 |  |  |  | 1 | 1 |  |  |  |  | 137031.31 | 2757.9682 | 137031.31 | 2757.9682 | 9.3593 | [5 empty] | 108.6247 | 2757.9682 |  | 104.98
20.03.2008 03:00 | 3600 | 2 | 761.49 | GGB | 763.004 | 772.711 | 767.766 | 264.62 | GGB | 10835.7 | GGB | 9.85 | GGB | 999.79 | GGB | 60.64 | GGB | 170336.69 | GGB | 137558.23 | GGB | 0 | 0 | 2894 | 3600 | 2878.53 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 176926.63 | GGB | 176928.73 | 2878.53 | 2747.4038 |  |  |  | 0 | 1 | [14 empty] | 109.9904 | 2747.4038 |  | 104.98
20.03.2008 04:00 | 3600 | 2 | 761.84 | GGB | 761.538 | 770.648 | 766.667 | 264.95 | GGB | 10846.8 | GGB | 9.85 | GGB | 999.94 | GGB | 60.58 | GGB | 170412.61 | GGB | 137666.91 | GGB | 0 | 0 | 2887 | 3600 | 2871.52 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 176966.23 | GGB | 176968.34 | 2871.52 | 2745.2349 |  |  |  | 0 | 1 | [14 empty] | 109.8092 | 2745.2349 |  | 104.98
20.03.2008 05:00 | 3600 | 2 | 761.62 | GGB | 764.102 | 772.852 | 768.864 | 265.03 | GGB | 10853.6 | GGB | 9.85 | GGB | 999.98 | GGB | 60.4 | GGB | 170708.6 | GGB | 137987.69 | GGB | 0 | 0 | 2912 | 3600 | 2896.46 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 177006.68 | GGB | 177008.79 | 2896.46 | 2738.853 |  |  |  | 1 | 1 |  |  |  |  | 137987.69 | 2738.853 | 137987.69 | 2738.853 | 9.3431 | [5 empty] | 111.0211 | 2738.853 |  | 104.98
20.03.2008 06:00 | 3600 | 2 | 762.2 | GGB | 765.201 | 773.742 | 768.864 | 264.86 | GGB | 10861.3 | GGB | 9.86 | GGB | 1000.14 | GGB | 60.33 | GGB | 170440.12 | GGB | 137818.51 | GGB | 0 | 0 | 2883 | 3600 | 2867.16 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 177046.47 | GGB | 177048.58 | 2867.16 | 2742.2151 |  |  |  | 1 | 1 |  |  |  |  | 137818.51 | 2742.2151 | 137818.51 | 2742.2151 | 9.4981 | [5 empty] | 109.7633 | 2742.2151 |  | 104.98
20.03.2008 07:00 | 3600 | 2 | 761.43 | GGB | 763.004 | 771.75 | 766.667 | 265.16 | GGB | 10848.3 | GGB | 9.85 | GGB | 1000.12 | GGB | 60.28 | GGB | 170863.75 | GGB | 138180.26 | GGB | 0 | 0 | 2910 | 3600 | 2894.18 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 177085.99 | GGB | 177088.1 | 2894.18 | 2735.0361 |  |  |  | 0 | 1 | [14 empty] | 111.0885 | 2735.0361 |  | 104.98
20.03.2008 08:00 | 3600 | 2 | 761.57 | GGB | 763.004 | 771.094 | 767.766 | 265.24 | GGB | 10858.8 | GGB | 9.86 | GGB | 1000.27 | GGB | 60.27 | GGB | 170724 | GGB | 138092.62 | GGB | 0 | 0 | 2901 | 3600 | 2885.11 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 177126.56 | GGB | 177128.66 | 2885.11 | 2736.7719 |  |  |  | 0 | 1 | [14 empty] | 110.6701 | 2736.7719 |  | 104.98
20.03.2008 09:00 | 3600 | 2 | 761.83 | GGB | 764.102 | 772.664 | 768.864 | 265.03 | GGB | 10858.3 | GGB | 9.86 | GGB | 1000.48 | GGB | 60.31 | GGB | 170696.5 | GGB | 138080.52 | GGB | 0 | 0 | 2896 | 3600 | 2880.65 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 177166.29 | GGB | 177168.39 | 2880.65 | 2737.0117 |  |  |  | 1 | 1 |  |  |  |  | 138080.52 | 2737.0117 | 138080.52 | 2737.0117 | 9.5124 | [5 empty] | 110.4893 | 2737.0117 |  | 104.98
20.03.2008 10:00 | 3600 | 2 | 762.2 | GGB | 763.004 | 771.586 | 767.766 | 264.57 | GGB | 10838.5 | GGB | 9.85 | GGB | 1000.64 | GGB | 60.41 | GGB | 170282.77 | GGB | 137729.76 | GGB | 0 | 0 | 2865 | 3600 | 2849.24 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 177205.45 | GGB | 177207.56 | 2849.24 | 2743.9821 |  |  |  | 0 | 1 | [14 empty] | 109.007 | 2743.9821 |  | 104.98
20.03.2008 11:00 | 3600 | 2 | 762.36 | GGB | 764.102 | 772.055 | 767.766 | 264.24 | GGB | 10826.2 | GGB | 9.85 | GGB | 1000.94 | GGB | 60.67 | GGB | 169743.6 | GGB | 137226.93 | GGB | 0 | 0 | 2852 | 3600 | 2836.37 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 177245.76 | GGB | 177247.87 | 2836.37 | 2754.0367 |  |  |  | 1 | 1 |  |  |  |  | 137226.93 | 2754.0367 | 137226.93 | 2754.0367 | 9.3755 | [5 empty] | 108.1184 | 2754.0367 |  | 104.98
20.03.2008 12:00 | 3600 | 2 | 762.52 | GGB | 764.102 | 772.313 | 768.864 | 263.54 | GGB | 10800.1 | GGB | 9.85 | GGB | 1000.87 | GGB | 60.81 | GGB | 169397 | GGB | 136880.46 | GGB | 0 | 0 | 2811 | 3600 | 2795.56 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 177285.27 | GGB | 177287.38 | 2795.56 | 2761.0077 |  |  |  | 1 | 1 |  |  |  |  | 136880.46 | 2761.0077 | 136880.46 | 2761.0077 | 9.5654 | [5 empty] | 106.2938 | 2761.0077 |  | 104.98
20.03.2008 13:00 | 3600 | 2 | 764.04 | GGB | 767.766 | 776.602 | 772.527 | 264.2 | GGB | 10773.4 | GGB | 9.86 | GGB | 1000.52 | GGB | 60.26 | GGB | 170525.94 | GGB | 137969.17 | GGB | 0 | 0 | 2723 | 3600 | 2707.94 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 177324.46 | GGB | 177326.57 | 2707.94 | 2707.94 |  |  |  | 1 | 1 |  |  |  |  | 137969.17 | 2707.94 | 137969.17 | 2707.94 | 9.5334 | [5 empty] | 103.7812 |  |  | #VALUE!
20.03.2008 14:00 | 3600 | 2 | 764.47 | GGB | 767.766 | 776.883 | 772.527 | 263.51 | GGB | 10766.5 | GGB | 9.86 | GGB | 999.87 | GGB | 60.4 | GGB | 169881.15 | GGB | 137302.16 | GGB | 0 | 0 | 2692 | 3600 | 2676.73 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 177364.5 | GGB | 177366.61 | 2676.73 | 2676.73 |  |  |  | 1 | 1 |  |  |  |  | 137302.16 | 2676.73 | 137302.16 | 2676.73 | 9.1788 | [5 empty] | 102.0891 |  |  | #VALUE!
20.03.2008 15:00 | 3600 | 2 | 764.25 | GGB | 769.963 | 778.102 | 773.626 | 262.33 | GGB | 10748.1 | GGB | 9.85 | GGB | 998.96 | GGB | 60.89 | GGB | 168637.76 | GGB | 135975.2 | GGB | 0 | 0 | 2707 | 3600 | 2691.41 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 177403.92 | GGB | 177406.03 | 2691.41 | 2691.41 |  |  |  | 1 | 1 |  |  |  |  | 135975.2 | 2691.41 | 135975.2 | 2691.41 | 9.2837 | [5 empty] | 101.6569 |  |  | #VALUE!
20.03.2008 16:00 | 3600 | 2 | 764.76 | GGB | 766.3 | 774.727 | 770.696 | 262.21 | GGB | 10748.4 | GGB | 9.86 | GGB | 998.18 | GGB | 61.06 | GGB | 168292.26 | GGB | 135520.33 | GGB | 0 | 0 | 2680 | 3600 | 2664.76 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 177443.02 | GGB | 177445.13 | 2664.76 | 2664.76 |  |  |  | 1 | 1 |  |  |  |  | 135520.33 | 2664.76 | 135520.33 | 2664.76 | 9.236 | [5 empty] | 100.3137 |  |  | #VALUE!
20.03.2008 17:00 | 3600 | 2 | 764.92 | GGB | 767.766 | 775.992 | 772.161 | 261.06 | GGB | 10746.1 | GGB | 9.86 | GGB | 997.01 | GGB | 61.8 | GGB | 166955.35 | GGB | 133989.14 | GGB | 0 | 0 | 2673 | 3600 | 2658.07 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 177482.93 | GGB | 177485.03 | 2658.07 | 2658.07 |  |  |  | 1 | 1 |  |  |  |  | 133989.14 | 2658.07 | 133989.14 | 2658.07 | 8.9261 | [5 empty] | 98.9313 |  |  | #VALUE!
20.03.2008 18:00 | 3600 | 2 | 764.04 | GGB | 765.201 | 774.352 | 770.696 | 261.34 | GGB | 10722.6 | GGB | 9.85 | GGB | 996.89 | GGB | 61.51 | GGB | 166868.42 | GGB | 134020.19 | GGB | 0 | 0 | 2705 | 3600 | 2689.14 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 177522.45 | GGB | 177524.56 | 2689.14 | 2689.14 |  |  |  | 1 | 1 |  |  |  |  | 134020.19 | 2689.14 | 134020.19 | 2689.14 | 9.1171 | [5 empty] | 100.1108 |  |  | #VALUE!
20.03.2008 19:00 | 3600 | 2 | 760.73 | GGB | 762.637 | 771.844 | 767.766 | 264.19 | GGB | 10794.5 | GGB | 9.83 | GGB | 997.4 | GGB | 60.43 | GGB | 169881.15 | GGB | 136949.09 | GGB | 0 | 0 | 2901 | 3600 | 2885.44 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 177561.73 | GGB | 177563.84 | 2885.44 | 2759.624 |  |  |  | 0 | 1 | [14 empty] | 109.7662 | 2759.624 |  | 104.98
20.03.2008 20:00 | 3600 | 2 | 761.76 | GGB | 761.538 | 769.734 | 765.201 | 264.97 | GGB | 10826.1 | GGB | 9.86 | GGB | 997.89 | GGB | 60.88 | GGB | 170155.13 | GGB | 137052.72 | GGB | 0 | 0 | 2877 | 3600 | 2861.38 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 177601.65 | GGB | 177603.77 | 2861.38 | 2757.5374 |  |  |  | 0 | 1 | [14 empty] | 108.9333 | 2757.5374 |  | 104.98
20.03.2008 21:00 | 3600 | 2 | 761.37 | GGB | 764.102 | 772.266 | 767.766 | 265.69 | GGB | 10853.9 | GGB | 9.86 | GGB | 997.68 | GGB | 60.61 | GGB | 171197.15 | GGB | 137974.68 | GGB | 0 | 0 | 2905 | 3600 | 2889.17 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 177641.1 | GGB | 177643.22 | 2889.17 | 2739.1113 |  |  |  | 1 | 1 |  |  |  |  | 137974.68 | 2739.1113 | 137974.68 | 2739.1113 | 9.5799 | [5 empty] | 110.7312 | 2739.1113 |  | 104.98
20.03.2008 22:00 | 3600 | 2 | 760.84 | GGB | 762.637 | 771.281 | 767.766 | 265.69 | GGB | 10836.7 | GGB | 9.85 | GGB | 996.99 | GGB | 60.42 | GGB | 171390.81 | GGB | 138116.12 | GGB | 0 | 0 | 2919 | 3600 | 2903.33 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 177680.68 | GGB | 177682.79 | 2903.33 | 2736.3062 |  |  |  | 0 | 1 | [14 empty] | 111.388 | 2736.3062 |  | 104.98
20.03.2008 23:00 | 3600 | 2 | 761.91 | GGB | 765.201 | 773.906 | 769.963 | 264.85 | GGB | 10858.5 | GGB | 9.87 | GGB | 996.43 | GGB | 60.35 | GGB | 171499.74 | GGB | 138154.42 | GGB | 0 | 0 | 2874 | 3600 | 2858.16 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 177719.75 | GGB | 177721.87 | 2858.16 | 2735.5477 |  |  |  | 1 | 1 |  |  |  |  | 138154.42 | 2735.5477 | 138154.42 | 2735.5477 | 9.6706 | [5 empty] | 109.6854 | 2735.5477 |  | 104.98
20.03.2008 24:00 | 3600 | 2 | 760.85 | GGB | 764.102 | 772.641 | 768.864 | 265.45 | GGB | 10830.3 | GGB | 9.85 | GGB | 996 | GGB | 60.09 | GGB | 171440.32 | GGB | 138155.3 | GGB | 0 | 0 | 2918 | 3600 | 2902.78 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 177759.37 | GGB | 177761.49 | 2902.78 | 2735.5302 |  |  |  | 1 | 1 |  |  |  |  | 138155.3 | 2735.5302 | 138155.3 | 2735.5302 | 9.5388 | [5 empty] | 111.3985 | 2735.5302 |  | 104.98
21.03.2008 01:00 | 3600 | 2 | 761.25 | GGB | 765.201 | 773.109 | 768.864 | 265.85 | GGB | 10839.7 | GGB | 9.86 | GGB | 995.27 | GGB | 59.91 | GGB | 171929.97 | GGB | 138523.72 | GGB | 0 | 0 | 2910 | 3600 | 2894.24 | GGB | 100 | GGB | 41.21 | GGB | 41.21 | GGB | 177800.58 | GGB | 177802.7 | 2894.24 | 2728.2548 |  |  |  | 1 | 1 |  |  |  |  | 138523.72 | 2728.2548 | 138523.72 | 2728.2548 | 9.1708 | [5 empty] | 111.3669 | 2728.2548 |  | 104.98
21.03.2008 02:00 | 3600 | 2 | 760.95 | GGB | 761.538 | 770.063 | 766.667 | 265.6 | GGB | 10818 | GGB | 9.85 | GGB | 994.67 | GGB | 60.16 | GGB | 171594.37 | GGB | 138065.78 | GGB | 0 | 0 | 2897 | 3600 | 2881.33 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 177839.56 | GGB | 177841.68 | 2881.33 | 2737.3039 |  |  |  | 0 | 1 | [14 empty] | 110.5036 | 2737.3039 |  | 104.98
21.03.2008 03:00 | 3600 | 2 | 761.67 | GGB | 764.102 | 773.109 | 768.864 | 264.75 | GGB | 10835.7 | GGB | 9.87 | GGB | 994.15 | GGB | 60.26 | GGB | 170853.84 | GGB | 137355.97 | GGB | 0 | 0 | 2877 | 3600 | 2861.75 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 177878.84 | GGB | 177880.96 | 2861.75 | 2751.4494 |  |  |  | 1 | 1 |  |  |  |  | 137355.97 | 2751.4494 | 137355.97 | 2751.4494 | 9.6214 | [5 empty] | 109.1885 | 2751.4494 |  | 104.98
21.03.2008 04:00 | 3600 | 2 | 761.29 | GGB | 762.637 | 770.742 | 766.667 | 265.27 | GGB | 10797.1 | GGB | 9.85 | GGB | 993.53 | GGB | 60.06 | GGB | 171336.89 | GGB | 137740.36 | GGB | 0 | 0 | 2882 | 3600 | 2866.54 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 177919.67 | GGB | 177921.79 | 2866.54 | 2743.771 |  |  |  | 0 | 1 | [14 empty] | 109.6773 | 2743.771 |  | 104.98
21.03.2008 05:00 | 3600 | 2 | 761.43 | GGB | 761.538 | 770.273 | 766.667 | 264.49 | GGB | 10817.5 | GGB | 9.86 | GGB | 992.68 | GGB | 59.99 | GGB | 170922.06 | GGB | 137320.99 | GGB | 0 | 0 | 2878 | 3600 | 2862.62 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 177958.11 | GGB | 177960.23 | 2862.62 | 2752.1503 |  |  |  | 0 | 1 | [14 empty] | 109.1938 | 2752.1503 |  | 104.98
21.03.2008 06:00 | 3600 | 2 | 761.17 | GGB | 762.637 | 771.75 | 767.766 | 263.79 | GGB | 10819.2 | GGB | 9.86 | GGB | 992.06 | GGB | 59.84 | GGB | 170194.74 | GGB | 136710.65 | GGB | 0 | 0 | 2890 | 3600 | 2874.54 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 177997.22 | GGB | 177999.34 | 2874.54 | 2764.4372 |  |  |  | 0 | 1 | [14 empty] | 109.1612 | 2764.4372 |  | 104.98
21.03.2008 07:00 | 3600 | 2 | 760.43 | GGB | 761.538 | 770.039 | 765.201 | 264.12 | GGB | 10820.3 | GGB | 9.85 | GGB | 991.45 | GGB | 59.65 | GGB | 170936.37 | GGB | 137302.26 | GGB | 0 | 0 | 2935 | 3600 | 2919.66 | GGB | 100 | GGB | 41.89 | GGB | 41.89 | GGB | 178039.11 | GGB | 178041.23 | 2919.66 | 2752.5257 |  |  |  | 0 | 1 | [14 empty] | 111.3544 | 2752.5257 |  | 104.98
21.03.2008 08:00 | 3600 | 2 | 760.97 | GGB | 762.637 | 770.367 | 766.667 | 264.11 | GGB | 10832.8 | GGB | 9.86 | GGB | 991.76 | GGB | 60 | GGB | 170857.15 | GGB | 137133.63 | GGB | 0 | 0 | 2894 | 3208 | 2878.4 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 178077.33 | GGB | 178079.45 | 2878.4 | 2755.9104 |  |  |  | 0 | 1 | [14 empty] | 109.646 | 2755.9104 |  | 104.98
21.03.2008 09:00 | 3600 | 2 | 760.99 | GGB | 763.004 | 771.305 | 766.667 | 263.31 | GGB | 10827.9 | GGB | 9.86 | GGB | 991.46 | GGB | 60.02 | GGB | 170600.77 | GGB | 136879.51 | GGB | 0 | 0 | 2885 | 3600 | 2868.98 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 178117.86 | GGB | 178119.98 | 2868.98 | 2761.0268 |  |  |  | 0 | 1 | [14 empty] | 109.0846 | 2761.0268 |  | 104.98
21.03.2008 10:00 | 3600 | 2 | 762.37 | GGB | 765.201 | 773.531 | 769.597 | 262.2 | GGB | 10822.8 | GGB | 9.87 | GGB | 991.13 | GGB | 60.2 | GGB | 169851.44 | GGB | 136160.27 | GGB | 0 | 0 | 2831 | 3600 | 2814.99 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 178157.37 | GGB | 178159.49 | 2814.99 | 2775.6114 |  |  |  | 1 | 1 |  |  |  |  | 136160.27 | 2775.6114 | 136160.27 | 2775.6114 | 9.5654 | [5 empty] | 106.4694 | 2775.6114 |  | 104.98
21.03.2008 11:00 | 3600 | 2 | 762.58 | GGB | 764.102 | 772.688 | 768.498 | 261.94 | GGB | 10759.6 | GGB | 9.85 | GGB | 990.12 | GGB | 60.47 | GGB | 169011.88 | GGB | 135239.17 | GGB | 0 | 0 | 2799 | 3600 | 2783.48 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 178197.7 | GGB | 178199.82 | 2783.48 | 2783.48 |  |  |  | 1 | 1 |  |  |  |  | 135239.17 | 2783.48 | 135239.17 | 2783.48 | 9.3339 | [5 empty] | 104.5654 |  |  | #VALUE!
21.03.2008 12:00 | 3600 | 2 | 762.54 | GGB | 766.3 | 774.703 | 771.795 | 261.81 | GGB | 10746.5 | GGB | 9.85 | GGB | 989.51 | GGB | 60.9 | GGB | 168862.23 | GGB | 134860.53 | GGB | 0 | 0 | 2793 | 3600 | 2777.06 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 178235.97 | GGB | 178238.09 | 2777.06 | 2777.06 |  |  |  | 1 | 1 |  |  |  |  | 134860.53 | 2777.06 | 134860.53 | 2777.06 | 9.7861 | [5 empty] | 104.0322 |  |  | #VALUE!
21.03.2008 13:00 | 3600 | 2 | 763.34 | GGB | 764.102 | 772.805 | 769.597 | 261.62 | GGB | 10737.6 | GGB | 9.86 | GGB | 989.1 | GGB | 60.48 | GGB | 169433.31 | GGB | 135433.52 | GGB | 0 | 0 | 2744 | 3600 | 2728.18 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 178275.95 | GGB | 178278.08 | 2728.18 | 2728.18 |  |  |  | 1 | 1 |  |  |  |  | 135433.52 | 2728.18 | 135433.52 | 2728.18 | 9.2395 | [5 empty] | 102.6353 |  |  | #VALUE!
21.03.2008 14:00 | 3600 | 2 | 764.3 | GGB | 766.3 | 774.961 | 770.696 | 259.4 | GGB | 10707.8 | GGB | 9.86 | GGB | 988.01 | GGB | 61.17 | GGB | 167049.98 | GGB | 133105.42 | GGB | 0 | 0 | 2697 | 3600 | 2681.79 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 178315.82 | GGB | 178317.95 | 2681.79 | 2681.79 |  |  |  | 1 | 1 |  |  |  |  | 133105.42 | 2681.79 | 133105.42 | 2681.79 | 8.9531 | [5 empty] | 99.1558 |  |  | #VALUE!
21.03.2008 15:00 | 3600 | 2 | 764.6 | GGB | 766.667 | 775.008 | 771.795 | 258.6 | GGB | 10664.5 | GGB | 9.86 | GGB | 987.19 | GGB | 61.34 | GGB | 165828.6 | GGB | 131952.69 | GGB | 0 | 0 | 2655 | 3600 | 2639.58 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 178353.92 | GGB | 178356.05 | 2639.58 | 2639.58 |  |  |  | 1 | 1 |  |  |  |  | 131952.69 | 2639.58 | 131952.69 | 2639.58 | 9.1417 | [5 empty] | 96.7499 |  |  | #VALUE!
21.03.2008 16:00 | 3600 | 2 | 764.87 | GGB | 766.667 | 775.055 | 772.161 | 258.48 | GGB | 10659.6 | GGB | 9.86 | GGB | 986.79 | GGB | 61.42 | GGB | 165629.44 | GGB | 131710.84 | GGB | 0 | 0 | 2643 | 3600 | 2627.7 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 178393.19 | GGB | 178395.32 | 2627.7 | 2627.7 |  |  |  | 1 | 1 |  |  |  |  | 131710.84 | 2627.7 | 131710.84 | 2627.7 | 8.8133 | [5 empty] | 96.1379 |  |  | #VALUE!
21.03.2008 17:00 | 3600 | 2 | 764.02 | GGB | 766.3 | 774.961 | 770.696 | 258.87 | GGB | 10665.9 | GGB | 9.85 | GGB | 986.72 | GGB | 61.36 | GGB | 166175.21 | GGB | 132158.81 | GGB | 0 | 0 | 2684 | 3600 | 2669.1 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 178433.63 | GGB | 178435.76 | 2669.1 | 2669.1 |  |  |  | 1 | 1 |  |  |  |  | 132158.81 | 2669.1 | 132158.81 | 2669.1 | 8.7227 | [5 empty] | 97.9847 |  |  | #VALUE!
21.03.2008 18:00 | 3600 | 2 | 763.53 | GGB | 764.102 | 773.109 | 768.498 | 259.29 | GGB | 10681.4 | GGB | 9.85 | GGB | 986.76 | GGB | 61.14 | GGB | 166893.73 | GGB | 132824.86 | GGB | 0 | 0 | 2705 | 3600 | 2689.68 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 178472.06 | GGB | 178474.19 | 2689.68 | 2689.68 |  |  |  | 1 | 1 |  |  |  |  | 132824.86 | 2689.68 | 132824.86 | 2689.68 | 9.2963 | [5 empty] | 99.2379 |  |  | #VALUE!
21.03.2008 19:00 | 3600 | 2 | 763.56 | GGB | 763.004 | 772.078 | 768.498 | 260.09 | GGB | 10689.8 | GGB | 9.85 | GGB | 986.79 | GGB | 61.22 | GGB | 166717.67 | GGB | 132656.64 | GGB | 0 | 0 | 2727 | 3600 | 2711.6 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 178511.49 | GGB | 178513.62 | 2711.6 | 2711.6 |  |  |  | 0 | 1 | [14 empty] | 99.9199 |  |  | #VALUE!
21.03.2008 20:00 | 3600 | 2 | 763.7 | GGB | 765.201 | 773.18 | 769.597 | 259.25 | GGB | 10702.6 | GGB | 9.86 | GGB | 986.63 | GGB | 60.99 | GGB | 166938.84 | GGB | 132900.82 | GGB | 0 | 0 | 2711 | 3600 | 2695.51 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 178550.59 | GGB | 178552.72 | 2695.51 | 2695.51 |  |  |  | 1 | 1 |  |  |  |  | 132900.82 | 2695.51 | 132900.82 | 2695.51 | 9.162 | [5 empty] | 99.5099 |  |  | #VALUE!
21.03.2008 21:00 | 3600 | 2 | 763.52 | GGB | 764.102 | 773.063 | 769.597 | 259.75 | GGB | 10680.7 | GGB | 9.85 | GGB | 986.48 | GGB | 61.2 | GGB | 166813.4 | GGB | 132700.25 | GGB | 0 | 0 | 2717 | 3600 | 2701.54 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 178588.88 | GGB | 178591.01 | 2701.54 | 2701.54 |  |  |  | 1 | 1 |  |  |  |  | 132700.25 | 2701.54 | 132700.25 | 2701.54 | 9.3626 | [5 empty] | 99.582 |  |  | #VALUE!
21.03.2008 22:00 | 3600 | 2 | 763.91 | GGB | 765.201 | 774.375 | 770.696 | 259.78 | GGB | 10695.4 | GGB | 9.86 | GGB | 986.28 | GGB | 61.18 | GGB | 166772.69 | GGB | 132646.38 | GGB | 0 | 0 | 2707 | 3600 | 2692.01 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 178629.34 | GGB | 178631.47 | 2692.01 | 2692.01 |  |  |  | 1 | 1 |  |  |  |  | 132646.38 | 2692.01 | 132646.38 | 2692.01 | 8.8256 | [5 empty] | 99.1904 |  |  | #VALUE!
21.03.2008 23:00 | 3600 | 2 | 763.61 | GGB | 765.201 | 773.648 | 769.597 | 260.21 | GGB | 10676 | GGB | 9.85 | GGB | 986.48 | GGB | 61.12 | GGB | 167261.24 | GGB | 133085.71 | GGB | 0 | 0 | 2717 | 3600 | 2701.88 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 178668.46 | GGB | 178670.59 | 2701.88 | 2701.88 |  |  |  | 1 | 1 |  |  |  |  | 133085.71 | 2701.88 | 133085.71 | 2701.88 | 9.1918 | [5 empty] | 99.8838 |  |  | #VALUE!
21.03.2008 24:00 | 3600 | 2 | 763.92 | GGB | 764.102 | 772.898 | 769.597 | 259.81 | GGB | 10677.8 | GGB | 9.86 | GGB | 986.38 | GGB | 61 | GGB | 167093.99 | GGB | 132986.91 | GGB | 0 | 0 | 2700 | 3600 | 2684.33 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 178706.84 | GGB | 178708.97 | 2684.33 | 2684.33 |  |  |  | 1 | 1 |  |  |  |  | 132986.91 | 2684.33 | 132986.91 | 2684.33 | 9.3012 | [5 empty] | 99.1613 |  |  | #VALUE!
22.03.2008 01:00 | 3600 | 2 | 762.62 | GGB | 765.201 | 774 | 769.597 | 260.7 | GGB | 10689.4 | GGB | 9.85 | GGB | 986.11 | GGB | 60.72 | GGB | 167947.85 | GGB | 133741.33 | GGB | 0 | 0 | 2757 | 3600 | 2741.25 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 178747.54 | GGB | 178749.67 | 2741.25 | 2741.25 |  |  |  | 1 | 1 |  |  |  |  | 133741.33 | 2741.25 | 133741.33 | 2741.25 | 9.0078 | [5 empty] | 101.8385 |  |  | #VALUE!
22.03.2008 02:00 | 3600 | 2 | 763.58 | GGB | 765.201 | 774.07 | 769.597 | 259.7 | GGB | 10705.1 | GGB | 9.86 | GGB | 985.58 | GGB | 60.94 | GGB | 166766.09 | GGB | 132644.43 | GGB | 0 | 0 | 2722 | 3600 | 2706.49 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 178786.39 | GGB | 178788.52 | 2706.49 | 2706.49 |  |  |  | 1 | 1 |  |  |  |  | 132644.43 | 2706.49 | 132644.43 | 2706.49 | 9.2407 | [5 empty] | 99.7225 |  |  | #VALUE!
22.03.2008 03:00 | 3600 | 2 | 763.2 | GGB | 763.004 | 772.289 | 768.498 | 259.55 | GGB | 10673.3 | GGB | 9.85 | GGB | 985.13 | GGB | 60.93 | GGB | 166718.77 | GGB | 132549.2 | GGB | 0 | 0 | 2734 | 3600 | 2718.25 | GGB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 178824.73 | GGB | 178826.86 | 2718.25 | 2718.25 |  |  |  | 0 | 1 | [14 empty] | 100.0839 |  |  | #VALUE!
22.03.2008 04:00 | 3600 | 2 | 763.16 | GGB | 765.201 | 773.578 | 769.597 | 259.53 | GGB | 10686.1 | GGB | 9.86 | GGB | 984.64 | GGB | 60.88 | GGB | 166693.47 | GGB | 132483.12 | GGB | 0 | 0 | 2734 | 3600 | 2718.82 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 178865.21 | GGB | 178867.34 | 2718.82 | 2718.82 |  |  |  | 1 | 1 |  |  |  |  | 132483.12 | 2718.82 | 132483.12 | 2718.82 | 8.8982 | [5 empty] | 100.0549 |  |  | #VALUE!
22.03.2008 05:00 | 3600 | 2 | 763.06 | GGB | 763.004 | 771.82 | 767.033 | 259.67 | GGB | 10678.6 | GGB | 9.85 | GGB | 984.25 | GGB | 60.94 | GGB | 166592.24 | GGB | 132327.73 | GGB | 0 | 0 | 2742 | 3600 | 2726.85 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 178904.19 | GGB | 178906.32 | 2726.85 | 2726.85 |  |  |  | 0 | 1 | [14 empty] | 100.2327 |  |  | #VALUE!
22.03.2008 06:00 | 3600 | 2 | 762.39 | GGB | 765.201 | 774.07 | 769.597 | 260.14 | GGB | 10694.4 | GGB | 9.85 | GGB | 984.14 | GGB | 60.69 | GGB | 166934.44 | GGB | 132682.49 | GGB | 0 | 0 | 2774 | 3600 | 2758.38 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 178942.64 | GGB | 178944.76 | 2758.38 | 2758.38 |  |  |  | 1 | 1 |  |  |  |  | 132682.49 | 2758.38 | 132682.49 | 2758.38 | 9.521 | [5 empty] | 101.6635 |  |  | #VALUE!
22.03.2008 07:00 | 3600 | 2 | 761.97 | GGB | 764.102 | 772.195 | 768.498 | 260.3 | GGB | 10698.8 | GGB | 9.85 | GGB | 984.04 | GGB | 60.58 | GGB | 167163.31 | GGB | 132892.79 | GGB | 0 | 0 | 2798 | 3600 | 2782.18 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 178982.97 | GGB | 178985.09 | 2782.18 | 2782.18 |  |  |  | 1 | 1 |  |  |  |  | 132892.79 | 2782.18 | 132892.79 | 2782.18 | 9.1677 | [5 empty] | 102.7032 |  |  | #VALUE!
22.03.2008 08:00 | 3600 | 2 | 762.35 | GGB | 764.102 | 772.102 | 768.498 | 260.04 | GGB | 10699.7 | GGB | 9.86 | GGB | 984.21 | GGB | 60.53 | GGB | 166777.09 | GGB | 132629.25 | GGB | 0 | 0 | 2784 | 3600 | 2768.67 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 179022.03 | GGB | 179024.16 | 2768.67 | 2768.67 |  |  |  | 1 | 1 |  |  |  |  | 132629.25 | 2768.67 | 132629.25 | 2768.67 | 9.3987 | [5 empty] | 102.0018 |  |  | #VALUE!
22.03.2008 09:00 | 3600 | 2 | 762.34 | GGB | 763.004 | 770.883 | 767.033 | 259.53 | GGB | 10676.7 | GGB | 9.85 | GGB | 984.22 | GGB | 60.78 | GGB | 166377.67 | GGB | 132215.12 | GGB | 0 | 0 | 2776 | 3600 | 2760.45 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 179060.55 | GGB | 179062.67 | 2760.45 | 2760.45 |  |  |  | 0 | 1 | [14 empty] | 101.3815 |  |  | #VALUE!
22.03.2008 10:00 | 3600 | 2 | 763.02 | GGB | 765.201 | 774.188 | 770.696 | 259.26 | GGB | 10673.6 | GGB | 9.86 | GGB | 984.18 | GGB | 61.12 | GGB | 165884.72 | GGB | 131683.86 | GGB | 0 | 0 | 2750 | 3600 | 2734.42 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 179100.51 | GGB | 179102.63 | 2734.42 | 2734.42 |  |  |  | 1 | 1 |  |  |  |  | 131683.86 | 2734.42 | 131683.86 | 2734.42 | 9.011 | [5 empty] | 100.0219 |  |  | #VALUE!
22.03.2008 11:00 | 3600 | 2 | 762.38 | GGB | 763.004 | 772.031 | 768.498 | 259.07 | GGB | 10650.9 | GGB | 9.85 | GGB | 984.02 | GGB | 61.23 | GGB | 165645.95 | GGB | 131428.65 | GGB | 0 | 0 | 2749 | 3600 | 2733.89 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 179139.62 | GGB | 179141.74 | 2733.89 | 2733.89 |  |  |  | 0 | 1 | [14 empty] | 99.8087 |  |  | #VALUE!
22.03.2008 12:00 | 3600 | 2 | 763.03 | GGB | 765.201 | 773.133 | 769.597 | 258.32 | GGB | 10639.2 | GGB | 9.86 | GGB | 983.68 | GGB | 61.53 | GGB | 164875.71 | GGB | 130657.33 | GGB | 0 | 0 | 2713 | 3600 | 2697.61 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 179178.12 | GGB | 179180.24 | 2697.61 | 2697.61 |  |  |  | 1 | 1 |  |  |  |  | 130657.33 | 2697.61 | 130657.33 | 2697.61 | 9.1549 | [5 empty] | 97.9063 |  |  | #VALUE!
22.03.2008 13:00 | 3600 | 2 | 763.55 | GGB | 765.201 | 774.984 | 770.696 | 257.81 | GGB | 10620.9 | GGB | 9.86 | GGB | 983.6 | GGB | 61.73 | GGB | 164226.51 | GGB | 130052.7 | GGB | 0 | 0 | 2692 | 3600 | 2677.08 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 179217.82 | GGB | 179219.93 | 2677.08 | 2677.08 |  |  |  | 1 | 1 |  |  |  |  | 130052.7 | 2677.08 | 130052.7 | 2677.08 | 8.772 | [5 empty] | 96.7115 |  |  | #VALUE!
22.03.2008 14:00 | 3600 | 2 | 763.74 | GGB | 765.201 | 774.938 | 770.696 | 257.19 | GGB | 10603.7 | GGB | 9.86 | GGB | 983.42 | GGB | 61.96 | GGB | 163696.15 | GGB | 129520.34 | GGB | 0 | 0 | 2677 | 3600 | 2661.62 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 179256.67 | GGB | 179258.78 | 2661.62 | 2661.62 |  |  |  | 1 | 1 |  |  |  |  | 129520.34 | 2661.62 | 129520.34 | 2661.62 | 8.8735 | [5 empty] | 95.7594 |  |  | #VALUE!
22.03.2008 15:00 | 3600 | 2 | 763.5 | GGB | 764.102 | 772.57 | 768.498 | 256.9 | GGB | 10589 | GGB | 9.85 | GGB | 982.71 | GGB | 61.92 | GGB | 163553.1 | GGB | 129328.48 | GGB | 0 | 0 | 2674 | 3600 | 2658.99 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 179295.19 | GGB | 179297.3 | 2658.99 | 2658.99 |  |  |  | 1 | 1 |  |  |  |  | 129328.48 | 2658.99 | 129328.48 | 2658.99 | 8.9274 | [5 empty] | 95.5231 |  |  | #VALUE!
22.03.2008 16:00 | 3600 | 2 | 762.81 | GGB | 766.3 | 774.492 | 771.795 | 258.01 | GGB | 10625 | GGB | 9.86 | GGB | 983.12 | GGB | 61.37 | GGB | 164585.22 | GGB | 130414.68 | GGB | 0 | 0 | 2720 | 3600 | 2704.97 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 179335.41 | GGB | 179337.52 | 2704.97 | 2704.97 |  |  |  | 1 | 1 |  |  |  |  | 130414.68 | 2704.97 | 130414.68 | 2704.97 | 8.771 | [5 empty] | 97.9911 |  |  | #VALUE!
22.03.2008 17:00 | 3600 | 2 | 763.6 | GGB | 765.201 | 774.352 | 769.597 | 257.3 | GGB | 10594.3 | GGB | 9.85 | GGB | 982.83 | GGB | 61.97 | GGB | 163752.26 | GGB | 129483.33 | GGB | 0 | 0 | 2685 | 3600 | 2669.91 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 179373.44 | GGB | 179375.55 | 2669.91 | 2669.91 |  |  |  | 1 | 1 |  |  |  |  | 129483.33 | 2669.91 | 129483.33 | 2669.91 | 9.0904 | [5 empty] | 96.0302 |  |  | #VALUE!
22.03.2008 18:00 | 3600 | 2 | 763.92 | GGB | 765.201 | 774.258 | 770.696 | 256.8 | GGB | 10585.2 | GGB | 9.86 | GGB | 982.71 | GGB | 62.09 | GGB | 163224.1 | GGB | 129004.08 | GGB | 0 | 0 | 2666 | 3600 | 2650.66 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 179411.41 | GGB | 179413.52 | 2650.66 | 2650.66 |  |  |  | 1 | 1 |  |  |  |  | 129004.08 | 2650.66 | 129004.08 | 2650.66 | 9.0057 | [5 empty] | 94.985 |  |  | #VALUE!
22.03.2008 19:00 | 3600 | 2 | 764.11 | GGB | 765.201 | 774.281 | 770.696 | 256.49 | GGB | 10571.1 | GGB | 9.85 | GGB | 982.82 | GGB | 62.34 | GGB | 162606.81 | GGB | 128435.16 | GGB | 0 | 0 | 2648 | 3600 | 2632.16 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 179451.12 | GGB | 179453.23 | 2632.16 | 2632.16 |  |  |  | 1 | 1 |  |  |  |  | 128435.16 | 2632.16 | 128435.16 | 2632.16 | 8.5133 | [5 empty] | 93.9061 |  |  | #VALUE!
22.03.2008 20:00 | 3600 | 2 | 763.81 | GGB | 766.3 | 774.328 | 770.696 | 256.78 | GGB | 10578.5 | GGB | 9.85 | GGB | 982.75 | GGB | 62.33 | GGB | 163158.08 | GGB | 128865.79 | GGB | 0 | 0 | 2669 | 3600 | 2653.42 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 179490 | GGB | 179492.11 | 2653.42 | 2653.42 |  |  |  | 1 | 1 |  |  |  |  | 128865.79 | 2653.42 | 128865.79 | 2653.42 | 8.7946 | [5 empty] | 94.982 |  |  | #VALUE!
22.03.2008 21:00 | 3600 | 2 | 763.43 | GGB | 764.102 | 773.25 | 769.597 | 257.12 | GGB | 10591.6 | GGB | 9.85 | GGB | 982.7 | GGB | 62.15 | GGB | 163695.05 | GGB | 129352.61 | GGB | 0 | 0 | 2680 | 3600 | 2665.09 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 179528.91 | GGB | 179531.02 | 2665.09 | 2665.09 |  |  |  | 1 | 1 |  |  |  |  | 129352.61 | 2665.09 | 129352.61 | 2665.09 | 8.8598 | [5 empty] | 95.7601 |  |  | #VALUE!
22.03.2008 22:00 | 3600 | 2 | 763.2 | GGB | 767.766 | 776.438 | 773.26 | 257.52 | GGB | 10606.5 | GGB | 9.86 | GGB | 983.32 | GGB | 61.17 | GGB | 165294.94 | GGB | 131079.26 | GGB | 0 | 0 | 2692 | 3600 | 2676.31 | GGB | 100 | GGB | 37.5 | GGB | 37.5 | GGB | 179566.41 | GGB | 179568.52 | 2676.31 | 2676.31 |  |  |  | 1 | 1 |  |  |  |  | 131079.26 | 2676.31 | 131079.26 | 2676.31 | 9.3549 | [5 empty] | 97.4469 |  |  | #VALUE!
22.03.2008 23:00 | 3600 | 2 | 762.59 | GGB | 764.102 | 772.898 | 768.132 | 258.44 | GGB | 10614.6 | GGB | 9.84 | GGB | 983.6 | GGB | 60.84 | GGB | 165042.96 | GGB | 131048.91 | GGB | 0 | 0 | 2734 | 3600 | 2718.91 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 179607.12 | GGB | 179609.23 | 2718.91 | 2718.91 |  |  |  | 1 | 1 |  |  |  |  | 131048.91 | 2718.91 | 131048.91 | 2718.91 | 8.7524 | [5 empty] | 98.9751 |  |  | #VALUE!
22.03.2008 24:00 | 3600 | 2 | 763.82 | GGB | 766.3 | 775.336 | 770.696 | 259.13 | GGB | 10603.4 | GGB | 9.86 | GGB | 983.53 | GGB | 61.31 | GGB | 166088.28 | GGB | 131681.37 | GGB | 0 | 0 | 2674 | 3600 | 2658.51 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 179645.42 | GGB | 179647.53 | 2658.51 | 2658.51 |  |  |  | 1 | 1 |  |  |  |  | 131681.37 | 2658.51 | 131681.37 | 2658.51 | 9.1404 | [5 empty] | 97.2434 |  |  | #VALUE!
23.03.2008 01:00 | 3600 | 2 | 763.82 | GGB | 765.201 | 774.023 | 769.597 | 258.09 | GGB | 10613.8 | GGB | 9.86 | GGB | 983.07 | GGB | 61.69 | GGB | 164691.95 | GGB | 130367.54 | GGB | 0 | 0 | 2680 | 3600 | 2664.65 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 179683.16 | GGB | 179685.27 | 2664.65 | 2664.65 |  |  |  | 1 | 1 |  |  |  |  | 130367.54 | 2664.65 | 130367.54 | 2664.65 | 9.2047 | [5 empty] | 96.4955 |  |  | #VALUE!
23.03.2008 02:00 | 3600 | 2 | 763.19 | GGB | 764.102 | 772.781 | 768.498 | 258.16 | GGB | 10609.3 | GGB | 9.85 | GGB | 983.07 | GGB | 61.66 | GGB | 164539.01 | GGB | 130257.76 | GGB | 0 | 0 | 2707 | 3600 | 2691.93 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 179723.16 | GGB | 179725.27 | 2691.93 | 2691.93 |  |  |  | 1 | 1 |  |  |  |  | 130257.76 | 2691.93 | 130257.76 | 2691.93 | 8.7661 | [5 empty] | 97.4013 |  |  | #VALUE!
23.03.2008 03:00 | 3600 | 2 | 763.4 | GGB | 765.201 | 774.117 | 770.696 | 259.06 | GGB | 10608.1 | GGB | 9.85 | GGB | 983.04 | GGB | 61.42 | GGB | 165223.42 | GGB | 130887.34 | GGB | 0 | 0 | 2704 | 3600 | 2688.13 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 179762.86 | GGB | 179764.97 | 2688.13 | 2688.13 |  |  |  | 1 | 1 |  |  |  |  | 130887.34 | 2688.13 | 130887.34 | 2688.13 | 8.8625 | [5 empty] | 97.7339 |  |  | #VALUE!
23.03.2008 04:00 | 3600 | 2 | 763.27 | GGB | 764.102 | 772.969 | 769.597 | 258.92 | GGB | 10615.3 | GGB | 9.85 | GGB | 983.12 | GGB | 61.59 | GGB | 164903.22 | GGB | 130579.6 | GGB | 0 | 0 | 2705 | 3600 | 2689.33 | GGB | 100 | GGB | 38.47 | GGB | 38.47 | GGB | 179801.33 | GGB | 179803.44 | 2689.33 | 2689.33 |  |  |  | 1 | 1 |  |  |  |  | 130579.6 | 2689.33 | 130579.6 | 2689.33 | 9.1285 | [5 empty] | 97.5477 |  |  | #VALUE!
23.03.2008 05:00 | 3600 | 2 | 763.12 | GGB | 765.201 | 773.836 | 769.597 | 260.13 | GGB | 10584.9 | GGB | 9.84 | GGB | 983.62 | GGB | 61.04 | GGB | 166935.54 | GGB | 132475.02 | GGB | 0 | 0 | 2697 | 3600 | 2681.97 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 179840.1 | GGB | 179842.21 | 2681.97 | 2681.97 |  |  |  | 1 | 1 |  |  |  |  | 132475.02 | 2681.97 | 132475.02 | 2681.97 | 9.1641 | [5 empty] | 98.6928 |  |  | #VALUE!
23.03.2008 06:00 | 3600 | 2 | 763.44 | GGB | 765.201 | 773.602 | 769.597 | 258.28 | GGB | 10666.7 | GGB | 9.87 | GGB | 984.12 | GGB | 60.79 | GGB | 166184.01 | GGB | 132043.23 | GGB | 0 | 0 | 2704 | 3600 | 2688.65 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 179879.81 | GGB | 179881.92 | 2688.65 | 2688.65 |  |  |  | 1 | 1 |  |  |  |  | 132043.23 | 2688.65 | 132043.23 | 2688.65 | 8.9403 | [5 empty] | 98.6161 |  |  | #VALUE!
23.03.2008 07:00 | 3600 | 2 | 762.56 | GGB | 764.102 | 773.602 | 769.597 | 257.53 | GGB | 10680.1 | GGB | 9.85 | GGB | 984.98 | GGB | 60.51 | GGB | 165922.13 | GGB | 132061.75 | GGB | 0 | 0 | 2743 | 3600 | 2727.49 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 179919.02 | GGB | 179921.13 | 2727.49 | 2727.49 |  |  |  | 1 | 1 |  |  |  |  | 132061.75 | 2727.49 | 132061.75 | 2727.49 | 9.1864 | [5 empty] | 100.0548 |  |  | #VALUE!
23.03.2008 08:00 | 3600 | 2 | 762.57 | GGB | 763.004 | 772.336 | 768.498 | 257.46 | GGB | 10692.6 | GGB | 9.85 | GGB | 985.91 | GGB | 60.46 | GGB | 166095.98 | GGB | 132347.16 | GGB | 0 | 0 | 2742 | 3600 | 2726.94 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 179958.31 | GGB | 179960.42 | 2726.94 | 2726.94 |  |  |  | 0 | 1 | [14 empty] | 100.2508 |  |  | #VALUE!
23.03.2008 09:00 | 3600 | 2 | 762.73 | GGB | 764.102 | 771.844 | 768.498 | 257.88 | GGB | 10711.3 | GGB | 9.86 | GGB | 986.88 | GGB | 60.22 | GGB | 166668.16 | GGB | 133028.51 | GGB | 0 | 0 | 2749 | 3600 | 2733.09 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 179997.82 | GGB | 179999.93 | 2733.09 | 2733.09 |  |  |  | 1 | 1 |  |  |  |  | 133028.51 | 2733.09 | 133028.51 | 2733.09 | 9.2022 | [5 empty] | 100.9941 |  |  | #VALUE!
23.03.2008 10:00 | 3600 | 2 | 763.18 | GGB | 763.004 | 771.867 | 767.033 | 257.68 | GGB | 10712.9 | GGB | 9.86 | GGB | 987.94 | GGB | 60.1 | GGB | 166632.95 | GGB | 133189.42 | GGB | 0 | 0 | 2735 | 3600 | 2719.13 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 180037.1 | GGB | 180039.2 | 2719.13 | 2719.13 |  |  |  | 0 | 1 | [14 empty] | 100.5998 |  |  | #VALUE!
23.03.2008 11:00 | 3600 | 2 | 763.57 | GGB | 765.201 | 774.445 | 770.696 | 257.15 | GGB | 10710.2 | GGB | 9.86 | GGB | 988.53 | GGB | 60.34 | GGB | 166157.6 | GGB | 132792.76 | GGB | 0 | 0 | 2706 | 3600 | 2690.65 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 180076.37 | GGB | 180078.47 | 2690.65 | 2690.65 |  |  |  | 1 | 1 |  |  |  |  | 132792.76 | 2690.65 | 132792.76 | 2690.65 | 9.0985 | [5 empty] | 99.2497 |  |  | #VALUE!
23.03.2008 12:00 | 3600 | 2 | 764.09 | GGB | 766.3 | 775.219 | 770.696 | 256.33 | GGB | 10676.1 | GGB | 9.86 | GGB | 988.81 | GGB | 60.53 | GGB | 165106.78 | GGB | 131915.53 | GGB | 0 | 0 | 2678 | 3600 | 2662.86 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 180115.84 | GGB | 180117.94 | 2662.86 | 2662.86 |  |  |  | 1 | 1 |  |  |  |  | 131915.53 | 2662.86 | 131915.53 | 2662.86 | 8.8997 | [5 empty] | 97.5757 |  |  | #VALUE!
23.03.2008 13:00 | 3600 | 2 | 764.24 | GGB | 766.3 | 775.125 | 770.696 | 256.25 | GGB | 10669.4 | GGB | 9.85 | GGB | 989.15 | GGB | 60.59 | GGB | 164929.63 | GGB | 131797.61 | GGB | 0 | 0 | 2667 | 3600 | 2652.02 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 180155.01 | GGB | 180157.11 | 2652.02 | 2652.02 |  |  |  | 1 | 1 |  |  |  |  | 131797.61 | 2652.02 | 131797.61 | 2652.02 | 8.9234 | [5 empty] | 97.0916 |  |  | #VALUE!
23.03.2008 14:00 | 3600 | 2 | 764.37 | GGB | 763.004 | 772.875 | 768.498 | 255.79 | GGB | 10650.7 | GGB | 9.85 | GGB | 989.28 | GGB | 60.78 | GGB | 164404.76 | GGB | 131318.51 | GGB | 0 | 0 | 2644 | 3600 | 2628.82 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 180194.42 | GGB | 180196.52 | 2628.82 | 2628.82 |  |  |  | 0 | 1 | [14 empty] | 95.8924 |  |  | #VALUE!
23.03.2008 15:00 | 3600 | 2 | 764.15 | GGB | 764.102 | 773.25 | 768.498 | 256.12 | GGB | 10671.1 | GGB | 9.86 | GGB | 989.6 | GGB | 60.68 | GGB | 164914.22 | GGB | 131808.97 | GGB | 0 | 0 | 2661 | 3600 | 2645.94 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 180233.78 | GGB | 180235.88 | 2645.94 | 2645.94 |  |  |  | 1 | 1 |  |  |  |  | 131808.97 | 2645.94 | 131808.97 | 2645.94 | 8.8607 | [5 empty] | 96.8774 |  |  | #VALUE!
23.03.2008 16:00 | 3600 | 2 | 763.77 | GGB | 765.201 | 773.461 | 769.597 | 257.09 | GGB | 10702.4 | GGB | 9.85 | GGB | 990.02 | GGB | 60.29 | GGB | 166128.99 | GGB | 132992.06 | GGB | 0 | 0 | 2699 | 3600 | 2683.35 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 180273.45 | GGB | 180275.55 | 2683.35 | 2683.35 |  |  |  | 1 | 1 |  |  |  |  | 132992.06 | 2683.35 | 132992.06 | 2683.35 | 8.9958 | [5 empty] | 99.129 |  |  | #VALUE!
23.03.2008 17:00 | 3600 | 2 | 763.29 | GGB | 765.201 | 774.352 | 769.597 | 257.96 | GGB | 10723.1 | GGB | 9.85 | GGB | 990.6 | GGB | 60.1 | GGB | 166964.15 | GGB | 133812.53 | GGB | 0 | 0 | 2725 | 3600 | 2709.82 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 180312.45 | GGB | 180314.54 | 2709.82 | 2709.82 |  |  |  | 1 | 1 |  |  |  |  | 133812.53 | 2709.82 | 133812.53 | 2709.82 | 9.3 | [5 empty] | 100.7244 |  |  | #VALUE!
23.03.2008 18:00 | 3600 | 2 | 763.39 | GGB | 764.102 | 772.172 | 768.498 | 258.25 | GGB | 10742.1 | GGB | 9.85 | GGB | 991.54 | GGB | 59.77 | GGB | 167359.17 | GGB | 134391.97 | GGB | 0 | 0 | 2718 | 3600 | 2702.58 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 180351.79 | GGB | 180353.89 | 2702.58 | 2702.58 |  |  |  | 1 | 1 |  |  |  |  | 134391.97 | 2702.58 | 134391.97 | 2702.58 | 9.2301 | [5 empty] | 100.8903 |  |  | #VALUE!
23.03.2008 19:00 | 3600 | 2 | 763.08 | GGB | 766.3 | 774.445 | 770.696 | 259.05 | GGB | 10777.4 | GGB | 9.85 | GGB | 992.72 | GGB | 59.52 | GGB | 168430.9 | GGB | 135514.08 | GGB | 0 | 0 | 2740 | 3600 | 2725.04 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 180391.44 | GGB | 180393.54 | 2725.04 | 2725.04 |  |  |  | 1 | 1 |  |  |  |  | 135514.08 | 2725.04 | 135514.08 | 2725.04 | 9.3135 | [5 empty] | 102.5781 |  |  | #VALUE!
23.03.2008 20:00 | 3600 | 2 | 761.6 | GGB | 764.102 | 772.102 | 768.132 | 260.7 | GGB | 10817.5 | GGB | 9.84 | GGB | 993.88 | GGB | 58.82 | GGB | 170505.04 | GGB | 137634.22 | GGB | 0 | 0 | 2822 | 3600 | 2805.99 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 180430.91 | GGB | 180433.01 | 2805.99 | 2745.8869 |  |  |  | 1 | 1 |  |  |  |  | 137634.22 | 2745.8869 | 137634.22 | 2745.8869 | 9.5751 | [5 empty] | 107.2778 | 2745.8869 |  | 104.98
23.03.2008 21:00 | 3600 | 2 | 761.73 | GGB | 763.004 | 772.055 | 768.132 | 262.51 | GGB | 10872.4 | GGB | 9.85 | GGB | 995.23 | GGB | 58.67 | GGB | 171931.07 | GGB | 139036.05 | GGB | 0 | 0 | 2847 | 3600 | 2831.09 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 180470.62 | GGB | 180472.73 | 2831.09 | 2718.2015 |  |  |  | 0 | 1 | [14 empty] | 109.3399 | 2718.2015 |  | 104.98
23.03.2008 22:00 | 3600 | 2 | 760.61 | GGB | 760.44 | 767.461 | 764.469 | 263.02 | GGB | 10852 | GGB | 9.84 | GGB | 996.6 | GGB | 58.74 | GGB | 172136.84 | GGB | 139362.75 | GGB | 0 | 0 | 2906 | 3600 | 2890.13 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 180510 | GGB | 180512.1 | 2890.13 | 2711.8294 |  |  |  | 0 | 1 | [14 empty] | 111.8824 | 2711.8294 |  | 104.98
23.03.2008 23:00 | 3600 | 2 | 760.64 | GGB | 762.637 | 770.672 | 767.033 | 264.76 | GGB | 10890.7 | GGB | 9.85 | GGB | 997.37 | GGB | 58.6 | GGB | 172960.99 | GGB | 140199.46 | GGB | 0 | 0 | 2934 | 3600 | 2918.67 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 180549.57 | GGB | 180551.67 | 2918.67 | 2695.6452 |  |  |  | 0 | 1 | [14 empty] | 113.6655 | 2695.6452 |  | 104.98
23.03.2008 24:00 | 3600 | 2 | 760.61 | GGB | 760.44 | 768.328 | 764.835 | 265.17 | GGB | 10902 | GGB | 9.85 | GGB | 997.69 | GGB | 58.63 | GGB | 173382.42 | GGB | 140572.34 | GGB | 0 | 0 | 2941 | 3600 | 2925.05 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 180589.21 | GGB | 180591.31 | 2925.05 | 2688.4948 |  |  |  | 0 | 1 | [14 empty] | 114.217 | 2688.4948 |  | 104.98
24.03.2008 01:00 | 3600 | 2 | 760.43 | GGB | 762.637 | 771.703 | 767.033 | 266.16 | GGB | 10933 | GGB | 9.85 | GGB | 997.98 | GGB | 58.58 | GGB | 174340.81 | GGB | 141411.3 | GGB | 0 | 0 | 2971 | 3600 | 2955.83 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 180628.81 | GGB | 180630.91 | 2955.83 | 2672.5446 |  |  |  | 0 | 1 | [14 empty] | 116.1077 | 2672.5446 |  | 104.98
24.03.2008 02:00 | 3600 | 2 | 760.13 | GGB | 761.172 | 769.523 | 765.934 | 266.95 | GGB | 10959.5 | GGB | 9.85 | GGB | 998.2 | GGB | 58.47 | GGB | 175328.92 | GGB | 142294.1 | GGB | 0 | 0 | 3004 | 3600 | 2988.05 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 180669.37 | GGB | 180671.48 | 2988.05 | 2655.964 |  |  |  | 0 | 1 | [14 empty] | 118.1061 | 2655.964 |  | 104.98
24.03.2008 03:00 | 3600 | 2 | 760.74 | GGB | 761.172 | 770.414 | 764.835 | 267.21 | GGB | 10978 | GGB | 9.86 | GGB | 998.23 | GGB | 58.36 | GGB | 175770.15 | GGB | 142703.61 | GGB | 0 | 0 | 2985 | 3600 | 2969.49 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 180709.91 | GGB | 180712.02 | 2969.49 | 2648.3423 |  |  |  | 0 | 1 | [14 empty] | 117.7103 | 2648.3423 |  | 104.98
24.03.2008 04:00 | 3600 | 2 | 758.93 | GGB | 759.707 | 767.813 | 764.469 | 269.81 | GGB | 10936.2 | GGB | 9.82 | GGB | 999.32 | GGB | 57.57 | GGB | 178965.53 | GGB | 145800.07 | GGB | 0 | 0 | 3063 | 3600 | 3047.19 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 180749.77 | GGB | 180751.88 | 3047.19 | 2592.0975 |  |  |  | 0 | 1 | [14 empty] | 123.4113 | 2592.0975 |  | 104.98
24.03.2008 05:00 | 3600 | 2 | 760.69 | GGB | 761.172 | 769.477 | 764.835 | 268.53 | GGB | 11043.9 | GGB | 9.87 | GGB | 999.61 | GGB | 58.15 | GGB | 177086.16 | GGB | 144060.76 | GGB | 0 | 0 | 3027 | 3600 | 3011.08 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 180789.6 | GGB | 180791.71 | 3011.08 | 2623.3931 |  |  |  | 0 | 1 | [14 empty] | 120.494 | 2623.3931 |  | 104.98
24.03.2008 06:00 | 3600 | 2 | 759.55 | GGB | 759.707 | 767.719 | 764.469 | 268.87 | GGB | 11047.1 | GGB | 9.85 | GGB | 999.57 | GGB | 58 | GGB | 178035.75 | GGB | 144890.9 | GGB | 0 | 0 | 3076 | 3600 | 3060.37 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 180830.04 | GGB | 180832.15 | 3060.37 | 2608.3626 |  |  |  | 0 | 1 | [14 empty] | 123.1722 | 2608.3626 |  | 104.98
24.03.2008 07:00 | 3600 | 2 | 759.8 | GGB | 764.835 | 772.57 | 769.597 | 269.04 | GGB | 11090.4 | GGB | 9.87 | GGB | 999.76 | GGB | 57.78 | GGB | 178662.94 | GGB | 145524.82 | GGB | 0 | 0 | 3082 | 3600 | 3066.31 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 180871.11 | GGB | 180873.22 | 3066.31 | 2597.0003 |  |  |  | 1 | 1 |  |  |  |  | 145524.82 | 2597.0003 | 145524.82 | 2597.0003 | 9.202 | [5 empty] | 123.9512 | 2597.0003 |  | 104.98
24.03.2008 08:00 | 3600 | 2 | 759.58 | GGB | 761.172 | 770.273 | 765.934 | 268.44 | GGB | 11072.1 | GGB | 9.86 | GGB | 999.91 | GGB | 57.73 | GGB | 178665.14 | GGB | 145575.64 | GGB | 0 | 0 | 3087 | 3600 | 3071.61 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 180911.98 | GGB | 180914.08 | 3071.61 | 2596.0937 |  |  |  | 0 | 1 | [14 empty] | 124.2088 | 2596.0937 |  | 104.98
24.03.2008 09:00 | 3600 | 2 | 761.99 | GGB | 764.835 | 772.875 | 768.498 | 265.75 | GGB | 11020.6 | GGB | 9.88 | GGB | 999.46 | GGB | 58.46 | GGB | 175403.74 | GGB | 142535.47 | GGB | 0 | 0 | 2953 | 3600 | 2937.78 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 180951.91 | GGB | 180954.02 | 2937.78 | 2651.4663 |  |  |  | 1 | 1 |  |  |  |  | 142535.47 | 2651.4663 | 142535.47 | 2651.4663 | 9.4624 | [5 empty] | 116.3161 | 2651.4663 |  | 104.98
24.03.2008 10:00 | 3600 | 2 | 763.28 | GGB | 765.934 | 774.305 | 770.696 | 263.63 | GGB | 10924 | GGB | 9.87 | GGB | 998.94 | GGB | 59.31 | GGB | 172093.92 | GGB | 139416.59 | GGB | 0 | 0 | 2846 | 3600 | 2830.9 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 180991.64 | GGB | 180993.74 | 2830.9 | 2710.7821 |  |  |  | 1 | 1 |  |  |  |  | 139416.59 | 2710.7821 | 139416.59 | 2710.7821 | 9.5148 | [5 empty] | 109.6318 | 2710.7821 |  | 104.98
24.03.2008 11:00 | 3600 | 2 | 763.6 | GGB | 764.835 | 773.93 | 770.696 | 262.4 | GGB | 10856.8 | GGB | 9.86 | GGB | 998 | GGB | 59.82 | GGB | 170499.54 | GGB | 137785 | GGB | 0 | 0 | 2802 | 3600 | 2786.82 | GGB | 100 | GGB | 41.35 | GGB | 41.35 | GGB | 181032.99 | GGB | 181035.09 | 2786.82 | 2742.882 |  |  |  | 1 | 1 |  |  |  |  | 137785 | 2742.882 | 137785 | 2742.882 | 9.1397 | [5 empty] | 106.6617 | 2742.882 |  | 104.98
24.03.2008 12:00 | 3600 | 2 | 764.33 | GGB | 768.132 | 777.422 | 773.26 | 261.52 | GGB | 10779.6 | GGB | 9.86 | GGB | 996.71 | GGB | 59.91 | GGB | 169987.88 | GGB | 137158.14 | GGB | 0 | 0 | 2728 | 3600 | 2712.18 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 181072.28 | GGB | 181074.38 | 2712.18 | 2712.18 |  |  |  | 1 | 1 |  |  |  |  | 137158.14 | 2712.18 | 137158.14 | 2712.18 | 9.468 | [5 empty] | 103.3327 |  |  | #VALUE!
24.03.2008 13:00 | 3600 | 2 | 764.07 | GGB | 763.37 | 772.734 | 768.498 | 260.12 | GGB | 10769.8 | GGB | 9.85 | GGB | 995.82 | GGB | 60.17 | GGB | 168373.68 | GGB | 135626.43 | GGB | 0 | 0 | 2729 | 3600 | 2713.88 | GGB | 100 | GGB | 38.63 | GGB | 38.63 | GGB | 181110.91 | GGB | 181113.01 | 2713.88 | 2713.88 |  |  |  | 0 | 1 | [14 empty] | 102.2427 |  |  | #VALUE!
24.03.2008 14:00 | 3600 | 2 | 764.46 | GGB | 765.934 | 775.219 | 770.696 | 260.06 | GGB | 10760 | GGB | 9.86 | GGB | 995.31 | GGB | 60.64 | GGB | 167870.83 | GGB | 134960.3 | GGB | 0 | 0 | 2716 | 3600 | 2700.76 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 181152.19 | GGB | 181154.29 | 2700.76 | 2700.76 |  |  |  | 1 | 1 |  |  |  |  | 134960.3 | 2700.76 | 134960.3 | 2700.76 | 8.8298 | [5 empty] | 101.2487 |  |  | #VALUE!
24.03.2008 15:00 | 3600 | 2 | 765.08 | GGB | 765.934 | 774.492 | 770.696 | 259.12 | GGB | 10729.4 | GGB | 9.86 | GGB | 994.27 | GGB | 60.91 | GGB | 166890.43 | GGB | 133923.54 | GGB | 0 | 0 | 2674 | 3600 | 2658.43 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 181191.31 | GGB | 181193.41 | 2658.43 | 2658.43 |  |  |  | 1 | 1 |  |  |  |  | 133923.54 | 2658.43 | 133923.54 | 2658.43 | 9.1009 | [5 empty] | 98.8962 |  |  | #VALUE!
24.03.2008 16:00 | 3600 | 2 | 765.47 | GGB | 765.934 | 774.492 | 770.696 | 258.72 | GGB | 10712.9 | GGB | 9.86 | GGB | 993.75 | GGB | 61.08 | GGB | 166306.15 | GGB | 133319.74 | GGB | 0 | 0 | 2645 | 3600 | 2629.62 | GGB | 100 | GGB | 38.21 | GGB | 38.21 | GGB | 181229.51 | GGB | 181231.62 | 2629.62 | 2629.62 |  |  |  | 1 | 1 |  |  |  |  | 133319.74 | 2629.62 | 133319.74 | 2629.62 | 9.1751 | [5 empty] | 97.3834 |  |  | #VALUE!
24.03.2008 17:00 | 3600 | 2 | 764.83 | GGB | 765.934 | 774.773 | 770.696 | 258.93 | GGB | 10706.3 | GGB | 9.85 | GGB | 992.92 | GGB | 61.09 | GGB | 166401.88 | GGB | 133280.61 | GGB | 0 | 0 | 2667 | 3600 | 2651.89 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 181270.91 | GGB | 181273.02 | 2651.89 | 2651.89 |  |  |  | 1 | 1 |  |  |  |  | 133280.61 | 2651.89 | 133280.61 | 2651.89 | 8.5373 | [5 empty] | 98.1793 |  |  | #VALUE!
24.03.2008 18:00 | 3600 | 2 | 764.86 | GGB | 764.835 | 773.578 | 769.597 | 259.03 | GGB | 10712.4 | GGB | 9.86 | GGB | 993.23 | GGB | 61.09 | GGB | 166516.31 | GGB | 133411.26 | GGB | 0 | 0 | 2662 | 3600 | 2646.22 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 181309.96 | GGB | 181312.07 | 2646.22 | 2646.22 |  |  |  | 1 | 1 |  |  |  |  | 133411.26 | 2646.22 | 133411.26 | 2646.22 | 9.0406 | [5 empty] | 98.0654 |  |  | #VALUE!
24.03.2008 19:00 | 3600 | 2 | 763.88 | GGB | 764.469 | 773.531 | 769.597 | 260.32 | GGB | 10732.1 | GGB | 9.85 | GGB | 993.26 | GGB | 60.87 | GGB | 167677.17 | GGB | 134434.9 | GGB | 0 | 0 | 2714 | 3600 | 2698.74 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 181349.28 | GGB | 181351.4 | 2698.74 | 2698.74 |  |  |  | 1 | 1 |  |  |  |  | 134434.9 | 2698.74 | 134434.9 | 2698.74 | 9.2246 | [5 empty] | 100.7791 |  |  | #VALUE!
24.03.2008 20:00 | 3600 | 2 | 763.21 | GGB | 764.835 | 773.93 | 769.597 | 261.39 | GGB | 10765.7 | GGB | 9.85 | GGB | 993.34 | GGB | 60.57 | GGB | 168764.3 | GGB | 135437.54 | GGB | 0 | 0 | 2761 | 3600 | 2745.87 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 181388.96 | GGB | 181391.07 | 2745.87 | 2745.87 |  |  |  | 1 | 1 |  |  |  |  | 135437.54 | 2745.87 | 135437.54 | 2745.87 | 9.3747 | [5 empty] | 103.3039 |  |  | #VALUE!
24.03.2008 21:00 | 3600 | 2 | 762.31 | GGB | 763.37 | 772.43 | 768.498 | 261.24 | GGB | 10794.2 | GGB | 9.85 | GGB | 993.8 | GGB | 59.88 | GGB | 169864.64 | GGB | 136669.85 | GGB | 0 | 0 | 2803 | 3600 | 2787.56 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 181428.24 | GGB | 181430.35 | 2787.56 | 2765.2624 |  |  |  | 0 | 1 | [14 empty] | 105.8265 | 2765.2624 |  | 104.98
24.03.2008 22:00 | 3600 | 2 | 763.48 | GGB | 764.835 | 773.508 | 769.597 | 262.19 | GGB | 10808.7 | GGB | 9.86 | GGB | 993.51 | GGB | 60.11 | GGB | 169659.98 | GGB | 136371.19 | GGB | 0 | 0 | 2770 | 3600 | 2754.94 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 181467.42 | GGB | 181469.53 | 2754.94 | 2754.94 |  |  |  | 1 | 1 |  |  |  |  | 136371.19 | 2754.94 | 136371.19 | 2754.94 | 9.5889 | [5 empty] | 104.3596 |  |  | #VALUE!
24.03.2008 23:00 | 3600 | 2 | 762.39 | GGB | 765.934 | 774.492 | 769.597 | 262.2 | GGB | 10795.6 | GGB | 9.85 | GGB | 992.45 | GGB | 59.99 | GGB | 170028.59 | GGB | 136567.99 | GGB | 0 | 0 | 2816 | 3600 | 2800.28 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 181507.64 | GGB | 181509.75 | 2800.28 | 2767.3249 |  |  |  | 1 | 1 |  |  |  |  | 136567.99 | 2767.3249 | 136567.99 | 2767.3249 | 9.3965 | [5 empty] | 106.2302 | 2767.3249 |  | 104.98
24.03.2008 24:00 | 3600 | 2 | 762.6 | GGB | 762.271 | 770.297 | 766.3 | 262.43 | GGB | 10814.6 | GGB | 9.85 | GGB | 992.07 | GGB | 59.93 | GGB | 170637.08 | GGB | 137030.93 | GGB | 0 | 0 | 2804 | 3600 | 2788.19 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 181547.51 | GGB | 181549.62 | 2788.19 | 2757.9759 |  |  |  | 0 | 1 | [14 empty] | 106.1301 | 2757.9759 |  | 104.98
25.03.2008 01:00 | 3600 | 2 | 763.04 | GGB | 763.37 | 772.266 | 768.864 | 262.14 | GGB | 10814.3 | GGB | 9.86 | GGB | 991.34 | GGB | 59.84 | GGB | 170206.85 | GGB | 136623.56 | GGB | 0 | 0 | 2788 | 3600 | 2772.98 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 181586.44 | GGB | 181588.55 | 2772.98 | 2766.1993 |  |  |  | 0 | 1 | [14 empty] | 105.2373 | 2766.1993 |  | 104.98
25.03.2008 02:00 | 3600 | 2 | 762.39 | GGB | 763.37 | 772.359 | 767.766 | 261.6 | GGB | 10803.1 | GGB | 9.85 | GGB | 990.38 | GGB | 59.38 | GGB | 170196.94 | GGB | 136670.81 | GGB | 0 | 0 | 2809 | 3600 | 2793.04 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 181624.96 | GGB | 181627.07 | 2793.04 | 2765.243 |  |  |  | 0 | 1 | [14 empty] | 106.0353 | 2765.243 |  | 104.98
25.03.2008 03:00 | 3600 | 2 | 762.33 | GGB | 764.835 | 773.086 | 768.864 | 261.65 | GGB | 10816 | GGB | 9.86 | GGB | 989.73 | GGB | 59.27 | GGB | 170574.36 | GGB | 136928.11 | GGB | 0 | 0 | 2811 | 3600 | 2795.38 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 181664.13 | GGB | 181666.24 | 2795.38 | 2760.0469 |  |  |  | 1 | 1 |  |  |  |  | 136928.11 | 2760.0469 | 136928.11 | 2760.0469 | 9.6484 | [5 empty] | 106.3239 | 2760.0469 |  | 104.98
25.03.2008 04:00 | 3600 | 2 | 762.3 | GGB | 763.37 | 772.172 | 767.766 | 261.28 | GGB | 10816.2 | GGB | 9.85 | GGB | 988.68 | GGB | 59.11 | GGB | 170551.25 | GGB | 136829.42 | GGB | 0 | 0 | 2801 | 3600 | 2785.05 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 181704.11 | GGB | 181706.22 | 2785.05 | 2762.0376 |  |  |  | 0 | 1 | [14 empty] | 105.8547 | 2762.0376 |  | 104.98
25.03.2008 05:00 | 3600 | 2 | 762.37 | GGB | 763.37 | 771.82 | 767.766 | 261.18 | GGB | 10823.6 | GGB | 9.86 | GGB | 987.96 | GGB | 59.03 | GGB | 170533.65 | GGB | 136749.4 | GGB | 0 | 0 | 2804 | 3600 | 2788.86 | GGB | 100 | GGB | 42.06 | GGB | 42.06 | GGB | 181746.18 | GGB | 181748.28 | 2788.86 | 2763.6538 |  |  |  | 0 | 1 | [14 empty] | 105.9375 | 2763.6538 |  | 104.98
25.03.2008 06:00 | 3600 | 2 | 761.97 | GGB | 764.469 | 773.063 | 767.766 | 261.27 | GGB | 10819.8 | GGB | 9.85 | GGB | 987.42 | GGB | 59.02 | GGB | 170752.61 | GGB | 136854.88 | GGB | 0 | 0 | 2817 | 3600 | 2801.89 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 181786.86 | GGB | 181788.97 | 2801.89 | 2761.5237 |  |  |  | 1 | 1 |  |  |  |  | 136854.88 | 2761.5237 | 136854.88 | 2761.5237 | 9.288 | [5 empty] | 106.5145 | 2761.5237 |  | 104.98
25.03.2008 07:00 | 3600 | 2 | 761.27 | GGB | 763.37 | 771.75 | 767.766 | 262.01 | GGB | 10832.3 | GGB | 9.85 | GGB | 987.04 | GGB | 58.65 | GGB | 171379.81 | GGB | 137459.64 | GGB | 0 | 0 | 2857 | 3600 | 2841.77 | GGB | 100 | GGB | 37.11 | GGB | 37.11 | GGB | 181823.98 | GGB | 181826.08 | 2841.77 | 2749.3743 |  |  |  | 0 | 1 | [14 empty] | 108.508 | 2749.3743 |  | 104.98
25.03.2008 08:00 | 3600 | 2 | 761.49 | GGB | 763.37 | 772.898 | 768.864 | 261.79 | GGB | 10854.4 | GGB | 9.86 | GGB | 986.31 | GGB | 58.54 | GGB | 171550.36 | GGB | 137537.92 | GGB | 0 | 0 | 2864 | 3600 | 2848.34 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 181865.49 | GGB | 181867.59 | 2848.34 | 2747.8095 |  |  |  | 0 | 1 | [14 empty] | 108.8208 | 2747.8095 |  | 104.98
25.03.2008 09:00 | 3600 | 2 | 761.9 | GGB | 763.37 | 771.563 | 767.766 | 261.25 | GGB | 10843.1 | GGB | 9.86 | GGB | 985.85 | GGB | 58.62 | GGB | 171145.43 | GGB | 137118.37 | GGB | 0 | 0 | 2842 | 3600 | 2826.51 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 181904.94 | GGB | 181907.04 | 2826.51 | 2756.2171 |  |  |  | 0 | 1 | [14 empty] | 107.6573 | 2756.2171 |  | 104.98
25.03.2008 10:00 | 3600 | 2 | 762.21 | GGB | 764.469 | 772.711 | 767.766 | 260.72 | GGB | 10834 | GGB | 9.86 | GGB | 985.31 | GGB | 58.73 | GGB | 170698.7 | GGB | 136637.69 | GGB | 0 | 0 | 2824 | 3600 | 2808.8 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 181944.42 | GGB | 181946.52 | 2808.8 | 2765.9133 |  |  |  | 1 | 1 |  |  |  |  | 136637.69 | 2765.9133 | 136637.69 | 2765.9133 | 9.5726 | [5 empty] | 106.6078 | 2765.9133 |  | 104.98
25.03.2008 11:00 | 3600 | 2 | 762.34 | GGB | 763.37 | 772.031 | 767.766 | 259.93 | GGB | 10807.5 | GGB | 9.86 | GGB | 984.5 | GGB | 58.91 | GGB | 169932.86 | GGB | 135841.48 | GGB | 0 | 0 | 2804 | 3600 | 2788.88 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 181983.95 | GGB | 181986.04 | 2788.88 | 2782.1252 |  |  |  | 0 | 1 | [14 empty] | 105.2349 | 2782.1252 |  | 104.98
25.03.2008 12:00 | 3600 | 2 | 762.33 | GGB | 763.37 | 772.102 | 767.766 | 259.4 | GGB | 10789 | GGB | 9.86 | GGB | 984.12 | GGB | 58.82 | GGB | 169146.12 | GGB | 135194.57 | GGB | 0 | 0 | 2804 | 3600 | 2788.53 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 182024.22 | GGB | 182026.31 | 2788.53 | 2788.53 |  |  |  | 0 | 1 | [14 empty] | 104.7206 |  |  | #VALUE!
25.03.2008 13:00 | 3600 | 2 | 763.05 | GGB | 765.934 | 774.328 | 770.696 | 258.85 | GGB | 10767.6 | GGB | 9.86 | GGB | 983.9 | GGB | 59.34 | GGB | 168436.4 | GGB | 134384.93 | GGB | 0 | 0 | 2769 | 3600 | 2753.33 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 182063.68 | GGB | 182065.77 | 2753.33 | 2753.33 |  |  |  | 1 | 1 |  |  |  |  | 134384.93 | 2753.33 | 134384.93 | 2753.33 | 9.3767 | [5 empty] | 102.7795 |  |  | #VALUE!
25.03.2008 14:00 | 3600 | 2 | 763.89 | GGB | 764.835 | 774.539 | 770.696 | 257.07 | GGB | 10706.1 | GGB | 9.86 | GGB | 983.5 | GGB | 59.82 | GGB | 166135.6 | GGB | 132306.2 | GGB | 0 | 0 | 2710 | 3600 | 2695.02 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 182102.22 | GGB | 182104.31 | 2695.02 | 2695.02 |  |  |  | 1 | 1 |  |  |  |  | 132306.2 | 2695.02 | 132306.2 | 2695.02 | 9.2519 | [5 empty] | 99.0466 |  |  | #VALUE!
25.03.2008 15:00 | 3600 | 2 | 763.9 | GGB | 764.835 | 773.695 | 769.597 | 256.36 | GGB | 10661.7 | GGB | 9.86 | GGB | 983.55 | GGB | 60.21 | GGB | 165101.28 | GGB | 131336.56 | GGB | 0 | 0 | 2695 | 3600 | 2679.9 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 182142.45 | GGB | 182144.54 | 2679.9 | 2679.9 |  |  |  | 1 | 1 |  |  |  |  | 131336.56 | 2679.9 | 131336.56 | 2679.9 | 8.7489 | [5 empty] | 97.7691 |  |  | #VALUE!
25.03.2008 16:00 | 3600 | 2 | 764.24 | GGB | 765.934 | 774.867 | 770.696 | 256.03 | GGB | 10650.4 | GGB | 9.86 | GGB | 983.04 | GGB | 60.25 | GGB | 164529.1 | GGB | 130797.54 | GGB | 0 | 0 | 2676 | 3600 | 2660.39 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 182182.22 | GGB | 182184.31 | 2660.39 | 2660.39 |  |  |  | 1 | 1 |  |  |  |  | 130797.54 | 2660.39 | 130797.54 | 2660.39 | 8.7496 | [5 empty] | 96.659 |  |  | #VALUE!
25.03.2008 17:00 | 3600 | 2 | 763.9 | GGB | 764.835 | 773.719 | 769.597 | 256.33 | GGB | 10645.4 | GGB | 9.85 | GGB | 983.22 | GGB | 60.23 | GGB | 164611.63 | GGB | 130893.89 | GGB | 0 | 0 | 2690 | 3600 | 2674.15 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 182221.11 | GGB | 182223.2 | 2674.15 | 2674.15 |  |  |  | 1 | 1 |  |  |  |  | 130893.89 | 2674.15 | 130893.89 | 2674.15 | 9.0005 | [5 empty] | 97.2305 |  |  | #VALUE!
25.03.2008 18:00 | 3600 | 2 | 764.45 | GGB | 765.934 | 774.773 | 770.696 | 255.81 | GGB | 10629.9 | GGB | 9.86 | GGB | 983.06 | GGB | 60.5 | GGB | 164080.16 | GGB | 130344.11 | GGB | 0 | 0 | 2654 | 3600 | 2638.94 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 182259.66 | GGB | 182261.76 | 2638.94 | 2638.94 |  |  |  | 1 | 1 |  |  |  |  | 130344.11 | 2638.94 | 130344.11 | 2638.94 | 8.9204 | [5 empty] | 95.5473 |  |  | #VALUE!
25.03.2008 19:00 | 3600 | 2 | 763.98 | GGB | 763.37 | 772.992 | 768.498 | 256.22 | GGB | 10643.4 | GGB | 9.85 | GGB | 983.1 | GGB | 60.28 | GGB | 164621.53 | GGB | 130865.5 | GGB | 0 | 0 | 2674 | 3600 | 2658.51 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 182298.43 | GGB | 182300.53 | 2658.51 | 2658.51 |  |  |  | 0 | 1 | [14 empty] | 96.6409 |  |  | #VALUE!
25.03.2008 20:00 | 3600 | 2 | 763.52 | GGB | 762.271 | 771.258 | 767.033 | 255.92 | GGB | 10679.5 | GGB | 9.86 | GGB | 983.53 | GGB | 59.81 | GGB | 165944.14 | GGB | 132163.68 | GGB | 0 | 0 | 2704 | 3600 | 2688.19 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 182337.31 | GGB | 182339.41 | 2688.19 | 2688.19 |  |  |  | 0 | 1 | [14 empty] | 98.6892 |  |  | #VALUE!
25.03.2008 21:00 | 3600 | 2 | 763.25 | GGB | 763.37 | 773.672 | 768.498 | 256.89 | GGB | 10669.2 | GGB | 9.85 | GGB | 983.4 | GGB | 59.97 | GGB | 165815.4 | GGB | 131977.26 | GGB | 0 | 0 | 2725 | 3600 | 2709.57 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 182376.49 | GGB | 182378.59 | 2709.57 | 2709.57 |  |  |  | 0 | 1 | [14 empty] | 99.3338 |  |  | #VALUE!
25.03.2008 22:00 | 3600 | 2 | 763.41 | GGB | 762.271 | 771.703 | 767.033 | 257.36 | GGB | 10681.4 | GGB | 9.86 | GGB | 982.81 | GGB | 59.97 | GGB | 166314.95 | GGB | 132298.29 | GGB | 0 | 0 | 2724 | 3600 | 2708.85 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 182416.33 | GGB | 182418.43 | 2708.85 | 2708.85 |  |  |  | 0 | 1 | [14 empty] | 99.549 |  |  | #VALUE!
25.03.2008 23:00 | 3600 | 2 | 763.63 | GGB | 764.469 | 772.969 | 768.498 | 256.7 | GGB | 10685.6 | GGB | 9.86 | GGB | 982.56 | GGB | 59.93 | GGB | 165766.98 | GGB | 131843.87 | GGB | 0 | 0 | 2711 | 3600 | 2695.18 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 182456.13 | GGB | 182458.24 | 2695.18 | 2695.18 |  |  |  | 1 | 1 |  |  |  |  | 131843.87 | 2695.18 | 131843.87 | 2695.18 | 8.926 | [5 empty] | 98.7064 |  |  | #VALUE!
25.03.2008 24:00 | 3600 | 2 | 763.52 | GGB | 764.469 | 774.07 | 769.597 | 256.45 | GGB | 10682.3 | GGB | 9.85 | GGB | 982.32 | GGB | 59.78 | GGB | 165956.24 | GGB | 132018.9 | GGB | 0 | 0 | 2713 | 3600 | 2697.47 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 182495.16 | GGB | 182497.27 | 2697.47 | 2697.47 |  |  |  | 1 | 1 |  |  |  |  | 132018.9 | 2697.47 | 132018.9 | 2697.47 | 9.1242 | [5 empty] | 98.9214 |  |  | #VALUE!
26.03.2008 01:00 | 3600 | 2 | 763.51 | GGB | 763.37 | 773.016 | 768.498 | 256.45 | GGB | 10687.5 | GGB | 9.86 | GGB | 982.22 | GGB | 59.53 | GGB | 165828.6 | GGB | 132005.18 | GGB | 0 | 0 | 2710 | 3600 | 2694.72 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 182534.74 | GGB | 182536.85 | 2694.72 | 2694.72 |  |  |  | 0 | 1 | [14 empty] | 98.8103 |  |  | #VALUE!
26.03.2008 02:00 | 3600 | 2 | 763.14 | GGB | 763.37 | 772.828 | 768.498 | 256.68 | GGB | 10700.3 | GGB | 9.85 | GGB | 981.84 | GGB | 59.26 | GGB | 166656.06 | GGB | 132720.54 | GGB | 0 | 0 | 2728 | 3600 | 2712.42 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 182574.4 | GGB | 182576.5 | 2712.42 | 2712.42 |  |  |  | 0 | 1 | [14 empty] | 99.9983 |  |  | #VALUE!
26.03.2008 03:00 | 3600 | 2 | 762.96 | GGB | 762.271 | 771.211 | 767.033 | 257.39 | GGB | 10713 | GGB | 9.85 | GGB | 982.1 | GGB | 59.22 | GGB | 167030.17 | GGB | 133069.68 | GGB | 0 | 0 | 2730 | 3600 | 2714.46 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 182613.28 | GGB | 182615.38 | 2714.46 | 2714.46 |  |  |  | 0 | 1 | [14 empty] | 100.3368 |  |  | #VALUE!
26.03.2008 04:00 | 3600 | 2 | 762.08 | GGB | 762.271 | 771.328 | 767.033 | 258.58 | GGB | 10745.4 | GGB | 9.85 | GGB | 982.37 | GGB | 58.68 | GGB | 168433.1 | GGB | 134440.66 | GGB | 0 | 0 | 2769 | 3600 | 2753.26 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 182652.03 | GGB | 182654.13 | 2753.26 | 2753.26 |  |  |  | 0 | 1 | [14 empty] | 102.8195 |  |  | #VALUE!
26.03.2008 05:00 | 3600 | 2 | 762.12 | GGB | 763.37 | 772.359 | 768.498 | 259.33 | GGB | 10780.9 | GGB | 9.86 | GGB | 982.91 | GGB | 58.51 | GGB | 169492.73 | GGB | 135432.21 | GGB | 0 | 0 | 2790 | 3600 | 2774.22 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 182691.55 | GGB | 182693.66 | 2774.22 | 2774.22 |  |  |  | 0 | 1 | [14 empty] | 104.3663 |  |  | #VALUE!
26.03.2008 06:00 | 3600 | 2 | 762.41 | GGB | 764.469 | 773.484 | 769.597 | 259.8 | GGB | 10784 | GGB | 9.85 | GGB | 983.85 | GGB | 58.86 | GGB | 169452.01 | GGB | 135384.22 | GGB | 0 | 0 | 2784 | 3600 | 2768.55 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 182731.63 | GGB | 182733.74 | 2768.55 | 2768.55 |  |  |  | 1 | 1 |  |  |  |  | 135384.22 | 2768.55 | 135384.22 | 2768.55 | 9.3517 | [5 empty] | 104.1161 |  |  | #VALUE!
26.03.2008 07:00 | 3600 | 2 | 762.21 | GGB | 762.271 | 771.258 | 767.033 | 260.73 | GGB | 10780.4 | GGB | 9.85 | GGB | 984.72 | GGB | 58.74 | GGB | 170428.01 | GGB | 136335.33 | GGB | 0 | 0 | 2804 | 3600 | 2788.1 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 182770.98 | GGB | 182773.08 | 2788.1 | 2772.0474 |  |  |  | 0 | 1 | [14 empty] | 105.5879 | 2772.0474 |  | 104.98
26.03.2008 08:00 | 3600 | 2 | 763.34 | GGB | 765.934 | 774.352 | 769.597 | 261.36 | GGB | 10771.3 | GGB | 9.86 | GGB | 985.26 | GGB | 58.28 | GGB | 171621.88 | GGB | 137557.3 | GGB | 0 | 0 | 2747 | 3600 | 2731.97 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 182810.45 | GGB | 182812.56 | 2731.97 | 2731.97 |  |  |  | 1 | 1 |  |  |  |  | 137557.3 | 2731.97 | 137557.3 | 2731.97 | 9.5188 | [5 empty] | 104.3896 |  |  | #VALUE!
26.03.2008 09:00 | 3600 | 2 | 763.66 | GGB | 768.132 | 776.227 | 771.795 | 259.03 | GGB | 10780.8 | GGB | 9.87 | GGB | 985.35 | GGB | 58.98 | GGB | 168616.86 | GGB | 134873.76 | GGB | 0 | 0 | 2737 | 3600 | 2721.09 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 182850.06 | GGB | 182852.17 | 2721.09 | 2721.09 |  |  |  | 1 | 1 |  |  |  |  | 134873.76 | 2721.09 | 134873.76 | 2721.09 | 9.2654 | [5 empty] | 101.9455 |  |  | #VALUE!
26.03.2008 10:00 | 3600 | 2 | 763.65 | GGB | 765.934 | 774 | 770.696 | 259.01 | GGB | 10712.7 | GGB | 9.85 | GGB | 986.02 | GGB | 59.16 | GGB | 168600.35 | GGB | 134879.36 | GGB | 0 | 0 | 2710 | 3600 | 2694.76 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 182890.24 | GGB | 182892.35 | 2694.76 | 2694.76 |  |  |  | 1 | 1 |  |  |  |  | 134879.36 | 2694.76 | 134879.36 | 2694.76 | 9.046 | [5 empty] | 100.9632 |  |  | #VALUE!
26.03.2008 11:00 | 3600 | 2 | 765.04 | GGB | 767.033 | 775.992 | 771.795 | 257.77 | GGB | 10703.2 | GGB | 9.87 | GGB | 986.23 | GGB | 59.43 | GGB | 167274.45 | GGB | 133740.47 | GGB | 0 | 0 | 2638 | 3600 | 2622.26 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 182929.26 | GGB | 182931.37 | 2622.26 | 2622.26 |  |  |  | 1 | 1 |  |  |  |  | 133740.47 | 2622.26 | 133740.47 | 2622.26 | 8.9878 | [5 empty] | 97.4173 |  |  | #VALUE!
26.03.2008 12:00 | 3600 | 2 | 764.98 | GGB | 765.934 | 774.867 | 770.696 | 256.9 | GGB | 10651.2 | GGB | 9.85 | GGB | 986.56 | GGB | 59.93 | GGB | 165750.48 | GGB | 132365.24 | GGB | 0 | 0 | 2631 | 3600 | 2615.98 | GGB | 100 | GGB | 37.31 | GGB | 37.31 | GGB | 182966.57 | GGB | 182968.68 | 2615.98 | 2615.98 |  |  |  | 1 | 1 |  |  |  |  | 132365.24 | 2615.98 | 132365.24 | 2615.98 | 9.2808 | [5 empty] | 96.1847 |  |  | #VALUE!
26.03.2008 13:00 | 3600 | 2 | 764.95 | GGB | 767.033 | 776.391 | 771.795 | 257.73 | GGB | 10663.2 | GGB | 9.86 | GGB | 987.28 | GGB | 59.93 | GGB | 165947.44 | GGB | 132621.94 | GGB | 0 | 0 | 2643 | 3600 | 2627.91 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 183007.02 | GGB | 183009.13 | 2627.91 | 2627.91 |  |  |  | 1 | 1 |  |  |  |  | 132621.94 | 2627.91 | 132621.94 | 2627.91 | 8.616 | [5 empty] | 96.8107 |  |  | #VALUE!
26.03.2008 14:00 | 3600 | 2 | 764.53 | GGB | 764.835 | 774.07 | 768.864 | 257.23 | GGB | 10646.2 | GGB | 9.84 | GGB | 987.02 | GGB | 60.38 | GGB | 165322.45 | GGB | 131909.94 | GGB | 0 | 0 | 2652 | 3600 | 2637.14 | GGB | 100 | GGB | 42.53 | GGB | 42.53 | GGB | 183049.56 | GGB | 183051.66 | 2637.14 | 2637.14 |  |  |  | 1 | 1 |  |  |  |  | 131909.94 | 2637.14 | 131909.94 | 2637.14 | 8.1793 | [5 empty] | 96.6292 |  |  | #VALUE!
26.03.2008 15:00 | 3600 | 2 | 764.51 | GGB | 764.835 | 773.133 | 768.864 | 259.07 | GGB | 10650.9 | GGB | 9.85 | GGB | 987.37 | GGB | 59.69 | GGB | 167448.3 | GGB | 133928.58 | GGB | 0 | 0 | 2672 | 3600 | 2656.56 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 183088.05 | GGB | 183090.16 | 2656.56 | 2656.56 |  |  |  | 1 | 1 |  |  |  |  | 133928.58 | 2656.56 | 133928.58 | 2656.56 | 9.2413 | [5 empty] | 98.8304 |  |  | #VALUE!
26.03.2008 16:00 | 3600 | 2 | 765.95 | GGB | 765.934 | 775.008 | 770.33 | 257.57 | GGB | 10652.3 | GGB | 9.87 | GGB | 987.45 | GGB | 60.06 | GGB | 165700.96 | GGB | 132392.79 | GGB | 0 | 0 | 2598 | 3600 | 2583.11 | GGB | 100 | GGB | 36.88 | GGB | 36.88 | GGB | 183124.93 | GGB | 183127.04 | 2583.11 | 2583.11 |  |  |  | 1 | 1 |  |  |  |  | 132392.79 | 2583.11 | 132392.79 | 2583.11 | 9.2729 | [5 empty] | 94.9959 |  |  | #VALUE!
26.03.2008 17:00 | 3600 | 2 | 765.5 | GGB | 765.934 | 775.781 | 771.429 | 256.1 | GGB | 10639.8 | GGB | 9.85 | GGB | 987.69 | GGB | 60.83 | GGB | 163607.02 | GGB | 130452.2 | GGB | 0 | 0 | 2615 | 3600 | 2599.47 | GGB | 100 | GGB | 41.87 | GGB | 41.87 | GGB | 183166.8 | GGB | 183168.91 | 2599.47 | 2599.47 |  |  |  | 1 | 1 |  |  |  |  | 130452.2 | 2599.47 | 130452.2 | 2599.47 | 8.099 | [5 empty] | 94.1963 |  |  | #VALUE!
26.03.2008 18:00 | 3600 | 2 | 764.95 | GGB | 764.469 | 773.602 | 769.963 | 257.3 | GGB | 10639.3 | GGB | 9.84 | GGB | 988.57 | GGB | 60.54 | GGB | 164965.94 | GGB | 131766.8 | GGB | 0 | 0 | 2634 | 3600 | 2618.75 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 183204.91 | GGB | 183207.02 | 2618.75 | 2618.75 |  |  |  | 1 | 1 |  |  |  |  | 131766.8 | 2618.75 | 131766.8 | 2618.75 | 9.0544 | [5 empty] | 95.8512 |  |  | #VALUE!
26.03.2008 19:00 | 3600 | 2 | 765.06 | GGB | 764.835 | 773.602 | 770.33 | 258.89 | GGB | 10685.5 | GGB | 9.86 | GGB | 989.86 | GGB | 60.2 | GGB | 166255.53 | GGB | 133105.81 | GGB | 0 | 0 | 2649 | 3600 | 2634.11 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 183243.86 | GGB | 183245.98 | 2634.11 | 2634.11 |  |  |  | 1 | 1 |  |  |  |  | 133105.81 | 2634.11 | 133105.81 | 2634.11 | 8.9994 | [5 empty] | 97.3932 |  |  | #VALUE!
26.03.2008 20:00 | 3600 | 2 | 764.36 | GGB | 764.835 | 774.398 | 770.33 | 258.94 | GGB | 10703.9 | GGB | 9.85 | GGB | 990.9 | GGB | 60.76 | GGB | 165850.61 | GGB | 132697.82 | GGB | 0 | 0 | 2689 | 3600 | 2673.76 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 183283.19 | GGB | 183285.31 | 2673.76 | 2673.76 |  |  |  | 1 | 1 |  |  |  |  | 132697.82 | 2673.76 | 132697.82 | 2673.76 | 9.0212 | [5 empty] | 98.5561 |  |  | #VALUE!
26.03.2008 21:00 | 3600 | 2 | 763.86 | GGB | 767.033 | 775.523 | 771.429 | 260.17 | GGB | 10727.1 | GGB | 9.85 | GGB | 991.94 | GGB | 60.72 | GGB | 166784.8 | GGB | 133601.11 | GGB | 0 | 0 | 2734 | 3600 | 2718.98 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 183322.04 | GGB | 183324.16 | 2718.98 | 2718.98 |  |  |  | 1 | 1 |  |  |  |  | 133601.11 | 2718.98 | 133601.11 | 2718.98 | 9.3503 | [5 empty] | 100.9052 |  |  | #VALUE!
26.03.2008 22:00 | 3600 | 2 | 763.66 | GGB | 768.132 | 777.375 | 773.626 | 261.19 | GGB | 10743.4 | GGB | 9.85 | GGB | 992.68 | GGB | 60.28 | GGB | 168825.92 | GGB | 135517.44 | GGB | 0 | 0 | 2749 | 3600 | 2733.92 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 183361.82 | GGB | 183363.95 | 2733.92 | 2733.92 |  |  |  | 1 | 1 |  |  |  |  | 135517.44 | 2733.92 | 135517.44 | 2733.92 | 9.3112 | [5 empty] | 102.915 |  |  | #VALUE!
26.03.2008 23:00 | 3600 | 2 | 763.99 | GGB | 764.469 | 773.25 | 768.864 | 263.12 | GGB | 10733 | GGB | 9.85 | GGB | 993.22 | GGB | 60.08 | GGB | 170146.33 | GGB | 136731.67 | GGB | 0 | 0 | 2735 | 3600 | 2719.41 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 183402.04 | GGB | 183404.17 | 2719.41 | 2719.41 |  |  |  | 1 | 1 |  |  |  |  | 136731.67 | 2719.41 | 136731.67 | 2719.41 | 9.2449 | [5 empty] | 103.286 |  |  | #VALUE!
26.03.2008 24:00 | 3600 | 2 | 764.16 | GGB | 765.934 | 774.797 | 771.429 | 263.24 | GGB | 10774.1 | GGB | 9.86 | GGB | 993.78 | GGB | 59.9 | GGB | 170225.55 | GGB | 136948.56 | GGB | 0 | 0 | 2742 | 3600 | 2726.11 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 183440.53 | GGB | 183442.66 | 2726.11 | 2726.11 |  |  |  | 1 | 1 |  |  |  |  | 136948.56 | 2726.11 | 136948.56 | 2726.11 | 9.6996 | [5 empty] | 103.7047 |  |  | #VALUE!
27.03.2008 01:00 | 3600 | 2 | 763.14 | GGB | 767.033 | 775.617 | 771.429 | 262.38 | GGB | 10798 | GGB | 9.85 | GGB | 994.18 | GGB | 60.43 | GGB | 169021.78 | GGB | 135819.14 | GGB | 0 | 0 | 2796 | 3600 | 2780.67 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 183478.8 | GGB | 183480.93 | 2780.67 | 2780.67 |  |  |  | 1 | 1 |  |  |  |  | 135819.14 | 2780.67 | 135819.14 | 2780.67 | 9.8685 | [5 empty] | 104.9078 |  |  | #VALUE!
27.03.2008 02:00 | 3600 | 2 | 763.12 | GGB | 765.934 | 774.258 | 769.963 | 262.82 | GGB | 10802.5 | GGB | 9.85 | GGB | 994.69 | GGB | 60.21 | GGB | 169830.53 | GGB | 136629.85 | GGB | 0 | 0 | 2804 | 3600 | 2788.93 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 183519.6 | GGB | 183521.73 | 2788.93 | 2766.072 |  |  |  | 1 | 1 |  |  |  |  | 136629.85 | 2766.072 | 136629.85 | 2766.072 | 9.2629 | [5 empty] | 105.8475 | 2766.072 |  | 104.98
27.03.2008 03:00 | 3600 | 2 | 762.74 | GGB | 763.37 | 772.148 | 767.766 | 263.45 | GGB | 10809.5 | GGB | 9.85 | GGB | 995.65 | GGB | 60.04 | GGB | 170470.93 | GGB | 137346.23 | GGB | 0 | 0 | 2823 | 3600 | 2807.61 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 183560.36 | GGB | 183562.49 | 2807.61 | 2751.6445 |  |  |  | 0 | 1 | [14 empty] | 107.1152 | 2751.6445 |  | 104.98
27.03.2008 04:00 | 3600 | 2 | 762.56 | GGB | 763.37 | 771.305 | 767.766 | 263.95 | GGB | 10822.1 | GGB | 9.85 | GGB | 996.3 | GGB | 59.76 | GGB | 171183.95 | GGB | 138126.12 | GGB | 0 | 0 | 2839 | 3600 | 2823.44 | GGB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 183598.48 | GGB | 183600.61 | 2823.44 | 2736.1081 |  |  |  | 0 | 1 | [14 empty] | 108.3308 | 2736.1081 |  | 104.98
27.03.2008 05:00 | 3600 | 2 | 762.74 | GGB | 763.37 | 773.039 | 768.498 | 264.39 | GGB | 10863.4 | GGB | 9.86 | GGB | 996.85 | GGB | 59.67 | GGB | 171522.85 | GGB | 138513.02 | GGB | 0 | 0 | 2850 | 3600 | 2834.6 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 183638.42 | GGB | 183640.55 | 2834.6 | 2728.4655 |  |  |  | 0 | 1 | [14 empty] | 109.0636 | 2728.4655 |  | 104.98
27.03.2008 06:00 | 3600 | 2 | 762.34 | GGB | 765.934 | 774.75 | 770.696 | 263.94 | GGB | 10877.7 | GGB | 9.86 | GGB | 997.46 | GGB | 59.78 | GGB | 171104.72 | GGB | 138213.19 | GGB | 0 | 0 | 2873 | 3600 | 2857.83 | GGB | 100 | GGB | 41.73 | GGB | 41.73 | GGB | 183680.16 | GGB | 183682.28 | 2857.83 | 2734.3845 |  |  |  | 1 | 1 |  |  |  |  | 138213.19 | 2734.3845 | 138213.19 | 2734.3845 | 9.0565 | [5 empty] | 109.7194 | 2734.3845 |  | 104.98
27.03.2008 07:00 | 3600 | 2 | 762.2 | GGB | 762.271 | 771.047 | 767.033 | 264.01 | GGB | 10870.7 | GGB | 9.85 | GGB | 998.13 | GGB | 59.8 | GGB | 171183.95 | GGB | 138363.89 | GGB | 0 | 0 | 2878 | 3600 | 2862.03 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 183719.12 | GGB | 183721.24 | 2862.03 | 2731.4063 |  |  |  | 0 | 1 | [14 empty] | 110.0004 | 2731.4063 |  | 104.98
27.03.2008 08:00 | 3600 | 2 | 763.03 | GGB | 765.934 | 773.906 | 770.696 | 263.82 | GGB | 10877.5 | GGB | 9.86 | GGB | 998.78 | GGB | 59.81 | GGB | 170862.65 | GGB | 138191.64 | GGB | 0 | 0 | 2862 | 3600 | 2846.26 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 183757.6 | GGB | 183759.73 | 2846.26 | 2734.8109 |  |  |  | 1 | 1 |  |  |  |  | 138191.64 | 2734.8109 | 138191.64 | 2734.8109 | 9.8189 | [5 empty] | 109.2581 | 2734.8109 |  | 104.98
27.03.2008 09:00 | 3600 | 2 | 764.34 | GGB | 764.835 | 773.977 | 770.696 | 263.25 | GGB | 10822.8 | GGB | 9.86 | GGB | 999.91 | GGB | 59.8 | GGB | 170503.94 | GGB | 138061.32 | GGB | 0 | 0 | 2773 | 3600 | 2757.94 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 183798.37 | GGB | 183800.5 | 2757.94 | 2737.3923 |  |  |  | 1 | 1 |  |  |  |  | 138061.32 | 2737.3923 | 138061.32 | 2737.3923 | 9.2698 | [5 empty] | 105.768 | 2737.3923 |  | 104.98
27.03.2008 10:00 | 3600 | 2 | 765.38 | GGB | 768.132 | 777.188 | 773.26 | 260.94 | GGB | 10806.6 | GGB | 9.87 | GGB | 1000.58 | GGB | 60.72 | GGB | 167328.36 | GGB | 135204.28 | GGB | 0 | 0 | 2724 | 3600 | 2708.67 | GGB | 100 | GGB | 42.2 | GGB | 42.2 | GGB | 183840.56 | GGB | 183842.7 | 2708.67 | 2708.67 |  |  |  | 1 | 1 |  |  |  |  | 135204.28 | 2708.67 | 135204.28 | 2708.67 | 8.6783 | [5 empty] | 101.7288 |  |  | #VALUE!
27.03.2008 11:00 | 3600 | 2 | 766.14 | GGB | 767.033 | 776.484 | 771.795 | 259.76 | GGB | 10754.8 | GGB | 9.85 | GGB | 1000.93 | GGB | 61.3 | GGB | 166262.13 | GGB | 134157.21 | GGB | 0 | 0 | 2661 | 3600 | 2645.93 | GGB | 100 | GGB | 36.67 | GGB | 36.67 | GGB | 183877.24 | GGB | 183879.37 | 2645.93 | 2645.93 |  |  |  | 1 | 1 |  |  |  |  | 134157.21 | 2645.93 | 134157.21 | 2645.93 | 9.6801 | [5 empty] | 98.6029 |  |  | #VALUE!
27.03.2008 12:00 | 3600 | 2 | 767.18 | GGB | 769.597 | 778.828 | 774.359 | 259.81 | GGB | 10728.6 | GGB | 9.86 | GGB | 1001.02 | GGB | 61.45 | GGB | 166531.72 | GGB | 134327.12 | GGB | 0 | 0 | 2594 | 3600 | 2578.38 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 183916.22 | GGB | 183918.36 | 2578.38 | 2578.38 |  |  |  | 0 | 1 | [14 empty] | 96.2073 |  |  | #VALUE!
27.03.2008 13:00 | 3600 | 2 | 767.88 | GGB | 768.498 | 777.82 | 773.26 | 259.95 | GGB | 10722.2 | GGB | 9.86 | GGB | 1001.56 | GGB | 61.44 | GGB | 166565.83 | GGB | 134432 | GGB | 0 | 0 | 2556 | 3600 | 2540.49 | GGB | 100 | GGB | 43 | GGB | 43 | GGB | 183959.22 | GGB | 183961.36 | 2540.49 | 2540.49 |  |  |  | 1 | 1 |  |  |  |  | 134432 | 2540.49 | 134432 | 2540.49 | 7.9424 | [5 empty] | 94.8675 |  |  | #VALUE!
27.03.2008 14:00 | 3600 | 2 | 768.1 | GGB | 769.597 | 778.219 | 773.26 | 258.13 | GGB | 10711.1 | GGB | 9.86 | GGB | 1001.91 | GGB | 62.36 | GGB | 164238.61 | GGB | 132234.22 | GGB | 0 | 0 | 2541 | 3600 | 2525.24 | GGB | 100 | GGB | 37.81 | GGB | 37.81 | GGB | 183997.03 | GGB | 183999.17 | 2525.24 | 2525.24 |  |  |  | 1 | 1 |  |  |  |  | 132234.22 | 2525.24 | 132234.22 | 2525.24 | 8.8316 | [5 empty] | 92.7564 |  |  | #VALUE!
27.03.2008 15:00 | 3600 | 2 | 767.61 | GGB | 764.835 | 775.031 | 770.696 | 258.21 | GGB | 10687.5 | GGB | 9.84 | GGB | 1002.27 | GGB | 62.48 | GGB | 164234.21 | GGB | 132231.07 | GGB | 0 | 0 | 2550 | 3600 | 2534.65 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 184036.73 | GGB | 184038.87 | 2534.65 | 2534.65 |  |  |  | 1 | 1 |  |  |  |  | 132231.07 | 2534.65 | 132231.07 | 2534.65 | 8.4423 | [5 empty] | 93.0999 |  |  | #VALUE!
27.03.2008 16:00 | 3600 | 2 | 769 | GGB | 770.696 | 780.586 | 775.824 | 259.22 | GGB | 10704.9 | GGB | 9.87 | GGB | 1002.82 | GGB | 62.44 | GGB | 165437.98 | GGB | 133287.72 | GGB | 0 | 0 | 2508 | 3600 | 2492.99 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 184077.69 | GGB | 184079.83 | 2492.99 | 2492.99 |  |  |  | 0 | 1 | [14 empty] | 92.3014 |  |  | #VALUE!
27.03.2008 17:00 | 3600 | 2 | 767.59 | GGB | 768.498 | 778.477 | 773.26 | 258.61 | GGB | 10704.3 | GGB | 9.85 | GGB | 1003.05 | GGB | 62.58 | GGB | 164740.37 | GGB | 132702.16 | GGB | 0 | 0 | 2562 | 3600 | 2546.68 | GGB | 100 | GGB | 36.88 | GGB | 36.88 | GGB | 184114.56 | GGB | 184116.71 | 2546.68 | 2546.68 |  |  |  | 1 | 1 |  |  |  |  | 132702.16 | 2546.68 | 132702.16 | 2546.68 | 9.1635 | [5 empty] | 93.875 |  |  | #VALUE!
27.03.2008 18:00 | 3600 | 2 | 767.45 | GGB | 769.597 | 779.203 | 773.993 | 259.86 | GGB | 10742.8 | GGB | 9.86 | GGB | 1004.35 | GGB | 62.56 | GGB | 165344.45 | GGB | 133369.73 | GGB | 0 | 0 | 2580 | 3600 | 2564.81 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 184152.92 | GGB | 184155.07 | 2564.81 | 2564.81 |  |  |  | 0 | 1 | [14 empty] | 95.0189 |  |  | #VALUE!
27.03.2008 19:00 | 3600 | 2 | 767.14 | GGB | 768.132 | 777.117 | 772.527 | 261.05 | GGB | 10708.8 | GGB | 9.84 | GGB | 1005.29 | GGB | 62.15 | GGB | 166700.07 | GGB | 134753.12 | GGB | 0 | 0 | 2573 | 3600 | 2557.91 | GGB | 100 | GGB | 42.14 | GGB | 42.14 | GGB | 184195.06 | GGB | 184197.21 | 2557.91 | 2557.91 |  |  |  | 1 | 1 |  |  |  |  | 134753.12 | 2557.91 | 134753.12 | 2557.91 | 8.1796 | [5 empty] | 95.7462 |  |  | #VALUE!
27.03.2008 20:00 | 3600 | 2 | 766.09 | GGB | 764.469 | 773.25 | 768.864 | 262.21 | GGB | 10783.6 | GGB | 9.85 | GGB | 1006.48 | GGB | 61.88 | GGB | 167548.43 | GGB | 135711.34 | GGB | 0 | 0 | 2645 | 3600 | 2630.12 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 184234.37 | GGB | 184236.52 | 2630.12 | 2630.12 |  |  |  | 1 | 1 |  |  |  |  | 135711.34 | 2630.12 | 135711.34 | 2630.12 | 9.0801 | [5 empty] | 99.1492 |  |  | #VALUE!
27.03.2008 21:00 | 3600 | 2 | 764.66 | GGB | 763.37 | 772.242 | 767.766 | 263.52 | GGB | 10821.5 | GGB | 9.84 | GGB | 1007.47 | GGB | 61.8 | GGB | 168549.74 | GGB | 136688.81 | GGB | 0 | 0 | 2739 | 3600 | 2723.64 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 184273.59 | GGB | 184275.75 | 2723.64 | 2723.64 |  |  |  | 0 | 1 | [14 empty] | 103.4142 |  |  | #VALUE!
27.03.2008 22:00 | 3600 | 2 | 763.99 | GGB | 765.934 | 774.773 | 771.429 | 264.86 | GGB | 10886.6 | GGB | 9.85 | GGB | 1008.74 | GGB | 61.09 | GGB | 170543.55 | GGB | 138772.91 | GGB | 0 | 0 | 2809 | 3600 | 2793.45 | GGB | 100 | GGB | 38.04 | GGB | 38.04 | GGB | 184311.64 | GGB | 184313.79 | 2793.45 | 2723.3557 |  |  |  | 1 | 1 |  |  |  |  | 138772.91 | 2723.3557 | 138772.91 | 2723.3557 | 9.935 | [5 empty] | 107.682 | 2723.3557 |  | 104.98
27.03.2008 23:00 | 3600 | 2 | 763.63 | GGB | 763.37 | 771.773 | 767.766 | 266.01 | GGB | 10901.5 | GGB | 9.84 | GGB | 1009.56 | GGB | 61.03 | GGB | 171042 | GGB | 139318.91 | GGB | 0 | 0 | 2833 | 3600 | 2817.96 | GGB | 100 | GGB | 42.87 | GGB | 42.87 | GGB | 184354.5 | GGB | 184356.66 | 2817.96 | 2712.6827 |  |  |  | 0 | 1 | [14 empty] | 109.0542 | 2712.6827 |  | 104.98
27.03.2008 24:00 | 3600 | 2 | 763.07 | GGB | 763.37 | 772.57 | 768.864 | 267.07 | GGB | 10940.2 | GGB | 9.85 | GGB | 1010.46 | GGB | 60.74 | GGB | 172198.46 | GGB | 140506.68 | GGB | 0 | 0 | 2878 | 3600 | 2862.88 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 184395.19 | GGB | 184397.35 | 2862.88 | 2689.7511 |  |  |  | 0 | 1 | [14 empty] | 111.7372 | 2689.7511 |  | 104.98
28.03.2008 01:00 | 3600 | 2 | 762.3 | GGB | 764.469 | 772.594 | 768.864 | 267.4 | GGB | 10954 | GGB | 9.85 | GGB | 1011.23 | GGB | 60.45 | GGB | 172771.73 | GGB | 141204.02 | GGB | 0 | 0 | 2920 | 3600 | 2904.58 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 184435.81 | GGB | 184437.97 | 2904.58 | 2676.4677 |  |  |  | 1 | 1 |  |  |  |  | 141204.02 | 2676.4677 | 141204.02 | 2676.4677 | 9.304 | [5 empty] | 113.9273 | 2676.4677 |  | 104.98
28.03.2008 02:00 | 3600 | 2 | 762.48 | GGB | 764.835 | 773.461 | 768.864 | 268.09 | GGB | 10989.8 | GGB | 9.86 | GGB | 1012.06 | GGB | 60.22 | GGB | 173836.86 | GGB | 142289.09 | GGB | 0 | 0 | 2933 | 3600 | 2917.79 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 184476.27 | GGB | 184478.43 | 2917.79 | 2656.0575 |  |  |  | 1 | 1 |  |  |  |  | 142289.09 | 2656.0575 | 142289.09 | 2656.0575 | 9.3408 | [5 empty] | 115.3249 | 2656.0575 |  | 104.98
28.03.2008 03:00 | 3600 | 2 | 761.59 | GGB | 763.37 | 772.336 | 767.766 | 268.49 | GGB | 10997 | GGB | 9.85 | GGB | 1012.81 | GGB | 59.96 | GGB | 174372.72 | GGB | 142944.12 | GGB | 0 | 0 | 2976 | 3600 | 2959.86 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 184516.79 | GGB | 184518.96 | 2959.86 | 2643.8863 |  |  |  | 0 | 1 | [14 empty] | 117.5263 | 2643.8863 |  | 104.98
28.03.2008 04:00 | 3600 | 2 | 762.09 | GGB | 763.37 | 772.125 | 767.766 | 269.59 | GGB | 11005.6 | GGB | 9.85 | GGB | 1013.34 | GGB | 59.48 | GGB | 175593 | GGB | 144229.85 | GGB | 0 | 0 | 2964 | 3600 | 2948.14 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 184557.27 | GGB | 184559.44 | 2948.14 | 2620.3175 |  |  |  | 0 | 1 | [14 empty] | 118.1138 | 2620.3175 |  | 104.98
28.03.2008 05:00 | 3600 | 2 | 761.74 | GGB | 764.469 | 773.227 | 768.864 | 269.27 | GGB | 11031.7 | GGB | 9.85 | GGB | 1014.02 | GGB | 59.53 | GGB | 174947.1 | GGB | 143772.33 | GGB | 0 | 0 | 2995 | 3600 | 2979.83 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 184597.74 | GGB | 184599.91 | 2979.83 | 2628.656 |  |  |  | 1 | 1 |  |  |  |  | 143772.33 | 2628.656 | 143772.33 | 2628.656 | 9.3385 | [5 empty] | 119.0048 | 2628.656 |  | 104.98
28.03.2008 06:00 | 3600 | 2 | 761.95 | GGB | 764.835 | 773.109 | 769.963 | 271.38 | GGB | 11014.7 | GGB | 9.85 | GGB | 1014.8 | GGB | 58.83 | GGB | 177757.36 | GGB | 146502.53 | GGB | 0 | 0 | 2985 | 3600 | 2969.61 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 184638.42 | GGB | 184640.59 | 2969.61 | 2579.6688 |  |  |  | 1 | 1 |  |  |  |  | 146502.53 | 2579.6688 | 146502.53 | 2579.6688 | 9.2903 | [5 empty] | 120.8487 | 2579.6688 |  | 104.98
28.03.2008 07:00 | 3600 | 2 | 762.44 | GGB | 764.469 | 772.992 | 769.963 | 270.2 | GGB | 11057.3 | GGB | 9.86 | GGB | 1016 | GGB | 59.15 | GGB | 176100.25 | GGB | 145170.16 | GGB | 0 | 0 | 2980 | 3600 | 2964 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 184678.43 | GGB | 184680.6 | 2964 | 2603.3449 |  |  |  | 1 | 1 |  |  |  |  | 145170.16 | 2603.3449 | 145170.16 | 2603.3449 | 9.4458 | [5 empty] | 119.5234 | 2603.3449 |  | 104.98
28.03.2008 08:00 | 3600 | 2 | 762.99 | GGB | 765.934 | 774.07 | 769.963 | 270.12 | GGB | 11018.8 | GGB | 9.86 | GGB | 1017.06 | GGB | 59.4 | GGB | 175905.49 | GGB | 145049.35 | GGB | 0 | 0 | 2957 | 3208 | 2941.54 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 184718.34 | GGB | 184720.51 | 2941.54 | 2605.5132 |  |  |  | 1 | 1 |  |  |  |  | 145049.35 | 2605.5132 | 145049.35 | 2605.5132 | 9.4695 | [5 empty] | 118.519 | 2605.5132 |  | 104.98
28.03.2008 09:00 | 3600 | 2 | 765.89 | GGB | 767.033 | 776.531 | 771.429 | 267.06 | GGB | 10988 | GGB | 9.89 | GGB | 1018.05 | GGB | 60.29 | GGB | 172143.44 | GGB | 141706.11 | GGB | 0 | 0 | 2797 | 3600 | 2781.66 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 184757.81 | GGB | 184759.98 | 2781.66 | 2666.9845 |  |  |  | 1 | 1 |  |  |  |  | 141706.11 | 2666.9845 | 141706.11 | 2666.9845 | 9.5751 | [5 empty] | 109.4939 | 2666.9845 |  | 104.98
28.03.2008 10:00 | 3600 | 2 | 766.5 | GGB | 769.597 | 778.336 | 773.993 | 265.76 | GGB | 10882.3 | GGB | 9.86 | GGB | 1018.65 | GGB | 60.91 | GGB | 170996.89 | GGB | 140585.12 | GGB | 0 | 0 | 2734 | 3600 | 2718.35 | GGB | 100 | GGB | 41.71 | GGB | 41.71 | GGB | 184799.52 | GGB | 184801.69 | 2718.35 | 2688.2504 |  |  |  | 1 | 1 |  |  |  |  | 140585.12 | 2688.2504 | 140585.12 | 2688.2504 | 9.0608 | [5 empty] | 106.1554 | 2688.2504 |  | 104.98
28.03.2008 11:00 | 3600 | 2 | 768.56 | GGB | 770.696 | 780.07 | 776.19 | 263.83 | GGB | 10864.6 | GGB | 9.88 | GGB | 1018.15 | GGB | 61.41 | GGB | 168944.76 | GGB | 138622.32 | GGB | 0 | 0 | 2624 | 3600 | 2609.15 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 184838.26 | GGB | 184840.43 | 2609.15 | 2609.15 |  |  |  | 0 | 1 | [14 empty] | 100.4685 |  |  | #VALUE!
28.03.2008 12:00 | 3600 | 2 | 768.27 | GGB | 768.498 | 778.031 | 772.527 | 262.82 | GGB | 10830.9 | GGB | 9.85 | GGB | 1017.73 | GGB | 62.41 | GGB | 167670.57 | GGB | 137109.48 | GGB | 0 | 0 | 2627 | 3600 | 2611.31 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 184878.61 | GGB | 184880.79 | 2611.31 | 2611.31 |  |  |  | 1 | 1 |  |  |  |  | 137109.48 | 2611.31 | 137109.48 | 2611.31 | 8.871 | [5 empty] | 99.4543 |  |  | #VALUE!
28.03.2008 13:00 | 3600 | 2 | 768.72 | GGB | 769.597 | 778.453 | 775.091 | 262.67 | GGB | 10805.6 | GGB | 9.85 | GGB | 1018.11 | GGB | 62.82 | GGB | 167151.21 | GGB | 136569.94 | GGB | 0 | 0 | 2598 | 3600 | 2582.89 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 184918.71 | GGB | 184920.88 | 2582.89 | 2582.89 |  |  |  | 1 | 1 |  |  |  |  | 136569.94 | 2582.89 | 136569.94 | 2582.89 | 8.7988 | [5 empty] | 97.9848 |  |  | #VALUE!
28.03.2008 14:00 | 3600 | 2 | 770.26 | GGB | 768.498 | 777.398 | 773.993 | 262.11 | GGB | 10821.2 | GGB | 9.87 | GGB | 1018.1 | GGB | 63.42 | GGB | 166462.4 | GGB | 135764.29 | GGB | 0 | 0 | 2537 | 3600 | 2521.9 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 184957.47 | GGB | 184959.64 | 2521.9 | 2521.9 |  |  |  | 0 | 1 | [14 empty] | 95.1067 |  |  | #VALUE!
28.03.2008 15:00 | 3600 | 2 | 769.95 | GGB | 773.26 | 782.648 | 778.755 | 262.44 | GGB | 10769.4 | GGB | 9.85 | GGB | 1018.3 | GGB | 63.35 | GGB | 166735.28 | GGB | 136039.61 | GGB | 0 | 0 | 2531 | 3600 | 2516.12 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 184996.95 | GGB | 184999.12 | 2516.12 | 2516.12 |  |  |  | 0 | 1 | [14 empty] | 95.0811 |  |  | #VALUE!
28.03.2008 16:00 | 3600 | 2 | 770.49 | GGB | 771.795 | 781.477 | 776.19 | 262.25 | GGB | 10731.1 | GGB | 9.85 | GGB | 1018.33 | GGB | 63.46 | GGB | 166516.31 | GGB | 135821.54 | GGB | 0 | 0 | 2485 | 3600 | 2470.06 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 185036.82 | GGB | 185038.99 | 2470.06 | 2470.06 |  |  |  | 0 | 1 | [14 empty] | 93.1909 |  |  | #VALUE!
28.03.2008 17:00 | 3600 | 2 | 771.15 | GGB | 770.696 | 780.164 | 776.19 | 261.18 | GGB | 10759.8 | GGB | 9.86 | GGB | 1018.43 | GGB | 64.25 | GGB | 165092.48 | GGB | 134355.64 | GGB | 0 | 0 | 2477 | 3600 | 2461.4 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 185076.49 | GGB | 185078.66 | 2461.4 | 2461.4 |  |  |  | 0 | 1 | [14 empty] | 91.8619 |  |  | #VALUE!
28.03.2008 18:00 | 3600 | 2 | 770.67 | GGB | 769.597 | 779.086 | 775.091 | 260.42 | GGB | 10756.7 | GGB | 9.86 | GGB | 1018.07 | GGB | 64.6 | GGB | 164289.23 | GGB | 133516.35 | GGB | 0 | 0 | 2495 | 3600 | 2479.35 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 185116.1 | GGB | 185118.27 | 2479.35 | 2479.35 |  |  |  | 0 | 1 | [14 empty] | 91.9538 |  |  | #VALUE!
28.03.2008 19:00 | 3600 | 2 | 769.53 | GGB | 770.696 | 780.375 | 776.19 | 262.6 | GGB | 10753.6 | GGB | 9.85 | GGB | 1018.29 | GGB | 63.35 | GGB | 166542.72 | GGB | 135879.79 | GGB | 0 | 0 | 2518 | 3600 | 2502.28 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 185156.49 | GGB | 185158.66 | 2502.28 | 2502.28 |  |  |  | 0 | 1 | [14 empty] | 94.447 |  |  | #VALUE!
28.03.2008 20:00 | 3600 | 2 | 768.55 | GGB | 769.597 | 778.453 | 773.993 | 263.62 | GGB | 10802.5 | GGB | 9.85 | GGB | 1019.09 | GGB | 63.07 | GGB | 167590.24 | GGB | 136959.27 | GGB | 0 | 0 | 2573 | 3600 | 2557.57 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 185197.17 | GGB | 185199.35 | 2557.57 | 2557.57 |  |  |  | 1 | 1 |  |  |  |  | 136959.27 | 2557.57 | 136959.27 | 2557.57 | 8.6086 | [5 empty] | 97.3008 |  |  | #VALUE!
28.03.2008 21:00 | 3600 | 2 | 766.74 | GGB | 767.033 | 777.141 | 771.429 | 264.37 | GGB | 10861.3 | GGB | 9.84 | GGB | 1019.36 | GGB | 62.86 | GGB | 168462.81 | GGB | 137792.03 | GGB | 0 | 0 | 2688 | 3600 | 2672.6 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 185237.21 | GGB | 185239.38 | 2672.6 | 2672.6 |  |  |  | 1 | 1 |  |  |  |  | 137792.03 | 2672.6 | 137792.03 | 2672.6 | 9.1997 | [5 empty] | 102.2953 |  |  | #VALUE!
28.03.2008 22:00 | 3600 | 2 | 766.53 | GGB | 767.033 | 777 | 772.527 | 265.13 | GGB | 10918.9 | GGB | 9.85 | GGB | 1019.93 | GGB | 62.38 | GGB | 169562.05 | GGB | 138969.17 | GGB | 0 | 0 | 2719 | 3600 | 2703.67 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 185277.9 | GGB | 185280.08 | 2703.67 | 2703.67 |  |  |  | 1 | 1 |  |  |  |  | 138969.17 | 2703.67 | 138969.17 | 2703.67 | 9.2316 | [5 empty] | 104.3685 |  |  | #VALUE!
28.03.2008 23:00 | 3600 | 2 | 765.33 | GGB | 764.835 | 774.398 | 770.33 | 267.99 | GGB | 10906.2 | GGB | 9.84 | GGB | 1020.59 | GGB | 61.07 | GGB | 172580.27 | GGB | 142087.98 | GGB | 0 | 0 | 2765 | 3600 | 2749.85 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 185318.07 | GGB | 185320.24 | 2749.85 | 2659.8168 |  |  |  | 1 | 1 |  |  |  |  | 142087.98 | 2659.8168 | 142087.98 | 2659.8168 | 9.4106 | [5 empty] | 108.5335 | 2659.8168 |  | 104.98
28.03.2008 24:00 | 3600 | 2 | 765.98 | GGB | 767.033 | 776.25 | 771.429 | 268.03 | GGB | 10946.2 | GGB | 9.86 | GGB | 1020.68 | GGB | 61.69 | GGB | 170886.85 | GGB | 140444.12 | GGB | 0 | 0 | 2782 | 3600 | 2766.79 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 185358.11 | GGB | 185360.28 | 2766.79 | 2690.9493 |  |  |  | 1 | 1 |  |  |  |  | 140444.12 | 2690.9493 | 140444.12 | 2690.9493 | 9.4388 | [5 empty] | 107.9387 | 2690.9493 |  | 104.98
29.03.2008 01:00 | 3600 | 2 | 765.66 | GGB | 768.132 | 777.375 | 772.527 | 268.12 | GGB | 10959.1 | GGB | 9.86 | GGB | 1020.67 | GGB | 61.67 | GGB | 170674.49 | GGB | 140278.15 | GGB | 0 | 0 | 2812 | 3600 | 2796.79 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 185398.6 | GGB | 185400.77 | 2796.79 | 2694.133 |  |  |  | 1 | 1 |  |  |  |  | 140278.15 | 2694.133 | 140278.15 | 2694.133 | 9.3339 | [5 empty] | 108.9801 | 2694.133 |  | 104.98
29.03.2008 02:00 | 3600 | 2 | 765.04 | GGB | 765.934 | 774.398 | 770.33 | 268.52 | GGB | 10957.7 | GGB | 9.85 | GGB | 1020.56 | GGB | 61.38 | GGB | 171251.07 | GGB | 140861.17 | GGB | 0 | 0 | 2840 | 3600 | 2824.2 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 185437.16 | GGB | 185439.33 | 2824.2 | 2682.9821 |  |  |  | 1 | 1 |  |  |  |  | 140861.17 | 2682.9821 | 140861.17 | 2682.9821 | 9.801 | [5 empty] | 110.5056 | 2682.9821 |  | 104.98
29.03.2008 03:00 | 3600 | 2 | 765.01 | GGB | 767.033 | 776.484 | 772.527 | 268.31 | GGB | 10975.9 | GGB | 9.86 | GGB | 1020.42 | GGB | 61.12 | GGB | 171532.75 | GGB | 141182.99 | GGB | 0 | 0 | 2850 | 3600 | 2834.93 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 185478.34 | GGB | 185480.51 | 2834.93 | 2676.8664 |  |  |  | 1 | 1 |  |  |  |  | 141182.99 | 2676.8664 | 141182.99 | 2676.8664 | 9.1775 | [5 empty] | 111.1789 | 2676.8664 |  | 104.98
29.03.2008 04:00 | 3600 | 2 | 765.04 | GGB | 765.934 | 775.617 | 771.429 | 269.43 | GGB | 10929.6 | GGB | 9.85 | GGB | 1020.25 | GGB | 60.53 | GGB | 173302.1 | GGB | 142865.32 | GGB | 0 | 0 | 2827 | 3600 | 2811.44 | GGB | 100 | GGB | 41.71 | GGB | 41.71 | GGB | 185520.04 | GGB | 185522.22 | 2811.44 | 2645.3446 |  |  |  | 1 | 1 |  |  |  |  | 142865.32 | 2645.3446 | 142865.32 | 2645.3446 | 9.0608 | [5 empty] | 111.5715 | 2645.3446 |  | 104.98
29.03.2008 05:00 | 3600 | 2 | 765.71 | GGB | 767.033 | 775.547 | 771.429 | 267.73 | GGB | 10975.8 | GGB | 9.87 | GGB | 1019.74 | GGB | 60.66 | GGB | 171830.94 | GGB | 141525.05 | GGB | 0 | 0 | 2799 | 3600 | 2783.62 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 185558.37 | GGB | 185560.54 | 2783.62 | 2670.3965 |  |  |  | 1 | 1 |  |  |  |  | 141525.05 | 2670.3965 | 141525.05 | 2670.3965 | 9.8624 | [5 empty] | 109.4311 | 2670.3965 |  | 104.98
29.03.2008 06:00 | 3600 | 2 | 764.9 | GGB | 764.835 | 773.016 | 768.864 | 267.09 | GGB | 10950.3 | GGB | 9.85 | GGB | 1019.55 | GGB | 60.98 | GGB | 170896.76 | GGB | 140596.9 | GGB | 0 | 0 | 2830 | 3600 | 2814.29 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 185598.85 | GGB | 185601.02 | 2814.29 | 2688.0251 |  |  |  | 1 | 1 |  |  |  |  | 140596.9 | 2688.0251 | 140596.9 | 2688.0251 | 9.3362 | [5 empty] | 109.9112 | 2688.0251 |  | 104.98
29.03.2008 07:00 | 3600 | 2 | 765.37 | GGB | 765.934 | 774.586 | 770.33 | 266.42 | GGB | 10955.7 | GGB | 9.86 | GGB | 1018.84 | GGB | 60.93 | GGB | 170422.51 | GGB | 140128.26 | GGB | 0 | 0 | 2813 | 3600 | 2797.77 | GGB | 100 | GGB | 41.99 | GGB | 41.99 | GGB | 185640.84 | GGB | 185643.01 | 2797.77 | 2697.0149 |  |  |  | 1 | 1 |  |  |  |  | 140128.26 | 2697.0149 | 140128.26 | 2697.0149 | 9.0004 | [5 empty] | 108.9018 | 2697.0149 |  | 104.98
29.03.2008 08:00 | 3600 | 2 | 766.37 | GGB | 767.033 | 776.156 | 772.527 | 264.79 | GGB | 10929.4 | GGB | 9.87 | GGB | 1019.03 | GGB | 61.31 | GGB | 169170.33 | GGB | 138968.85 | GGB | 0 | 0 | 2759 | 3600 | 2743.31 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 185681.48 | GGB | 185683.65 | 2743.31 | 2719.5159 |  |  |  | 1 | 1 |  |  |  |  | 138968.85 | 2719.5159 | 138968.85 | 2719.5159 | 9.2994 | [5 empty] | 105.8985 | 2719.5159 |  | 104.98
29.03.2008 09:00 | 3600 | 2 | 767.83 | GGB | 769.597 | 779.578 | 776.19 | 262.24 | GGB | 10872.2 | GGB | 9.87 | GGB | 1019.04 | GGB | 62.22 | GGB | 166469 | GGB | 136380.36 | GGB | 0 | 0 | 2663 | 3600 | 2647.35 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 185720.98 | GGB | 185723.14 | 2647.35 | 2647.35 |  |  |  | 0 | 1 | [14 empty] | 100.2907 |  |  | #VALUE!
29.03.2008 10:00 | 3600 | 2 | 769.42 | GGB | 768.498 | 778.453 | 773.993 | 258.92 | GGB | 10805.7 | GGB | 9.87 | GGB | 1017.64 | GGB | 62.89 | GGB | 164096.67 | GGB | 133982.64 | GGB | 0 | 0 | 2563 | 3600 | 2547.61 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 185760.36 | GGB | 185762.52 | 2547.61 | 2547.61 |  |  |  | 1 | 1 |  |  |  |  | 133982.64 | 2547.61 | 133982.64 | 2547.61 | 8.6677 | [5 empty] | 94.8154 |  |  | #VALUE!
29.03.2008 11:00 | 3600 | 2 | 769.57 | GGB | 770.696 | 780.469 | 776.19 | 258.3 | GGB | 10782.1 | GGB | 9.86 | GGB | 1016.82 | GGB | 62.99 | GGB | 163799.58 | GGB | 133591.05 | GGB | 0 | 0 | 2557 | 3600 | 2541.45 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 185800.03 | GGB | 185802.19 | 2541.45 | 2541.45 |  |  |  | 0 | 1 | [14 empty] | 94.3097 |  |  | #VALUE!
29.03.2008 12:00 | 3600 | 2 | 771.47 | GGB | 773.26 | 782.461 | 778.755 | 255.87 | GGB | 10715.1 | GGB | 9.87 | GGB | 1015.76 | GGB | 64.03 | GGB | 161538.38 | GGB | 131203 | GGB | 0 | 0 | 2454 | 3600 | 2439.01 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 185840.12 | GGB | 185842.29 | 2439.01 | 2439.01 |  |  |  | 0 | 1 | [14 empty] | 88.8904 |  |  | #VALUE!
29.03.2008 13:00 | 3600 | 2 | 772.32 | GGB | 773.26 | 783.375 | 778.755 | 254.22 | GGB | 10649.9 | GGB | 9.86 | GGB | 1014.12 | GGB | 64.39 | GGB | 159923.09 | GGB | 129545.46 | GGB | 0 | 0 | 2396 | 3600 | 2380.99 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 185880.14 | GGB | 185882.31 | 2380.99 | 2380.99 |  |  |  | 0 | 1 | [14 empty] | 85.6796 |  |  | #VALUE!
29.03.2008 14:00 | 3600 | 2 | 772.26 | GGB | 768.498 | 778.875 | 773.993 | 253.55 | GGB | 10596 | GGB | 9.84 | GGB | 1013.25 | GGB | 64.89 | GGB | 159433.44 | GGB | 128846.44 | GGB | 0 | 0 | 2385 | 3600 | 2370.29 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 185920.06 | GGB | 185922.23 | 2370.29 | 2370.29 |  |  |  | 0 | 1 | [14 empty] | 84.8343 |  |  | #VALUE!
29.03.2008 15:00 | 3600 | 2 | 771.5 | GGB | 770.696 | 780.914 | 776.19 | 254.33 | GGB | 10649.2 | GGB | 9.85 | GGB | 1012.67 | GGB | 64.37 | GGB | 160923.3 | GGB | 130177.4 | GGB | 0 | 0 | 2432 | 3600 | 2417.17 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 185959.98 | GGB | 185962.15 | 2417.17 | 2417.17 |  |  |  | 0 | 1 | [14 empty] | 87.4058 |  |  | #VALUE!
29.03.2008 16:00 | 3600 | 2 | 769.92 | GGB | 769.597 | 779.906 | 775.091 | 255.28 | GGB | 10670.3 | GGB | 9.83 | GGB | 1012.72 | GGB | 63.62 | GGB | 162190.88 | GGB | 131499.9 | GGB | 0 | 0 | 2487 | 3600 | 2472.22 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 185999.94 | GGB | 186002.11 | 2472.22 | 2472.22 |  |  |  | 0 | 1 | [14 empty] | 90.3046 |  |  | #VALUE!
29.03.2008 17:00 | 3600 | 2 | 769.94 | GGB | 770.696 | 780.727 | 776.19 | 255.6 | GGB | 10663 | GGB | 9.84 | GGB | 1012.47 | GGB | 63.23 | GGB | 162794.97 | GGB | 132109.59 | GGB | 0 | 0 | 2479 | 3600 | 2463.56 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 186040.04 | GGB | 186042.21 | 2463.56 | 2463.56 |  |  |  | 0 | 1 | [14 empty] | 90.4055 |  |  | #VALUE!
29.03.2008 18:00 | 3600 | 2 | 769.36 | GGB | 770.696 | 781.125 | 775.824 | 255.54 | GGB | 10661.6 | GGB | 9.83 | GGB | 1012.81 | GGB | 63.29 | GGB | 161984.02 | GGB | 131473.06 | GGB | 0 | 0 | 2507 | 3600 | 2491.58 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 186079.95 | GGB | 186082.13 | 2491.58 | 2491.58 |  |  |  | 0 | 1 | [14 empty] | 90.9932 |  |  | #VALUE!
29.03.2008 19:00 | 3600 | 2 | 769.89 | GGB | 771.795 | 781.945 | 778.022 | 255.63 | GGB | 10671.2 | GGB | 9.84 | GGB | 1013.46 | GGB | 63.31 | GGB | 161912.5 | GGB | 131492.55 | GGB | 0 | 0 | 2487 | 3600 | 2472.09 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 186119.8 | GGB | 186121.98 | 2472.09 | 2472.09 |  |  |  | 0 | 1 | [14 empty] | 90.2948 |  |  | #VALUE!
29.03.2008 20:00 | 3600 | 2 | 767.77 | GGB | 770.696 | 780.914 | 775.824 | 256.3 | GGB | 10672.7 | GGB | 9.82 | GGB | 1014.19 | GGB | 63.38 | GGB | 161955.41 | GGB | 131595.23 | GGB | 0 | 0 | 2580 | 3600 | 2564.75 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 186159.66 | GGB | 186161.84 | 2564.75 | 2564.75 |  |  |  | 0 | 1 | [14 empty] | 93.7525 |  |  | #VALUE!
29.03.2008 21:00 | 3600 | 2 | 768.34 | GGB | 765.934 | 775.711 | 770.696 | 257.39 | GGB | 10722.5 | GGB | 9.84 | GGB | 1014.7 | GGB | 63.41 | GGB | 162658.53 | GGB | 132222.46 | GGB | 0 | 0 | 2577 | 3600 | 2562.02 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 186199.53 | GGB | 186201.71 | 2562.02 | 2562.02 |  |  |  | 1 | 1 |  |  |  |  | 132222.46 | 2562.02 | 132222.46 | 2562.02 | 8.4965 | [5 empty] | 94.0991 |  |  | #VALUE!
29.03.2008 22:00 | 3600 | 2 | 768.23 | GGB | 768.498 | 777.398 | 772.161 | 257.29 | GGB | 10730.3 | GGB | 9.84 | GGB | 1014.57 | GGB | 63.2 | GGB | 163331.94 | GGB | 132832.44 | GGB | 0 | 0 | 2592 | 3600 | 2576.47 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 186239.17 | GGB | 186241.35 | 2576.47 | 2576.47 |  |  |  | 1 | 1 |  |  |  |  | 132832.44 | 2576.47 | 132832.44 | 2576.47 | 8.6337 | [5 empty] | 95.0663 |  |  | #VALUE!
29.03.2008 23:00 | 3600 | 2 | 767.84 | GGB | 771.795 | 781.781 | 778.022 | 258.07 | GGB | 10727.7 | GGB | 9.83 | GGB | 1015.3 | GGB | 63.16 | GGB | 163986.64 | GGB | 133476.68 | GGB | 0 | 0 | 2594 | 3600 | 2579.19 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 186275.27 | GGB | 186277.45 | 2579.19 | 2579.19 |  |  |  | 0 | 1 | [14 empty] | 95.6283 |  |  | #VALUE!
29.03.2008 24:00 | 3600 | 2 | 766.92 | GGB | 765.934 | 776.086 | 770.696 | 258.88 | GGB | 10765.9 | GGB | 9.83 | GGB | 1015.91 | GGB | 62.95 | GGB | 164458.68 | GGB | 134026.3 | GGB | 0 | 0 | 2653 | 3600 | 2638.12 | GGB | 100 | GGB | 42.77 | GGB | 42.77 | GGB | 186318.04 | GGB | 186320.22 | 2638.12 | 2638.12 |  |  |  | 1 | 1 |  |  |  |  | 134026.3 | 2638.12 | 134026.3 | 2638.12 | 8.267 | [5 empty] | 98.216 |  |  | #VALUE!
30.03.2008 01:00 | 3600 | 2 | 766.52 | GGB | 768.132 | 778.172 | 774.359 | 258.99 | GGB | 10770.5 | GGB | 9.83 | GGB | 1016.25 | GGB | 62.81 | GGB | 164651.24 | GGB | 134285.82 | GGB | 0 | 0 | 2672 | 3600 | 2656.37 | GGB | 100 | GGB | 38.35 | GGB | 38.35 | GGB | 186356.39 | GGB | 186358.57 | 2656.37 | 2656.37 |  |  |  | 1 | 1 |  |  |  |  | 134285.82 | 2656.37 | 134285.82 | 2656.37 | 9.3015 | [5 empty] | 99.0869 |  |  | #VALUE!
30.03.2008 03:00 | 3600 | 2 | 766.31 | GGB | 765.934 | 775.641 | 770.696 | 260.05 | GGB | 10796.8 | GGB | 9.83 | GGB | 1017.11 | GGB | 62.87 | GGB | 165260.83 | GGB | 134872.52 | GGB | 0 | 0 | 2707 | 3600 | 2691.62 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 186396.46 | GGB | 186398.64 | 2691.62 | 2691.62 |  |  |  | 1 | 1 |  |  |  |  | 134872.52 | 2691.62 | 134872.52 | 2691.62 | 9.0598 | [5 empty] | 100.8404 |  |  | #VALUE!
30.03.2008 04:00 | 3600 | 2 | 765.59 | GGB | 765.934 | 774.281 | 770.696 | 260.62 | GGB | 10806.4 | GGB | 9.83 | GGB | 1017.29 | GGB | 62.76 | GGB | 165760.38 | GGB | 135347.55 | GGB | 0 | 0 | 2752 | 3599 | 2736.88 | GGB | 100 | GGB | 41.67 | GGB | 41.67 | GGB | 186438.13 | GGB | 186440.31 | 2736.88 | 2736.88 |  |  |  | 1 | 1 |  |  |  |  | 135347.55 | 2736.88 | 135347.55 | 2736.88 | 8.8896 | [5 empty] | 102.8972 |  |  | #VALUE!
30.03.2008 05:00 | 3600 | 2 | 765.45 | GGB | 763.37 | 773.461 | 768.864 | 261.12 | GGB | 10826.7 | GGB | 9.83 | GGB | 1017.91 | GGB | 62.69 | GGB | 166355.66 | GGB | 135945.7 | GGB | 0 | 0 | 2770 | 3517 | 2754.43 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 186476.87 | GGB | 186479.05 | 2754.43 | 2754.43 |  |  |  | 0 | 1 | [14 empty] | 104.0147 |  |  | #VALUE!
30.03.2008 06:00 | 3600 | 2 | 764.77 | GGB | 765.934 | 774.586 | 770.33 | 261.47 | GGB | 10838.9 | GGB | 9.83 | GGB | 1018.53 | GGB | 62.42 | GGB | 166887.13 | GGB | 136571.58 | GGB | 0 | 0 | 2810 | 3600 | 2794.14 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 186516.15 | GGB | 186518.33 | 2794.14 | 2767.2522 |  |  |  | 1 | 1 |  |  |  |  | 136571.58 | 2767.2522 | 136571.58 | 2767.2522 | 9.6214 | [5 empty] | 106 | 2767.2522 |  | 104.98
30.03.2008 07:00 | 3600 | 2 | 764.9 | GGB | 767.033 | 775.805 | 771.429 | 261.83 | GGB | 10856.8 | GGB | 9.84 | GGB | 1019.05 | GGB | 62.32 | GGB | 167055.48 | GGB | 136822.49 | GGB | 0 | 0 | 2812 | 3600 | 2796.23 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 186556.91 | GGB | 186559.09 | 2796.23 | 2762.1775 |  |  |  | 1 | 1 |  |  |  |  | 136822.49 | 2762.1775 | 136822.49 | 2762.1775 | 9.272 | [5 empty] | 106.2742 | 2762.1775 |  | 104.98
30.03.2008 08:00 | 3600 | 2 | 764.63 | GGB | 765.934 | 775.711 | 771.429 | 262.11 | GGB | 10862.9 | GGB | 9.83 | GGB | 1019.49 | GGB | 62.29 | GGB | 167330.56 | GGB | 137118.58 | GGB | 0 | 0 | 2825 | 3600 | 2809.91 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 186597.24 | GGB | 186599.42 | 2809.91 | 2756.2129 |  |  |  | 1 | 1 |  |  |  |  | 137118.58 | 2756.2129 | 137118.58 | 2756.2129 | 9.3709 | [5 empty] | 107.0252 | 2756.2129 |  | 104.98
30.03.2008 09:00 | 3600 | 2 | 765.01 | GGB | 767.033 | 776.672 | 771.429 | 263.73 | GGB | 10842.2 | GGB | 9.83 | GGB | 1020.75 | GGB | 61.73 | GGB | 169340.88 | GGB | 139167.78 | GGB | 0 | 0 | 2801 | 3600 | 2785.7 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 186637.48 | GGB | 186639.66 | 2785.7 | 2715.6286 |  |  |  | 1 | 1 |  |  |  |  | 139167.78 | 2715.6286 | 139167.78 | 2715.6286 | 9.3918 | [5 empty] | 107.6888 | 2715.6286 |  | 104.98
30.03.2008 10:00 | 3600 | 2 | 765.94 | GGB | 765.934 | 775.945 | 771.429 | 262.89 | GGB | 10836.1 | GGB | 9.84 | GGB | 1020.88 | GGB | 61.76 | GGB | 168590.45 | GGB | 138555.57 | GGB | 0 | 0 | 2757 | 3600 | 2741.21 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 186677.12 | GGB | 186679.3 | 2741.21 | 2727.6276 |  |  |  | 1 | 1 |  |  |  |  | 138555.57 | 2727.6276 | 138555.57 | 2727.6276 | 9.534 | [5 empty] | 105.5028 | 2727.6276 |  | 104.98
30.03.2008 11:00 | 3600 | 2 | 766.9 | GGB | 767.033 | 777.469 | 773.26 | 260.71 | GGB | 10845.7 | GGB | 9.85 | GGB | 1020.96 | GGB | 62.73 | GGB | 165966.14 | GGB | 136016.56 | GGB | 0 | 0 | 2720 | 3600 | 2704.93 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 186716.79 | GGB | 186718.98 | 2704.93 | 2704.93 |  |  |  | 1 | 1 |  |  |  |  | 136016.56 | 2704.93 | 136016.56 | 2704.93 | 9.2721 | [5 empty] | 102.1987 |  |  | #VALUE!
30.03.2008 12:00 | 3600 | 2 | 766.62 | GGB | 768.132 | 778.617 | 773.26 | 260.52 | GGB | 10786.8 | GGB | 9.83 | GGB | 1021.38 | GGB | 62.85 | GGB | 166207.12 | GGB | 136222.09 | GGB | 0 | 0 | 2710 | 3600 | 2694.71 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 186757.08 | GGB | 186759.27 | 2694.71 | 2694.71 |  |  |  | 1 | 1 |  |  |  |  | 136222.09 | 2694.71 | 136222.09 | 2694.71 | 9.1109 | [5 empty] | 101.9664 |  |  | #VALUE!
30.03.2008 13:00 | 3600 | 2 | 768.27 | GGB | 769.597 | 780.117 | 775.458 | 259.02 | GGB | 10794.7 | GGB | 9.85 | GGB | 1021.26 | GGB | 63.32 | GGB | 164321.14 | GGB | 134470.15 | GGB | 0 | 0 | 2634 | 3600 | 2618.75 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 186796.82 | GGB | 186799.01 | 2618.75 | 2618.75 |  |  |  | 0 | 1 | [14 empty] | 97.8177 |  |  | #VALUE!
30.03.2008 14:00 | 3600 | 2 | 767.63 | GGB | 768.498 | 778.641 | 773.26 | 258.71 | GGB | 10777.3 | GGB | 9.84 | GGB | 1020.9 | GGB | 63.49 | GGB | 164259.52 | GGB | 134304.74 | GGB | 0 | 0 | 2657 | 3600 | 2641.37 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 186836.83 | GGB | 186839.02 | 2641.37 | 2641.37 |  |  |  | 1 | 1 |  |  |  |  | 134304.74 | 2641.37 | 134304.74 | 2641.37 | 8.8665 | [5 empty] | 98.5413 |  |  | #VALUE!
30.03.2008 15:00 | 3600 | 2 | 767.13 | GGB | 769.597 | 779.648 | 775.458 | 259.29 | GGB | 10782.8 | GGB | 9.83 | GGB | 1021.07 | GGB | 63.19 | GGB | 165056.16 | GGB | 135099.69 | GGB | 0 | 0 | 2698 | 3600 | 2682.39 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 186876.89 | GGB | 186879.08 | 2682.39 | 2682.39 |  |  |  | 0 | 1 | [14 empty] | 100.6639 |  |  | #VALUE!
30.03.2008 16:00 | 3600 | 2 | 768.07 | GGB | 768.132 | 777.586 | 773.26 | 258.67 | GGB | 10763.6 | GGB | 9.84 | GGB | 1020.67 | GGB | 63.47 | GGB | 164243.01 | GGB | 134268.58 | GGB | 0 | 0 | 2638 | 3600 | 2622.46 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 186916.57 | GGB | 186918.76 | 2622.46 | 2622.46 |  |  |  | 1 | 1 |  |  |  |  | 134268.58 | 2622.46 | 134268.58 | 2622.46 | 8.8738 | [5 empty] | 97.8094 |  |  | #VALUE!
30.03.2008 17:00 | 3600 | 2 | 769.04 | GGB | 770.696 | 779.695 | 775.824 | 258.05 | GGB | 10739.9 | GGB | 9.84 | GGB | 1020.36 | GGB | 63.66 | GGB | 163838.09 | GGB | 133823.99 | GGB | 0 | 0 | 2574 | 3600 | 2558.95 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 186956.38 | GGB | 186958.57 | 2558.95 | 2558.95 |  |  |  | 0 | 1 | [14 empty] | 95.1247 |  |  | #VALUE!
30.03.2008 18:00 | 3600 | 2 | 769.25 | GGB | 770.696 | 780.422 | 776.923 | 256.49 | GGB | 10714.8 | GGB | 9.84 | GGB | 1019.54 | GGB | 64.26 | GGB | 162283.31 | GGB | 132211.99 | GGB | 0 | 0 | 2568 | 3600 | 2552.48 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 186995.91 | GGB | 186998.11 | 2552.48 | 2552.48 |  |  |  | 0 | 1 | [14 empty] | 93.7412 |  |  | #VALUE!
30.03.2008 19:00 | 3600 | 2 | 769.14 | GGB | 769.597 | 779.297 | 774.359 | 256.64 | GGB | 10705.7 | GGB | 9.83 | GGB | 1019.34 | GGB | 64.37 | GGB | 162404.35 | GGB | 132239.15 | GGB | 0 | 0 | 2559 | 3600 | 2543.9 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 187035.7 | GGB | 187037.9 | 2543.9 | 2543.9 |  |  |  | 0 | 1 | [14 empty] | 93.4453 |  |  | #VALUE!
30.03.2008 20:00 | 3600 | 2 | 768.63 | GGB | 768.132 | 777.844 | 773.26 | 258.38 | GGB | 10695.6 | GGB | 9.83 | GGB | 1019.93 | GGB | 63.48 | GGB | 164249.62 | GGB | 134172.88 | GGB | 0 | 0 | 2561 | 3600 | 2546.06 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 187075.84 | GGB | 187078.04 | 2546.06 | 2546.06 |  |  |  | 1 | 1 |  |  |  |  | 134172.88 | 2546.06 | 134172.88 | 2546.06 | 8.5105 | [5 empty] | 94.8923 |  |  | #VALUE!
30.03.2008 21:00 | 3600 | 2 | 767.61 | GGB | 768.498 | 777.938 | 773.26 | 258.13 | GGB | 10756.3 | GGB | 9.83 | GGB | 1019.82 | GGB | 63.52 | GGB | 163643.33 | GGB | 133649.59 | GGB | 0 | 0 | 2632 | 3600 | 2616.18 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 187115.4 | GGB | 187117.6 | 2616.18 | 2616.18 |  |  |  | 1 | 1 |  |  |  |  | 133649.59 | 2616.18 | 133649.59 | 2616.18 | 8.8385 | [5 empty] | 97.1254 |  |  | #VALUE!
30.03.2008 22:00 | 3600 | 2 | 765.51 | GGB | 765.934 | 774.563 | 770.696 | 260.69 | GGB | 10806.3 | GGB | 9.82 | GGB | 1020.15 | GGB | 62.85 | GGB | 166385.37 | GGB | 136205.68 | GGB | 0 | 0 | 2750 | 3600 | 2735.04 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 187154.16 | GGB | 187156.36 | 2735.04 | 2735.04 |  |  |  | 1 | 1 |  |  |  |  | 136205.68 | 2735.04 | 136205.68 | 2735.04 | 9.6111 | [5 empty] | 103.48 |  |  | #VALUE!
30.03.2008 23:00 | 3600 | 2 | 764 | GGB | 764.835 | 773.273 | 768.498 | 262.08 | GGB | 10878.3 | GGB | 9.83 | GGB | 1020.32 | GGB | 61.98 | GGB | 168631.16 | GGB | 138423.44 | GGB | 0 | 0 | 2844 | 3600 | 2828.37 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 187193.33 | GGB | 187195.53 | 2828.37 | 2730.2312 |  |  |  | 1 | 1 |  |  |  |  | 138423.44 | 2730.2312 | 138423.44 | 2730.2312 | 9.6484 | [5 empty] | 108.7535 | 2730.2312 |  | 104.98
30.03.2008 24:00 | 3600 | 2 | 764.13 | GGB | 767.033 | 776.672 | 771.429 | 263.2 | GGB | 10911.6 | GGB | 9.84 | GGB | 1020.53 | GGB | 61.79 | GGB | 169388.19 | GGB | 139153.65 | GGB | 0 | 0 | 2870 | 3600 | 2854.59 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 187234.55 | GGB | 187236.75 | 2854.59 | 2715.9043 |  |  |  | 1 | 1 |  |  |  |  | 139153.65 | 2715.9043 | 139153.65 | 2715.9043 | 9.1686 | [5 empty] | 110.3407 | 2715.9043 |  | 104.98
31.03.2008 01:00 | 3600 | 2 | 762.04 | GGB | 764.835 | 774.914 | 768.864 | 265.62 | GGB | 10907.5 | GGB | 9.81 | GGB | 1020.98 | GGB | 60.81 | GGB | 172243.57 | GGB | 141973.26 | GGB | 0 | 0 | 2971 | 3600 | 2955 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 187275 | GGB | 187277.21 | 2955 | 2661.9661 |  |  |  | 1 | 1 |  |  |  |  | 141973.26 | 2661.9661 | 141973.26 | 2661.9661 | 9.3408 | [5 empty] | 116.5364 | 2661.9661 |  | 104.98
31.03.2008 02:00 | 3600 | 2 | 763.65 | GGB | 767.033 | 775.734 | 771.429 | 266.57 | GGB | 10965.9 | GGB | 9.85 | GGB | 1021.19 | GGB | 59.9 | GGB | 174103.14 | GGB | 143932.28 | GGB | 0 | 0 | 2913 | 3600 | 2897.02 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 187315.26 | GGB | 187317.46 | 2897.02 | 2625.7348 |  |  |  | 1 | 1 |  |  |  |  | 143932.28 | 2625.7348 | 143932.28 | 2625.7348 | 9.3895 | [5 empty] | 115.8263 | 2625.7348 |  | 104.98
31.03.2008 03:00 | 3600 | 2 | 763.39 | GGB | 765.934 | 774.328 | 770.33 | 265.22 | GGB | 10944.7 | GGB | 9.83 | GGB | 1021.3 | GGB | 59.68 | GGB | 173638.8 | GGB | 143656.7 | GGB | 0 | 0 | 2901 | 3600 | 2885.82 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 187355.33 | GGB | 187357.54 | 2885.82 | 2630.7718 |  |  |  | 1 | 1 |  |  |  |  | 143656.7 | 2630.7718 | 143656.7 | 2630.7718 | 9.4293 | [5 empty] | 115.1576 | 2630.7718 |  | 104.98
31.03.2008 04:00 | 3600 | 2 | 763.45 | GGB | 763.37 | 771.891 | 767.766 | 263.97 | GGB | 10995.7 | GGB | 9.85 | GGB | 1021.21 | GGB | 60.17 | GGB | 171906.87 | GGB | 142004.7 | GGB | 0 | 0 | 2926 | 3600 | 2910.67 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 187395.64 | GGB | 187397.85 | 2910.67 | 2661.3767 |  |  |  | 0 | 1 | [14 empty] | 114.8136 | 2661.3767 |  | 104.98
31.03.2008 05:00 | 3600 | 2 | 761.76 | GGB | 763.37 | 772.266 | 767.766 | 264.8 | GGB | 10987 | GGB | 9.82 | GGB | 1021.85 | GGB | 59.96 | GGB | 172909.27 | GGB | 143011.53 | GGB | 0 | 0 | 3011 | 3600 | 2995.44 | GGB | 100 | GGB | 40.88 | GGB | 40.88 | GGB | 187436.52 | GGB | 187438.73 | 2995.44 | 2642.6401 |  |  |  | 0 | 1 | [14 empty] | 118.9951 | 2642.6401 |  | 104.98
31.03.2008 06:00 | 3600 | 2 | 761.9 | GGB | 761.172 | 770.133 | 765.201 | 265.46 | GGB | 10988 | GGB | 9.83 | GGB | 1021.88 | GGB | 59.46 | GGB | 173577.18 | GGB | 143784.1 | GGB | 0 | 0 | 3005 | 3600 | 2988.94 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 187476.9 | GGB | 187479.11 | 2988.94 | 2628.4408 |  |  |  | 0 | 1 | [14 empty] | 119.3783 | 2628.4408 |  | 104.98
31.03.2008 07:00 | 3600 | 2 | 762.36 | GGB | 763.37 | 773.555 | 767.766 | 267.41 | GGB | 11008.3 | GGB | 9.84 | GGB | 1022.2 | GGB | 58.79 | GGB | 176059.54 | GGB | 146179.24 | GGB | 0 | 0 | 2994 | 3600 | 2978.3 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 187517.26 | GGB | 187519.47 | 2978.3 | 2585.374 |  |  |  | 0 | 1 | [14 empty] | 120.9349 | 2585.374 |  | 104.98
31.03.2008 08:00 | 3600 | 2 | 761.83 | GGB | 764.835 | 774.68 | 768.864 | 267.92 | GGB | 11024.9 | GGB | 9.83 | GGB | 1022.19 | GGB | 58.59 | GGB | 177042.14 | GGB | 147084.46 | GGB | 0 | 0 | 3025 | 3600 | 3009.54 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 187557.81 | GGB | 187560.02 | 3009.54 | 2569.4625 |  |  |  | 1 | 1 |  |  |  |  | 147084.46 | 2569.4625 | 147084.46 | 2569.4625 | 9.32 | [5 empty] | 122.9602 | 2569.4625 |  | 104.98
31.03.2008 09:00 | 3600 | 2 | 763.25 | GGB | 764.835 | 773.672 | 769.963 | 265.47 | GGB | 11052.9 | GGB | 9.86 | GGB | 1022.61 | GGB | 59.34 | GGB | 173984.3 | GGB | 144276.46 | GGB | 0 | 0 | 2986 | 3600 | 2970.32 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 187598.21 | GGB | 187600.42 | 2970.32 | 2619.471 |  |  |  | 1 | 1 |  |  |  |  | 144276.46 | 2619.471 | 144276.46 | 2619.471 | 9.3547 | [5 empty] | 119.0409 | 2619.471 |  | 104.98
31.03.2008 10:00 | 3600 | 2 | 764.51 | GGB | 767.033 | 775.969 | 771.429 | 262.92 | GGB | 10960 | GGB | 9.85 | GGB | 1023.1 | GGB | 60.41 | GGB | 170140.83 | GGB | 140703.83 | GGB | 0 | 0 | 2887 | 3600 | 2871.32 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 187638.81 | GGB | 187641.02 | 2871.32 | 2685.9823 |  |  |  | 1 | 1 |  |  |  |  | 140703.83 | 2685.9823 | 140703.83 | 2685.9823 | 9.3086 | [5 empty] | 112.2238 | 2685.9823 |  | 104.98
31.03.2008 11:00 | 3600 | 2 | 766.55 | GGB | 770.696 | 780.047 | 776.19 | 261.74 | GGB | 10861.1 | GGB | 9.85 | GGB | 1022.84 | GGB | 61.31 | GGB | 168699.38 | GGB | 139101.32 | GGB | 0 | 0 | 2738 | 3600 | 2722.89 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 187679.54 | GGB | 187681.75 | 2722.89 | 2716.9261 |  |  |  | 0 | 1 | [14 empty] | 105.2104 | 2716.9261 |  | 104.98
31.03.2008 12:00 | 3600 | 2 | 769.64 | GGB | 770.696 | 781.102 | 776.19 | 259.34 | GGB | 10779.5 | GGB | 9.85 | GGB | 1021.99 | GGB | 62.38 | GGB | 166294.04 | GGB | 136566.69 | GGB | 0 | 0 | 2570 | 3600 | 2555.13 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 187719.45 | GGB | 187721.66 | 2555.13 | 2555.13 |  |  |  | 0 | 1 | [14 empty] | 96.9293 |  |  | #VALUE!
31.03.2008 13:00 | 3600 | 2 | 770.89 | GGB | 771.795 | 781.898 | 777.289 | 257.55 | GGB | 10712.3 | GGB | 9.84 | GGB | 1021.05 | GGB | 63.22 | GGB | 164537.91 | GGB | 134659.51 | GGB | 0 | 0 | 2497 | 3600 | 2481.5 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 187759.07 | GGB | 187761.28 | 2481.5 | 2481.5 |  |  |  | 0 | 1 | [14 empty] | 92.8215 |  |  | #VALUE!
31.03.2008 14:00 | 3600 | 2 | 771.49 | GGB | 772.161 | 782.016 | 777.656 | 256.77 | GGB | 10658.9 | GGB | 9.83 | GGB | 1020.21 | GGB | 63.74 | GGB | 163702.75 | GGB | 133660.43 | GGB | 0 | 0 | 2448 | 3600 | 2432.42 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 187798.53 | GGB | 187800.74 | 2432.42 | 2432.42 |  |  |  | 0 | 1 | [14 empty] | 90.3106 |  |  | #VALUE!
31.03.2008 15:00 | 3600 | 2 | 771.89 | GGB | 770.696 | 781.875 | 776.923 | 254.95 | GGB | 10664.4 | GGB | 9.84 | GGB | 1019.31 | GGB | 64.72 | GGB | 161244.59 | GGB | 131154.67 | GGB | 0 | 0 | 2431 | 3600 | 2415.44 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 187837.78 | GGB | 187839.99 | 2415.44 | 2415.44 |  |  |  | 0 | 1 | [14 empty] | 87.999 |  |  | #VALUE!
31.03.2008 16:00 | 3600 | 2 | 772 | GGB | 772.161 | 781.781 | 778.022 | 255.22 | GGB | 10628.2 | GGB | 9.83 | GGB | 1018.75 | GGB | 65.23 | GGB | 161417.35 | GGB | 131027.12 | GGB | 0 | 0 | 2419 | 3600 | 2403.73 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 187877.6 | GGB | 187879.81 | 2403.73 | 2403.73 |  |  |  | 0 | 1 | [14 empty] | 87.4872 |  |  | #VALUE!
31.03.2008 17:00 | 3600 | 2 | 772.85 | GGB | 772.161 | 781.781 | 778.022 | 255.05 | GGB | 10627.4 | GGB | 9.84 | GGB | 1018.29 | GGB | 65.1 | GGB | 161544.99 | GGB | 131120.58 | GGB | 0 | 0 | 2383 | 3600 | 2368.17 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 187916.97 | GGB | 187919.19 | 2368.17 | 2368.17 |  |  |  | 0 | 1 | [14 empty] | 86.2544 |  |  | #VALUE!
31.03.2008 18:00 | 3600 | 2 | 771.94 | GGB | 772.161 | 783.352 | 778.755 | 254.62 | GGB | 10633 | GGB | 9.84 | GGB | 1017.98 | GGB | 65.39 | GGB | 160872.68 | GGB | 130425.7 | GGB | 0 | 0 | 2409 | 3600 | 2393.4 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 187955.71 | GGB | 187957.92 | 2393.4 | 2393.4 |  |  |  | 0 | 1 | [14 empty] | 86.7114 |  |  | #VALUE!
31.03.2008 19:00 | 3600 | 2 | 771.54 | GGB | 770.696 | 780.867 | 776.19 | 256.33 | GGB | 10609.7 | GGB | 9.82 | GGB | 1018.04 | GGB | 64.73 | GGB | 162627.72 | GGB | 132111.21 | GGB | 0 | 0 | 2417 | 3600 | 2401.55 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 187996.11 | GGB | 187998.32 | 2401.55 | 2401.55 |  |  |  | 0 | 1 | [14 empty] | 88.131 |  |  | #VALUE!
31.03.2008 20:00 | 3600 | 2 | 771.03 | GGB | 767.033 | 777.188 | 772.527 | 257.54 | GGB | 10631.8 | GGB | 9.82 | GGB | 1018.37 | GGB | 64.17 | GGB | 163469.48 | GGB | 133057.97 | GGB | 0 | 0 | 2439 | 3600 | 2423.97 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 188036.43 | GGB | 188038.65 | 2423.97 | 2423.97 |  |  |  | 0 | 1 | [14 empty] | 89.5913 |  |  | #VALUE!
31.03.2008 21:00 | 3600 | 2 | 769.19 | GGB | 769.597 | 780.305 | 776.19 | 259.8 | GGB | 10701.4 | GGB | 9.83 | GGB | 1019.63 | GGB | 63.4 | GGB | 165677.86 | GGB | 135332.98 | GGB | 0 | 0 | 2534 | 3600 | 2518.96 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 188076.35 | GGB | 188078.57 | 2518.96 | 2518.96 |  |  |  | 0 | 1 | [14 empty] | 94.694 |  |  | #VALUE!
31.03.2008 22:00 | 3600 | 2 | 767.62 | GGB | 764.835 | 773.602 | 768.864 | 260.92 | GGB | 10757.8 | GGB | 9.82 | GGB | 1020.33 | GGB | 62.6 | GGB | 167740.99 | GGB | 137440.59 | GGB | 0 | 0 | 2604 | 3600 | 2589.03 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 188115.47 | GGB | 188117.7 | 2589.03 | 2589.03 |  |  |  | 1 | 1 |  |  |  |  | 137440.59 | 2589.03 | 137440.59 | 2589.03 | 9.0937 | [5 empty] | 98.8438 |  |  | #VALUE!
31.03.2008 23:00 | 3600 | 2 | 766.85 | GGB | 767.033 | 776.789 | 771.429 | 262.12 | GGB | 10835.5 | GGB | 9.84 | GGB | 1020.73 | GGB | 62.47 | GGB | 167658.46 | GGB | 137480.78 | GGB | 0 | 0 | 2676 | 3600 | 2660.83 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 188154.38 | GGB | 188156.61 | 2660.83 | 2660.83 |  |  |  | 1 | 1 |  |  |  |  | 137480.78 | 2660.83 | 137480.78 | 2660.83 | 9.4015 | [5 empty] | 101.6147 |  |  | #VALUE!
31.03.2008 24:00 | 3600 | 2 | 764.89 | GGB | 767.033 | 776.953 | 772.527 | 263.13 | GGB | 10866.8 | GGB | 9.82 | GGB | 1021.39 | GGB | 62.4 | GGB | 168743.4 | GGB | 138488.73 | GGB | 0 | 0 | 2797 | 3600 | 2781.02 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 188195.11 | GGB | 188197.35 | 2781.02 | 2728.9441 |  |  |  | 1 | 1 |  |  |  |  | 138488.73 | 2728.9441 | 138488.73 | 2728.9441 | 9.2766 | [5 empty] | 106.9833 | 2728.9441 |  | 104.98
01.04.2008 01:00 | 3600 | 2 | 763.87 | GGB | 765.934 | 774.445 | 769.963 | 264.74 | GGB | 10919.2 | GGB | 9.82 | GGB | 1021.61 | GGB | 61.68 | GGB | 170670.09 | GGB | 140399.63 | GGB | 0 | 0 | 2867 | 3600 | 2851.67 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 188235.52 | GGB | 188237.75 | 2851.67 | 2691.802 |  |  |  | 1 | 1 |  |  |  |  | 140399.63 | 2691.802 | 140399.63 | 2691.802 | 9.3547 | [5 empty] | 111.2148 | 2691.802 |  | 104.98
01.04.2008 02:00 | 3600 | 2 | 762.57 | GGB | 764.469 | 773.414 | 768.864 | 266.88 | GGB | 10940.3 | GGB | 9.81 | GGB | 1021.88 | GGB | 60.88 | GGB | 173220.67 | GGB | 142876.45 | GGB | 0 | 0 | 2943 | 3600 | 2927.22 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 188275.74 | GGB | 188277.98 | 2927.22 | 2645.1385 |  |  |  | 1 | 1 |  |  |  |  | 142876.45 | 2645.1385 | 142876.45 | 2645.1385 | 9.3942 | [5 empty] | 116.1752 | 2645.1385 |  | 104.98
01.04.2008 03:00 | 3600 | 2 | 762.6 | GGB | 763.37 | 772.266 | 766.667 | 268.93 | GGB | 10972.9 | GGB | 9.83 | GGB | 1022.26 | GGB | 60.02 | GGB | 175795.46 | GGB | 145430.08 | GGB | 0 | 0 | 2950 | 3600 | 2934.05 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 188316.19 | GGB | 188318.42 | 2934.05 | 2598.6921 |  |  |  | 0 | 1 | [14 empty] | 118.5275 | 2598.6921 |  | 104.98
01.04.2008 04:00 | 3600 | 2 | 761.55 | GGB | 763.37 | 772.359 | 767.033 | 270.38 | GGB | 11024.6 | GGB | 9.83 | GGB | 1022.66 | GGB | 59.35 | GGB | 177744.16 | GGB | 147395.31 | GGB | 0 | 0 | 3039 | 3600 | 3023.41 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 188356.59 | GGB | 188358.82 | 3023.41 | 2564.0436 |  |  |  | 0 | 1 | [14 empty] | 123.7879 | 2564.0436 |  | 104.98
01.04.2008 05:00 | 3600 | 2 | 762.01 | GGB | 768.132 | 778.219 | 772.527 | 270.41 | GGB | 11083.2 | GGB | 9.85 | GGB | 1022.78 | GGB | 59.02 | GGB | 177976.33 | GGB | 147752.42 | GGB | 0 | 0 | 3057 | 3600 | 3040.92 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 188396.97 | GGB | 188399.2 | 3040.92 | 2557.8464 |  |  |  | 1 | 1 |  |  |  |  | 147752.42 | 2557.8464 | 147752.42 | 2557.8464 | 9.3593 | [5 empty] | 124.8065 | 2557.8464 |  | 104.98
01.04.2008 06:00 | 3600 | 2 | 761.71 | GGB | 762.271 | 770.438 | 766.3 | 267.57 | GGB | 11050.7 | GGB | 9.83 | GGB | 1023.12 | GGB | 59.73 | GGB | 174877.78 | GGB | 144917.74 | GGB | 0 | 0 | 3046 | 3600 | 3030.53 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 188437.1 | GGB | 188439.34 | 3030.53 | 2607.8795 |  |  |  | 0 | 1 | [14 empty] | 121.9938 | 2607.8795 |  | 104.98
01.04.2008 07:00 | 3600 | 2 | 761.14 | GGB | 762.271 | 771.258 | 767.766 | 268.03 | GGB | 11074.8 | GGB | 9.83 | GGB | 1023.19 | GGB | 59.24 | GGB | 175615.01 | GGB | 145752.65 | GGB | 0 | 0 | 3103 | 3600 | 3087.31 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 188477.42 | GGB | 188479.66 | 3087.31 | 2592.9408 |  |  |  | 0 | 1 | [14 empty] | 124.9954 | 2592.9408 |  | 104.98
01.04.2008 08:00 | 3600 | 2 | 761.97 | GGB | 764.835 | 773.883 | 769.963 | 267.66 | GGB | 11095.1 | GGB | 9.85 | GGB | 1023.59 | GGB | 59.27 | GGB | 175377.33 | GGB | 145599.7 | GGB | 0 | 0 | 3072 | 3600 | 3056.76 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 188518.25 | GGB | 188520.49 | 3056.76 | 2595.6647 |  |  |  | 1 | 1 |  |  |  |  | 145599.7 | 2595.6647 | 145599.7 | 2595.6647 | 9.2561 | [5 empty] | 123.6287 | 2595.6647 |  | 104.98
01.04.2008 09:00 | 3600 | 2 | 761.32 | GGB | 763.37 | 772.125 | 766.667 | 267.67 | GGB | 11036.2 | GGB | 9.83 | GGB | 1023.68 | GGB | 59.19 | GGB | 175759.15 | GGB | 145965.08 | GGB | 0 | 0 | 3074 | 3600 | 3058.15 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 188559.53 | GGB | 188561.77 | 3058.15 | 2589.1672 |  |  |  | 0 | 1 | [14 empty] | 123.9953 | 2589.1672 |  | 104.98
01.04.2008 10:00 | 3600 | 2 | 765.16 | GGB | 768.132 | 777.352 | 772.527 | 265.58 | GGB | 10999 | GGB | 9.87 | GGB | 1023.67 | GGB | 59.59 | GGB | 173658.6 | GGB | 144044.55 | GGB | 0 | 0 | 2870 | 3600 | 2854.52 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 188600.48 | GGB | 188602.73 | 2854.52 | 2623.6883 |  |  |  | 1 | 1 |  |  |  |  | 144044.55 | 2623.6883 | 144044.55 | 2623.6883 | 9.2268 | [5 empty] | 114.2161 | 2623.6883 |  | 104.98
01.04.2008 11:00 | 3600 | 2 | 766.62 | GGB | 768.132 | 777.164 | 772.527 | 260.9 | GGB | 10818.8 | GGB | 9.87 | GGB | 1022.55 | GGB | 61.21 | GGB | 168046.88 | GGB | 138565.64 | GGB | 0 | 0 | 2683 | 3600 | 2667.38 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 188640.81 | GGB | 188643.05 | 2667.38 | 2667.38 |  |  |  | 1 | 1 |  |  |  |  | 138565.64 | 2667.38 | 138565.64 | 2667.38 | 9.1668 | [5 empty] | 102.6687 |  |  | #VALUE!
01.04.2008 12:00 | 3600 | 2 | 766.92 | GGB | 768.498 | 778.617 | 773.993 | 258.2 | GGB | 10630.1 | GGB | 9.85 | GGB | 1020.27 | GGB | 62.25 | GGB | 164441.08 | GGB | 134869.79 | GGB | 0 | 0 | 2600 | 3600 | 2584.72 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 188680.69 | GGB | 188682.93 | 2584.72 | 2584.72 |  |  |  | 1 | 1 |  |  |  |  | 134869.79 | 2584.72 | 134869.79 | 2584.72 | 8.7412 | [5 empty] | 96.8335 |  |  | #VALUE!
01.04.2008 13:00 | 3600 | 2 | 767.33 | GGB | 768.132 | 777.609 | 773.626 | 255.07 | GGB | 10570.5 | GGB | 9.84 | GGB | 1018.59 | GGB | 63.33 | GGB | 161230.29 | GGB | 131593.07 | GGB | 0 | 0 | 2566 | 3600 | 2550.69 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 188720.1 | GGB | 188722.34 | 2550.69 | 2550.69 |  |  |  | 1 | 1 |  |  |  |  | 131593.07 | 2550.69 | 131593.07 | 2550.69 | 8.517 | [5 empty] | 93.237 |  |  | #VALUE!
01.04.2008 14:00 | 3600 | 2 | 767.52 | GGB | 768.498 | 778.758 | 773.993 | 254.3 | GGB | 10505 | GGB | 9.84 | GGB | 1016.81 | GGB | 64.07 | GGB | 160017.72 | GGB | 130089.39 | GGB | 0 | 0 | 2533 | 3600 | 2517.45 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 188759.21 | GGB | 188761.46 | 2517.45 | 2517.45 |  |  |  | 0 | 1 | [14 empty] | 90.9704 |  |  | #VALUE!
01.04.2008 15:00 | 3600 | 2 | 767.93 | GGB | 768.498 | 778.758 | 773.993 | 254.69 | GGB | 10445.3 | GGB | 9.83 | GGB | 1016 | GGB | 63.68 | GGB | 161170.87 | GGB | 131074.59 | GGB | 0 | 0 | 2490 | 3600 | 2474.56 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 188798.4 | GGB | 188800.65 | 2474.56 | 2474.56 |  |  |  | 0 | 1 | [14 empty] | 90.0978 |  |  | #VALUE!
01.04.2008 16:00 | 3600 | 2 | 768.2 | GGB | 769.597 | 779.813 | 774.359 | 253.87 | GGB | 10413.7 | GGB | 9.84 | GGB | 1015.3 | GGB | 64.01 | GGB | 160613 | GGB | 130403.44 | GGB | 0 | 0 | 2464 | 3600 | 2448.48 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 188837.38 | GGB | 188839.63 | 2448.48 | 2448.48 |  |  |  | 0 | 1 | [14 empty] | 88.6917 |  |  | #VALUE!
01.04.2008 17:00 | 3600 | 2 | 768.11 | GGB | 769.597 | 778.781 | 775.458 | 253.27 | GGB | 10387.1 | GGB | 9.84 | GGB | 1014.24 | GGB | 64.21 | GGB | 160068.33 | GGB | 129747.56 | GGB | 0 | 0 | 2450 | 3600 | 2434.77 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 188876.25 | GGB | 188878.49 | 2434.77 | 2434.77 |  |  |  | 0 | 1 | [14 empty] | 87.7515 |  |  | #VALUE!
01.04.2008 18:00 | 3600 | 2 | 768 | GGB | 768.132 | 778.008 | 774.359 | 252.03 | GGB | 10404.1 | GGB | 9.84 | GGB | 1013.37 | GGB | 64.56 | GGB | 158657.7 | GGB | 128360.28 | GGB | 0 | 0 | 2462 | 3600 | 2447.01 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 188914.95 | GGB | 188917.19 | 2447.01 | 2447.01 |  |  |  | 1 | 1 |  |  |  |  | 128360.28 | 2447.01 | 128360.28 | 2447.01 | 8.1163 | [5 empty] | 87.2497 |  |  | #VALUE!
01.04.2008 19:00 | 3600 | 2 | 767.85 | GGB | 768.498 | 778.852 | 773.26 | 252.41 | GGB | 10413.2 | GGB | 9.83 | GGB | 1013.01 | GGB | 64.63 | GGB | 158947.09 | GGB | 128523.99 | GGB | 0 | 0 | 2482 | 3600 | 2466.46 | GGB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 188953.48 | GGB | 188955.72 | 2466.46 | 2466.46 |  |  |  | 0 | 1 | [14 empty] | 88.0554 |  |  | #VALUE!
01.04.2008 20:00 | 3600 | 2 | 767.18 | GGB | 770.696 | 779.883 | 775.458 | 254.36 | GGB | 10415.3 | GGB | 9.83 | GGB | 1013.6 | GGB | 63.82 | GGB | 161019.03 | GGB | 130584.71 | GGB | 0 | 0 | 2509 | 3600 | 2493.84 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 188991.94 | GGB | 188994.18 | 2493.84 | 2493.84 |  |  |  | 0 | 1 | [14 empty] | 90.4604 |  |  | #VALUE!
01.04.2008 21:00 | 3600 | 2 | 766.59 | GGB | 767.033 | 777.727 | 773.26 | 256.19 | GGB | 10496.7 | GGB | 9.83 | GGB | 1014.06 | GGB | 63.19 | GGB | 162894 | GGB | 132414.38 | GGB | 0 | 0 | 2561 | 3600 | 2545.31 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 189030.31 | GGB | 189032.55 | 2545.31 | 2545.31 |  |  |  | 1 | 1 |  |  |  |  | 132414.38 | 2545.31 | 132414.38 | 2545.31 | 8.7838 | [5 empty] | 93.621 |  |  | #VALUE!
01.04.2008 22:00 | 3600 | 2 | 765.97 | GGB | 767.033 | 776.555 | 772.161 | 257.42 | GGB | 10564.6 | GGB | 9.83 | GGB | 1014.49 | GGB | 62.69 | GGB | 164364.05 | GGB | 133867.18 | GGB | 0 | 0 | 2596 | 3600 | 2581.07 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 189069.25 | GGB | 189071.49 | 2581.07 | 2581.07 |  |  |  | 1 | 1 |  |  |  |  | 133867.18 | 2581.07 | 133867.18 | 2581.07 | 8.8732 | [5 empty] | 95.9779 |  |  | #VALUE!
01.04.2008 23:00 | 3600 | 2 | 765.34 | GGB | 765.934 | 775.359 | 770.696 | 258.19 | GGB | 10665.8 | GGB | 9.83 | GGB | 1014.68 | GGB | 62.31 | GGB | 165238.82 | GGB | 134757.38 | GGB | 0 | 0 | 2659 | 3600 | 2644 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 189108.29 | GGB | 189110.53 | 2644 | 2644 |  |  |  | 1 | 1 |  |  |  |  | 134757.38 | 2644 | 134757.38 | 2644 | 9.1265 | [5 empty] | 98.9718 |  |  | #VALUE!
01.04.2008 24:00 | 3600 | 2 | 764.47 | GGB | 765.934 | 775.477 | 771.795 | 259.8 | GGB | 10752.6 | GGB | 9.83 | GGB | 1014.93 | GGB | 62.05 | GGB | 166506.41 | GGB | 135931 | GGB | 0 | 0 | 2747 | 3600 | 2731.55 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 189147.28 | GGB | 189149.52 | 2731.55 | 2731.55 |  |  |  | 1 | 1 |  |  |  |  | 135931 | 2731.55 | 135931 | 2731.55 | 9.523 | [5 empty] | 103.1395 |  |  | #VALUE!
02.04.2008 01:00 | 3600 | 2 | 764.46 | GGB | 765.934 | 775.734 | 770.696 | 262.38 | GGB | 10788.4 | GGB | 9.83 | GGB | 1015.01 | GGB | 61.23 | GGB | 169548.84 | GGB | 138761.83 | GGB | 0 | 0 | 2762 | 3600 | 2746.22 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 189186.88 | GGB | 189189.13 | 2746.22 | 2723.5732 |  |  |  | 1 | 1 |  |  |  |  | 138761.83 | 2723.5732 | 138761.83 | 2723.5732 | 9.5412 | [5 empty] | 105.8529 | 2723.5732 |  | 104.98
02.04.2008 02:00 | 3600 | 2 | 765.12 | GGB | 767.033 | 777.07 | 771.429 | 262.17 | GGB | 10799.7 | GGB | 9.84 | GGB | 1014.69 | GGB | 60.85 | GGB | 169950.47 | GGB | 139204.27 | GGB | 0 | 0 | 2733 | 3600 | 2717.41 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 189226.65 | GGB | 189228.9 | 2717.41 | 2714.9167 |  |  |  | 1 | 1 |  |  |  |  | 139204.27 | 2714.9167 | 139204.27 | 2714.9167 | 9.5028 | [5 empty] | 105.0764 | 2714.9167 |  | 104.98
02.04.2008 03:00 | 3600 | 2 | 764.19 | GGB | 765.934 | 775.828 | 770.696 | 261.02 | GGB | 10836.9 | GGB | 9.83 | GGB | 1014.29 | GGB | 61.14 | GGB | 168622.36 | GGB | 137943.49 | GGB | 0 | 0 | 2795 | 3600 | 2779.44 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 189266.33 | GGB | 189268.58 | 2779.44 | 2739.7306 |  |  |  | 1 | 1 |  |  |  |  | 137943.49 | 2739.7306 | 137943.49 | 2739.7306 | 9.5244 | [5 empty] | 106.5016 | 2739.7306 |  | 104.98
02.04.2008 04:00 | 3600 | 2 | 763.44 | GGB | 764.469 | 773.602 | 769.597 | 261.96 | GGB | 10872.7 | GGB | 9.82 | GGB | 1013.97 | GGB | 60.9 | GGB | 169387.09 | GGB | 138624.32 | GGB | 0 | 0 | 2849 | 3600 | 2833.57 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 189306.19 | GGB | 189308.44 | 2833.57 | 2726.2749 |  |  |  | 1 | 1 |  |  |  |  | 138624.32 | 2726.2749 | 138624.32 | 2726.2749 | 9.4814 | [5 empty] | 109.1116 | 2726.2749 |  | 104.98
02.04.2008 05:00 | 3600 | 2 | 763.64 | GGB | 764.835 | 773.672 | 768.498 | 262.8 | GGB | 10920.4 | GGB | 9.84 | GGB | 1013.73 | GGB | 60.67 | GGB | 170452.22 | GGB | 139559.49 | GGB | 0 | 0 | 2860 | 3600 | 2844.88 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 189346.2 | GGB | 189348.45 | 2844.88 | 2708.0065 |  |  |  | 1 | 1 |  |  |  |  | 139559.49 | 2708.0065 | 139559.49 | 2708.0065 | 9.4458 | [5 empty] | 110.2861 | 2708.0065 |  | 104.98
02.04.2008 06:00 | 3600 | 2 | 763.33 | GGB | 764.835 | 773.672 | 769.597 | 263.24 | GGB | 10921.9 | GGB | 9.83 | GGB | 1013.36 | GGB | 60.43 | GGB | 171064.01 | GGB | 140112.15 | GGB | 0 | 0 | 2881 | 3600 | 2865.4 | GGB | 100 | GGB | 40.28 | GGB | 40.28 | GGB | 189386.48 | GGB | 189388.73 | 2865.4 | 2697.325 |  |  |  | 1 | 1 |  |  |  |  | 140112.15 | 2697.325 | 140112.15 | 2697.325 | 9.3825 | [5 empty] | 111.5215 | 2697.325 |  | 104.98
02.04.2008 07:00 | 3600 | 2 | 763.21 | GGB | 763.37 | 772.828 | 768.132 | 263.73 | GGB | 10925.5 | GGB | 9.83 | GGB | 1013.3 | GGB | 60.05 | GGB | 171959.68 | GGB | 140995.65 | GGB | 0 | 0 | 2878 | 3600 | 2862.43 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 189426.83 | GGB | 189429.08 | 2862.43 | 2680.4231 |  |  |  | 0 | 1 | [14 empty] | 112.1084 | 2680.4231 |  | 104.98
02.04.2008 08:00 | 3600 | 2 | 764.35 | GGB | 767.033 | 775.805 | 771.795 | 263.25 | GGB | 10902.1 | GGB | 9.85 | GGB | 1013.19 | GGB | 60.1 | GGB | 171512.95 | GGB | 140594.29 | GGB | 0 | 0 | 2821 | 3600 | 2805.01 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 189467.23 | GGB | 189469.48 | 2805.01 | 2688.075 |  |  |  | 1 | 1 |  |  |  |  | 140594.29 | 2688.075 | 140594.29 | 2688.075 | 9.3547 | [5 empty] | 109.5468 | 2688.075 |  | 104.98
02.04.2008 09:00 | 3600 | 2 | 764.72 | GGB | 765.934 | 774.727 | 770.696 | 261.89 | GGB | 10850.2 | GGB | 9.85 | GGB | 1012.97 | GGB | 60.05 | GGB | 170391.7 | GGB | 139666.89 | GGB | 0 | 0 | 2775 | 3600 | 2759.42 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 189507.36 | GGB | 189509.61 | 2759.42 | 2705.9241 |  |  |  | 1 | 1 |  |  |  |  | 139666.89 | 2705.9241 | 139666.89 | 2705.9241 | 9.4176 | [5 empty] | 107.0554 | 2705.9241 |  | 104.98
02.04.2008 10:00 | 3600 | 2 | 764.69 | GGB | 764.835 | 774.563 | 769.597 | 259 | GGB | 10814.8 | GGB | 9.84 | GGB | 1012.44 | GGB | 61.04 | GGB | 166947.65 | GGB | 136366.79 | GGB | 0 | 0 | 2768 | 3600 | 2752.47 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 189547.24 | GGB | 189549.49 | 2752.47 | 2752.47 |  |  |  | 1 | 1 |  |  |  |  | 136366.79 | 2752.47 | 136366.79 | 2752.47 | 9.4119 | [5 empty] | 104.2626 |  |  | #VALUE!
02.04.2008 11:00 | 3600 | 2 | 764.79 | GGB | 765.934 | 774.609 | 770.696 | 257.71 | GGB | 10771 | GGB | 9.85 | GGB | 1012.34 | GGB | 61.59 | GGB | 165382.96 | GGB | 134853.7 | GGB | 0 | 0 | 2728 | 3600 | 2712.27 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 189586.98 | GGB | 189589.24 | 2712.27 | 2712.27 |  |  |  | 1 | 1 |  |  |  |  | 134853.7 | 2712.27 | 134853.7 | 2712.27 | 9.2015 | [5 empty] | 101.5999 |  |  | #VALUE!
02.04.2008 12:00 | 3600 | 2 | 764.81 | GGB | 765.934 | 774.609 | 770.696 | 257.18 | GGB | 10699.1 | GGB | 9.83 | GGB | 1012.57 | GGB | 62.01 | GGB | 164596.22 | GGB | 134073.3 | GGB | 0 | 0 | 2711 | 3600 | 2695.83 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 189625.72 | GGB | 189627.98 | 2695.83 | 2695.83 |  |  |  | 1 | 1 |  |  |  |  | 134073.3 | 2695.83 | 134073.3 | 2695.83 | 9.3299 | [5 empty] | 100.3997 |  |  | #VALUE!
02.04.2008 13:00 | 3600 | 2 | 765.72 | GGB | 767.033 | 776.742 | 772.527 | 255.76 | GGB | 10672.7 | GGB | 9.85 | GGB | 1012.32 | GGB | 62.71 | GGB | 162706.94 | GGB | 132225.84 | GGB | 0 | 0 | 2671 | 3600 | 2655.51 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 189664.62 | GGB | 189666.88 | 2655.51 | 2655.51 |  |  |  | 1 | 1 |  |  |  |  | 132225.84 | 2655.51 | 132225.84 | 2655.51 | 9.0264 | [5 empty] | 97.5353 |  |  | #VALUE!
02.04.2008 14:00 | 3600 | 2 | 766.04 | GGB | 768.132 | 777.844 | 773.626 | 254.57 | GGB | 10607.9 | GGB | 9.84 | GGB | 1011.68 | GGB | 63.29 | GGB | 161237.99 | GGB | 130721.03 | GGB | 0 | 0 | 2634 | 3600 | 2618.15 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 189705.27 | GGB | 189707.53 | 2618.15 | 2618.15 |  |  |  | 1 | 1 |  |  |  |  | 130721.03 | 2618.15 | 130721.03 | 2618.15 | 8.4194 | [5 empty] | 95.0687 |  |  | #VALUE!
02.04.2008 15:00 | 3600 | 2 | 766.1 | GGB | 768.132 | 777.961 | 773.626 | 254.64 | GGB | 10534.9 | GGB | 9.84 | GGB | 1011.09 | GGB | 63.25 | GGB | 161663.82 | GGB | 131007.03 | GGB | 0 | 0 | 2606 | 3600 | 2590.22 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 189745.32 | GGB | 189747.58 | 2590.22 | 2590.22 |  |  |  | 1 | 1 |  |  |  |  | 131007.03 | 2590.22 | 131007.03 | 2590.22 | 8.4728 | [5 empty] | 94.2603 |  |  | #VALUE!
02.04.2008 16:00 | 3600 | 2 | 766.46 | GGB | 767.033 | 777.047 | 772.527 | 252.17 | GGB | 10503.1 | GGB | 9.84 | GGB | 1009.87 | GGB | 64.01 | GGB | 158985.6 | GGB | 128389.98 | GGB | 0 | 0 | 2585 | 3600 | 2569.4 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 189784.7 | GGB | 189786.96 | 2569.4 | 2569.4 |  |  |  | 1 | 1 |  |  |  |  | 128389.98 | 2569.4 | 128389.98 | 2569.4 | 8.377 | [5 empty] | 91.6348 |  |  | #VALUE!
02.04.2008 17:00 | 3600 | 2 | 766.21 | GGB | 765.934 | 775.828 | 771.429 | 252.12 | GGB | 10482.3 | GGB | 9.83 | GGB | 1009.53 | GGB | 64.27 | GGB | 158752.33 | GGB | 128062.51 | GGB | 0 | 0 | 2587 | 3600 | 2571.37 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 189823.96 | GGB | 189826.22 | 2571.37 | 2571.37 |  |  |  | 1 | 1 |  |  |  |  | 128062.51 | 2571.37 | 128062.51 | 2571.37 | 8.3876 | [5 empty] | 91.4711 |  |  | #VALUE!
02.04.2008 18:00 | 3600 | 2 | 766.31 | GGB | 767.033 | 777.211 | 772.527 | 252.63 | GGB | 10487.5 | GGB | 9.83 | GGB | 1009.88 | GGB | 64.38 | GGB | 158846.96 | GGB | 128140.42 | GGB | 0 | 0 | 2589 | 3600 | 2573.61 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 189863.25 | GGB | 189865.5 | 2573.61 | 2573.61 |  |  |  | 1 | 1 |  |  |  |  | 128140.42 | 2573.61 | 128140.42 | 2573.61 | 8.3957 | [5 empty] | 91.6065 |  |  | #VALUE!
02.04.2008 19:00 | 3600 | 2 | 766.05 | GGB | 767.033 | 777.492 | 772.527 | 253 | GGB | 10498 | GGB | 9.83 | GGB | 1010.11 | GGB | 64.39 | GGB | 159057.12 | GGB | 128334.21 | GGB | 0 | 0 | 2601 | 3600 | 2585.72 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 189902.05 | GGB | 189904.3 | 2585.72 | 2585.72 |  |  |  | 1 | 1 |  |  |  |  | 128334.21 | 2585.72 | 128334.21 | 2585.72 | 8.5525 | [5 empty] | 92.1768 |  |  | #VALUE!
02.04.2008 20:00 | 3600 | 2 | 766.03 | GGB | 767.033 | 776.156 | 772.527 | 254.3 | GGB | 10488.3 | GGB | 9.83 | GGB | 1010.3 | GGB | 64.15 | GGB | 160140.96 | GGB | 129323.98 | GGB | 0 | 0 | 2600 | 3600 | 2585.17 | GGB | 100 | GGB | 38.68 | GGB | 38.68 | GGB | 189940.73 | GGB | 189942.98 | 2585.17 | 2585.17 |  |  |  | 1 | 1 |  |  |  |  | 129323.98 | 2585.17 | 129323.98 | 2585.17 | 8.6433 | [5 empty] | 92.8679 |  |  | #VALUE!
02.04.2008 21:00 | 3600 | 2 | 766.53 | GGB | 767.033 | 776.789 | 771.429 | 255.7 | GGB | 10494.2 | GGB | 9.83 | GGB | 1011.55 | GGB | 63.58 | GGB | 161342.52 | GGB | 130678.59 | GGB | 0 | 0 | 2585 | 3600 | 2570.08 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 189979.25 | GGB | 189981.5 | 2570.08 | 2570.08 |  |  |  | 1 | 1 |  |  |  |  | 130678.59 | 2570.08 | 130678.59 | 2570.08 | 8.719 | [5 empty] | 93.2929 |  |  | #VALUE!
02.04.2008 22:00 | 3600 | 2 | 766.14 | GGB | 768.132 | 777.75 | 773.626 | 255.8 | GGB | 10537.1 | GGB | 9.84 | GGB | 1011.37 | GGB | 64.29 | GGB | 159772.34 | GGB | 129108.28 | GGB | 0 | 0 | 2636 | 3600 | 2620.49 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 190017.75 | GGB | 190020 | 2620.49 | 2620.49 |  |  |  | 1 | 1 |  |  |  |  | 129108.28 | 2620.49 | 129108.28 | 2620.49 | 8.7877 | [5 empty] | 93.9797 |  |  | #VALUE!
02.04.2008 23:00 | 3600 | 2 | 765.63 | GGB | 768.132 | 778.594 | 773.626 | 256.92 | GGB | 10565.7 | GGB | 9.83 | GGB | 1011.25 | GGB | 64.22 | GGB | 160863.88 | GGB | 130003.32 | GGB | 0 | 0 | 2678 | 3600 | 2662.71 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 190056.72 | GGB | 190058.97 | 2662.71 | 2662.71 |  |  |  | 1 | 1 |  |  |  |  | 130003.32 | 2662.71 | 130003.32 | 2662.71 | 8.8828 | [5 empty] | 96.1559 |  |  | #VALUE!
02.04.2008 24:00 | 3600 | 2 | 765.67 | GGB | 765.934 | 776.039 | 771.429 | 256.95 | GGB | 10600.7 | GGB | 9.83 | GGB | 1011.17 | GGB | 63.87 | GGB | 161646.22 | GGB | 130762.51 | GGB | 0 | 0 | 2685 | 3600 | 2669.14 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 190095.83 | GGB | 190098.08 | 2669.14 | 2669.14 |  |  |  | 1 | 1 |  |  |  |  | 130762.51 | 2669.14 | 130762.51 | 2669.14 | 8.9241 | [5 empty] | 96.951 |  |  | #VALUE!
03.04.2008 01:00 | 3600 | 2 | 765.47 | GGB | 765.934 | 776.203 | 771.429 | 256.93 | GGB | 10623.9 | GGB | 9.84 | GGB | 1011.5 | GGB | 63.64 | GGB | 162169.98 | GGB | 131317.26 | GGB | 0 | 0 | 2696 | 3600 | 2680.78 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 190135.03 | GGB | 190137.27 | 2680.78 | 2680.78 |  |  |  | 1 | 1 |  |  |  |  | 131317.26 | 2680.78 | 131317.26 | 2680.78 | 8.9827 | [5 empty] | 97.7869 |  |  | #VALUE!
03.04.2008 02:00 | 3600 | 2 | 765.33 | GGB | 767.033 | 775.805 | 771.429 | 256.8 | GGB | 10618.1 | GGB | 9.83 | GGB | 1011.36 | GGB | 63.62 | GGB | 162095.16 | GGB | 131245.34 | GGB | 0 | 0 | 2694 | 3600 | 2678.46 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 190174.31 | GGB | 190176.55 | 2678.46 | 2678.46 |  |  |  | 1 | 1 |  |  |  |  | 131245.34 | 2678.46 | 131245.34 | 2678.46 | 8.9495 | [5 empty] | 97.6487 |  |  | #VALUE!
03.04.2008 03:00 | 3600 | 2 | 764.98 | GGB | 764.835 | 774.422 | 769.597 | 257.26 | GGB | 10631.9 | GGB | 9.83 | GGB | 1011.45 | GGB | 63.47 | GGB | 162745.46 | GGB | 131843.95 | GGB | 0 | 0 | 2719 | 3600 | 2703.34 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 190213.59 | GGB | 190215.83 | 2703.34 | 2703.34 |  |  |  | 1 | 1 |  |  |  |  | 131843.95 | 2703.34 | 131843.95 | 2703.34 | 9.0738 | [5 empty] | 99.0053 |  |  | #VALUE!
03.04.2008 04:00 | 3600 | 2 | 765.38 | GGB | 765.934 | 776.414 | 770.696 | 258.77 | GGB | 10638.1 | GGB | 9.84 | GGB | 1011.54 | GGB | 63.09 | GGB | 164580.82 | GGB | 133492.42 | GGB | 0 | 0 | 2704 | 3600 | 2688.83 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 190253 | GGB | 190255.24 | 2688.83 | 2688.83 |  |  |  | 1 | 1 |  |  |  |  | 133492.42 | 2688.83 | 133492.42 | 2688.83 | 9.1078 | [5 empty] | 99.7051 |  |  | #VALUE!
03.04.2008 05:00 | 3600 | 2 | 765.52 | GGB | 767.033 | 776.578 | 770.696 | 259.02 | GGB | 10655.6 | GGB | 9.84 | GGB | 1011.65 | GGB | 62.86 | GGB | 164866.91 | GGB | 133830.72 | GGB | 0 | 0 | 2700 | 3600 | 2685.03 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 190292.46 | GGB | 190294.7 | 2685.03 | 2685.03 |  |  |  | 1 | 1 |  |  |  |  | 133830.72 | 2685.03 | 133830.72 | 2685.03 | 9.1064 | [5 empty] | 99.8165 |  |  | #VALUE!
03.04.2008 06:00 | 3600 | 2 | 765.02 | GGB | 767.033 | 777.469 | 772.161 | 258.28 | GGB | 10676.8 | GGB | 9.84 | GGB | 1011.92 | GGB | 63.24 | GGB | 163546.5 | GGB | 132645.68 | GGB | 0 | 0 | 2734 | 3600 | 2718.43 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 190331.82 | GGB | 190334.06 | 2718.43 | 2718.43 |  |  |  | 1 | 1 |  |  |  |  | 132645.68 | 2718.43 | 132645.68 | 2718.43 | 9.1613 | [5 empty] | 100.1633 |  |  | #VALUE!
03.04.2008 07:00 | 3600 | 2 | 765.04 | GGB | 765.934 | 775.57 | 770.696 | 259.09 | GGB | 10657.6 | GGB | 9.83 | GGB | 1012.07 | GGB | 62.92 | GGB | 164851.5 | GGB | 133849.02 | GGB | 0 | 0 | 2728 | 3600 | 2712.09 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 190371.26 | GGB | 190373.5 | 2712.09 | 2712.09 |  |  |  | 1 | 1 |  |  |  |  | 133849.02 | 2712.09 | 133849.02 | 2712.09 | 9.2041 | [5 empty] | 100.8363 |  |  | #VALUE!
03.04.2008 08:00 | 3600 | 2 | 765.42 | GGB | 765.934 | 775.5 | 770.696 | 258.77 | GGB | 10681.9 | GGB | 9.84 | GGB | 1012.09 | GGB | 62.87 | GGB | 164553.31 | GGB | 133631.06 | GGB | 0 | 0 | 2715 | 3600 | 2699.76 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 190410.42 | GGB | 190412.66 | 2699.76 | 2699.76 |  |  |  | 1 | 1 |  |  |  |  | 133631.06 | 2699.76 | 133631.06 | 2699.76 | 9.2128 | [5 empty] | 100.2144 |  |  | #VALUE!
03.04.2008 09:00 | 3600 | 2 | 765.16 | GGB | 767.033 | 776.766 | 771.795 | 259.17 | GGB | 10664.6 | GGB | 9.83 | GGB | 1012.41 | GGB | 62.75 | GGB | 164774.48 | GGB | 133901.82 | GGB | 0 | 0 | 2714 | 3600 | 2698.14 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 190449.76 | GGB | 190452 | 2698.14 | 2698.14 |  |  |  | 1 | 1 |  |  |  |  | 133901.82 | 2698.14 | 133901.82 | 2698.14 | 9.1837 | [5 empty] | 100.3572 |  |  | #VALUE!
03.04.2008 10:00 | 3600 | 2 | 760.13 | GGB | 765.934 | 775.898 | 770.696 | 271.65 | GGB | 10906.4 | GGB | 9.76 | GGB | 1013.47 | GGB | 60.65 | GGB | 175843.88 | GGB | 143946.49 | GGB | 0 | 0 | 3098 | 3600 | 3082.69 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 190489.98 | GGB | 190492.22 | 3082.69 | 2625.4756 |  |  |  | 1 | 1 |  |  |  |  | 143946.49 | 2625.4756 | 143946.49 | 2625.4756 | 9.3965 | [5 empty] | 123.2618 | 2625.4756 |  | 104.98
03.04.2008 11:00 | 3600 | 2 | 764.57 | GGB | 764.469 | 774.68 | 769.597 | 270.56 | GGB | 11022.5 | GGB | 9.86 | GGB | 1013.56 | GGB | 62.05 | GGB | 173854.47 | GGB | 141735.37 | GGB | 0 | 0 | 2964 | 3600 | 2948.63 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 190530.02 | GGB | 190532.27 | 2948.63 | 2666.4339 |  |  |  | 1 | 1 |  |  |  |  | 141735.37 | 2666.4339 | 141735.37 | 2666.4339 | 9.4364 | [5 empty] | 116.0903 | 2666.4339 |  | 104.98
03.04.2008 12:00 | 3600 | 2 | 765.35 | GGB | 764.835 | 775.617 | 770.696 | 268.06 | GGB | 11017.4 | GGB | 9.87 | GGB | 1013.36 | GGB | 62.75 | GGB | 172067.52 | GGB | 139959.52 | GGB | 0 | 0 | 2915 | 3600 | 2899.79 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 190570.2 | GGB | 190572.44 | 2899.79 | 2700.2665 |  |  |  | 1 | 1 |  |  |  |  | 139959.52 | 2700.2665 | 139959.52 | 2700.2665 | 9.4082 | [5 empty] | 112.737 | 2700.2665 |  | 104.98
03.04.2008 13:00 | 3600 | 2 | 764.59 | GGB | 764.102 | 774.328 | 769.597 | 267.4 | GGB | 10941.6 | GGB | 9.85 | GGB | 1013.41 | GGB | 62.53 | GGB | 171888.16 | GGB | 139910.59 | GGB | 0 | 0 | 2910 | 3600 | 2894.25 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 190610.5 | GGB | 190612.74 | 2894.25 | 2701.2108 |  |  |  | 1 | 1 |  |  |  |  | 139910.59 | 2701.2108 | 139910.59 | 2701.2108 | 9.3779 | [5 empty] | 112.4823 | 2701.2108 |  | 104.98
03.04.2008 14:00 | 3600 | 2 | 766.08 | GGB | 768.864 | 778.594 | 774.359 | 267.38 | GGB | 10949.7 | GGB | 9.88 | GGB | 1013.44 | GGB | 62.4 | GGB | 171755.02 | GGB | 139859.62 | GGB | 0 | 0 | 2839 | 3600 | 2823.97 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 190650.68 | GGB | 190652.93 | 2823.97 | 2702.1952 |  |  |  | 1 | 1 |  |  |  |  | 139859.62 | 2702.1952 | 139859.62 | 2702.1952 | 9.4035 | [5 empty] | 109.7109 | 2702.1952 |  | 104.98
03.04.2008 15:00 | 3600 | 2 | 765.14 | GGB | 766.3 | 776.391 | 771.795 | 265.99 | GGB | 10911.5 | GGB | 9.85 | GGB | 1013.22 | GGB | 63.09 | GGB | 170184.84 | GGB | 138267.98 | GGB | 0 | 0 | 2877 | 3600 | 2861.11 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 190690.74 | GGB | 190692.99 | 2861.11 | 2733.3009 |  |  |  | 1 | 1 |  |  |  |  | 138267.98 | 2733.3009 | 138267.98 | 2733.3009 | 9.434 | [5 empty] | 109.8889 | 2733.3009 |  | 104.98
03.04.2008 16:00 | 3600 | 2 | 766.19 | GGB | 766.667 | 776.508 | 770.696 | 266.27 | GGB | 10845.2 | GGB | 9.86 | GGB | 1013.13 | GGB | 62.85 | GGB | 170851.64 | GGB | 138898.31 | GGB | 0 | 0 | 2782 | 3600 | 2766.6 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 190730.94 | GGB | 190733.19 | 2766.6 | 2720.897 |  |  |  | 1 | 1 |  |  |  |  | 138898.31 | 2720.897 | 138898.31 | 2720.897 | 9.4012 | [5 empty] | 106.7434 | 2720.897 |  | 104.98
03.04.2008 17:00 | 3600 | 2 | 765.88 | GGB | 767.766 | 776.508 | 772.161 | 265.66 | GGB | 10837.7 | GGB | 9.86 | GGB | 1012.22 | GGB | 62.4 | GGB | 170357.59 | GGB | 138556.19 | GGB | 0 | 0 | 2786 | 3600 | 2770.26 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 190770.98 | GGB | 190773.23 | 2770.26 | 2727.6154 |  |  |  | 1 | 1 |  |  |  |  | 138556.19 | 2727.6154 | 138556.19 | 2727.6154 | 9.4388 | [5 empty] | 106.6213 | 2727.6154 |  | 104.98
03.04.2008 18:00 | 3600 | 2 | 765.8 | GGB | 766.667 | 776.555 | 772.161 | 264.63 | GGB | 10867.2 | GGB | 9.86 | GGB | 1012.14 | GGB | 63.06 | GGB | 168738.99 | GGB | 136959.75 | GGB | 0 | 0 | 2801 | 3600 | 2785.63 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 190810.95 | GGB | 190813.2 | 2785.63 | 2759.4092 |  |  |  | 1 | 1 |  |  |  |  | 136959.75 | 2759.4092 | 136959.75 | 2759.4092 | 9.4553 | [5 empty] | 105.9776 | 2759.4092 |  | 104.98
03.04.2008 19:00 | 3600 | 2 | 764.82 | GGB | 765.201 | 775.359 | 770.696 | 265.79 | GGB | 10838 | GGB | 9.84 | GGB | 1012.43 | GGB | 62.69 | GGB | 170370.8 | GGB | 138474.13 | GGB | 0 | 0 | 2849 | 3600 | 2833.3 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 190851.13 | GGB | 190853.37 | 2833.3 | 2729.2318 |  |  |  | 1 | 1 |  |  |  |  | 138474.13 | 2729.2318 | 138474.13 | 2729.2318 | 9.4082 | [5 empty] | 108.983 | 2729.2318 |  | 104.98
03.04.2008 20:00 | 3600 | 2 | 766.26 | GGB | 766.667 | 776.813 | 772.161 | 265.41 | GGB | 10881.7 | GGB | 9.88 | GGB | 1012.8 | GGB | 62.59 | GGB | 170034.09 | GGB | 138293.77 | GGB | 0 | 0 | 2795 | 3600 | 2779.94 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 190891.21 | GGB | 190893.46 | 2779.94 | 2732.7912 |  |  |  | 1 | 1 |  |  |  |  | 138293.77 | 2732.7912 | 138293.77 | 2732.7912 | 9.427 | [5 empty] | 106.7912 | 2732.7912 |  | 104.98
03.04.2008 21:00 | 3600 | 2 | 764.35 | GGB | 767.766 | 776.461 | 771.795 | 264.53 | GGB | 10871 | GGB | 9.84 | GGB | 1012.98 | GGB | 62.94 | GGB | 168665.27 | GGB | 137061.88 | GGB | 0 | 0 | 2895 | 3600 | 2879.34 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 190931.32 | GGB | 190933.57 | 2879.34 | 2757.3531 |  |  |  | 1 | 1 |  |  |  |  | 137061.88 | 2757.3531 | 137061.88 | 2757.3531 | 9.4223 | [5 empty] | 109.6244 | 2757.3531 |  | 104.98
03.04.2008 22:00 | 3600 | 2 | 764.81 | GGB | 764.102 | 774.211 | 768.498 | 265.46 | GGB | 10882.1 | GGB | 9.85 | GGB | 1014.35 | GGB | 62.3 | GGB | 170369.7 | GGB | 138898.17 | GGB | 0 | 0 | 2870 | 3600 | 2854.03 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 190971.51 | GGB | 190973.76 | 2854.03 | 2720.8998 |  |  |  | 1 | 1 |  |  |  |  | 138898.17 | 2720.8998 | 138898.17 | 2720.8998 | 9.4035 | [5 empty] | 110.1165 | 2720.8998 |  | 104.98
03.04.2008 23:00 | 3600 | 2 | 764.67 | GGB | 765.201 | 775.242 | 770.696 | 265.58 | GGB | 10911.1 | GGB | 9.85 | GGB | 1013.76 | GGB | 62.53 | GGB | 169726 | GGB | 138198.33 | GGB | 0 | 0 | 2899 | 3600 | 2883.91 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 191011.55 | GGB | 191013.8 | 2883.91 | 2734.6785 |  |  |  | 1 | 1 |  |  |  |  | 138198.33 | 2734.6785 | 138198.33 | 2734.6785 | 9.4388 | [5 empty] | 110.7088 | 2734.6785 |  | 104.98
03.04.2008 24:00 | 3600 | 2 | 764.7 | GGB | 765.201 | 776.086 | 770.696 | 266.86 | GGB | 10934.1 | GGB | 9.85 | GGB | 1013.61 | GGB | 62.04 | GGB | 170788.92 | GGB | 139245.05 | GGB | 0 | 0 | 2901 | 3600 | 2885.63 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 191051.67 | GGB | 191053.91 | 2885.63 | 2714.1216 |  |  |  | 1 | 1 |  |  |  |  | 139245.05 | 2714.1216 | 139245.05 | 2714.1216 | 9.4223 | [5 empty] | 111.6138 | 2714.1216 |  | 104.98
04.04.2008 01:00 | 3600 | 2 | 763.09 | GGB | 762.637 | 773.508 | 768.132 | 268.64 | GGB | 10904.8 | GGB | 9.82 | GGB | 1013.88 | GGB | 61.16 | GGB | 173626.7 | GGB | 141972.25 | GGB | 0 | 0 | 2971 | 3600 | 2955.51 | GGB | 100 | GGB | 40.32 | GGB | 40.32 | GGB | 191091.98 | GGB | 191094.23 | 2955.51 | 2661.985 |  |  |  | 0 | 1 | [14 empty] | 116.5557 | 2661.985 |  | 104.98
04.04.2008 02:00 | 3600 | 2 | 764.81 | GGB | 762.637 | 772.078 | 767.033 | 267.78 | GGB | 11007.8 | GGB | 9.87 | GGB | 1013.99 | GGB | 61.78 | GGB | 172161.05 | GGB | 140529.73 | GGB | 0 | 0 | 2928 | 3600 | 2912.72 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 191132.16 | GGB | 191134.41 | 2912.72 | 2689.3099 |  |  |  | 0 | 1 | [14 empty] | 113.701 | 2689.3099 |  | 104.98
04.04.2008 03:00 | 3600 | 2 | 763.68 | GGB | 759.341 | 767.789 | 763.37 | 268.63 | GGB | 11020.3 | GGB | 9.84 | GGB | 1014.02 | GGB | 61.63 | GGB | 173009.41 | GGB | 141289.68 | GGB | 0 | 0 | 2993 | 3600 | 2977.15 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 191172.46 | GGB | 191174.71 | 2977.15 | 2674.845 |  |  |  | 0 | 1 | [14 empty] | 116.8446 | 2674.845 |  | 104.98
04.04.2008 04:00 | 3600 | 2 | 763.65 | GGB | 767.766 | 776.227 | 771.795 | 270.21 | GGB | 11079.6 | GGB | 9.86 | GGB | 1014.13 | GGB | 61.21 | GGB | 174877.78 | GGB | 143010.83 | GGB | 0 | 0 | 3036 | 3600 | 3020.29 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 191212.96 | GGB | 191215.2 | 3020.29 | 2642.653 |  |  |  | 1 | 1 |  |  |  |  | 143010.83 | 2642.653 | 143010.83 | 2642.653 | 9.3339 | [5 empty] | 119.9817 | 2642.653 |  | 104.98
04.04.2008 05:00 | 3600 | 2 | 763.2 | GGB | 764.102 | 773.367 | 769.597 | 271.58 | GGB | 11116.7 | GGB | 9.84 | GGB | 1014.35 | GGB | 61.11 | GGB | 176070.55 | GGB | 144056.61 | GGB | 0 | 0 | 3061 | 3600 | 3045.02 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 191253.5 | GGB | 191255.74 | 3045.02 | 2623.4686 |  |  |  | 1 | 1 |  |  |  |  | 144056.61 | 2623.4686 | 144056.61 | 2623.4686 | 9.3223 | [5 empty] | 121.8487 | 2623.4686 |  | 104.98
04.04.2008 06:00 | 3600 | 2 | 763.06 | GGB | 765.201 | 774.398 | 769.963 | 272.18 | GGB | 11159.1 | GGB | 9.85 | GGB | 1014.68 | GGB | 60.91 | GGB | 176932.11 | GGB | 144896.97 | GGB | 0 | 0 | 3094 | 3600 | 3077.98 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 191294.23 | GGB | 191296.48 | 3077.98 | 2608.2533 |  |  |  | 1 | 1 |  |  |  |  | 144896.97 | 2608.2533 | 144896.97 | 2608.2533 | 9.2766 | [5 empty] | 123.8861 | 2608.2533 |  | 104.98
04.04.2008 07:00 | 3600 | 2 | 763.39 | GGB | 767.766 | 776.977 | 772.527 | 273.36 | GGB | 11147.2 | GGB | 9.85 | GGB | 1015.08 | GGB | 60.27 | GGB | 179158.09 | GGB | 147058.84 | GGB | 0 | 0 | 3071 | 3600 | 3055.21 | GGB | 100 | GGB | 41.11 | GGB | 41.11 | GGB | 191335.35 | GGB | 191337.59 | 3055.21 | 2569.9101 |  |  |  | 1 | 1 |  |  |  |  | 147058.84 | 2569.9101 | 147058.84 | 2569.9101 | 9.1931 | [5 empty] | 124.8043 | 2569.9101 |  | 104.98
04.04.2008 08:00 | 3600 | 2 | 764.07 | GGB | 765.201 | 775.031 | 769.963 | 271.75 | GGB | 11188.7 | GGB | 9.87 | GGB | 1015.32 | GGB | 60.66 | GGB | 176921.11 | GGB | 145087.47 | GGB | 0 | 0 | 3050 | 3600 | 3034.49 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 191376.26 | GGB | 191378.5 | 3034.49 | 2604.8287 |  |  |  | 1 | 1 |  |  |  |  | 145087.47 | 2604.8287 | 145087.47 | 2604.8287 | 9.238 | [5 empty] | 122.2962 | 2604.8287 |  | 104.98
04.04.2008 09:00 | 3600 | 2 | 763.67 | GGB | 766.667 | 776.063 | 770.696 | 270.98 | GGB | 11162.2 | GGB | 9.86 | GGB | 1015.73 | GGB | 60.84 | GGB | 176147.57 | GGB | 144434.97 | GGB | 0 | 0 | 3069 | 3208 | 3053.03 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 191417.3 | GGB | 191419.55 | 3053.03 | 2616.5962 |  |  |  | 1 | 1 |  |  |  |  | 144434.97 | 2616.5962 | 144434.97 | 2616.5962 | 9.2065 | [5 empty] | 122.4901 | 2616.5962 |  | 104.98
04.04.2008 10:00 | 3600 | 2 | 763.71 | GGB | 766.3 | 775.219 | 770.696 | 270.93 | GGB | 11157.8 | GGB | 9.86 | GGB | 1016.1 | GGB | 60.96 | GGB | 175876.89 | GGB | 144214.34 | GGB | 0 | 0 | 3065 | 3600 | 3049.59 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 191458.3 | GGB | 191460.55 | 3049.59 | 2620.5993 |  |  |  | 1 | 1 |  |  |  |  | 144214.34 | 2620.5993 | 144214.34 | 2620.5993 | 9.2178 | [5 empty] | 122.1652 | 2620.5993 |  | 104.98
04.04.2008 11:00 | 3600 | 2 | 764.21 | GGB | 765.201 | 774.023 | 770.696 | 269.68 | GGB | 11123 | GGB | 9.86 | GGB | 1016.36 | GGB | 61.45 | GGB | 174547.68 | GGB | 142950.56 | GGB | 0 | 0 | 3016 | 3600 | 2999.94 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 191499.19 | GGB | 191501.44 | 2999.94 | 2643.7672 |  |  |  | 1 | 1 |  |  |  |  | 142950.56 | 2643.7672 | 142950.56 | 2643.7672 | 9.2426 | [5 empty] | 119.1231 | 2643.7672 |  | 104.98
04.04.2008 12:00 | 3600 | 2 | 764.87 | GGB | 765.201 | 774.773 | 769.597 | 267.95 | GGB | 11068.1 | GGB | 9.87 | GGB | 1015.56 | GGB | 61.69 | GGB | 173042.42 | GGB | 141503.77 | GGB | 0 | 0 | 2935 | 3600 | 2919.08 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 191539.98 | GGB | 191542.23 | 2919.08 | 2670.7981 |  |  |  | 1 | 1 |  |  |  |  | 141503.77 | 2670.7981 | 141503.77 | 2670.7981 | 9.2652 | [5 empty] | 114.7391 | 2670.7981 |  | 104.98
04.04.2008 13:00 | 3600 | 2 | 765.44 | GGB | 765.201 | 774.844 | 770.696 | 265.51 | GGB | 10987.2 | GGB | 9.88 | GGB | 1014.7 | GGB | 62.29 | GGB | 170812.03 | GGB | 139313.02 | GGB | 0 | 0 | 2875 | 3600 | 2859.59 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 191580.64 | GGB | 191582.89 | 2859.59 | 2712.7974 |  |  |  | 1 | 1 |  |  |  |  | 139313.02 | 2712.7974 | 139313.02 | 2712.7974 | 9.2948 | [5 empty] | 110.6606 | 2712.7974 |  | 104.98
04.04.2008 14:00 | 3600 | 2 | 765.08 | GGB | 767.766 | 777.07 | 772.161 | 265.93 | GGB | 10876.9 | GGB | 9.86 | GGB | 1014.3 | GGB | 62.19 | GGB | 171600.97 | GGB | 139940.18 | GGB | 0 | 0 | 2851 | 3600 | 2835.78 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 191621.3 | GGB | 191623.55 | 2835.78 | 2700.6397 |  |  |  | 1 | 1 |  |  |  |  | 139940.18 | 2700.6397 | 139940.18 | 2700.6397 | 9.2948 | [5 empty] | 110.2332 | 2700.6397 |  | 104.98
04.04.2008 15:00 | 3600 | 2 | 766.19 | GGB | 767.766 | 777.258 | 773.26 | 264.29 | GGB | 10858.2 | GGB | 9.87 | GGB | 1012.96 | GGB | 62.63 | GGB | 169602.76 | GGB | 137949.29 | GGB | 0 | 0 | 2786 | 3600 | 2770.41 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 191661.61 | GGB | 191663.86 | 2770.41 | 2739.6154 |  |  |  | 1 | 1 |  |  |  |  | 137949.29 | 2739.6154 | 137949.29 | 2739.6154 | 9.3755 | [5 empty] | 106.16 | 2739.6154 |  | 104.98
04.04.2008 16:00 | 3600 | 2 | 765.35 | GGB | 764.102 | 774.117 | 769.597 | 263 | GGB | 10824.1 | GGB | 9.85 | GGB | 1012.33 | GGB | 63.47 | GGB | 168039.18 | GGB | 136250.91 | GGB | 0 | 0 | 2823 | 3600 | 2807.91 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 191701.74 | GGB | 191704 | 2807.91 | 2773.765 |  |  |  | 1 | 1 |  |  |  |  | 136250.91 | 2773.765 | 136250.91 | 2773.765 | 9.4152 | [5 empty] | 106.2723 | 2773.765 |  | 104.98
04.04.2008 17:00 | 3600 | 2 | 765.94 | GGB | 766.667 | 776.508 | 772.161 | 262.96 | GGB | 10807.5 | GGB | 9.87 | GGB | 1011.47 | GGB | 63.25 | GGB | 168229.54 | GGB | 136378.88 | GGB | 0 | 0 | 2781 | 3600 | 2765.14 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 191741.87 | GGB | 191744.13 | 2765.14 | 2765.14 |  |  |  | 1 | 1 |  |  |  |  | 136378.88 | 2765.14 | 136378.88 | 2765.14 | 9.3971 | [5 empty] | 104.7519 |  |  | #VALUE!
04.04.2008 18:00 | 3600 | 2 | 764.4 | GGB | 769.963 | 779.648 | 775.091 | 262.8 | GGB | 10805.5 | GGB | 9.84 | GGB | 1011.28 | GGB | 63.35 | GGB | 167796.01 | GGB | 135961.82 | GGB | 0 | 0 | 2889 | 3600 | 2873.08 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 191781.81 | GGB | 191784.07 | 2873.08 | 2779.6627 |  |  |  | 0 | 1 | [14 empty] | 108.5081 | 2779.6627 |  | 104.98
04.04.2008 19:00 | 3600 | 2 | 765.19 | GGB | 761.538 | 770.883 | 766.3 | 262.79 | GGB | 10821.9 | GGB | 9.85 | GGB | 1011.07 | GGB | 63.47 | GGB | 167541.83 | GGB | 135678.64 | GGB | 0 | 0 | 2846 | 3600 | 2830.45 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 191821.78 | GGB | 191824.03 | 2830.45 | 2785.4642 |  |  |  | 0 | 1 | [14 empty] | 106.6754 | 2785.4642 |  | 104.98
04.04.2008 20:00 | 3600 | 2 | 765.95 | GGB | 766.667 | 777.469 | 772.527 | 263.57 | GGB | 10866.4 | GGB | 9.87 | GGB | 1011.65 | GGB | 63.11 | GGB | 168205.33 | GGB | 136441.77 | GGB | 0 | 0 | 2839 | 3600 | 2823.32 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 191861.76 | GGB | 191864.01 | 2823.32 | 2769.8849 |  |  |  | 1 | 1 |  |  |  |  | 136441.77 | 2769.8849 | 136441.77 | 2769.8849 | 9.4529 | [5 empty] | 107.0052 | 2769.8849 |  | 104.98
04.04.2008 21:00 | 3600 | 2 | 762.73 | GGB | 761.538 | 770.531 | 765.201 | 264.71 | GGB | 10826.3 | GGB | 9.81 | GGB | 1012.03 | GGB | 62.8 | GGB | 169479.52 | GGB | 137653.94 | GGB | 0 | 0 | 2984 | 3600 | 2968.24 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 191901.78 | GGB | 191904.03 | 2968.24 | 2745.4935 |  |  |  | 0 | 1 | [14 empty] | 113.4972 | 2745.4935 |  | 104.98
04.04.2008 22:00 | 3600 | 2 | 764.16 | GGB | 764.102 | 773.414 | 767.766 | 265.83 | GGB | 10925 | GGB | 9.85 | GGB | 1012.32 | GGB | 62.46 | GGB | 170727.31 | GGB | 138845.02 | GGB | 0 | 0 | 2949 | 3600 | 2933.76 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 191941.91 | GGB | 191944.16 | 2933.76 | 2721.9413 |  |  |  | 1 | 1 |  |  |  |  | 138845.02 | 2721.9413 | 138845.02 | 2721.9413 | 9.4176 | [5 empty] | 113.1494 | 2721.9413 |  | 104.98
04.04.2008 23:00 | 3600 | 2 | 763.6 | GGB | 767.766 | 776.438 | 771.429 | 267.74 | GGB | 11002.9 | GGB | 9.84 | GGB | 1012.58 | GGB | 61.56 | GGB | 172920.28 | GGB | 141043.01 | GGB | 0 | 0 | 3001 | 3600 | 2985.16 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 191982.3 | GGB | 191984.56 | 2985.16 | 2679.5231 |  |  |  | 1 | 1 |  |  |  |  | 141043.01 | 2679.5231 | 141043.01 | 2679.5231 | 9.3547 | [5 empty] | 116.9544 | 2679.5231 |  | 104.98
04.04.2008 24:00 | 3600 | 2 | 762.73 | GGB | 764.102 | 772.992 | 768.864 | 269.83 | GGB | 11056.9 | GGB | 9.84 | GGB | 1012.94 | GGB | 61.19 | GGB | 174710.53 | GGB | 142711.66 | GGB | 0 | 0 | 3060 | 3600 | 3044.03 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 192022.81 | GGB | 192025.06 | 3044.03 | 2648.1929 |  |  |  | 1 | 1 |  |  |  |  | 142711.66 | 2648.1929 | 142711.66 | 2648.1929 | 9.3316 | [5 empty] | 120.6718 | 2648.1929 |  | 104.98
05.04.2008 01:00 | 3600 | 2 | 762.5 | GGB | 764.102 | 772.008 | 768.132 | 271.22 | GGB | 11118.9 | GGB | 9.84 | GGB | 1013.23 | GGB | 60.82 | GGB | 176219.09 | GGB | 144145.11 | GGB | 0 | 0 | 3090 | 3600 | 3073.97 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 192063.53 | GGB | 192065.78 | 3073.97 | 2621.8579 |  |  |  | 1 | 1 |  |  |  |  | 144145.11 | 2621.8579 | 144145.11 | 2621.8579 | 9.2811 | [5 empty] | 123.0827 | 2621.8579 |  | 104.98
05.04.2008 02:00 | 3600 | 2 | 762.26 | GGB | 762.637 | 771.633 | 765.934 | 272.75 | GGB | 11194.5 | GGB | 9.84 | GGB | 1013.34 | GGB | 60.12 | GGB | 178377.95 | GGB | 146233.73 | GGB | 0 | 0 | 3135 | 3600 | 3119.34 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 192104.5 | GGB | 192106.75 | 3119.34 | 2584.4106 |  |  |  | 0 | 1 | [14 empty] | 126.7091 | 2584.4106 |  | 104.98
05.04.2008 03:00 | 3600 | 2 | 761.9 | GGB | 762.637 | 771.234 | 765.934 | 273.98 | GGB | 11255.7 | GGB | 9.85 | GGB | 1014.06 | GGB | 59.56 | GGB | 179926.13 | GGB | 147858.43 | GGB | 0 | 0 | 3180 | 3600 | 3164.43 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 192145.66 | GGB | 192147.9 | 3164.43 | 2556.0125 |  |  |  | 0 | 1 | [14 empty] | 129.9688 | 2556.0125 |  | 104.98
05.04.2008 04:00 | 3600 | 2 | 762.24 | GGB | 763.004 | 772.523 | 767.033 | 273.63 | GGB | 11287.2 | GGB | 9.86 | GGB | 1013.8 | GGB | 59.25 | GGB | 180099.98 | GGB | 148102.5 | GGB | 0 | 0 | 3164 | 3600 | 3148.61 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 192186.86 | GGB | 192189.1 | 3148.61 | 2551.8003 |  |  |  | 0 | 1 | [14 empty] | 129.5325 | 2551.8003 |  | 104.98
05.04.2008 05:00 | 3600 | 2 | 761.2 | GGB | 762.637 | 772.359 | 767.033 | 273.86 | GGB | 11276.8 | GGB | 9.85 | GGB | 1013.81 | GGB | 59.05 | GGB | 180334.35 | GGB | 148382.88 | GGB | 0 | 0 | 3216 | 3600 | 3200.09 | GGB | 100 | GGB | 41.3 | GGB | 41.3 | GGB | 192228.16 | GGB | 192230.4 | 3200.09 | 2546.9785 |  |  |  | 0 | 1 | [14 empty] | 131.8996 | 2546.9785 |  | 104.98
05.04.2008 06:00 | 3600 | 2 | 761.92 | GGB | 760.44 | 769.242 | 765.201 | 273.98 | GGB | 11304.9 | GGB | 9.86 | GGB | 1013.77 | GGB | 58.89 | GGB | 180652.35 | GGB | 148711.4 | GGB | 0 | 0 | 3198 | 3600 | 3181.89 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 192269.52 | GGB | 192271.76 | 3181.89 | 2541.3519 |  |  |  | 0 | 1 | [14 empty] | 131.4398 | 2541.3519 |  | 104.98
05.04.2008 07:00 | 3600 | 2 | 761.32 | GGB | 764.102 | 773.508 | 768.864 | 274.31 | GGB | 11306.2 | GGB | 9.85 | GGB | 1013.65 | GGB | 58.69 | GGB | 180936.24 | GGB | 149018.19 | GGB | 0 | 0 | 3232 | 3600 | 3216.57 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 192310.92 | GGB | 192313.16 | 3216.57 | 2536.1199 |  |  |  | 1 | 1 |  |  |  |  | 149018.19 | 2536.1199 | 149018.19 | 2536.1199 | 9.1287 | [5 empty] | 133.1465 | 2536.1199 |  | 104.98
05.04.2008 08:00 | 3600 | 2 | 761.81 | GGB | 764.102 | 772.359 | 767.766 | 273.96 | GGB | 11304.6 | GGB | 9.86 | GGB | 1013.98 | GGB | 58.82 | GGB | 180566.53 | GGB | 148704.66 | GGB | 0 | 0 | 3202 | 3600 | 3185.97 | GGB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 192352.29 | GGB | 192354.54 | 3185.97 | 2541.4671 |  |  |  | 1 | 1 |  |  |  |  | 148704.66 | 2541.4671 | 148704.66 | 2541.4671 | 9.1331 | [5 empty] | 131.6024 | 2541.4671 |  | 104.98
05.04.2008 09:00 | 3600 | 2 | 762.09 | GGB | 760.44 | 770.109 | 765.201 | 273.51 | GGB | 11289.3 | GGB | 9.86 | GGB | 1013.65 | GGB | 58.95 | GGB | 179940.43 | GGB | 148080.77 | GGB | 0 | 0 | 3189 | 3600 | 3172.92 | GGB | 100 | GGB | 41.31 | GGB | 41.31 | GGB | 192393.61 | GGB | 192395.85 | 3172.92 | 2552.1747 |  |  |  | 0 | 1 | [14 empty] | 130.5135 | 2552.1747 |  | 104.98
05.04.2008 10:00 | 3600 | 2 | 762.46 | GGB | 764.102 | 773.766 | 768.864 | 273.53 | GGB | 11296.9 | GGB | 9.86 | GGB | 1012.92 | GGB | 58.92 | GGB | 180287.04 | GGB | 148271.85 | GGB | 0 | 0 | 3183 | 3600 | 3166.97 | GGB | 100 | GGB | 41.37 | GGB | 41.37 | GGB | 192434.97 | GGB | 192437.22 | 3166.97 | 2548.8857 |  |  |  | 1 | 1 |  |  |  |  | 148271.85 | 2548.8857 | 148271.85 | 2548.8857 | 9.1353 | [5 empty] | 130.4368 | 2548.8857 |  | 104.98
05.04.2008 11:00 | 3600 | 2 | 762.48 | GGB | 764.102 | 772.969 | 767.766 | 272.91 | GGB | 11266.5 | GGB | 9.86 | GGB | 1012.68 | GGB | 59.16 | GGB | 179129.48 | GGB | 147177.97 | GGB | 0 | 0 | 3159 | 3600 | 3143.43 | GGB | 100 | GGB | 41.27 | GGB | 41.27 | GGB | 192476.24 | GGB | 192478.49 | 3143.43 | 2567.83 |  |  |  | 1 | 1 |  |  |  |  | 147177.97 | 2567.83 | 147177.97 | 2567.83 | 9.1575 | [5 empty] | 128.5121 | 2567.83 |  | 104.98
05.04.2008 12:00 | 3600 | 2 | 763.19 | GGB | 766.667 | 776.25 | 771.429 | 272.07 | GGB | 11246.7 | GGB | 9.87 | GGB | 1012.24 | GGB | 59.54 | GGB | 178362.55 | GGB | 146318.8 | GGB | 0 | 0 | 3128 | 3600 | 3111.75 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 192517.44 | GGB | 192519.68 | 3111.75 | 2582.908 |  |  |  | 1 | 1 |  |  |  |  | 146318.8 | 2582.908 | 146318.8 | 2582.908 | 9.1752 | [5 empty] | 126.4743 | 2582.908 |  | 104.98
05.04.2008 13:00 | 3600 | 2 | 762.26 | GGB | 764.102 | 772.641 | 767.766 | 271.5 | GGB | 11189.7 | GGB | 9.85 | GGB | 1011.72 | GGB | 59.79 | GGB | 177781.57 | GGB | 145658 | GGB | 0 | 0 | 3140 | 3600 | 3124.34 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 192558.64 | GGB | 192560.88 | 3124.34 | 2594.6258 |  |  |  | 1 | 1 |  |  |  |  | 145658 | 2594.6258 | 145658 | 2594.6258 | 9.173 | [5 empty] | 126.4125 | 2594.6258 |  | 104.98
05.04.2008 14:00 | 3600 | 2 | 763.38 | GGB | 765.201 | 775.102 | 769.963 | 271.14 | GGB | 11196.2 | GGB | 9.87 | GGB | 1010.97 | GGB | 60.05 | GGB | 177305.12 | GGB | 145046.7 | GGB | 0 | 0 | 3080 | 3600 | 3064.4 | GGB | 100 | GGB | 41.51 | GGB | 41.51 | GGB | 192600.15 | GGB | 192602.39 | 3064.4 | 2605.5608 |  |  |  | 1 | 1 |  |  |  |  | 145046.7 | 2605.5608 | 145046.7 | 2605.5608 | 9.1045 | [5 empty] | 123.467 | 2605.5608 |  | 104.98
05.04.2008 15:00 | 3600 | 2 | 762.86 | GGB | 763.004 | 771.773 | 766.667 | 270.45 | GGB | 11154 | GGB | 9.85 | GGB | 1010.41 | GGB | 60.17 | GGB | 176743.95 | GGB | 144454 | GGB | 0 | 0 | 3091 | 3600 | 3075.14 | GGB | 100 | GGB | 41.39 | GGB | 41.39 | GGB | 192641.54 | GGB | 192643.78 | 3075.14 | 2616.2515 |  |  |  | 0 | 1 | [14 empty] | 123.3934 | 2616.2515 |  | 104.98
05.04.2008 16:00 | 3600 | 2 | 763.61 | GGB | 766.667 | 776.602 | 771.429 | 269.87 | GGB | 11144.5 | GGB | 9.87 | GGB | 1009.82 | GGB | 60.43 | GGB | 176128.86 | GGB | 143754.04 | GGB | 0 | 0 | 3051 | 3600 | 3035.1 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 192682.44 | GGB | 192684.69 | 3035.1 | 2628.9905 |  |  |  | 1 | 1 |  |  |  |  | 143754.04 | 2628.9905 | 143754.04 | 2628.9905 | 9.238 | [5 empty] | 121.1966 | 2628.9905 |  | 104.98
05.04.2008 17:00 | 3600 | 2 | 763.33 | GGB | 767.766 | 776.672 | 771.429 | 269.23 | GGB | 11104.3 | GGB | 9.86 | GGB | 1009.16 | GGB | 60.65 | GGB | 175469.76 | GGB | 143029.31 | GGB | 0 | 0 | 3042 | 3600 | 3026.71 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 192723.24 | GGB | 192725.48 | 3026.71 | 2642.3116 |  |  |  | 1 | 1 |  |  |  |  | 143029.31 | 2642.3116 | 143029.31 | 2642.3116 | 9.2652 | [5 empty] | 120.2523 | 2642.3116 |  | 104.98
05.04.2008 18:00 | 3600 | 2 | 763.83 | GGB | 766.3 | 776.695 | 771.429 | 268.74 | GGB | 11082.2 | GGB | 9.86 | GGB | 1008.42 | GGB | 60.91 | GGB | 174820.56 | GGB | 142286.08 | GGB | 0 | 0 | 3014 | 3600 | 2998.53 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 192763.93 | GGB | 192766.18 | 2998.53 | 2656.1137 |  |  |  | 1 | 1 |  |  |  |  | 142286.08 | 2656.1137 | 142286.08 | 2656.1137 | 9.2857 | [5 empty] | 118.5136 | 2656.1137 |  | 104.98
05.04.2008 19:00 | 3600 | 2 | 763.03 | GGB | 764.102 | 773.367 | 767.766 | 269.21 | GGB | 11072.3 | GGB | 9.85 | GGB | 1007.81 | GGB | 60.83 | GGB | 175283.8 | GGB | 142608.88 | GGB | 0 | 0 | 3038 | 3600 | 3022.18 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 192804.56 | GGB | 192806.8 | 3022.18 | 2650.1015 |  |  |  | 1 | 1 |  |  |  |  | 142608.88 | 2650.1015 | 142608.88 | 2650.1015 | 9.304 | [5 empty] | 119.7194 | 2650.1015 |  | 104.98
05.04.2008 20:00 | 3600 | 2 | 763.21 | GGB | 764.102 | 773.414 | 768.498 | 269.47 | GGB | 11088.1 | GGB | 9.85 | GGB | 1007.44 | GGB | 60.71 | GGB | 175570.99 | GGB | 142840.7 | GGB | 0 | 0 | 3044 | 3600 | 3027.82 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 192845.14 | GGB | 192847.39 | 3027.82 | 2645.8005 |  |  |  | 1 | 1 |  |  |  |  | 142840.7 | 2645.8005 | 142840.7 | 2645.8005 | 9.3109 | [5 empty] | 120.1378 | 2645.8005 |  | 104.98
05.04.2008 21:00 | 3600 | 2 | 762.37 | GGB | 761.538 | 771.305 | 765.934 | 270.2 | GGB | 11100.9 | GGB | 9.84 | GGB | 1007.43 | GGB | 60.52 | GGB | 176389.64 | GGB | 143589.33 | GGB | 0 | 0 | 3082 | 3600 | 3065.93 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 192885.91 | GGB | 192888.16 | 3065.93 | 2632.0062 |  |  |  | 0 | 1 | [14 empty] | 122.2875 | 2632.0062 |  | 104.98
05.04.2008 22:00 | 3600 | 2 | 763.34 | GGB | 765.201 | 774.773 | 769.597 | 270.67 | GGB | 11169.9 | GGB | 9.87 | GGB | 1007.87 | GGB | 60.24 | GGB | 176939.81 | GGB | 144222.09 | GGB | 0 | 0 | 3067 | 3600 | 3050.93 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 192926.81 | GGB | 192929.06 | 3050.93 | 2620.4585 |  |  |  | 1 | 1 |  |  |  |  | 144222.09 | 2620.4585 | 144222.09 | 2620.4585 | 9.2403 | [5 empty] | 122.2254 | 2620.4585 |  | 104.98
05.04.2008 23:00 | 3600 | 2 | 761.88 | GGB | 763.004 | 772.031 | 767.033 | 271.23 | GGB | 11136.8 | GGB | 9.83 | GGB | 1007.01 | GGB | 59.88 | GGB | 177365.64 | GGB | 144601.25 | GGB | 0 | 0 | 3126 | 3600 | 3110.4 | GGB | 100 | GGB | 41.03 | GGB | 41.03 | GGB | 192967.84 | GGB | 192970.09 | 3110.4 | 2613.5874 |  |  |  | 0 | 1 | [14 empty] | 124.9355 | 2613.5874 |  | 104.98
05.04.2008 24:00 | 3600 | 2 | 762.93 | GGB | 765.201 | 773.648 | 768.498 | 272.78 | GGB | 11147.4 | GGB | 9.85 | GGB | 1006.68 | GGB | 59.65 | GGB | 179145.99 | GGB | 146104.8 | GGB | 0 | 0 | 3081 | 3600 | 3065.54 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 193009.13 | GGB | 193011.38 | 3065.54 | 2586.6912 |  |  |  | 1 | 1 |  |  |  |  | 146104.8 | 2586.6912 | 146104.8 | 2586.6912 | 9.153 | [5 empty] | 124.4139 | 2586.6912 |  | 104.98
06.04.2008 01:00 | 3600 | 2 | 763.04 | GGB | 766.3 | 775.008 | 770.696 | 271.71 | GGB | 11191.4 | GGB | 9.87 | GGB | 1006.5 | GGB | 59.86 | GGB | 177777.17 | GGB | 144872.01 | GGB | 0 | 0 | 3083 | 3600 | 3067.28 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 193050.22 | GGB | 193052.47 | 3067.28 | 2608.7027 |  |  |  | 1 | 1 |  |  |  |  | 144872.01 | 2608.7027 | 144872.01 | 2608.7027 | 9.1976 | [5 empty] | 123.4342 | 2608.7027 |  | 104.98
06.04.2008 02:00 | 3600 | 2 | 762.45 | GGB | 765.201 | 773.813 | 768.864 | 271.55 | GGB | 11171.3 | GGB | 9.85 | GGB | 1005.73 | GGB | 60.05 | GGB | 177750.76 | GGB | 144656.93 | GGB | 0 | 0 | 3112 | 3600 | 3096.04 | GGB | 100 | GGB | 41.18 | GGB | 41.18 | GGB | 193091.39 | GGB | 193093.65 | 3096.04 | 2612.5814 |  |  |  | 1 | 1 |  |  |  |  | 144656.93 | 2612.5814 | 144656.93 | 2612.5814 | 9.1775 | [5 empty] | 124.4066 | 2612.5814 |  | 104.98
06.04.2008 03:00 | 3600 | 2 | 763.4 | GGB | 764.102 | 773.555 | 768.864 | 270.59 | GGB | 11167.8 | GGB | 9.87 | GGB | 1004.75 | GGB | 59.99 | GGB | 176980.52 | GGB | 143912.76 | GGB | 0 | 0 | 3057 | 3600 | 3041.71 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 193132.65 | GGB | 193134.91 | 3041.71 | 2626.091 |  |  |  | 1 | 1 |  |  |  |  | 143912.76 | 2626.091 | 143912.76 | 2626.091 | 9.1597 | [5 empty] | 121.5947 | 2626.091 |  | 104.98
06.04.2008 04:00 | 3600 | 2 | 761.29 | GGB | 760.44 | 769.477 | 765.201 | 271.54 | GGB | 11119.6 | GGB | 9.83 | GGB | 1003.89 | GGB | 59.79 | GGB | 178327.34 | GGB | 144974.22 | GGB | 0 | 0 | 3150 | 3600 | 3134.05 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 193173.71 | GGB | 193175.96 | 3134.05 | 2606.8635 |  |  |  | 0 | 1 | [14 empty] | 126.2101 | 2606.8635 |  | 104.98
06.04.2008 05:00 | 3600 | 2 | 763.28 | GGB | 764.102 | 773.461 | 768.864 | 271.27 | GGB | 11168.6 | GGB | 9.87 | GGB | 1002.97 | GGB | 59.79 | GGB | 177641.83 | GGB | 144281.79 | GGB | 0 | 0 | 3072 | 3600 | 3056.19 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 193214.3 | GGB | 193216.56 | 3056.19 | 2619.3742 |  |  |  | 1 | 1 |  |  |  |  | 144281.79 | 2619.3742 | 144281.79 | 2619.3742 | 9.3086 | [5 empty] | 122.4868 | 2619.3742 |  | 104.98
06.04.2008 06:00 | 3600 | 2 | 762.17 | GGB | 765.201 | 774.914 | 769.963 | 271.93 | GGB | 11131 | GGB | 9.85 | GGB | 1002.61 | GGB | 59.67 | GGB | 178835.69 | GGB | 145254.07 | GGB | 0 | 0 | 3107 | 3600 | 3091.25 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 193255.08 | GGB | 193257.33 | 3091.25 | 2601.841 |  |  |  | 1 | 1 |  |  |  |  | 145254.07 | 2601.841 | 145254.07 | 2601.841 | 9.2698 | [5 empty] | 124.7268 | 2601.841 |  | 104.98
06.04.2008 07:00 | 3600 | 2 | 763 | GGB | 764.102 | 773.836 | 768.864 | 272.36 | GGB | 11141.2 | GGB | 9.86 | GGB | 1001.87 | GGB | 58.97 | GGB | 179578.42 | GGB | 146054.36 | GGB | 0 | 0 | 3058 | 3600 | 3042.08 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 193295.72 | GGB | 193297.97 | 3042.08 | 2587.5845 |  |  |  | 1 | 1 |  |  |  |  | 146054.36 | 2587.5845 | 146054.36 | 2587.5845 | 9.2994 | [5 empty] | 123.4192 | 2587.5845 |  | 104.98
06.04.2008 08:00 | 3600 | 2 | 762.77 | GGB | 764.102 | 773.813 | 769.963 | 270.39 | GGB | 11152.6 | GGB | 9.87 | GGB | 1001.68 | GGB | 59.86 | GGB | 176739.55 | GGB | 143337.18 | GGB | 0 | 0 | 3077 | 3600 | 3061.51 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 193336.3 | GGB | 193338.55 | 3061.51 | 2636.6362 |  |  |  | 1 | 1 |  |  |  |  | 143337.18 | 2636.6362 | 143337.18 | 2636.6362 | 9.3132 | [5 empty] | 121.8967 | 2636.6362 |  | 104.98
06.04.2008 09:00 | 3600 | 2 | 762.83 | GGB | 764.102 | 773.508 | 768.864 | 269.56 | GGB | 11134.8 | GGB | 9.87 | GGB | 1001.47 | GGB | 60.29 | GGB | 176118.96 | GGB | 142619.34 | GGB | 0 | 0 | 3064 | 3600 | 3048.54 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 193376.94 | GGB | 193379.19 | 3048.54 | 2649.9071 |  |  |  | 1 | 1 |  |  |  |  | 142619.34 | 2649.9071 | 142619.34 | 2649.9071 | 9.2994 | [5 empty] | 120.7724 | 2649.9071 |  | 104.98
06.04.2008 10:00 | 3600 | 2 | 762.72 | GGB | 764.102 | 773.719 | 767.766 | 269.21 | GGB | 11108.6 | GGB | 9.86 | GGB | 1000.25 | GGB | 60.43 | GGB | 175715.14 | GGB | 142059.91 | GGB | 0 | 0 | 3061 | 3600 | 3045.13 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 193418.01 | GGB | 193420.26 | 3045.13 | 2660.3424 |  |  |  | 1 | 1 |  |  |  |  | 142059.91 | 2660.3424 | 142059.91 | 2660.3424 | 9.202 | [5 empty] | 120.1641 | 2660.3424 |  | 104.98
06.04.2008 11:00 | 3600 | 2 | 764.18 | GGB | 764.102 | 774.469 | 769.963 | 266.63 | GGB | 11042.5 | GGB | 9.88 | GGB | 999.51 | GGB | 61.01 | GGB | 172952.19 | GGB | 139478.41 | GGB | 0 | 0 | 2982 | 3600 | 2966.64 | GGB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 193458.99 | GGB | 193461.24 | 2966.64 | 2709.5806 |  |  |  | 1 | 1 |  |  |  |  | 139478.41 | 2709.5806 | 139478.41 | 2709.5806 | 9.2223 | [5 empty] | 114.9395 | 2709.5806 |  | 104.98
06.04.2008 12:00 | 3600 | 2 | 765.4 | GGB | 765.201 | 775.641 | 770.696 | 262.5 | GGB | 10907 | GGB | 9.89 | GGB | 998.5 | GGB | 62.04 | GGB | 168754.4 | GGB | 135538.83 | GGB | 0 | 0 | 2863 | 3600 | 2846.97 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 193499.18 | GGB | 193501.43 | 2846.97 | 2788.3375 |  |  |  | 1 | 1 |  |  |  |  | 135538.83 | 2788.3375 | 135538.83 | 2788.3375 | 9.4035 | [5 empty] | 107.1875 | 2788.3375 |  | 104.98
06.04.2008 13:00 | 3600 | 2 | 765 | GGB | 765.201 | 775.758 | 770.696 | 260.17 | GGB | 10772 | GGB | 9.86 | GGB | 997.36 | GGB | 63.04 | GGB | 166138.9 | GGB | 132886.72 | GGB | 0 | 0 | 2830 | 3600 | 2814.48 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 193539.1 | GGB | 193541.35 | 2814.48 | 2814.48 |  |  |  | 1 | 1 |  |  |  |  | 132886.72 | 2814.48 | 132886.72 | 2814.48 | 9.3689 | [5 empty] | 103.8908 |  |  | #VALUE!
06.04.2008 14:00 | 3600 | 2 | 765.07 | GGB | 766.667 | 776.813 | 773.26 | 260.51 | GGB | 10713.6 | GGB | 9.86 | GGB | 996.74 | GGB | 62.75 | GGB | 166899.23 | GGB | 133529.96 | GGB | 0 | 0 | 2802 | 3600 | 2786.36 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 193578.88 | GGB | 193581.14 | 2786.36 | 2786.36 |  |  |  | 1 | 1 |  |  |  |  | 133529.96 | 2786.36 | 133529.96 | 2786.36 | 9.3507 | [5 empty] | 103.3507 |  |  | #VALUE!
06.04.2008 15:00 | 3600 | 2 | 764.85 | GGB | 765.201 | 775.875 | 769.597 | 259.3 | GGB | 10701.3 | GGB | 9.85 | GGB | 995.99 | GGB | 63.2 | GGB | 165238.82 | GGB | 131923.55 | GGB | 0 | 0 | 2806 | 3600 | 2790.1 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 193618.39 | GGB | 193620.65 | 2790.1 | 2790.1 |  |  |  | 1 | 1 |  |  |  |  | 131923.55 | 2790.1 | 131923.55 | 2790.1 | 9.3161 | [5 empty] | 102.2444 |  |  | #VALUE!
06.04.2008 16:00 | 3600 | 2 | 765.25 | GGB | 765.201 | 775.852 | 770.696 | 259.44 | GGB | 10710.4 | GGB | 9.86 | GGB | 995.95 | GGB | 63.28 | GGB | 165568.92 | GGB | 132151.78 | GGB | 0 | 0 | 2794 | 3600 | 2778.77 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 193657.78 | GGB | 193660.04 | 2778.77 | 2778.77 |  |  |  | 1 | 1 |  |  |  |  | 132151.78 | 2778.77 | 132151.78 | 2778.77 | 9.3227 | [5 empty] | 102.0054 |  |  | #VALUE!
06.04.2008 17:00 | 3600 | 2 | 763.91 | GGB | 764.102 | 774.375 | 768.132 | 260.71 | GGB | 10742.2 | GGB | 9.84 | GGB | 996.16 | GGB | 62.76 | GGB | 166964.15 | GGB | 133499.1 | GGB | 0 | 0 | 2875 | 3600 | 2859.66 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 193697.92 | GGB | 193700.18 | 2859.66 | 2830.9404 |  |  |  | 1 | 1 |  |  |  |  | 133499.1 | 2830.9404 | 133499.1 | 2830.9404 | 9.4152 | [5 empty] | 106.045 | 2830.9404 |  | 104.98
06.04.2008 18:00 | 3600 | 2 | 764.2 | GGB | 769.963 | 780.844 | 775.458 | 261.5 | GGB | 10787.8 | GGB | 9.86 | GGB | 996.52 | GGB | 62.63 | GGB | 167450.5 | GGB | 133987.21 | GGB | 0 | 0 | 2878 | 3600 | 2862.71 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 193737.71 | GGB | 193739.97 | 2862.71 | 2820.6274 |  |  |  | 0 | 1 | [14 empty] | 106.5463 | 2820.6274 |  | 104.98
06.04.2008 19:00 | 3600 | 2 | 763.14 | GGB | 756.776 | 765.797 | 760.44 | 263.36 | GGB | 10737.2 | GGB | 9.82 | GGB | 997.12 | GGB | 61.95 | GGB | 169973.57 | GGB | 136363.19 | GGB | 0 | 0 | 2903 | 3600 | 2886.99 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 193777.44 | GGB | 193779.7 | 2886.99 | 2771.4811 |  |  |  | 0 | 1 | [14 empty] | 109.3553 | 2771.4811 |  | 104.98
06.04.2008 20:00 | 3600 | 2 | 762.85 | GGB | 764.102 | 773.602 | 768.864 | 263.6 | GGB | 10826.2 | GGB | 9.84 | GGB | 997.45 | GGB | 61.16 | GGB | 170108.92 | GGB | 136842.22 | GGB | 0 | 0 | 2952 | 3600 | 2936.6 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 193817.12 | GGB | 193819.38 | 2936.6 | 2761.7792 |  |  |  | 1 | 1 |  |  |  |  | 136842.22 | 2761.7792 | 136842.22 | 2761.7792 | 9.5244 | [5 empty] | 111.6252 | 2761.7792 |  | 104.98
06.04.2008 21:00 | 3600 | 2 | 762.21 | GGB | 764.102 | 773.203 | 767.766 | 264.35 | GGB | 10873.2 | GGB | 9.83 | GGB | 998.35 | GGB | 61.69 | GGB | 170290.47 | GGB | 136892.94 | GGB | 0 | 0 | 3002 | 3600 | 2986.06 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 193856.62 | GGB | 193858.89 | 2986.06 | 2760.756 |  |  |  | 1 | 1 |  |  |  |  | 136892.94 | 2760.756 | 136892.94 | 2760.756 | 9.5654 | [5 empty] | 113.5474 | 2760.756 |  | 104.98
06.04.2008 22:00 | 3600 | 2 | 762.53 | GGB | 763.004 | 773.039 | 767.766 | 264.74 | GGB | 10890.9 | GGB | 9.83 | GGB | 998.92 | GGB | 61.64 | GGB | 170662.39 | GGB | 137291.75 | GGB | 0 | 0 | 2992 | 3600 | 2975.9 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 193896.04 | GGB | 193898.31 | 2975.9 | 2752.7364 |  |  |  | 0 | 1 | [14 empty] | 113.4907 | 2752.7364 |  | 104.98
06.04.2008 23:00 | 3600 | 2 | 761.76 | GGB | 763.004 | 773.344 | 767.766 | 264.9 | GGB | 10913.4 | GGB | 9.83 | GGB | 999.63 | GGB | 61.18 | GGB | 171738.52 | GGB | 138445.96 | GGB | 0 | 0 | 3030 | 3600 | 3013.82 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 193935.8 | GGB | 193938.07 | 3013.82 | 2729.7871 |  |  |  | 0 | 1 | [14 empty] | 115.9031 | 2729.7871 |  | 104.98
06.04.2008 24:00 | 3600 | 2 | 762.03 | GGB | 763.004 | 773.156 | 767.766 | 266.98 | GGB | 10898.2 | GGB | 9.82 | GGB | 1000.47 | GGB | 61 | GGB | 173250.38 | GGB | 139856.91 | GGB | 0 | 0 | 3016 | 3600 | 3000.51 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 193975.6 | GGB | 193977.87 | 3000.51 | 2702.2476 |  |  |  | 0 | 1 | [14 empty] | 116.5672 | 2702.2476 |  | 104.98
07.04.2008 01:00 | 3600 | 2 | 763.07 | GGB | 764.102 | 773.438 | 768.864 | 266.06 | GGB | 10935.6 | GGB | 9.85 | GGB | 1000.56 | GGB | 61.1 | GGB | 172133.54 | GGB | 138927.28 | GGB | 0 | 0 | 2984 | 3600 | 2968.29 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 194015.43 | GGB | 194017.69 | 2968.29 | 2720.3297 |  |  |  | 1 | 1 |  |  |  |  | 138927.28 | 2720.3297 | 138927.28 | 2720.3297 | 9.4909 | [5 empty] | 114.549 | 2720.3297 |  | 104.98
07.04.2008 02:00 | 3600 | 2 | 762.08 | GGB | 761.538 | 772.266 | 766.667 | 265.78 | GGB | 10925.5 | GGB | 9.83 | GGB | 1000.5 | GGB | 61.55 | GGB | 171730.81 | GGB | 138408.02 | GGB | 0 | 0 | 3020 | 3600 | 3004.46 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 194055.39 | GGB | 194057.65 | 3004.46 | 2730.5354 |  |  |  | 0 | 1 | [14 empty] | 115.5115 | 2730.5354 |  | 104.98
07.04.2008 03:00 | 3600 | 2 | 762.03 | GGB | 763.004 | 773.344 | 767.766 | 266.43 | GGB | 10944 | GGB | 9.83 | GGB | 1000.49 | GGB | 61.14 | GGB | 172147.84 | GGB | 138910.48 | GGB | 0 | 0 | 3037 | 3600 | 3021.24 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 194095.68 | GGB | 194097.95 | 3021.24 | 2720.6587 |  |  |  | 0 | 1 | [14 empty] | 116.5783 | 2720.6587 |  | 104.98
07.04.2008 04:00 | 3600 | 2 | 762.2 | GGB | 763.004 | 772.477 | 766.667 | 266.73 | GGB | 10949.9 | GGB | 9.83 | GGB | 1000.61 | GGB | 61.22 | GGB | 172392.12 | GGB | 139093.76 | GGB | 0 | 0 | 3038 | 3600 | 3022.72 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 194136.12 | GGB | 194138.38 | 3022.72 | 2717.0737 |  |  |  | 0 | 1 | [14 empty] | 116.7893 | 2717.0737 |  | 104.98
07.04.2008 05:00 | 3600 | 2 | 762.21 | GGB | 762.637 | 772.102 | 766.3 | 266.8 | GGB | 10965.4 | GGB | 9.84 | GGB | 1000.29 | GGB | 61.11 | GGB | 172930.18 | GGB | 139526.34 | GGB | 0 | 0 | 3047 | 3600 | 3031.34 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 194176.6 | GGB | 194178.87 | 3031.34 | 2708.6499 |  |  |  | 0 | 1 | [14 empty] | 117.4866 | 2708.6499 |  | 104.98
07.04.2008 06:00 | 3600 | 2 | 762.46 | GGB | 764.102 | 774.07 | 768.864 | 266.35 | GGB | 10969.4 | GGB | 9.84 | GGB | 1000.23 | GGB | 60.98 | GGB | 172349.2 | GGB | 139104.5 | GGB | 0 | 0 | 3032 | 3600 | 3016.57 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 194217.19 | GGB | 194219.45 | 3016.57 | 2716.8639 |  |  |  | 1 | 1 |  |  |  |  | 139104.5 | 2716.8639 | 139104.5 | 2716.8639 | 9.3132 | [5 empty] | 116.5607 | 2716.8639 |  | 104.98
07.04.2008 07:00 | 3600 | 2 | 762.25 | GGB | 764.102 | 773.859 | 768.864 | 265.88 | GGB | 10955.6 | GGB | 9.84 | GGB | 1000.21 | GGB | 60.98 | GGB | 171911.27 | GGB | 138749.88 | GGB | 0 | 0 | 3043 | 3600 | 3027.55 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 194257.71 | GGB | 194259.97 | 3027.55 | 2723.8078 |  |  |  | 1 | 1 |  |  |  |  | 138749.88 | 2723.8078 | 138749.88 | 2723.8078 | 9.3269 | [5 empty] | 116.6867 | 2723.8078 |  | 104.98
07.04.2008 08:00 | 3600 | 2 | 762.29 | GGB | 763.004 | 773.859 | 767.766 | 265.47 | GGB | 10942.9 | GGB | 9.84 | GGB | 1000.51 | GGB | 61.02 | GGB | 171389.71 | GGB | 138350.97 | GGB | 0 | 0 | 3034 | 3600 | 3018.07 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 194298.17 | GGB | 194300.44 | 3018.07 | 2731.6614 |  |  |  | 0 | 1 | [14 empty] | 115.9869 | 2731.6614 |  | 104.98
07.04.2008 09:00 | 3600 | 2 | 762.13 | GGB | 764.102 | 773.836 | 768.864 | 265.47 | GGB | 10930.4 | GGB | 9.84 | GGB | 1000.89 | GGB | 61.29 | GGB | 171029.9 | GGB | 138003.16 | GGB | 0 | 0 | 3044 | 3600 | 3028.1 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 194338.9 | GGB | 194341.17 | 3028.1 | 2738.546 |  |  |  | 1 | 1 |  |  |  |  | 138003.16 | 2738.546 | 138003.16 | 2738.546 | 9.2789 | [5 empty] | 116.0798 | 2738.546 |  | 104.98
07.04.2008 10:00 | 3600 | 2 | 762.1 | GGB | 761.538 | 772.547 | 766.667 | 265.49 | GGB | 10914.9 | GGB | 9.83 | GGB | 1001.08 | GGB | 61.54 | GGB | 170851.64 | GGB | 137780.9 | GGB | 0 | 0 | 3044 | 3600 | 3028.07 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 194378.92 | GGB | 194381.2 | 3028.07 | 2742.9636 |  |  |  | 0 | 1 | [14 empty] | 115.8917 | 2742.9636 |  | 104.98
07.04.2008 11:00 | 3600 | 2 | 762.57 | GGB | 765.201 | 775.102 | 769.963 | 265.14 | GGB | 10916.8 | GGB | 9.84 | GGB | 1000.97 | GGB | 61.83 | GGB | 170564.46 | GGB | 137417.69 | GGB | 0 | 0 | 3028 | 3600 | 3012.03 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 194418.99 | GGB | 194421.27 | 3012.03 | 2750.2136 |  |  |  | 1 | 1 |  |  |  |  | 137417.69 | 2750.2136 | 137417.69 | 2750.2136 | 9.4317 | [5 empty] | 114.9739 | 2750.2136 |  | 104.98
07.04.2008 12:00 | 3600 | 2 | 762.98 | GGB | 763.004 | 773.063 | 767.766 | 264.66 | GGB | 10882.3 | GGB | 9.84 | GGB | 1000.4 | GGB | 62.27 | GGB | 169942.76 | GGB | 136658.36 | GGB | 0 | 0 | 2999 | 3600 | 2983.6 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 194458.55 | GGB | 194460.83 | 2983.6 | 2765.4949 |  |  |  | 0 | 1 | [14 empty] | 113.2594 | 2765.4949 |  | 104.98
07.04.2008 13:00 | 3600 | 2 | 763.27 | GGB | 765.201 | 775.219 | 769.963 | 263.81 | GGB | 10855.1 | GGB | 9.84 | GGB | 1000.41 | GGB | 62.42 | GGB | 169146.12 | GGB | 135957.73 | GGB | 0 | 0 | 2971 | 3600 | 2955.81 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 194498.71 | GGB | 194500.99 | 2955.81 | 2779.7463 |  |  |  | 1 | 1 |  |  |  |  | 135957.73 | 2779.7463 | 135957.73 | 2779.7463 | 9.4106 | [5 empty] | 111.6292 | 2779.7463 |  | 104.98
07.04.2008 14:00 | 3600 | 2 | 763.3 | GGB | 765.201 | 775.078 | 770.33 | 263.56 | GGB | 10834.3 | GGB | 9.84 | GGB | 1000.62 | GGB | 62.5 | GGB | 169006.38 | GGB | 135842.56 | GGB | 0 | 0 | 2952 | 3600 | 2936.78 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 194538.36 | GGB | 194540.64 | 2936.78 | 2782.103 |  |  |  | 1 | 1 |  |  |  |  | 135842.56 | 2782.103 | 135842.56 | 2782.103 | 9.5316 | [5 empty] | 110.8166 | 2782.103 |  | 104.98
07.04.2008 15:00 | 3600 | 2 | 761.18 | GGB | 762.637 | 772.898 | 767.766 | 263.51 | GGB | 10776.5 | GGB | 9.79 | GGB | 1000.85 | GGB | 62.33 | GGB | 169200.04 | GGB | 136096.2 | GGB | 0 | 0 | 3034 | 3600 | 3018.19 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 194579.2 | GGB | 194581.48 | 3018.19 | 2776.9181 |  |  |  | 0 | 1 | [14 empty] | 114.1012 | 2776.9181 |  | 104.98
07.04.2008 16:00 | 3600 | 2 | 761.35 | GGB | 761.538 | 771.82 | 766.667 | 262.82 | GGB | 10751.7 | GGB | 9.79 | GGB | 1000.53 | GGB | 62.51 | GGB | 168649.87 | GGB | 135540.04 | GGB | 0 | 0 | 3010 | 3600 | 2994.47 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 194618.89 | GGB | 194621.17 | 2994.47 | 2788.3126 |  |  |  | 0 | 1 | [14 empty] | 112.7418 | 2788.3126 |  | 104.98
07.04.2008 17:00 | 3600 | 2 | 761.12 | GGB | 764.102 | 773.109 | 767.766 | 262.76 | GGB | 10715.1 | GGB | 9.79 | GGB | 1000.18 | GGB | 62.36 | GGB | 168683.98 | GGB | 135580.16 | GGB | 0 | 0 | 3012 | 3600 | 2996.35 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 194658.6 | GGB | 194660.88 | 2996.35 | 2787.4875 |  |  |  | 1 | 1 |  |  |  |  | 135580.16 | 2787.4875 | 135580.16 | 2787.4875 | 9.5172 | [5 empty] | 112.846 | 2787.4875 |  | 104.98
07.04.2008 18:00 | 3600 | 2 | 761.64 | GGB | 761.538 | 771.867 | 766.667 | 262.88 | GGB | 10678.5 | GGB | 9.79 | GGB | 999.81 | GGB | 62.07 | GGB | 169345.28 | GGB | 136177.8 | GGB | 0 | 0 | 2965 | 3600 | 2949.05 | GGB | 100 | GGB | 40.79 | GGB | 40.79 | GGB | 194699.39 | GGB | 194701.67 | 2949.05 | 2775.2541 |  |  |  | 0 | 1 | [14 empty] | 111.5542 | 2775.2541 |  | 104.98
07.04.2008 19:00 | 3600 | 2 | 761.15 | GGB | 760.44 | 770.578 | 765.201 | 262.72 | GGB | 10724.8 | GGB | 9.79 | GGB | 999.59 | GGB | 62 | GGB | 169044.89 | GGB | 135933.91 | GGB | 0 | 0 | 3023 | 3600 | 3007.74 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 194738.26 | GGB | 194740.53 | 3007.74 | 2780.2334 |  |  |  | 0 | 1 | [14 empty] | 113.5705 | 2780.2334 |  | 104.98
07.04.2008 20:00 | 3600 | 2 | 760.35 | GGB | 761.538 | 772.664 | 766.667 | 263.19 | GGB | 10753 | GGB | 9.78 | GGB | 999.64 | GGB | 62.14 | GGB | 168990.97 | GGB | 135841.34 | GGB | 0 | 0 | 3092 | 3600 | 3076.32 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 194777.19 | GGB | 194779.46 | 3076.32 | 2782.128 |  |  |  | 0 | 1 | [14 empty] | 116.081 | 2782.128 |  | 104.98
07.04.2008 21:00 | 3600 | 2 | 760.48 | GGB | 762.637 | 772.641 | 767.766 | 263.45 | GGB | 10774.6 | GGB | 9.79 | GGB | 999.46 | GGB | 62.09 | GGB | 169073.5 | GGB | 135903.86 | GGB | 0 | 0 | 3094 | 3600 | 3078.35 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 194817.92 | GGB | 194820.19 | 3078.35 | 2780.8482 |  |  |  | 0 | 1 | [14 empty] | 116.211 | 2780.8482 |  | 104.98
07.04.2008 22:00 | 3600 | 2 | 760.39 | GGB | 760.44 | 770.414 | 765.201 | 263.47 | GGB | 10766.6 | GGB | 9.78 | GGB | 999.27 | GGB | 62.12 | GGB | 169060.29 | GGB | 135855.59 | GGB | 0 | 0 | 3098 | 3600 | 3082.55 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 194857.69 | GGB | 194859.96 | 3082.55 | 2781.8362 |  |  |  | 0 | 1 | [14 empty] | 116.3282 | 2781.8362 |  | 104.98
07.04.2008 23:00 | 3600 | 2 | 760.6 | GGB | 762.637 | 772.453 | 766.667 | 263.55 | GGB | 10782.5 | GGB | 9.79 | GGB | 998.42 | GGB | 61.85 | GGB | 169231.95 | GGB | 135986.48 | GGB | 0 | 0 | 3088 | 3600 | 3072.76 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 194898.05 | GGB | 194900.32 | 3072.76 | 2779.1586 |  |  |  | 0 | 1 | [14 empty] | 116.0705 | 2779.1586 |  | 104.98
07.04.2008 24:00 | 3600 | 2 | 760.1 | GGB | 761.538 | 770.391 | 765.201 | 263.93 | GGB | 10779.1 | GGB | 9.78 | GGB | 997.68 | GGB | 61.87 | GGB | 169622.57 | GGB | 136194.65 | GGB | 0 | 0 | 3119 | 3600 | 3103.56 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 194937.77 | GGB | 194940.04 | 3103.56 | 2774.9108 |  |  |  | 0 | 1 | [14 empty] | 117.4134 | 2774.9108 |  | 104.98
08.04.2008 01:00 | 3600 | 2 | 759.93 | GGB | 760.44 | 770.625 | 765.201 | 265.03 | GGB | 10773.4 | GGB | 9.78 | GGB | 996.73 | GGB | 61.39 | GGB | 170974.88 | GGB | 137345.64 | GGB | 0 | 0 | 3118 | 3600 | 3102.65 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 194976.65 | GGB | 194978.92 | 3102.65 | 2751.6563 |  |  |  | 0 | 1 | [14 empty] | 118.371 | 2751.6563 |  | 104.98
08.04.2008 02:00 | 3600 | 2 | 760.41 | GGB | 761.538 | 771.563 | 766.667 | 265.62 | GGB | 10764.8 | GGB | 9.79 | GGB | 995.98 | GGB | 60.83 | GGB | 172122.53 | GGB | 138395.22 | GGB | 0 | 0 | 3084 | 3600 | 3068.02 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 195016.1 | GGB | 195018.37 | 3068.02 | 2730.788 |  |  |  | 0 | 1 | [14 empty] | 117.9443 | 2730.788 |  | 104.98
08.04.2008 03:00 | 3600 | 2 | 760.36 | GGB | 761.538 | 771.727 | 766.3 | 265.53 | GGB | 10754.5 | GGB | 9.79 | GGB | 994.86 | GGB | 60.88 | GGB | 171922.27 | GGB | 138055.52 | GGB | 0 | 0 | 3079 | 3600 | 3063.29 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 195055.86 | GGB | 195058.13 | 3063.29 | 2737.5073 |  |  |  | 0 | 1 | [14 empty] | 117.4734 | 2737.5073 |  | 104.98
08.04.2008 04:00 | 3600 | 2 | 760.4 | GGB | 762.637 | 772.875 | 767.766 | 265.11 | GGB | 10759.2 | GGB | 9.79 | GGB | 994.01 | GGB | 60.89 | GGB | 171297.28 | GGB | 137433.35 | GGB | 0 | 0 | 3085 | 3600 | 3069 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 195095.31 | GGB | 195097.58 | 3069 | 2749.9002 |  |  |  | 0 | 1 | [14 empty] | 117.1619 | 2749.9002 |  | 104.98
08.04.2008 05:00 | 3600 | 2 | 760.12 | GGB | 760.44 | 770.438 | 765.201 | 263.62 | GGB | 10776.7 | GGB | 9.79 | GGB | 992.74 | GGB | 61.34 | GGB | 169632.47 | GGB | 135739.79 | GGB | 0 | 0 | 3111 | 3600 | 3095.24 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 195134.52 | GGB | 195136.79 | 3095.24 | 2784.2094 |  |  |  | 0 | 1 | [14 empty] | 116.7076 | 2784.2094 |  | 104.98
08.04.2008 06:00 | 3600 | 2 | 759.97 | GGB | 760.44 | 770.414 | 765.201 | 263.78 | GGB | 10762.4 | GGB | 9.79 | GGB | 991.72 | GGB | 61.43 | GGB | 170096.81 | GGB | 135936.61 | GGB | 0 | 0 | 3110 | 3600 | 3094.06 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 195173.91 | GGB | 195176.17 | 3094.06 | 2780.1782 |  |  |  | 0 | 1 | [14 empty] | 116.8322 | 2780.1782 |  | 104.98
08.04.2008 07:00 | 3600 | 2 | 760.08 | GGB | 761.538 | 771.727 | 765.201 | 264.02 | GGB | 10762.2 | GGB | 9.79 | GGB | 990.7 | GGB | 61.09 | GGB | 170615.07 | GGB | 136348.45 | GGB | 0 | 0 | 3104 | 3600 | 3088.46 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 195213.75 | GGB | 195216.01 | 3088.46 | 2771.7807 |  |  |  | 0 | 1 | [14 empty] | 116.9741 | 2771.7807 |  | 104.98
08.04.2008 08:00 | 3600 | 2 | 760.02 | GGB | 761.538 | 770.836 | 765.201 | 264.4 | GGB | 10739.2 | GGB | 9.78 | GGB | 990.43 | GGB | 60.94 | GGB | 171300.58 | GGB | 136921.37 | GGB | 0 | 0 | 3099 | 3600 | 3083.23 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 195253.59 | GGB | 195255.85 | 3083.23 | 2760.1827 |  |  |  | 0 | 1 | [14 empty] | 117.2667 | 2760.1827 |  | 104.98
08.04.2008 09:00 | 3600 | 2 | 760.26 | GGB | 762.637 | 771.984 | 766.3 | 263.56 | GGB | 10769.3 | GGB | 9.79 | GGB | 989.89 | GGB | 61.07 | GGB | 170309.18 | GGB | 135999.27 | GGB | 0 | 0 | 3098 | 3600 | 3082.62 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 195293.08 | GGB | 195295.35 | 3082.62 | 2778.8973 |  |  |  | 0 | 1 | [14 empty] | 116.4539 | 2778.8973 |  | 104.98
08.04.2008 10:00 | 3600 | 2 | 759.84 | GGB | 761.538 | 771.117 | 765.201 | 264.33 | GGB | 10728.1 | GGB | 9.78 | GGB | 989.45 | GGB | 60.78 | GGB | 171401.81 | GGB | 136929.73 | GGB | 0 | 0 | 3094 | 3600 | 3078.15 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 195332.64 | GGB | 195334.91 | 3078.15 | 2760.0142 |  |  |  | 0 | 1 | [14 empty] | 117.0806 | 2760.0142 |  | 104.98
08.04.2008 11:00 | 3600 | 2 | 759.07 | GGB | 759.341 | 768.445 | 764.102 | 265.84 | GGB | 10767.3 | GGB | 9.76 | GGB | 989.01 | GGB | 59.25 | GGB | 173778.54 | GGB | 139406.88 | GGB | 0 | 0 | 3141 | 3600 | 3125.39 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 195372.55 | GGB | 195374.82 | 3125.39 | 2710.9709 |  |  |  | 0 | 1 | [14 empty] | 121.028 | 2710.9709 |  | 104.98
08.04.2008 12:00 | 3600 | 2 | 757.93 | GGB | 761.538 | 771.633 | 766.667 | 269.4 | GGB | 10934 | GGB | 9.77 | GGB | 990.63 | GGB | 58.12 | GGB | 177878.4 | GGB | 143417.88 | GGB | 0 | 0 | 3285 | 3600 | 3268.8 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 195411.27 | GGB | 195413.55 | 3268.8 | 2635.1526 |  |  |  | 0 | 1 | [14 empty] | 130.2234 | 2635.1526 |  | 104.98
08.04.2008 13:00 | 3600 | 2 | 759.44 | GGB | 760.44 | 769.523 | 765.201 | 267.97 | GGB | 11000.8 | GGB | 9.8 | GGB | 991.34 | GGB | 58.6 | GGB | 176288.41 | GGB | 142031.14 | GGB | 0 | 0 | 3219 | 3600 | 3203.13 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 195450.7 | GGB | 195452.97 | 3203.13 | 2660.8813 |  |  |  | 0 | 1 | [14 empty] | 126.3734 | 2660.8813 |  | 104.98
08.04.2008 14:00 | 3600 | 2 | 758.79 | GGB | 760.44 | 769.711 | 764.102 | 268.49 | GGB | 10945.8 | GGB | 9.78 | GGB | 991.57 | GGB | 58.69 | GGB | 176422.65 | GGB | 142133.25 | GGB | 0 | 0 | 3230 | 3600 | 3214.6 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 195490.5 | GGB | 195492.78 | 3214.6 | 2658.9697 |  |  |  | 0 | 1 | [14 empty] | 126.9171 | 2658.9697 |  | 104.98
08.04.2008 15:00 | 3600 | 2 | 759.96 | GGB | 762.637 | 771.516 | 766.667 | 269.43 | GGB | 10915.8 | GGB | 9.79 | GGB | 991.76 | GGB | 58.53 | GGB | 177348.04 | GGB | 142977.76 | GGB | 0 | 0 | 3153 | 3600 | 3137.25 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 195530.39 | GGB | 195532.67 | 3137.25 | 2643.2642 |  |  |  | 0 | 1 | [14 empty] | 124.5992 | 2643.2642 |  | 104.98
08.04.2008 16:00 | 3600 | 2 | 759.95 | GGB | 760.44 | 770.438 | 765.201 | 268.52 | GGB | 10926.1 | GGB | 9.79 | GGB | 992.24 | GGB | 58.98 | GGB | 176134.36 | GGB | 141874.57 | GGB | 0 | 0 | 3156 | 3600 | 3140.16 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 195570.03 | GGB | 195572.31 | 3140.16 | 2663.8178 |  |  |  | 0 | 1 | [14 empty] | 123.7525 | 2663.8178 |  | 104.98
08.04.2008 17:00 | 3600 | 2 | 759.29 | GGB | 761.538 | 770.484 | 765.201 | 268.57 | GGB | 10907 | GGB | 9.78 | GGB | 992.66 | GGB | 59.15 | GGB | 175892.29 | GGB | 141668.27 | GGB | 0 | 0 | 3197 | 3600 | 3181.06 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 195609.79 | GGB | 195612.07 | 3181.06 | 2667.6969 |  |  |  | 0 | 1 | [14 empty] | 125.182 | 2667.6969 |  | 104.98
08.04.2008 18:00 | 3600 | 2 | 759.67 | GGB | 760.44 | 769.57 | 764.102 | 269.34 | GGB | 10946.8 | GGB | 9.78 | GGB | 993.33 | GGB | 58.97 | GGB | 176297.21 | GGB | 142165.39 | GGB | 0 | 0 | 3195 | 3600 | 3179.59 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 195650.32 | GGB | 195652.6 | 3179.59 | 2658.3685 |  |  |  | 0 | 1 | [14 empty] | 125.5632 | 2658.3685 |  | 104.98
08.04.2008 19:00 | 3600 | 2 | 759.44 | GGB | 761.538 | 770.672 | 766.3 | 270.42 | GGB | 10928.2 | GGB | 9.78 | GGB | 993.82 | GGB | 58.4 | GGB | 177642.93 | GGB | 143567.26 | GGB | 0 | 0 | 3211 | 3600 | 3194.72 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 195690.04 | GGB | 195692.32 | 3194.72 | 2632.4108 |  |  |  | 0 | 1 | [14 empty] | 127.4048 | 2632.4108 |  | 104.98
08.04.2008 20:00 | 3600 | 2 | 760.57 | GGB | 761.538 | 770.648 | 766.3 | 268.68 | GGB | 10959 | GGB | 9.81 | GGB | 994.16 | GGB | 59.03 | GGB | 175445.55 | GGB | 141572.68 | GGB | 0 | 0 | 3153 | 3600 | 3136.82 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 195729.62 | GGB | 195731.91 | 3136.82 | 2669.4981 |  |  |  | 0 | 1 | [14 empty] | 123.3578 | 2669.4981 |  | 104.98
08.04.2008 21:00 | 3600 | 2 | 759.46 | GGB | 761.538 | 771.797 | 766.3 | 267.95 | GGB | 10928.6 | GGB | 9.79 | GGB | 995.02 | GGB | 59.49 | GGB | 174335.31 | GGB | 140600.41 | GGB | 0 | 0 | 3207 | 3600 | 3191.05 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 195769.44 | GGB | 195771.73 | 3191.05 | 2687.958 |  |  |  | 0 | 1 | [14 empty] | 124.6286 | 2687.958 |  | 104.98
08.04.2008 22:00 | 3600 | 2 | 759.47 | GGB | 761.538 | 770.813 | 765.201 | 269.25 | GGB | 10920.9 | GGB | 9.78 | GGB | 996.23 | GGB | 58.82 | GGB | 177066.35 | GGB | 143265.91 | GGB | 0 | 0 | 3204 | 3600 | 3187.68 | GGB | 100 | GGB | 40.7 | GGB | 40.7 | GGB | 195810.14 | GGB | 195812.43 | 3187.68 | 2637.9479 |  |  |  | 0 | 1 | [14 empty] | 126.8572 | 2637.9479 |  | 104.98
08.04.2008 23:00 | 3600 | 2 | 758.44 | GGB | 760.44 | 769.664 | 764.102 | 269.77 | GGB | 10936.1 | GGB | 9.76 | GGB | 997.03 | GGB | 59.13 | GGB | 176124.46 | GGB | 142484.43 | GGB | 0 | 0 | 3283 | 3600 | 3267.29 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 195850.34 | GGB | 195852.63 | 3267.29 | 2652.4161 |  |  |  | 0 | 1 | [14 empty] | 129.3161 | 2652.4161 |  | 104.98
08.04.2008 24:00 | 3600 | 2 | 759.73 | GGB | 760.44 | 769.688 | 765.201 | 270.9 | GGB | 10996.2 | GGB | 9.79 | GGB | 997.79 | GGB | 58.8 | GGB | 177405.25 | GGB | 143775.61 | GGB | 0 | 0 | 3239 | 3600 | 3223.25 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 195889.94 | GGB | 195892.23 | 3223.25 | 2628.596 |  |  |  | 0 | 1 | [14 empty] | 128.7291 | 2628.596 |  | 104.98
09.04.2008 01:00 | 3600 | 2 | 759.37 | GGB | 760.44 | 769.945 | 765.201 | 270.68 | GGB | 11021.8 | GGB | 9.78 | GGB | 998.4 | GGB | 59.17 | GGB | 176869.39 | GGB | 143268.8 | GGB | 0 | 0 | 3271 | 3600 | 3254.63 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 195929.47 | GGB | 195931.77 | 3254.63 | 2637.8946 |  |  |  | 0 | 1 | [14 empty] | 129.5241 | 2637.8946 |  | 104.98
09.04.2008 02:00 | 3600 | 2 | 759.24 | GGB | 761.538 | 770.109 | 765.201 | 272.13 | GGB | 10996.4 | GGB | 9.78 | GGB | 998.85 | GGB | 58.7 | GGB | 178702.55 | GGB | 145023.61 | GGB | 0 | 0 | 3263 | 3600 | 3246.89 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 195970.1 | GGB | 195972.4 | 3246.89 | 2605.9757 |  |  |  | 0 | 1 | [14 empty] | 130.7988 | 2605.9757 |  | 104.98
09.04.2008 03:00 | 3600 | 2 | 760.06 | GGB | 761.538 | 771.422 | 765.201 | 272.53 | GGB | 11009.2 | GGB | 9.79 | GGB | 999.61 | GGB | 58.5 | GGB | 179098.67 | GGB | 145542.21 | GGB | 0 | 0 | 3213 | 3600 | 3197.43 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 196010.63 | GGB | 196012.94 | 3197.43 | 2596.69 |  |  |  | 0 | 1 | [14 empty] | 129.267 | 2596.69 |  | 104.98
09.04.2008 04:00 | 3600 | 2 | 760.04 | GGB | 761.538 | 770.273 | 766.3 | 271.12 | GGB | 11041.8 | GGB | 9.79 | GGB | 999.8 | GGB | 59.06 | GGB | 177119.17 | GGB | 143718.97 | GGB | 0 | 0 | 3230 | 3600 | 3213.99 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 196050.35 | GGB | 196052.65 | 3213.99 | 2629.632 |  |  |  | 0 | 1 | [14 empty] | 128.3087 | 2629.632 |  | 104.98
09.04.2008 05:00 | 3600 | 2 | 759.37 | GGB | 761.538 | 770.086 | 765.201 | 271.55 | GGB | 11036.4 | GGB | 9.78 | GGB | 1000.48 | GGB | 59.19 | GGB | 177223.7 | GGB | 143847.05 | GGB | 0 | 0 | 3275 | 3600 | 3259.52 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 196090.12 | GGB | 196092.42 | 3259.52 | 2627.2906 |  |  |  | 0 | 1 | [14 empty] | 130.2423 | 2627.2906 |  | 104.98
09.04.2008 06:00 | 3600 | 2 | 759.54 | GGB | 761.538 | 771.023 | 766.3 | 272.64 | GGB | 11037.1 | GGB | 9.78 | GGB | 1000.99 | GGB | 58.73 | GGB | 178909.42 | GGB | 145492.02 | GGB | 0 | 0 | 3267 | 3600 | 3251.33 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 196131.21 | GGB | 196133.51 | 3251.33 | 2597.5858 |  |  |  | 0 | 1 | [14 empty] | 131.4007 | 2597.5858 |  | 104.98
09.04.2008 07:00 | 3600 | 2 | 759.95 | GGB | 761.538 | 769.945 | 766.3 | 273.44 | GGB | 11032 | GGB | 9.78 | GGB | 1001.84 | GGB | 58.48 | GGB | 179873.31 | GGB | 146506.87 | GGB | 0 | 0 | 3238 | 3600 | 3222.32 | GGB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 196172.53 | GGB | 196174.84 | 3222.32 | 2579.5923 |  |  |  | 0 | 1 | [14 empty] | 131.1367 | 2579.5923 |  | 104.98
09.04.2008 08:00 | 3600 | 2 | 759.84 | GGB | 761.538 | 771.164 | 766.667 | 272.54 | GGB | 11096.7 | GGB | 9.79 | GGB | 1002.26 | GGB | 58.88 | GGB | 178339.44 | GGB | 145146.28 | GGB | 0 | 0 | 3273 | 3600 | 3257.15 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 196213.63 | GGB | 196215.94 | 3257.15 | 2603.7732 |  |  |  | 0 | 1 | [14 empty] | 131.3231 | 2603.7732 |  | 104.98
09.04.2008 09:00 | 3600 | 2 | 759.43 | GGB | 761.538 | 770.086 | 765.201 | 273.56 | GGB | 11073.7 | GGB | 9.77 | GGB | 1002.75 | GGB | 58.59 | GGB | 179951.44 | GGB | 146657.53 | GGB | 0 | 0 | 3284 | 3600 | 3268.21 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 196254.63 | GGB | 196256.93 | 3268.21 | 2576.9423 |  |  |  | 0 | 1 | [14 empty] | 133.141 | 2576.9423 |  | 104.98
09.04.2008 10:00 | 3600 | 2 | 760.57 | GGB | 762.637 | 771.375 | 766.3 | 273.85 | GGB | 11064.2 | GGB | 9.8 | GGB | 1003.25 | GGB | 58.47 | GGB | 180762.39 | GGB | 147446.02 | GGB | 0 | 0 | 3201 | 3600 | 3185.38 | GGB | 100 | GGB | 42.09 | GGB | 42.09 | GGB | 196296.72 | GGB | 196299.02 | 3185.38 | 2563.1618 |  |  |  | 0 | 1 | [14 empty] | 130.4643 | 2563.1618 |  | 104.98
09.04.2008 11:00 | 3600 | 2 | 761.39 | GGB | 763.004 | 771.891 | 767.766 | 271.29 | GGB | 11057 | GGB | 9.81 | GGB | 1003.35 | GGB | 59.49 | GGB | 177392.05 | GGB | 144266.29 | GGB | 0 | 0 | 3154 | 3600 | 3138.56 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 196336.68 | GGB | 196338.99 | 3138.56 | 2619.6556 |  |  |  | 0 | 1 | [14 empty] | 125.7746 | 2619.6556 |  | 104.98
09.04.2008 12:00 | 3600 | 2 | 761.71 | GGB | 764.102 | 774.398 | 768.864 | 269.5 | GGB | 11010.3 | GGB | 9.81 | GGB | 1003.38 | GGB | 60.23 | GGB | 175751.45 | GGB | 142617.66 | GGB | 0 | 0 | 3124 | 3600 | 3108.16 | GGB | 100 | GGB | 41.04 | GGB | 41.04 | GGB | 196377.73 | GGB | 196380.03 | 3108.16 | 2649.9383 |  |  |  | 1 | 1 |  |  |  |  | 142617.66 | 2649.9383 | 142617.66 | 2649.9383 | 9.2088 | [5 empty] | 123.1329 | 2649.9383 |  | 104.98
09.04.2008 13:00 | 3600 | 2 | 761.63 | GGB | 765.201 | 774.656 | 768.864 | 269.22 | GGB | 10903.9 | GGB | 9.79 | GGB | 1003.21 | GGB | 60.25 | GGB | 175874.69 | GGB | 142684.01 | GGB | 0 | 0 | 3072 | 3600 | 3056.64 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 196417.57 | GGB | 196419.87 | 3056.64 | 2648.706 |  |  |  | 1 | 1 |  |  |  |  | 142684.01 | 2648.706 | 142684.01 | 2648.706 | 9.4861 | [5 empty] | 121.1482 | 2648.706 |  | 104.98
09.04.2008 14:00 | 3600 | 2 | 761.91 | GGB | 762.637 | 771.797 | 767.766 | 267.6 | GGB | 10868.8 | GGB | 9.79 | GGB | 1003.02 | GGB | 60.68 | GGB | 173866.57 | GGB | 140848.39 | GGB | 0 | 0 | 3035 | 3181 | 3019.05 | GGB | 100 | GGB | 41.05 | GGB | 41.05 | GGB | 196458.61 | GGB | 196460.92 | 3019.05 | 2683.2256 |  |  |  | 0 | 1 | [14 empty] | 118.119 | 2683.2256 |  | 104.98
09.04.2008 15:00 | 3600 | 2 | 762.9 | GGB | 765.201 | 774.703 | 768.864 | 268.1 | GGB | 10831.8 | GGB | 9.8 | GGB | 1002.74 | GGB | 60.72 | GGB | 174405.73 | GGB | 141228.81 | GGB | 0 | 0 | 2975 | 3600 | 2959.25 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 196498.38 | GGB | 196500.69 | 2959.25 | 2675.9979 |  |  |  | 1 | 1 |  |  |  |  | 141228.81 | 2675.9979 | 141228.81 | 2675.9979 | 9.5028 | [5 empty] | 116.092 | 2675.9979 |  | 104.98
09.04.2008 16:00 | 3600 | 2 | 762.49 | GGB | 764.102 | 773.461 | 767.766 | 267.32 | GGB | 10774.6 | GGB | 9.79 | GGB | 1002.38 | GGB | 60.99 | GGB | 173407.73 | GGB | 140255.11 | GGB | 0 | 0 | 2967 | 3600 | 2950.89 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 196539.34 | GGB | 196541.65 | 2950.89 | 2694.5756 |  |  |  | 1 | 1 |  |  |  |  | 140255.11 | 2694.5756 | 140255.11 | 2694.5756 | 9.2268 | [5 empty] | 114.9659 | 2694.5756 |  | 104.98
09.04.2008 17:00 | 3600 | 2 | 763 | GGB | 764.102 | 774.469 | 768.864 | 266.41 | GGB | 10729.5 | GGB | 9.79 | GGB | 1001.44 | GGB | 61.66 | GGB | 172045.51 | GGB | 138743.64 | GGB | 0 | 0 | 2920 | 3600 | 2904.72 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 196578.75 | GGB | 196581.06 | 2904.72 | 2723.9303 |  |  |  | 1 | 1 |  |  |  |  | 138743.64 | 2723.9303 | 138743.64 | 2723.9303 | 9.5896 | [5 empty] | 111.9476 | 2723.9303 |  | 104.98
09.04.2008 18:00 | 3600 | 2 | 763.23 | GGB | 763.004 | 773.156 | 767.766 | 265.25 | GGB | 10714.9 | GGB | 9.79 | GGB | 1000.66 | GGB | 62.09 | GGB | 170688.79 | GGB | 137365.03 | GGB | 0 | 0 | 2902 | 3600 | 2886.54 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 196619.46 | GGB | 196621.77 | 2886.54 | 2751.2679 |  |  |  | 0 | 1 | [14 empty] | 110.1416 | 2751.2679 |  | 104.98
09.04.2008 19:00 | 3600 | 2 | 762.14 | GGB | 762.637 | 773.039 | 767.766 | 265.12 | GGB | 10686.9 | GGB | 9.78 | GGB | 1000.11 | GGB | 62.34 | GGB | 170343.29 | GGB | 136913.05 | GGB | 0 | 0 | 2958 | 3600 | 2941.94 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 196658.64 | GGB | 196660.95 | 2941.94 | 2760.3505 |  |  |  | 0 | 1 | [14 empty] | 111.8861 | 2760.3505 |  | 104.98
09.04.2008 20:00 | 3600 | 2 | 762.85 | GGB | 760.44 | 770.555 | 765.201 | 265.71 | GGB | 10687.3 | GGB | 9.79 | GGB | 999.7 | GGB | 62.22 | GGB | 170295.97 | GGB | 136865.81 | GGB | 0 | 0 | 2932 | 3600 | 2915.9 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 196698.03 | GGB | 196700.34 | 2915.9 | 2761.3032 |  |  |  | 0 | 1 | [14 empty] | 110.8575 | 2761.3032 |  | 104.98
09.04.2008 21:00 | 3600 | 2 | 762.13 | GGB | 762.637 | 772.992 | 767.766 | 265.36 | GGB | 10725.5 | GGB | 9.79 | GGB | 998.98 | GGB | 62.69 | GGB | 169055.89 | GGB | 135581.51 | GGB | 0 | 0 | 2986 | 3600 | 2970.36 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 196738.27 | GGB | 196740.58 | 2970.36 | 2787.4597 |  |  |  | 0 | 1 | [14 empty] | 111.8683 | 2787.4597 |  | 104.98
09.04.2008 22:00 | 3600 | 2 | 762 | GGB | 763.004 | 772.898 | 767.766 | 266.2 | GGB | 10773.3 | GGB | 9.79 | GGB | 998.38 | GGB | 62.51 | GGB | 170158.43 | GGB | 136456.83 | GGB | 0 | 0 | 3022 | 3600 | 3006.05 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 196777.86 | GGB | 196780.18 | 3006.05 | 2769.5792 |  |  |  | 0 | 1 | [14 empty] | 113.9433 | 2769.5792 |  | 104.98
09.04.2008 23:00 | 3600 | 2 | 761.3 | GGB | 763.004 | 773.039 | 767.766 | 266.26 | GGB | 10769.5 | GGB | 9.78 | GGB | 997.88 | GGB | 62.35 | GGB | 170391.7 | GGB | 136642.4 | GGB | 0 | 0 | 3056 | 3600 | 3039.97 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 196818.96 | GGB | 196821.27 | 3039.97 | 2765.8179 |  |  |  | 0 | 1 | [14 empty] | 115.3858 | 2765.8179 |  | 104.98
09.04.2008 24:00 | 3600 | 2 | 761.32 | GGB | 761.538 | 771.281 | 766.3 | 265.67 | GGB | 10770 | GGB | 9.78 | GGB | 997.12 | GGB | 62.29 | GGB | 170323.48 | GGB | 136506.66 | GGB | 0 | 0 | 3049 | 3600 | 3033.56 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 196858.51 | GGB | 196860.83 | 3033.56 | 2768.5682 |  |  |  | 0 | 1 | [14 empty] | 115.0281 | 2768.5682 |  | 104.98
10.04.2008 01:00 | 3600 | 2 | 761.54 | GGB | 761.538 | 771.328 | 766.667 | 265.59 | GGB | 10771.5 | GGB | 9.79 | GGB | 997.13 | GGB | 62.42 | GGB | 170100.11 | GGB | 136274.52 | GGB | 0 | 0 | 3039 | 3600 | 3023.43 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 196898.16 | GGB | 196900.48 | 3023.43 | 2773.2844 |  |  |  | 0 | 1 | [14 empty] | 114.449 | 2773.2844 |  | 104.98
10.04.2008 02:00 | 3600 | 2 | 761.17 | GGB | 762.637 | 772.594 | 766.667 | 265.95 | GGB | 10763.8 | GGB | 9.78 | GGB | 997.03 | GGB | 62.47 | GGB | 170233.25 | GGB | 136349.17 | GGB | 0 | 0 | 3053 | 3600 | 3037.08 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 196937.71 | GGB | 196940.02 | 3037.08 | 2771.766 |  |  |  | 0 | 1 | [14 empty] | 115.0287 | 2771.766 |  | 104.98
10.04.2008 03:00 | 3600 | 2 | 760.75 | GGB | 762.637 | 771.609 | 766.3 | 266.56 | GGB | 10770.4 | GGB | 9.78 | GGB | 996.78 | GGB | 62.39 | GGB | 170588.66 | GGB | 136634.05 | GGB | 0 | 0 | 3078 | 3600 | 3062.21 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 196977.24 | GGB | 196979.55 | 3062.21 | 2765.987 |  |  |  | 0 | 1 | [14 empty] | 116.2228 | 2765.987 |  | 104.98
10.04.2008 04:00 | 3600 | 2 | 760.86 | GGB | 762.637 | 772.523 | 767.766 | 267.36 | GGB | 10798.7 | GGB | 9.78 | GGB | 997.07 | GGB | 62.29 | GGB | 171324.79 | GGB | 137303.54 | GGB | 0 | 0 | 3100 | 3600 | 3083.77 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 197016.82 | GGB | 197019.13 | 3083.77 | 2752.5 |  |  |  | 0 | 1 | [14 empty] | 117.6146 | 2752.5 |  | 104.98
10.04.2008 05:00 | 3600 | 2 | 760.75 | GGB | 760.44 | 769.523 | 764.102 | 267.65 | GGB | 10808.4 | GGB | 9.78 | GGB | 996.89 | GGB | 62.24 | GGB | 171525.05 | GGB | 137460.85 | GGB | 0 | 0 | 3107 | 3600 | 3091.34 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 197056.4 | GGB | 197058.71 | 3091.34 | 2749.3501 |  |  |  | 0 | 1 | [14 empty] | 118.0384 | 2749.3501 |  | 104.98
10.04.2008 06:00 | 3600 | 2 | 761.18 | GGB | 761.538 | 770.578 | 765.201 | 267.45 | GGB | 10830.8 | GGB | 9.8 | GGB | 996.79 | GGB | 62.24 | GGB | 171465.63 | GGB | 137398.54 | GGB | 0 | 0 | 3101 | 3600 | 3085.25 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 197096 | GGB | 197098.32 | 3085.25 | 2750.5969 |  |  |  | 0 | 1 | [14 empty] | 117.7525 | 2750.5969 |  | 104.98
10.04.2008 07:00 | 3600 | 2 | 759.68 | GGB | 759.341 | 768.984 | 764.102 | 267.98 | GGB | 10803.9 | GGB | 9.76 | GGB | 996.94 | GGB | 61.89 | GGB | 172291.99 | GGB | 138225.2 | GGB | 0 | 0 | 3175 | 3600 | 3158.75 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 197135.7 | GGB | 197138.01 | 3158.75 | 2734.1469 |  |  |  | 0 | 1 | [14 empty] | 121.283 | 2734.1469 |  | 104.98
10.04.2008 08:00 | 3600 | 2 | 760.11 | GGB | 760.44 | 769.875 | 765.201 | 269.59 | GGB | 10883.4 | GGB | 9.78 | GGB | 996.87 | GGB | 61.27 | GGB | 173749.93 | GGB | 139642.48 | GGB | 0 | 0 | 3189 | 3600 | 3173.11 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 197175.48 | GGB | 197177.79 | 3173.11 | 2706.3971 |  |  |  | 0 | 1 | [14 empty] | 123.0836 | 2706.3971 |  | 104.98
10.04.2008 09:00 | 3600 | 2 | 760.22 | GGB | 762.637 | 771.703 | 766.3 | 270.38 | GGB | 10933.1 | GGB | 9.79 | GGB | 996.91 | GGB | 61.22 | GGB | 174903.09 | GGB | 140597.54 | GGB | 0 | 0 | 3201 | 3600 | 3185.12 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 197215.32 | GGB | 197217.63 | 3185.12 | 2688.0129 |  |  |  | 0 | 1 | [14 empty] | 124.3945 | 2688.0129 |  | 104.98
10.04.2008 10:00 | 3600 | 2 | 760.68 | GGB | 759.341 | 769.383 | 764.102 | 269.45 | GGB | 10914.2 | GGB | 9.79 | GGB | 996.76 | GGB | 61.27 | GGB | 174005.21 | GGB | 139832.87 | GGB | 0 | 0 | 3152 | 3600 | 3136.09 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 197255.16 | GGB | 197257.47 | 3136.09 | 2702.7122 |  |  |  | 0 | 1 | [14 empty] | 121.8135 | 2702.7122 |  | 104.98
10.04.2008 11:00 | 3600 | 2 | 761.86 | GGB | 765.201 | 774.797 | 769.963 | 268.09 | GGB | 10897.6 | GGB | 9.82 | GGB | 996.57 | GGB | 61.87 | GGB | 172509.85 | GGB | 138355.87 | GGB | 0 | 0 | 3101 | 3600 | 3085.67 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 197294.96 | GGB | 197297.28 | 3085.67 | 2731.5646 |  |  |  | 1 | 1 |  |  |  |  | 138355.87 | 2731.5646 | 138355.87 | 2731.5646 | 9.4933 | [5 empty] | 118.589 | 2731.5646 |  | 104.98
10.04.2008 12:00 | 3600 | 2 | 761.43 | GGB | 762.637 | 771.469 | 767.033 | 265.84 | GGB | 10791.4 | GGB | 9.8 | GGB | 995.4 | GGB | 62.52 | GGB | 170234.35 | GGB | 136105.53 | GGB | 0 | 0 | 3065 | 3600 | 3049.58 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 197334.66 | GGB | 197336.98 | 3049.58 | 2776.7277 |  |  |  | 0 | 1 | [14 empty] | 115.2958 | 2776.7277 |  | 104.98
10.04.2008 13:00 | 3600 | 2 | 761.44 | GGB | 763.004 | 774.281 | 768.498 | 264.67 | GGB | 10743.8 | GGB | 9.79 | GGB | 995.06 | GGB | 62.81 | GGB | 169073.5 | GGB | 135014.42 | GGB | 0 | 0 | 3068 | 3600 | 3052.01 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 197374.19 | GGB | 197376.5 | 3052.01 | 2799.1677 |  |  |  | 0 | 1 | [14 empty] | 114.4626 | 2799.1677 |  | 104.98
10.04.2008 14:00 | 3600 | 2 | 762.49 | GGB | 765.201 | 775.594 | 770.696 | 261.98 | GGB | 10702.5 | GGB | 9.81 | GGB | 994.1 | GGB | 62.97 | GGB | 167044.47 | GGB | 133203.56 | GGB | 0 | 0 | 2987 | 3600 | 2970.9 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 197413.51 | GGB | 197415.82 | 2970.9 | 2837.2215 |  |  |  | 1 | 1 |  |  |  |  | 133203.56 | 2837.2215 | 133203.56 | 2837.2215 | 9.6116 | [5 empty] | 109.9262 | 2837.2215 |  | 104.98
10.04.2008 15:00 | 3600 | 2 | 762.46 | GGB | 763.004 | 773.484 | 768.498 | 260.17 | GGB | 10631.4 | GGB | 9.8 | GGB | 993.37 | GGB | 63.25 | GGB | 165156.3 | GGB | 131491.54 | GGB | 0 | 0 | 2955 | 3600 | 2939.82 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 197452.6 | GGB | 197454.91 | 2939.82 | 2874.1621 |  |  |  | 0 | 1 | [14 empty] | 107.3782 | 2874.1621 |  | 104.98
10.04.2008 16:00 | 3600 | 2 | 762.58 | GGB | 763.004 | 773.391 | 768.132 | 257.9 | GGB | 10518.1 | GGB | 9.79 | GGB | 992.53 | GGB | 63.78 | GGB | 163338.54 | GGB | 129730.46 | GGB | 0 | 0 | 2916 | 3600 | 2900.47 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 197491.62 | GGB | 197493.93 | 2900.47 | 2900.47 |  |  |  | 0 | 1 | [14 empty] | 104.522 |  |  | #VALUE!
10.04.2008 17:00 | 3600 | 2 | 761.53 | GGB | 762.637 | 772.43 | 768.132 | 259 | GGB | 10511.8 | GGB | 9.78 | GGB | 992.5 | GGB | 63.2 | GGB | 164041.65 | GGB | 130510.37 | GGB | 0 | 0 | 2960 | 3600 | 2944.08 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 197530.72 | GGB | 197533.03 | 2944.08 | 2895.7699 |  |  |  | 0 | 1 | [14 empty] | 106.7314 | 2895.7699 |  | 104.98
10.04.2008 18:00 | 3600 | 2 | 761.41 | GGB | 762.637 | 772.383 | 768.132 | 258.91 | GGB | 10549.8 | GGB | 9.78 | GGB | 992.18 | GGB | 63.85 | GGB | 163144.88 | GGB | 129501.69 | GGB | 0 | 0 | 2988 | 3600 | 2971.85 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 197569.96 | GGB | 197572.26 | 2971.85 | 2918.3248 |  |  |  | 0 | 1 | [14 empty] | 106.9054 | 2918.3248 |  | 104.98
10.04.2008 19:00 | 3600 | 2 | 760.57 | GGB | 759.341 | 770.086 | 764.835 | 260.95 | GGB | 10579.6 | GGB | 9.76 | GGB | 992.36 | GGB | 63.51 | GGB | 164804.19 | GGB | 130975.56 | GGB | 0 | 0 | 3052 | 3600 | 3036.42 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 197609.76 | GGB | 197612.06 | 3036.42 | 2885.4849 |  |  |  | 0 | 1 | [14 empty] | 110.4713 | 2885.4849 |  | 104.98
10.04.2008 20:00 | 3600 | 2 | 760.22 | GGB | 761.538 | 771.234 | 765.934 | 263.26 | GGB | 10672.2 | GGB | 9.77 | GGB | 993.26 | GGB | 62.98 | GGB | 167648.56 | GGB | 133567.27 | GGB | 0 | 0 | 3111 | 3600 | 3095.01 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 197648.98 | GGB | 197651.29 | 3095.01 | 2829.4956 |  |  |  | 0 | 1 | [14 empty] | 114.8311 | 2829.4956 |  | 104.98
10.04.2008 21:00 | 3600 | 2 | 760.25 | GGB | 761.538 | 771.234 | 765.934 | 264.74 | GGB | 10767 | GGB | 9.78 | GGB | 994 | GGB | 62.2 | GGB | 170050.6 | GGB | 135896.8 | GGB | 0 | 0 | 3144 | 3600 | 3128.15 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 197689.01 | GGB | 197691.31 | 3128.15 | 2780.9926 |  |  |  | 0 | 1 | [14 empty] | 118.0849 | 2780.9926 |  | 104.98
10.04.2008 22:00 | 3600 | 2 | 760.03 | GGB | 760.44 | 770.32 | 765.934 | 265.46 | GGB | 10808.6 | GGB | 9.78 | GGB | 994.21 | GGB | 61.75 | GGB | 171282.98 | GGB | 137094.63 | GGB | 0 | 0 | 3166 | 3600 | 3149.9 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 197728.6 | GGB | 197730.91 | 3149.9 | 2756.6944 |  |  |  | 0 | 1 | [14 empty] | 119.954 | 2756.6944 |  | 104.98
10.04.2008 23:00 | 3600 | 2 | 760.25 | GGB | 761.538 | 771.375 | 765.934 | 265.93 | GGB | 10851.3 | GGB | 9.79 | GGB | 994.49 | GGB | 61.22 | GGB | 172110.43 | GGB | 138017.28 | GGB | 0 | 0 | 3165 | 3600 | 3149.07 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 197768.27 | GGB | 197770.58 | 3149.07 | 2738.2658 |  |  |  | 0 | 1 | [14 empty] | 120.7295 | 2738.2658 |  | 104.98
10.04.2008 24:00 | 3600 | 2 | 759.13 | GGB | 760.44 | 768.914 | 764.469 | 267.76 | GGB | 10850.9 | GGB | 9.76 | GGB | 995.17 | GGB | 60.47 | GGB | 174253.89 | GGB | 140145.76 | GGB | 0 | 0 | 3226 | 3600 | 3209.87 | GGB | 100 | GGB | 41.17 | GGB | 41.17 | GGB | 197809.43 | GGB | 197811.75 | 3209.87 | 2696.6781 |  |  |  | 0 | 1 | [14 empty] | 124.9582 | 2696.6781 |  | 104.98
11.04.2008 01:00 | 3600 | 2 | 760.53 | GGB | 760.44 | 770.063 | 764.835 | 266.92 | GGB | 10918 | GGB | 9.8 | GGB | 995.76 | GGB | 60.65 | GGB | 173297.69 | GGB | 139383.03 | GGB | 0 | 0 | 3173 | 3600 | 3157.04 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 197850.52 | GGB | 197852.84 | 3157.04 | 2711.4348 |  |  |  | 0 | 1 | [14 empty] | 122.2327 | 2711.4348 |  | 104.98
11.04.2008 02:00 | 3600 | 2 | 759.52 | GGB | 760.44 | 769.383 | 764.835 | 267.51 | GGB | 10936.3 | GGB | 9.78 | GGB | 996.64 | GGB | 60.15 | GGB | 174457.45 | GGB | 140652.05 | GGB | 0 | 0 | 3226 | 3600 | 3210.2 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 197890.39 | GGB | 197892.71 | 3210.2 | 2686.9711 |  |  |  | 0 | 1 | [14 empty] | 125.4226 | 2686.9711 |  | 104.98
11.04.2008 03:00 | 3600 | 2 | 759.03 | GGB | 758.974 | 767.883 | 763.37 | 269.08 | GGB | 10983.5 | GGB | 9.77 | GGB | 998.22 | GGB | 59.61 | GGB | 176071.65 | GGB | 142406.82 | GGB | 0 | 0 | 3279 | 3600 | 3263.01 | GGB | 100 | GGB | 41.36 | GGB | 41.36 | GGB | 197931.75 | GGB | 197934.07 | 3263.01 | 2653.8617 |  |  |  | 0 | 1 | [14 empty] | 129.0764 | 2653.8617 |  | 104.98
11.04.2008 04:00 | 3600 | 2 | 759.52 | GGB | 759.341 | 767.625 | 763.37 | 269.6 | GGB | 11024.8 | GGB | 9.79 | GGB | 999.18 | GGB | 59.66 | GGB | 176580 | GGB | 142936.82 | GGB | 0 | 0 | 3268 | 3600 | 3252.34 | GGB | 100 | GGB | 41.39 | GGB | 41.39 | GGB | 197973.14 | GGB | 197975.46 | 3252.34 | 2644.0213 |  |  |  | 0 | 1 | [14 empty] | 129.1331 | 2644.0213 |  | 104.98
11.04.2008 05:00 | 3600 | 2 | 759.32 | GGB | 761.538 | 770.953 | 767.033 | 269.97 | GGB | 11042 | GGB | 9.78 | GGB | 999.38 | GGB | 59.35 | GGB | 177149.98 | GGB | 143560.75 | GGB | 0 | 0 | 3301 | 3600 | 3285.32 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 198013.39 | GGB | 198015.7 | 3285.32 | 2632.5301 |  |  |  | 0 | 1 | [14 empty] | 131.0119 | 2632.5301 |  | 104.98
11.04.2008 06:00 | 3600 | 2 | 759.5 | GGB | 759.341 | 768.492 | 763.37 | 269.86 | GGB | 11047.8 | GGB | 9.79 | GGB | 999.87 | GGB | 59.4 | GGB | 176997.03 | GGB | 143482.74 | GGB | 0 | 0 | 3281 | 3600 | 3265.1 | GGB | 100 | GGB | 41.53 | GGB | 41.53 | GGB | 198054.91 | GGB | 198057.23 | 3265.1 | 2633.9614 |  |  |  | 0 | 1 | [14 empty] | 130.1349 | 2633.9614 |  | 104.98
11.04.2008 07:00 | 3600 | 2 | 759.46 | GGB | 760.44 | 768.375 | 764.469 | 269.74 | GGB | 11049.8 | GGB | 9.78 | GGB | 1000.91 | GGB | 59.22 | GGB | 176923.31 | GGB | 143652.2 | GGB | 0 | 0 | 3283 | 3600 | 3267.05 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 198095.28 | GGB | 198097.6 | 3267.05 | 2630.8542 |  |  |  | 0 | 1 | [14 empty] | 130.3664 | 2630.8542 |  | 104.98
11.04.2008 08:00 | 3600 | 2 | 759.26 | GGB | 761.538 | 770.18 | 765.934 | 270.3 | GGB | 11063.1 | GGB | 9.79 | GGB | 1001.5 | GGB | 59.19 | GGB | 177233.6 | GGB | 144001.02 | GGB | 0 | 0 | 3304 | 3600 | 3288.06 | GGB | 100 | GGB | 41.81 | GGB | 41.81 | GGB | 198137.09 | GGB | 198139.41 | 3288.06 | 2624.4814 |  |  |  | 0 | 1 | [14 empty] | 131.5233 | 2624.4814 |  | 104.98
11.04.2008 09:00 | 3600 | 2 | 759.66 | GGB | 760.44 | 770.602 | 764.835 | 270.13 | GGB | 11065.4 | GGB | 9.79 | GGB | 1002.26 | GGB | 59.32 | GGB | 177160.98 | GGB | 143994.43 | GGB | 0 | 0 | 3291 | 3207 | 3274.98 | GGB | 100 | GGB | 41.83 | GGB | 41.83 | GGB | 198178.91 | GGB | 198181.24 | 3274.98 | 2624.6015 |  |  |  | 0 | 1 | [14 empty] | 130.9941 | 2624.6015 |  | 104.98
11.04.2008 10:00 | 3600 | 2 | 759.49 | GGB | 762.637 | 771.797 | 767.033 | 271.95 | GGB | 11020.7 | GGB | 9.78 | GGB | 1002.78 | GGB | 58.78 | GGB | 179192.2 | GGB | 145957.33 | GGB | 0 | 0 | 3287 | 3600 | 3270.83 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 198219.58 | GGB | 198221.91 | 3270.83 | 2589.3047 |  |  |  | 0 | 1 | [14 empty] | 132.6116 | 2589.3047 |  | 104.98
11.04.2008 11:00 | 3600 | 2 | 759.12 | GGB | 758.974 | 768.961 | 764.469 | 272.85 | GGB | 11027.8 | GGB | 9.77 | GGB | 1003.16 | GGB | 58.73 | GGB | 179987.75 | GGB | 146683.15 | GGB | 0 | 0 | 3297 | 3600 | 3281.38 | GGB | 100 | GGB | 41.82 | GGB | 41.82 | GGB | 198261.4 | GGB | 198263.73 | 3281.38 | 2576.4923 |  |  |  | 0 | 1 | [14 empty] | 133.7009 | 2576.4923 |  | 104.98
11.04.2008 12:00 | 3600 | 2 | 759.75 | GGB | 760.44 | 769.008 | 764.469 | 272.78 | GGB | 11051.4 | GGB | 9.79 | GGB | 1003.53 | GGB | 58.82 | GGB | 179987.75 | GGB | 146696.93 | GGB | 0 | 0 | 3263 | 3600 | 3247.09 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 198301.89 | GGB | 198304.22 | 3247.09 | 2576.2502 |  |  |  | 0 | 1 | [14 empty] | 132.3161 | 2576.2502 |  | 104.98
11.04.2008 13:00 | 3600 | 2 | 760.37 | GGB | 762.637 | 771.914 | 767.033 | 271.86 | GGB | 11038 | GGB | 9.79 | GGB | 1003.79 | GGB | 59.19 | GGB | 178703.65 | GGB | 145527.44 | GGB | 0 | 0 | 3239 | 3600 | 3222.66 | GGB | 100 | GGB | 41.55 | GGB | 41.55 | GGB | 198343.43 | GGB | 198345.77 | 3222.66 | 2596.9535 |  |  |  | 0 | 1 | [14 empty] | 130.2737 | 2596.9535 |  | 104.98
11.04.2008 14:00 | 3600 | 2 | 760.75 | GGB | 760.44 | 770.063 | 764.835 | 271.49 | GGB | 11029.6 | GGB | 9.79 | GGB | 1003.78 | GGB | 59.23 | GGB | 178413.16 | GGB | 145270.46 | GGB | 0 | 0 | 3205 | 3600 | 3189.58 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 198383.58 | GGB | 198385.92 | 3189.58 | 2601.5475 |  |  |  | 0 | 1 | [14 empty] | 128.7088 | 2601.5475 |  | 104.98
11.04.2008 15:00 | 3600 | 2 | 760.62 | GGB | 761.538 | 771.211 | 765.934 | 270 | GGB | 11049.6 | GGB | 9.79 | GGB | 1004.22 | GGB | 59.86 | GGB | 176397.35 | GGB | 143420.05 | GGB | 0 | 0 | 3219 | 3600 | 3203.32 | GGB | 100 | GGB | 41.2 | GGB | 41.2 | GGB | 198424.78 | GGB | 198427.12 | 3203.32 | 2635.1127 |  |  |  | 0 | 1 | [14 empty] | 127.6168 | 2635.1127 |  | 104.98
11.04.2008 16:00 | 3600 | 2 | 760.68 | GGB | 761.538 | 771.188 | 765.934 | 269.8 | GGB | 11030.1 | GGB | 9.79 | GGB | 1004.49 | GGB | 60.08 | GGB | 175993.52 | GGB | 143038.03 | GGB | 0 | 0 | 3217 | 3600 | 3200.69 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 198464.82 | GGB | 198467.16 | 3200.69 | 2642.1505 |  |  |  | 0 | 1 | [14 empty] | 127.1723 | 2642.1505 |  | 104.98
11.04.2008 17:00 | 3600 | 2 | 760.55 | GGB | 762.637 | 772.242 | 767.033 | 269.78 | GGB | 11025.9 | GGB | 9.79 | GGB | 1004.58 | GGB | 60.18 | GGB | 175880.19 | GGB | 142913.07 | GGB | 0 | 0 | 3218 | 3600 | 3201.66 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 198504.95 | GGB | 198507.29 | 3201.66 | 2644.4607 |  |  |  | 0 | 1 | [14 empty] | 127.0997 | 2644.4607 |  | 104.98
11.04.2008 18:00 | 3600 | 2 | 760.54 | GGB | 761.538 | 771.398 | 765.934 | 269.76 | GGB | 11019.9 | GGB | 9.79 | GGB | 1004.18 | GGB | 60.23 | GGB | 175697.53 | GGB | 142688.28 | GGB | 0 | 0 | 3211 | 3600 | 3195.29 | GGB | 100 | GGB | 41.53 | GGB | 41.53 | GGB | 198546.48 | GGB | 198548.82 | 3195.29 | 2648.6268 |  |  |  | 0 | 1 | [14 empty] | 126.6473 | 2648.6268 |  | 104.98
11.04.2008 19:00 | 3600 | 2 | 759.86 | GGB | 761.538 | 771.352 | 767.033 | 271.72 | GGB | 10970 | GGB | 9.77 | GGB | 1004.02 | GGB | 59.56 | GGB | 178077.56 | GGB | 144888.3 | GGB | 0 | 0 | 3231 | 3600 | 3215.28 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 198587.14 | GGB | 198589.49 | 3215.28 | 2608.4094 |  |  |  | 0 | 1 | [14 empty] | 129.4046 | 2608.4094 |  | 104.98
11.04.2008 20:00 | 3600 | 2 | 761.14 | GGB | 761.538 | 771.633 | 765.934 | 270.55 | GGB | 11025.9 | GGB | 9.8 | GGB | 1003.78 | GGB | 60.13 | GGB | 176483.17 | GGB | 143309.85 | GGB | 0 | 0 | 3173 | 3600 | 3157.23 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 198627.59 | GGB | 198629.93 | 3157.23 | 2637.139 |  |  |  | 0 | 1 | [14 empty] | 125.6839 | 2637.139 |  | 104.98
11.04.2008 21:00 | 3600 | 2 | 760.25 | GGB | 761.538 | 770.906 | 767.033 | 270.21 | GGB | 11020.3 | GGB | 9.78 | GGB | 1003.75 | GGB | 60.34 | GGB | 176246.6 | GGB | 143026.9 | GGB | 0 | 0 | 3230 | 3600 | 3213.87 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 198668.04 | GGB | 198670.38 | 3213.87 | 2642.3561 |  |  |  | 0 | 1 | [14 empty] | 127.6861 | 2642.3561 |  | 104.98
11.04.2008 22:00 | 3600 | 2 | 760.62 | GGB | 759.341 | 769.125 | 764.835 | 269.69 | GGB | 11041.4 | GGB | 9.79 | GGB | 1003.67 | GGB | 60.06 | GGB | 176456.76 | GGB | 143304.09 | GGB | 0 | 0 | 3209 | 3600 | 3193.65 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 198708.47 | GGB | 198710.81 | 3193.65 | 2637.245 |  |  |  | 0 | 1 | [14 empty] | 127.1286 | 2637.245 |  | 104.98
11.04.2008 23:00 | 3600 | 2 | 759.99 | GGB | 759.341 | 769.266 | 764.835 | 270.24 | GGB | 11023.9 | GGB | 9.78 | GGB | 1003.44 | GGB | 60.24 | GGB | 176347.83 | GGB | 143106.52 | GGB | 0 | 0 | 3251 | 3600 | 3234.87 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 198748.85 | GGB | 198751.2 | 3234.87 | 2640.886 |  |  |  | 0 | 1 | [14 empty] | 128.5919 | 2640.886 |  | 104.98
11.04.2008 24:00 | 3600 | 2 | 760.51 | GGB | 761.538 | 771.914 | 767.033 | 269.94 | GGB | 11033.2 | GGB | 9.79 | GGB | 1003.83 | GGB | 60.48 | GGB | 176177.28 | GGB | 142920.48 | GGB | 0 | 0 | 3226 | 3600 | 3210.59 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 198789.33 | GGB | 198791.68 | 3210.59 | 2644.3236 |  |  |  | 0 | 1 | [14 empty] | 127.4609 | 2644.3236 |  | 104.98
12.04.2008 01:00 | 3600 | 2 | 760.81 | GGB | 763.004 | 772.313 | 768.132 | 269.85 | GGB | 11028.6 | GGB | 9.79 | GGB | 1003.13 | GGB | 60.32 | GGB | 176074.95 | GGB | 142807.01 | GGB | 0 | 0 | 3217 | 3600 | 3201.18 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 198829.76 | GGB | 198832.11 | 3201.18 | 2646.4247 |  |  |  | 0 | 1 | [14 empty] | 126.9864 | 2646.4247 |  | 104.98
12.04.2008 02:00 | 3600 | 2 | 760.43 | GGB | 760.44 | 770.414 | 764.835 | 268.71 | GGB | 11005.7 | GGB | 9.79 | GGB | 1002.2 | GGB | 59.78 | GGB | 175504.97 | GGB | 142442.79 | GGB | 0 | 0 | 3212 | 3600 | 3196.08 | GGB | 100 | GGB | 41.34 | GGB | 41.34 | GGB | 198871.1 | GGB | 198873.45 | 3196.08 | 2653.1915 |  |  |  | 0 | 1 | [14 empty] | 126.4607 | 2653.1915 |  | 104.98
12.04.2008 03:00 | 3600 | 2 | 760.51 | GGB | 760.44 | 770.484 | 765.934 | 268.35 | GGB | 10986.5 | GGB | 9.79 | GGB | 1002.05 | GGB | 60.47 | GGB | 174762.24 | GGB | 141527 | GGB | 0 | 0 | 3203 | 3600 | 3186.95 | GGB | 100 | GGB | 41.09 | GGB | 41.09 | GGB | 198912.19 | GGB | 198914.54 | 3186.95 | 2670.3597 |  |  |  | 0 | 1 | [14 empty] | 125.2887 | 2670.3597 |  | 104.98
12.04.2008 04:00 | 3600 | 2 | 760.34 | GGB | 761.538 | 771.516 | 767.033 | 268.41 | GGB | 10974.2 | GGB | 9.79 | GGB | 1001.58 | GGB | 60.33 | GGB | 174629.1 | GGB | 141409.89 | GGB | 0 | 0 | 3213 | 3600 | 3197.03 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 198952.14 | GGB | 198954.5 | 3197.03 | 2672.5712 |  |  |  | 0 | 1 | [14 empty] | 125.581 | 2672.5712 |  | 104.98
12.04.2008 05:00 | 3600 | 2 | 760.44 | GGB | 761.538 | 770.367 | 765.934 | 268.01 | GGB | 10951.7 | GGB | 9.79 | GGB | 1001.14 | GGB | 60.6 | GGB | 174208.77 | GGB | 140896.31 | GGB | 0 | 0 | 3199 | 3600 | 3183.31 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 198992.08 | GGB | 198994.44 | 3183.31 | 2682.313 |  |  |  | 0 | 1 | [14 empty] | 124.588 | 2682.313 |  | 104.98
12.04.2008 06:00 | 3600 | 2 | 760.7 | GGB | 761.538 | 771.398 | 765.934 | 267.06 | GGB | 10944.3 | GGB | 9.8 | GGB | 1000.15 | GGB | 60.09 | GGB | 173314.2 | GGB | 140246.05 | GGB | 0 | 0 | 3169 | 3600 | 3153.52 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 199031.97 | GGB | 199034.33 | 3153.52 | 2694.7497 |  |  |  | 0 | 1 | [14 empty] | 122.8524 | 2694.7497 |  | 104.98
12.04.2008 07:00 | 3600 | 2 | 760.78 | GGB | 761.538 | 772.477 | 767.033 | 266.21 | GGB | 10902.7 | GGB | 9.8 | GGB | 999.76 | GGB | 60.84 | GGB | 172404.22 | GGB | 139139.56 | GGB | 0 | 0 | 3154 | 3600 | 3137.92 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 199072.08 | GGB | 199074.45 | 3137.92 | 2716.1794 |  |  |  | 0 | 1 | [14 empty] | 121.2802 | 2716.1794 |  | 104.98
12.04.2008 08:00 | 3600 | 2 | 760.66 | GGB | 762.637 | 771.445 | 767.033 | 265.4 | GGB | 10871.8 | GGB | 9.79 | GGB | 999.17 | GGB | 60.79 | GGB | 171565.76 | GGB | 138404.53 | GGB | 0 | 0 | 3150 | 3600 | 3133.75 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 199111.68 | GGB | 199114.04 | 3133.75 | 2730.6043 |  |  |  | 0 | 1 | [14 empty] | 120.4792 | 2730.6043 |  | 104.98
12.04.2008 09:00 | 3600 | 2 | 760.85 | GGB | 762.637 | 772.688 | 768.132 | 265.39 | GGB | 10855.4 | GGB | 9.79 | GGB | 999.26 | GGB | 61.41 | GGB | 171046.4 | GGB | 137741.39 | GGB | 0 | 0 | 3142 | 3600 | 3125.79 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 199151.56 | GGB | 199153.92 | 3125.79 | 2743.7504 |  |  |  | 0 | 1 | [14 empty] | 119.5974 | 2743.7504 |  | 104.98
12.04.2008 10:00 | 3600 | 2 | 761.38 | GGB | 763.004 | 772.922 | 768.132 | 264.06 | GGB | 10809.9 | GGB | 9.8 | GGB | 998.92 | GGB | 62.07 | GGB | 169416.8 | GGB | 136113.41 | GGB | 0 | 0 | 3101 | 3600 | 3084.94 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 199191.22 | GGB | 199193.58 | 3084.94 | 2776.567 |  |  |  | 0 | 1 | [14 empty] | 116.6394 | 2776.567 |  | 104.98
12.04.2008 11:00 | 3600 | 2 | 761.65 | GGB | 763.004 | 772.992 | 768.132 | 262.46 | GGB | 10750.1 | GGB | 9.8 | GGB | 998.1 | GGB | 62.58 | GGB | 167372.38 | GGB | 134156.45 | GGB | 0 | 0 | 3060 | 3600 | 3044.04 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 199230.6 | GGB | 199232.96 | 3044.04 | 2817.0692 |  |  |  | 0 | 1 | [14 empty] | 113.4382 | 2817.0692 |  | 104.98
12.04.2008 12:00 | 3600 | 2 | 761.36 | GGB | 761.538 | 771.797 | 767.033 | 261.12 | GGB | 10674.6 | GGB | 9.79 | GGB | 998.27 | GGB | 63.17 | GGB | 165736.17 | GGB | 132636.8 | GGB | 0 | 0 | 3056 | 3600 | 3039.85 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 199270.44 | GGB | 199272.8 | 3039.85 | 2849.345 |  |  |  | 0 | 1 | [14 empty] | 111.9989 | 2849.345 |  | 104.98
12.04.2008 13:00 | 3600 | 2 | 761.59 | GGB | 762.637 | 772.898 | 768.132 | 260.66 | GGB | 10640 | GGB | 9.79 | GGB | 998.07 | GGB | 63.46 | GGB | 164810.79 | GGB | 131754.23 | GGB | 0 | 0 | 3031 | 3600 | 3015.21 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 199310.75 | GGB | 199313.11 | 3015.21 | 2868.4316 |  |  |  | 0 | 1 | [14 empty] | 110.3519 | 2868.4316 |  | 104.98
12.04.2008 14:00 | 3600 | 2 | 761.45 | GGB | 764.102 | 774.305 | 768.132 | 259.88 | GGB | 10601.1 | GGB | 9.79 | GGB | 997.85 | GGB | 63.96 | GGB | 164194.6 | GGB | 131039.25 | GGB | 0 | 0 | 3042 | 3600 | 3026.41 | GGB | 100 | GGB | 38.84 | GGB | 38.84 | GGB | 199349.59 | GGB | 199351.95 | 3026.41 | 2884.0824 |  |  |  | 1 | 1 |  |  |  |  | 131039.25 | 2884.0824 | 131039.25 | 2884.0824 | 9.7304 | [5 empty] | 110.1607 | 2884.0824 |  | 104.98
12.04.2008 15:00 | 3600 | 2 | 763.59 | GGB | 764.102 | 774.234 | 768.498 | 259.14 | GGB | 10635.3 | GGB | 9.82 | GGB | 997.68 | GGB | 63.94 | GGB | 163847.99 | GGB | 130747.55 | GGB | 0 | 0 | 2958 | 3600 | 2942.42 | GGB | 100 | GGB | 37.89 | GGB | 37.89 | GGB | 199387.49 | GGB | 199389.84 | 2942.42 | 2890.5169 |  |  |  | 1 | 1 |  |  |  |  | 130747.55 | 2890.5169 | 130747.55 | 2890.5169 | 9.9743 | [5 empty] | 106.8651 | 2890.5169 |  | 104.98
12.04.2008 16:00 | 3600 | 2 | 763.25 | GGB | 764.102 | 774.422 | 768.498 | 258.52 | GGB | 10607.5 | GGB | 9.81 | GGB | 997.02 | GGB | 63.81 | GGB | 163413.36 | GGB | 130365.78 | GGB | 0 | 0 | 2961 | 3600 | 2945.18 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 199426.82 | GGB | 199429.17 | 2945.18 | 2898.9816 |  |  |  | 1 | 1 |  |  |  |  | 130365.78 | 2898.9816 | 130365.78 | 2898.9816 | 9.6092 | [5 empty] | 106.653 | 2898.9816 |  | 104.98
12.04.2008 17:00 | 3600 | 2 | 762.78 | GGB | 763.004 | 773.344 | 767.033 | 258.53 | GGB | 10605.5 | GGB | 9.8 | GGB | 996.68 | GGB | 63.78 | GGB | 163467.28 | GGB | 130374.92 | GGB | 0 | 0 | 2969 | 3600 | 2953.31 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 199466.97 | GGB | 199469.32 | 2953.31 | 2898.7784 |  |  |  | 0 | 1 | [14 empty] | 106.9549 | 2898.7784 |  | 104.98
12.04.2008 18:00 | 3600 | 2 | 763.2 | GGB | 764.102 | 774.422 | 768.132 | 258.6 | GGB | 10614.9 | GGB | 9.81 | GGB | 996.28 | GGB | 63.57 | GGB | 163706.05 | GGB | 130592.72 | GGB | 0 | 0 | 2956 | 3600 | 2939.98 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 199507.94 | GGB | 199510.29 | 2939.98 | 2893.9439 |  |  |  | 1 | 1 |  |  |  |  | 130592.72 | 2893.9439 | 130592.72 | 2893.9439 | 9.2245 | [5 empty] | 106.65 | 2893.9439 |  | 104.98
12.04.2008 19:00 | 3600 | 2 | 763.19 | GGB | 763.004 | 774.375 | 768.132 | 258.79 | GGB | 10615 | GGB | 9.81 | GGB | 996.4 | GGB | 63.65 | GGB | 164063.66 | GGB | 130865.25 | GGB | 0 | 0 | 2968 | 3600 | 2951.91 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 199547.08 | GGB | 199549.44 | 2951.91 | 2887.9172 |  |  |  | 0 | 1 | [14 empty] | 107.3062 | 2887.9172 |  | 104.98
12.04.2008 20:00 | 3600 | 2 | 762.63 | GGB | 762.637 | 773.227 | 768.132 | 258.84 | GGB | 10620.6 | GGB | 9.8 | GGB | 996.74 | GGB | 63.56 | GGB | 164118.68 | GGB | 130988.19 | GGB | 0 | 0 | 2973 | 3600 | 2957.11 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 199586.51 | GGB | 199588.87 | 2957.11 | 2885.2067 |  |  |  | 0 | 1 | [14 empty] | 107.5962 | 2885.2067 |  | 104.98
12.04.2008 21:00 | 3600 | 2 | 762.63 | GGB | 763.004 | 773.227 | 768.132 | 259.12 | GGB | 10632.7 | GGB | 9.81 | GGB | 996.83 | GGB | 63.47 | GGB | 164324.44 | GGB | 131199.4 | GGB | 0 | 0 | 2975 | 3600 | 2959.68 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 199625.95 | GGB | 199628.31 | 2959.68 | 2880.562 |  |  |  | 0 | 1 | [14 empty] | 107.8634 | 2880.562 |  | 104.98
12.04.2008 22:00 | 3600 | 2 | 762.68 | GGB | 763.004 | 774.258 | 768.864 | 259.13 | GGB | 10642.4 | GGB | 9.81 | GGB | 996.4 | GGB | 63.32 | GGB | 164433.37 | GGB | 131287.58 | GGB | 0 | 0 | 2973 | 3600 | 2956.88 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 199665.42 | GGB | 199667.77 | 2956.88 | 2878.6272 |  |  |  | 0 | 1 | [14 empty] | 107.8338 | 2878.6272 |  | 104.98
12.04.2008 23:00 | 3600 | 2 | 762.52 | GGB | 763.004 | 774.375 | 768.864 | 258.47 | GGB | 10655.5 | GGB | 9.81 | GGB | 996.38 | GGB | 63.13 | GGB | 164786.58 | GGB | 131642.6 | GGB | 0 | 0 | 2972 | 3600 | 2956.3 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 199704.83 | GGB | 199707.19 | 2956.3 | 2870.864 |  |  |  | 0 | 1 | [14 empty] | 108.1042 | 2870.864 |  | 104.98
12.04.2008 24:00 | 3600 | 2 | 761.98 | GGB | 762.637 | 773.227 | 768.864 | 258.8 | GGB | 10634.1 | GGB | 9.8 | GGB | 996.05 | GGB | 63.15 | GGB | 164477.39 | GGB | 131342.92 | GGB | 0 | 0 | 2992 | 3600 | 2976.77 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 199744.17 | GGB | 199746.53 | 2976.77 | 2877.4143 |  |  |  | 0 | 1 | [14 empty] | 108.6049 | 2877.4143 |  | 104.98
13.04.2008 01:00 | 3600 | 2 | 762.29 | GGB | 763.004 | 774.258 | 768.864 | 258.93 | GGB | 10645.7 | GGB | 9.81 | GGB | 995.91 | GGB | 63.13 | GGB | 164410.27 | GGB | 131280.75 | GGB | 0 | 0 | 2989 | 3600 | 2973.66 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 199783.51 | GGB | 199785.87 | 2973.66 | 2878.777 |  |  |  | 0 | 1 | [14 empty] | 108.4401 | 2878.777 |  | 104.98
13.04.2008 02:00 | 3600 | 2 | 762.11 | GGB | 764.102 | 774.352 | 768.864 | 259.09 | GGB | 10655 | GGB | 9.81 | GGB | 995.73 | GGB | 62.82 | GGB | 164642.44 | GGB | 131561.9 | GGB | 0 | 0 | 3007 | 3600 | 2991.5 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 199822.87 | GGB | 199825.23 | 2991.5 | 2872.625 |  |  |  | 1 | 1 |  |  |  |  | 131561.9 | 2872.625 | 131561.9 | 2872.625 | 9.6018 | [5 empty] | 109.3243 | 2872.625 |  | 104.98
13.04.2008 03:00 | 3600 | 2 | 761.16 | GGB | 761.538 | 772.125 | 766.3 | 260.16 | GGB | 10660.5 | GGB | 9.78 | GGB | 995.66 | GGB | 62.6 | GGB | 165540.31 | GGB | 132356.84 | GGB | 0 | 0 | 3046 | 3600 | 3030.06 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 199862.21 | GGB | 199864.58 | 3030.06 | 2855.3719 |  |  |  | 0 | 1 | [14 empty] | 111.4025 | 2855.3719 |  | 104.98
13.04.2008 04:00 | 3600 | 2 | 760.41 | GGB | 762.637 | 771.984 | 767.766 | 263.95 | GGB | 10792.7 | GGB | 9.78 | GGB | 996.4 | GGB | 61.41 | GGB | 170141.93 | GGB | 136620.7 | GGB | 0 | 0 | 3134 | 3600 | 3117.76 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 199901.78 | GGB | 199904.15 | 3117.76 | 2766.2572 |  |  |  | 0 | 1 | [14 empty] | 118.3196 | 2766.2572 |  | 104.98
13.04.2008 05:00 | 3600 | 2 | 760.91 | GGB | 762.637 | 771.75 | 767.766 | 264.89 | GGB | 10890.6 | GGB | 9.8 | GGB | 997.02 | GGB | 60.71 | GGB | 171962.98 | GGB | 138461.66 | GGB | 0 | 0 | 3126 | 3600 | 3110.17 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 199941.01 | GGB | 199943.39 | 3110.17 | 2729.4776 |  |  |  | 0 | 1 | [14 empty] | 119.622 | 2729.4776 |  | 104.98
13.04.2008 06:00 | 3600 | 2 | 760.55 | GGB | 761.538 | 770.648 | 765.201 | 265.86 | GGB | 10942 | GGB | 9.8 | GGB | 997.2 | GGB | 59.86 | GGB | 173740.03 | GGB | 140272.2 | GGB | 0 | 0 | 3153 | 3600 | 3137 | GGB | 100 | GGB | 37.88 | GGB | 37.88 | GGB | 199978.89 | GGB | 199981.27 | 3137 | 2694.2473 |  |  |  | 0 | 1 | [14 empty] | 122.2316 | 2694.2473 |  | 104.98
13.04.2008 07:00 | 3600 | 2 | 760.44 | GGB | 760.44 | 769.711 | 765.201 | 266.3 | GGB | 10975.8 | GGB | 9.8 | GGB | 997.88 | GGB | 59.44 | GGB | 174517.97 | GGB | 141177.72 | GGB | 0 | 0 | 3173 | 3600 | 3157.41 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 200017 | GGB | 200019.38 | 3157.41 | 2676.9663 |  |  |  | 0 | 1 | [14 empty] | 123.8211 | 2676.9663 |  | 104.98
13.04.2008 08:00 | 3600 | 2 | 760.44 | GGB | 760.44 | 769.805 | 765.201 | 266.87 | GGB | 11002.8 | GGB | 9.8 | GGB | 998.44 | GGB | 59.32 | GGB | 175059.33 | GGB | 141744.04 | GGB | 0 | 0 | 3183 | 3600 | 3166.72 | GGB | 100 | GGB | 42.08 | GGB | 42.08 | GGB | 200059.08 | GGB | 200061.46 | 3166.72 | 2666.2708 |  |  |  | 0 | 1 | [14 empty] | 124.6844 | 2666.2708 |  | 104.98
13.04.2008 09:00 | 3600 | 2 | 760.57 | GGB | 761.538 | 771.047 | 765.201 | 266.96 | GGB | 11014.7 | GGB | 9.81 | GGB | 998.73 | GGB | 59.16 | GGB | 175184.77 | GGB | 141954.64 | GGB | 0 | 0 | 3188 | 3600 | 3172.35 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 200099.13 | GGB | 200101.52 | 3172.35 | 2662.3152 |  |  |  | 0 | 1 | [14 empty] | 125.0916 | 2662.3152 |  | 104.98
13.04.2008 10:00 | 3600 | 2 | 760.36 | GGB | 760.44 | 770.109 | 764.102 | 266.89 | GGB | 11022.5 | GGB | 9.8 | GGB | 998.88 | GGB | 58.93 | GGB | 175376.23 | GGB | 142229.51 | GGB | 0 | 0 | 3195 | 3600 | 3179.59 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 200139.19 | GGB | 200141.57 | 3179.59 | 2657.1701 |  |  |  | 0 | 1 | [14 empty] | 125.6199 | 2657.1701 |  | 104.98
13.04.2008 11:00 | 3600 | 2 | 760.34 | GGB | 761.538 | 771 | 765.201 | 267.02 | GGB | 11032.3 | GGB | 9.81 | GGB | 999.84 | GGB | 58.89 | GGB | 175500.57 | GGB | 142486.17 | GGB | 0 | 0 | 3204 | 3600 | 3188.62 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 200179.69 | GGB | 200182.07 | 3188.62 | 2652.3837 |  |  |  | 0 | 1 | [14 empty] | 126.204 | 2652.3837 |  | 104.98
13.04.2008 12:00 | 3600 | 2 | 760.07 | GGB | 760.44 | 770.063 | 765.201 | 267.27 | GGB | 11040.3 | GGB | 9.8 | GGB | 1000.58 | GGB | 58.76 | GGB | 175868.08 | GGB | 142943.27 | GGB | 0 | 0 | 3224 | 3600 | 3208.16 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 200220.32 | GGB | 200222.7 | 3208.16 | 2643.902 |  |  |  | 0 | 1 | [14 empty] | 127.3847 | 2643.902 |  | 104.98
13.04.2008 13:00 | 3600 | 2 | 760.36 | GGB | 760.44 | 769.969 | 765.201 | 267.49 | GGB | 11055.7 | GGB | 9.81 | GGB | 1000.44 | GGB | 58.64 | GGB | 176162.97 | GGB | 143217.69 | GGB | 0 | 0 | 3215 | 3600 | 3198.84 | GGB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 200260.95 | GGB | 200263.34 | 3198.84 | 2638.836 |  |  |  | 0 | 1 | [14 empty] | 127.2585 | 2638.836 |  | 104.98
13.04.2008 14:00 | 3600 | 2 | 760.25 | GGB | 761.538 | 771.023 | 766.3 | 267.66 | GGB | 11070.1 | GGB | 9.81 | GGB | 1000.81 | GGB | 58.42 | GGB | 176553.59 | GGB | 143683.57 | GGB | 0 | 0 | 3231 | 3600 | 3214.9 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 200301.58 | GGB | 200303.97 | 3214.9 | 2630.2799 |  |  |  | 0 | 1 | [14 empty] | 128.3134 | 2630.2799 |  | 104.98
13.04.2008 15:00 | 3600 | 2 | 760.1 | GGB | 760.44 | 769.734 | 765.201 | 268.7 | GGB | 11056.3 | GGB | 9.8 | GGB | 1001.21 | GGB | 58.36 | GGB | 176825.38 | GGB | 143989.31 | GGB | 0 | 0 | 3243 | 3600 | 3227.5 | GGB | 100 | GGB | 40.76 | GGB | 40.76 | GGB | 200342.34 | GGB | 200344.73 | 3227.5 | 2624.6948 |  |  |  | 0 | 1 | [14 empty] | 129.0904 | 2624.6948 |  | 104.98
13.04.2008 16:00 | 3600 | 2 | 760.44 | GGB | 761.538 | 771.867 | 766.667 | 270.54 | GGB | 11026.8 | GGB | 9.8 | GGB | 1001.88 | GGB | 58.03 | GGB | 178810.39 | GGB | 145846.37 | GGB | 0 | 0 | 3199 | 3600 | 3182.91 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 200383.01 | GGB | 200385.4 | 3182.91 | 2591.2746 |  |  |  | 0 | 1 | [14 empty] | 128.9489 | 2591.2746 |  | 104.98
13.04.2008 17:00 | 3600 | 2 | 761.17 | GGB | 761.538 | 770.719 | 766.3 | 269.51 | GGB | 11064.6 | GGB | 9.81 | GGB | 1002.34 | GGB | 58.52 | GGB | 177047.65 | GGB | 144262.16 | GGB | 0 | 0 | 3175 | 3600 | 3159.48 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 200424.3 | GGB | 200426.69 | 3159.48 | 2619.7306 |  |  |  | 0 | 1 | [14 empty] | 126.6093 | 2619.7306 |  | 104.98
13.04.2008 18:00 | 3600 | 2 | 760.59 | GGB | 761.538 | 770.344 | 765.201 | 269.43 | GGB | 11072.4 | GGB | 9.8 | GGB | 1003.01 | GGB | 58.81 | GGB | 176936.51 | GGB | 144143.28 | GGB | 0 | 0 | 3220 | 3600 | 3204.41 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 200464.45 | GGB | 200466.84 | 3204.41 | 2621.8912 |  |  |  | 0 | 1 | [14 empty] | 128.3039 | 2621.8912 |  | 104.98
13.04.2008 19:00 | 3600 | 2 | 760.83 | GGB | 762.637 | 771.352 | 766.667 | 269.34 | GGB | 11079 | GGB | 9.81 | GGB | 1003.58 | GGB | 58.9 | GGB | 176615.21 | GGB | 143921.9 | GGB | 0 | 0 | 3207 | 3600 | 3191.4 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 200504.97 | GGB | 200507.36 | 3191.4 | 2625.9242 |  |  |  | 0 | 1 | [14 empty] | 127.5868 | 2625.9242 |  | 104.98
13.04.2008 20:00 | 3600 | 2 | 760.62 | GGB | 761.538 | 771.352 | 766.3 | 269.61 | GGB | 11067.7 | GGB | 9.8 | GGB | 1004.44 | GGB | 59.02 | GGB | 176540.39 | GGB | 143933.11 | GGB | 0 | 0 | 3217 | 3600 | 3201.11 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 200545.88 | GGB | 200548.27 | 3201.11 | 2625.7197 |  |  |  | 0 | 1 | [14 empty] | 127.9849 | 2625.7197 |  | 104.98
13.04.2008 21:00 | 3600 | 2 | 760.7 | GGB | 761.538 | 770.695 | 765.201 | 270.08 | GGB | 11054.7 | GGB | 9.8 | GGB | 1004.96 | GGB | 59.3 | GGB | 176259.8 | GGB | 143655.5 | GGB | 0 | 0 | 3218 | 3600 | 3201.65 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 200586.73 | GGB | 200589.12 | 3201.65 | 2630.7938 |  |  |  | 0 | 1 | [14 empty] | 127.7596 | 2630.7938 |  | 104.98
13.04.2008 22:00 | 3600 | 2 | 760.96 | GGB | 761.538 | 770.555 | 765.201 | 270.52 | GGB | 11065 | GGB | 9.8 | GGB | 1005.55 | GGB | 59.43 | GGB | 176407.25 | GGB | 143805.11 | GGB | 0 | 0 | 3207 | 3600 | 3191.59 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 200627.4 | GGB | 200629.79 | 3191.59 | 2628.0568 |  |  |  | 0 | 1 | [14 empty] | 127.4908 | 2628.0568 |  | 104.98
13.04.2008 23:00 | 3600 | 2 | 760.87 | GGB | 761.538 | 771.633 | 766.667 | 270.83 | GGB | 11070.7 | GGB | 9.81 | GGB | 1005.7 | GGB | 59.34 | GGB | 176987.13 | GGB | 144337.75 | GGB | 0 | 0 | 3209 | 3600 | 3193.53 | GGB | 100 | GGB | 40.66 | GGB | 40.66 | GGB | 200668.06 | GGB | 200670.45 | 3193.53 | 2618.3587 |  |  |  | 0 | 1 | [14 empty] | 128.0408 | 2618.3587 |  | 104.98
13.04.2008 24:00 | 3600 | 2 | 761.13 | GGB | 760.44 | 770.367 | 764.835 | 271.25 | GGB | 11055.1 | GGB | 9.8 | GGB | 1006.14 | GGB | 59.64 | GGB | 176987.13 | GGB | 144272.22 | GGB | 0 | 0 | 3190 | 3600 | 3174.01 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 200708.36 | GGB | 200710.75 | 3174.01 | 2619.548 |  |  |  | 0 | 1 | [14 empty] | 127.2004 | 2619.548 |  | 104.98
14.04.2008 01:00 | 3600 | 2 | 761.55 | GGB | 764.102 | 773.672 | 768.132 | 272.13 | GGB | 11028.8 | GGB | 9.8 | GGB | 1006.69 | GGB | 59.26 | GGB | 178310.83 | GGB | 145595.13 | GGB | 0 | 0 | 3165 | 3600 | 3149.27 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 200747.5 | GGB | 200749.89 | 3149.27 | 2595.7462 |  |  |  | 1 | 1 |  |  |  |  | 145595.13 | 2595.7462 | 145595.13 | 2595.7462 | 9.6558 | [5 empty] | 127.3662 | 2595.7462 |  | 104.98
14.04.2008 02:00 | 3600 | 2 | 761.43 | GGB | 761.538 | 770.93 | 765.934 | 271.14 | GGB | 11068.6 | GGB | 9.8 | GGB | 1006.97 | GGB | 59.98 | GGB | 176676.83 | GGB | 143991.44 | GGB | 0 | 0 | 3193 | 3600 | 3176.89 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 200787.6 | GGB | 200789.99 | 3176.89 | 2624.656 |  |  |  | 0 | 1 | [14 empty] | 127.068 | 2624.656 |  | 104.98
14.04.2008 03:00 | 3600 | 2 | 760.7 | GGB | 761.538 | 770.906 | 765.934 | 272.45 | GGB | 11095.8 | GGB | 9.79 | GGB | 1007.41 | GGB | 59.66 | GGB | 177777.17 | GGB | 145087.81 | GGB | 0 | 0 | 3252 | 3600 | 3236.33 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 200829 | GGB | 200831.39 | 3236.33 | 2604.8226 |  |  |  | 0 | 1 | [14 empty] | 130.4311 | 2604.8226 |  | 104.98
14.04.2008 04:00 | 3600 | 2 | 760.77 | GGB | 760.44 | 770.086 | 764.835 | 273.55 | GGB | 11133.4 | GGB | 9.8 | GGB | 1007.92 | GGB | 59.37 | GGB | 178839 | GGB | 146155.82 | GGB | 0 | 0 | 3264 | 3600 | 3248.37 | GGB | 100 | GGB | 41.52 | GGB | 41.52 | GGB | 200870.53 | GGB | 200872.91 | 3248.37 | 2585.7882 |  |  |  | 0 | 1 | [14 empty] | 131.8801 | 2585.7882 |  | 104.98
14.04.2008 05:00 | 3600 | 2 | 760.94 | GGB | 762.637 | 771.328 | 765.934 | 274.31 | GGB | 11163.3 | GGB | 9.81 | GGB | 1008.51 | GGB | 59.29 | GGB | 179282.43 | GGB | 146639.39 | GGB | 0 | 0 | 3268 | 3600 | 3251.86 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 200911.3 | GGB | 200913.69 | 3251.86 | 2577.2611 |  |  |  | 0 | 1 | [14 empty] | 132.4585 | 2577.2611 |  | 104.98
14.04.2008 06:00 | 3600 | 2 | 760.88 | GGB | 761.538 | 770.297 | 765.934 | 274.35 | GGB | 11164.3 | GGB | 9.8 | GGB | 1009.27 | GGB | 59.35 | GGB | 179352.85 | GGB | 146782.42 | GGB | 0 | 0 | 3272 | 3600 | 3255.97 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 200951.63 | GGB | 200954.02 | 3255.97 | 2574.7498 |  |  |  | 0 | 1 | [14 empty] | 132.7553 | 2574.7498 |  | 104.98
14.04.2008 07:00 | 3600 | 2 | 760.75 | GGB | 762.271 | 771.398 | 767.033 | 275.33 | GGB | 11180 | GGB | 9.8 | GGB | 1009.88 | GGB | 59.52 | GGB | 180028.46 | GGB | 147350.92 | GGB | 0 | 0 | 3297 | 3600 | 3281.34 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 200992 | GGB | 200994.39 | 3281.34 | 2564.816 |  |  |  | 0 | 1 | [14 empty] | 134.3079 | 2564.816 |  | 104.98
14.04.2008 08:00 | 3600 | 2 | 761.12 | GGB | 762.271 | 772.477 | 767.033 | 275.67 | GGB | 11204.1 | GGB | 9.81 | GGB | 1010.76 | GGB | 59.48 | GGB | 180228.72 | GGB | 147658.98 | GGB | 0 | 0 | 3287 | 3600 | 3271.33 | GGB | 100 | GGB | 41.43 | GGB | 41.43 | GGB | 201033.42 | GGB | 201035.82 | 3271.33 | 2559.4651 |  |  |  | 0 | 1 | [14 empty] | 134.1781 | 2559.4651 |  | 104.98
14.04.2008 09:00 | 3600 | 2 | 761.37 | GGB | 764.835 | 774.469 | 769.597 | 276.02 | GGB | 11186.7 | GGB | 9.81 | GGB | 1011.79 | GGB | 59.2 | GGB | 180840.51 | GGB | 148435.89 | GGB | 0 | 0 | 3266 | 3600 | 3249.85 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 201074.61 | GGB | 201077.01 | 3249.85 | 2546.0689 |  |  |  | 1 | 1 |  |  |  |  | 148435.89 | 2546.0689 | 148435.89 | 2546.0689 | 9.1752 | [5 empty] | 133.9984 | 2546.0689 |  | 104.98
14.04.2008 10:00 | 3600 | 2 | 761.59 | GGB | 762.271 | 771 | 765.934 | 274.71 | GGB | 11167.3 | GGB | 9.81 | GGB | 1012.44 | GGB | 59.89 | GGB | 179315.44 | GGB | 146972.05 | GGB | 0 | 0 | 3257 | 3600 | 3240.8 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 201114.79 | GGB | 201117.19 | 3240.8 | 2571.4277 |  |  |  | 0 | 1 | [14 empty] | 132.3075 | 2571.4277 |  | 104.98
14.04.2008 11:00 | 3600 | 2 | 762.64 | GGB | 764.469 | 773.18 | 768.498 | 274.86 | GGB | 11094.2 | GGB | 9.82 | GGB | 1012.38 | GGB | 59.81 | GGB | 179654.35 | GGB | 147277.21 | GGB | 0 | 0 | 3174 | 3600 | 3158.08 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 201156.19 | GGB | 201158.59 | 3158.08 | 2566.0997 |  |  |  | 1 | 1 |  |  |  |  | 147277.21 | 2566.0997 | 147277.21 | 2566.0997 | 9.1287 | [5 empty] | 129.1981 | 2566.0997 |  | 104.98
14.04.2008 12:00 | 3600 | 2 | 764.26 | GGB | 764.835 | 774.164 | 768.498 | 271.45 | GGB | 11049.9 | GGB | 9.84 | GGB | 1012.23 | GGB | 61.07 | GGB | 175820.77 | GGB | 143572.1 | GGB | 0 | 0 | 3063 | 3600 | 3047.22 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 201196.53 | GGB | 201198.93 | 3047.22 | 2632.322 |  |  |  | 1 | 1 |  |  |  |  | 143572.1 | 2632.322 | 143572.1 | 2632.322 | 9.3686 | [5 empty] | 121.5266 | 2632.322 |  | 104.98
14.04.2008 13:00 | 3600 | 2 | 764.35 | GGB | 764.835 | 775.359 | 769.597 | 268.04 | GGB | 10979.4 | GGB | 9.83 | GGB | 1011.7 | GGB | 61.99 | GGB | 173340.61 | GGB | 141083.02 | GGB | 0 | 0 | 3025 | 3600 | 3008.83 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 201236.75 | GGB | 201239.16 | 3008.83 | 2678.7632 |  |  |  | 1 | 1 |  |  |  |  | 141083.02 | 2678.7632 | 141083.02 | 2678.7632 | 9.3942 | [5 empty] | 117.9152 | 2678.7632 |  | 104.98
14.04.2008 14:00 | 3600 | 2 | 764.4 | GGB | 764.469 | 774.188 | 769.597 | 267.74 | GGB | 10877.9 | GGB | 9.81 | GGB | 1011.04 | GGB | 61.44 | GGB | 174070.13 | GGB | 141815.05 | GGB | 0 | 0 | 2959 | 3600 | 2943.77 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 201277.72 | GGB | 201280.12 | 2943.77 | 2664.9358 |  |  |  | 1 | 1 |  |  |  |  | 141815.05 | 2664.9358 | 141815.05 | 2664.9358 | 9.2268 | [5 empty] | 115.9641 | 2664.9358 |  | 104.98
14.04.2008 15:00 | 3600 | 2 | 765.06 | GGB | 768.132 | 778.641 | 773.26 | 266.2 | GGB | 10872.8 | GGB | 9.82 | GGB | 1010.33 | GGB | 61.45 | GGB | 172734.32 | GGB | 140625.65 | GGB | 0 | 0 | 2905 | 3600 | 2889.36 | GGB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 201319.29 | GGB | 201321.69 | 2889.36 | 2687.4756 |  |  |  | 1 | 1 |  |  |  |  | 140625.65 | 2687.4756 | 140625.65 | 2687.4756 | 9.0914 | [5 empty] | 112.8661 | 2687.4756 |  | 104.98
14.04.2008 16:00 | 3600 | 2 | 765.1 | GGB | 767.033 | 777.867 | 773.26 | 263.62 | GGB | 10829.3 | GGB | 9.82 | GGB | 1009.47 | GGB | 62.53 | GGB | 169975.77 | GGB | 137819.56 | GGB | 0 | 0 | 2882 | 3600 | 2866.92 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 201358.72 | GGB | 201361.12 | 2866.92 | 2742.1942 |  |  |  | 1 | 1 |  |  |  |  | 137819.56 | 2742.1942 | 137819.56 | 2742.1942 | 9.5848 | [5 empty] | 109.7549 | 2742.1942 |  | 104.98
14.04.2008 17:00 | 3600 | 2 | 764.54 | GGB | 764.835 | 774.891 | 770.696 | 264.04 | GGB | 10773.1 | GGB | 9.8 | GGB | 1009.3 | GGB | 62.34 | GGB | 170633.78 | GGB | 138404.21 | GGB | 0 | 0 | 2894 | 3600 | 2878.32 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 201398.24 | GGB | 201400.64 | 2878.32 | 2730.6106 |  |  |  | 1 | 1 |  |  |  |  | 138404.21 | 2730.6106 | 138404.21 | 2730.6106 | 9.563 | [5 empty] | 110.6588 | 2730.6106 |  | 104.98
14.04.2008 18:00 | 3600 | 2 | 765.71 | GGB | 767.033 | 777.211 | 771.795 | 263.5 | GGB | 10749.3 | GGB | 9.82 | GGB | 1008.98 | GGB | 62.5 | GGB | 169961.47 | GGB | 137751.59 | GGB | 0 | 0 | 2816 | 3600 | 2800.8 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 201439.07 | GGB | 201441.47 | 2800.8 | 2743.5473 |  |  |  | 1 | 1 |  |  |  |  | 137751.59 | 2743.5473 | 137751.59 | 2743.5473 | 9.2561 | [5 empty] | 107.1707 | 2743.5473 |  | 104.98
14.04.2008 19:00 | 3600 | 2 | 764.63 | GGB | 767.033 | 777.398 | 771.795 | 262.1 | GGB | 10733.7 | GGB | 9.8 | GGB | 1008.86 | GGB | 62.81 | GGB | 167970.96 | GGB | 135996.71 | GGB | 0 | 0 | 2865 | 3600 | 2849.18 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 201479.49 | GGB | 201481.89 | 2849.18 | 2778.9496 |  |  |  | 1 | 1 |  |  |  |  | 135996.71 | 2778.9496 | 135996.71 | 2778.9496 | 9.35 | [5 empty] | 107.6331 | 2778.9496 |  | 104.98
14.04.2008 20:00 | 3600 | 2 | 764.16 | GGB | 763.37 | 773.883 | 768.498 | 262.64 | GGB | 10744.9 | GGB | 9.79 | GGB | 1008.85 | GGB | 63.22 | GGB | 167955.55 | GGB | 135815.48 | GGB | 0 | 0 | 2907 | 3600 | 2891.44 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 201518.9 | GGB | 201521.3 | 2891.44 | 2782.6578 |  |  |  | 0 | 1 | [14 empty] | 109.084 | 2782.6578 |  | 104.98
14.04.2008 21:00 | 3600 | 2 | 763.61 | GGB | 764.469 | 774.141 | 769.597 | 264.35 | GGB | 10798.9 | GGB | 9.8 | GGB | 1009.44 | GGB | 62.71 | GGB | 169362.89 | GGB | 137243.43 | GGB | 0 | 0 | 2960 | 3600 | 2944.7 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 201558.14 | GGB | 201560.54 | 2944.7 | 2753.7056 |  |  |  | 1 | 1 |  |  |  |  | 137243.43 | 2753.7056 | 137243.43 | 2753.7056 | 9.6312 | [5 empty] | 112.2613 | 2753.7056 |  | 104.98
14.04.2008 22:00 | 3600 | 2 | 762.94 | GGB | 763.37 | 773.508 | 768.132 | 266.09 | GGB | 10878 | GGB | 9.79 | GGB | 1010.49 | GGB | 62.12 | GGB | 171761.62 | GGB | 139575.65 | GGB | 0 | 0 | 3023 | 3600 | 3007.28 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 201597.61 | GGB | 201600.01 | 3007.28 | 2707.6929 |  |  |  | 0 | 1 | [14 empty] | 116.5953 | 2707.6929 |  | 104.98
14.04.2008 23:00 | 3600 | 2 | 763.83 | GGB | 763.37 | 773.742 | 768.498 | 266.39 | GGB | 10901.4 | GGB | 9.81 | GGB | 1011.09 | GGB | 62.17 | GGB | 170881.35 | GGB | 138921.43 | GGB | 0 | 0 | 2997 | 3600 | 2981.14 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 201637.19 | GGB | 201639.59 | 2981.14 | 2720.4442 |  |  |  | 0 | 1 | [14 empty] | 115.0401 | 2720.4442 |  | 104.98
14.04.2008 24:00 | 3600 | 2 | 762.68 | GGB | 762.271 | 772.781 | 768.132 | 266.72 | GGB | 10881.8 | GGB | 9.79 | GGB | 1011.12 | GGB | 62.25 | GGB | 171311.58 | GGB | 139243.39 | GGB | 0 | 0 | 3056 | 3600 | 3040.73 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 201677.1 | GGB | 201679.5 | 3040.73 | 2714.154 |  |  |  | 0 | 1 | [14 empty] | 117.6115 | 2714.154 |  | 104.98
15.04.2008 01:00 | 3600 | 2 | 762.67 | GGB | 764.469 | 774.773 | 769.597 | 268.22 | GGB | 10956.2 | GGB | 9.8 | GGB | 1011.14 | GGB | 61.89 | GGB | 173167.85 | GGB | 140905.24 | GGB | 0 | 0 | 3086 | 3600 | 3069.97 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 201717.54 | GGB | 201719.93 | 3069.97 | 2682.143 |  |  |  | 1 | 1 |  |  |  |  | 140905.24 | 2682.143 | 140905.24 | 2682.143 | 9.3477 | [5 empty] | 120.1597 | 2682.143 |  | 104.98
15.04.2008 02:00 | 3600 | 2 | 761.46 | GGB | 761.172 | 771.258 | 765.934 | 270.23 | GGB | 10968 | GGB | 9.78 | GGB | 1010.57 | GGB | 61.4 | GGB | 174303.4 | GGB | 141958.12 | GGB | 0 | 0 | 3168 | 3600 | 3152.38 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 201758.16 | GGB | 201760.55 | 3152.38 | 2662.25 |  |  |  | 0 | 1 | [14 empty] | 124.3072 | 2662.25 |  | 104.98
15.04.2008 03:00 | 3600 | 2 | 761.17 | GGB | 763.37 | 773.32 | 768.132 | 272.43 | GGB | 11086.6 | GGB | 9.8 | GGB | 1010.62 | GGB | 60.53 | GGB | 177219.3 | GGB | 144718.41 | GGB | 0 | 0 | 3219 | 3600 | 3203.38 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 201798.98 | GGB | 201801.37 | 3203.38 | 2611.4715 |  |  |  | 0 | 1 | [14 empty] | 128.7745 | 2611.4715 |  | 104.98
15.04.2008 04:00 | 3600 | 2 | 761.41 | GGB | 763.37 | 773.32 | 768.132 | 274.06 | GGB | 11084.3 | GGB | 9.8 | GGB | 1010.98 | GGB | 59.77 | GGB | 179784.19 | GGB | 147198.5 | GGB | 0 | 0 | 3196 | 3600 | 3180.63 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 201840.05 | GGB | 201842.44 | 3180.63 | 2567.4718 |  |  |  | 0 | 1 | [14 empty] | 130.0511 | 2567.4718 |  | 104.98
15.04.2008 05:00 | 3600 | 2 | 761.95 | GGB | 763.37 | 773.109 | 768.132 | 272.85 | GGB | 11150.4 | GGB | 9.81 | GGB | 1011.21 | GGB | 60.09 | GGB | 178414.26 | GGB | 145969.44 | GGB | 0 | 0 | 3213 | 3600 | 3196.8 | GGB | 100 | GGB | 40.93 | GGB | 40.93 | GGB | 201880.98 | GGB | 201883.37 | 3196.8 | 2589.0899 |  |  |  | 0 | 1 | [14 empty] | 129.6209 | 2589.0899 |  | 104.98
15.04.2008 06:00 | 3600 | 2 | 760.85 | GGB | 759.707 | 769.758 | 764.835 | 274.01 | GGB | 11148.2 | GGB | 9.79 | GGB | 1011.67 | GGB | 59.96 | GGB | 179732.47 | GGB | 147174.15 | GGB | 0 | 0 | 3269 | 3600 | 3252.69 | GGB | 100 | GGB | 40.8 | GGB | 40.8 | GGB | 201921.78 | GGB | 201924.17 | 3252.69 | 2567.8966 |  |  |  | 0 | 1 | [14 empty] | 132.9755 | 2567.8966 |  | 104.98
15.04.2008 07:00 | 3600 | 2 | 762.04 | GGB | 764.469 | 774.094 | 768.498 | 274.81 | GGB | 11185.1 | GGB | 9.82 | GGB | 1012.03 | GGB | 59.48 | GGB | 180882.32 | GGB | 148381.21 | GGB | 0 | 0 | 3242 | 3600 | 3225.64 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 201962.34 | GGB | 201964.74 | 3225.64 | 2547.0071 |  |  |  | 1 | 1 |  |  |  |  | 148381.21 | 2547.0071 | 148381.21 | 2547.0071 | 9.3155 | [5 empty] | 132.9512 | 2547.0071 |  | 104.98
15.04.2008 08:00 | 3600 | 2 | 762.62 | GGB | 764.835 | 774.914 | 768.498 | 273.65 | GGB | 11121 | GGB | 9.82 | GGB | 1012.46 | GGB | 59.64 | GGB | 180113.19 | GGB | 147741.26 | GGB | 0 | 0 | 3182 | 3600 | 3166.38 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 202002.97 | GGB | 202005.37 | 3166.38 | 2558.0396 |  |  |  | 1 | 1 |  |  |  |  | 147741.26 | 2558.0396 | 147741.26 | 2558.0396 | 9.3017 | [5 empty] | 129.9458 | 2558.0396 |  | 104.98
15.04.2008 09:00 | 3600 | 2 | 763.65 | GGB | 767.033 | 777.023 | 771.795 | 271.62 | GGB | 11077.3 | GGB | 9.84 | GGB | 1012.99 | GGB | 60.2 | GGB | 177411.86 | GGB | 145357.13 | GGB | 0 | 0 | 3104 | 3600 | 3088.22 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 202043.46 | GGB | 202045.86 | 3088.22 | 2599.9963 |  |  |  | 1 | 1 |  |  |  |  | 145357.13 | 2599.9963 | 145357.13 | 2599.9963 | 9.3339 | [5 empty] | 124.693 | 2599.9963 |  | 104.98
15.04.2008 10:00 | 3600 | 2 | 765.58 | GGB | 768.132 | 778.266 | 773.26 | 266.76 | GGB | 10914.3 | GGB | 9.85 | GGB | 1012.97 | GGB | 61.78 | GGB | 171889.26 | GGB | 140167.07 | GGB | 0 | 0 | 2930 | 3600 | 2914.45 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 202083.73 | GGB | 202086.13 | 2914.45 | 2696.2681 |  |  |  | 1 | 1 |  |  |  |  | 140167.07 | 2696.2681 | 140167.07 | 2696.2681 | 9.3849 | [5 empty] | 113.475 | 2696.2681 |  | 104.98
15.04.2008 11:00 | 3600 | 2 | 765.55 | GGB | 767.033 | 778.289 | 773.26 | 262.65 | GGB | 10787.2 | GGB | 9.83 | GGB | 1012.33 | GGB | 63.36 | GGB | 167261.24 | GGB | 135664.72 | GGB | 0 | 0 | 2879 | 3600 | 2863.11 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 202123.57 | GGB | 202125.97 | 2863.11 | 2785.75 |  |  |  | 1 | 1 |  |  |  |  | 135664.72 | 2785.75 | 135664.72 | 2785.75 | 9.4861 | [5 empty] | 107.8953 | 2785.75 |  | 104.98
15.04.2008 12:00 | 3600 | 2 | 766.01 | GGB | 765.934 | 777.234 | 771.795 | 260.46 | GGB | 10680.2 | GGB | 9.82 | GGB | 1011.31 | GGB | 64.2 | GGB | 165260.83 | GGB | 133573.33 | GGB | 0 | 0 | 2821 | 3600 | 2805.72 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 202163.22 | GGB | 202165.63 | 2805.72 | 2805.72 |  |  |  | 1 | 1 |  |  |  |  | 133573.33 | 2805.72 | 133573.33 | 2805.72 | 9.4496 | [5 empty] | 104.1026 |  |  | #VALUE!
15.04.2008 13:00 | 3600 | 2 | 766.04 | GGB | 765.934 | 777.094 | 771.795 | 259.59 | GGB | 10622.5 | GGB | 9.81 | GGB | 1010.82 | GGB | 64.37 | GGB | 164540.11 | GGB | 132860.84 | GGB | 0 | 0 | 2793 | 3600 | 2777.05 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 202202.96 | GGB | 202205.37 | 2777.05 | 2777.05 |  |  |  | 1 | 1 |  |  |  |  | 132860.84 | 2777.05 | 132860.84 | 2777.05 | 9.2844 | [5 empty] | 102.4892 |  |  | #VALUE!
15.04.2008 14:00 | 3600 | 2 | 766.02 | GGB | 764.835 | 776.086 | 770.696 | 259.38 | GGB | 10608.9 | GGB | 9.81 | GGB | 1010.73 | GGB | 64.51 | GGB | 164499.39 | GGB | 132760.2 | GGB | 0 | 0 | 2782 | 3600 | 2766.48 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 202242.71 | GGB | 202245.12 | 2766.48 | 2766.48 |  |  |  | 1 | 1 |  |  |  |  | 132760.2 | 2766.48 | 132760.2 | 2766.48 | 9.2397 | [5 empty] | 102.0218 |  |  | #VALUE!
15.04.2008 15:00 | 3600 | 2 | 765.79 | GGB | 765.934 | 777.117 | 772.161 | 259.83 | GGB | 10631.4 | GGB | 9.81 | GGB | 1010.93 | GGB | 64.38 | GGB | 164842.7 | GGB | 133114.17 | GGB | 0 | 0 | 2793 | 3600 | 2777.36 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 202282.44 | GGB | 202284.84 | 2777.36 | 2777.36 |  |  |  | 1 | 1 |  |  |  |  | 133114.17 | 2777.36 | 133114.17 | 2777.36 | 9.3078 | [5 empty] | 102.6961 |  |  | #VALUE!
15.04.2008 16:00 | 3600 | 2 | 766.19 | GGB | 767.033 | 778.195 | 772.161 | 259.45 | GGB | 10602.2 | GGB | 9.81 | GGB | 1010.86 | GGB | 64.65 | GGB | 164368.45 | GGB | 132616.37 | GGB | 0 | 0 | 2759 | 3600 | 2743.15 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 202322.03 | GGB | 202324.43 | 2743.15 | 2743.15 |  |  |  | 1 | 1 |  |  |  |  | 132616.37 | 2743.15 | 132616.37 | 2743.15 | 9.1889 | [5 empty] | 101.0518 |  |  | #VALUE!
15.04.2008 17:00 | 3600 | 2 | 764.93 | GGB | 762.271 | 773.438 | 768.498 | 259.98 | GGB | 10593.3 | GGB | 9.79 | GGB | 1010.33 | GGB | 64.35 | GGB | 164880.11 | GGB | 133076.32 | GGB | 0 | 0 | 2811 | 3600 | 2795.22 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 202361.49 | GGB | 202363.89 | 2795.22 | 2795.22 |  |  |  | 0 | 1 | [14 empty] | 103.3271 |  |  | #VALUE!
15.04.2008 18:00 | 3600 | 2 | 766.34 | GGB | 765.934 | 776.953 | 771.429 | 259.72 | GGB | 10621.4 | GGB | 9.82 | GGB | 1009.85 | GGB | 64.6 | GGB | 164365.15 | GGB | 132500.79 | GGB | 0 | 0 | 2763 | 3600 | 2747.89 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 202400.85 | GGB | 202403.26 | 2747.89 | 2747.89 |  |  |  | 1 | 1 |  |  |  |  | 132500.79 | 2747.89 | 132500.79 | 2747.89 | 9.2481 | [5 empty] | 101.1382 |  |  | #VALUE!
15.04.2008 19:00 | 3600 | 2 | 765.45 | GGB | 765.934 | 777.164 | 771.429 | 259.93 | GGB | 10594.8 | GGB | 9.79 | GGB | 1009.71 | GGB | 64.45 | GGB | 164664.44 | GGB | 132781.6 | GGB | 0 | 0 | 2801 | 3600 | 2785.21 | GGB | 100 | GGB | 39.1 | GGB | 39.1 | GGB | 202439.95 | GGB | 202442.36 | 2785.21 | 2785.21 |  |  |  | 1 | 1 |  |  |  |  | 132781.6 | 2785.21 | 132781.6 | 2785.21 | 9.4584 | [5 empty] | 102.7291 |  |  | #VALUE!
15.04.2008 20:00 | 3600 | 2 | 765.84 | GGB | 764.835 | 775.969 | 770.33 | 260.79 | GGB | 10649 | GGB | 9.81 | GGB | 1009.76 | GGB | 64.18 | GGB | 165342.25 | GGB | 133442.8 | GGB | 0 | 0 | 2792 | 3600 | 2776.14 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 202479.06 | GGB | 202481.47 | 2776.14 | 2776.14 |  |  |  | 1 | 1 |  |  |  |  | 133442.8 | 2776.14 | 133442.8 | 2776.14 | 9.4722 | [5 empty] | 102.9044 |  |  | #VALUE!
15.04.2008 21:00 | 3600 | 2 | 764.75 | GGB | 763.37 | 774.82 | 768.864 | 261.91 | GGB | 10666.6 | GGB | 9.79 | GGB | 1010.53 | GGB | 64.08 | GGB | 166133.4 | GGB | 134225.27 | GGB | 0 | 0 | 2857 | 3600 | 2841.24 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 202518.75 | GGB | 202521.16 | 2841.24 | 2815.6248 |  |  |  | 0 | 1 | [14 empty] | 105.9351 | 2815.6248 |  | 104.98
15.04.2008 22:00 | 3600 | 2 | 764.22 | GGB | 764.469 | 776.016 | 769.963 | 263.78 | GGB | 10743.5 | GGB | 9.8 | GGB | 1011.6 | GGB | 63.51 | GGB | 167911.54 | GGB | 136032.85 | GGB | 0 | 0 | 2923 | 3600 | 2907.56 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 202558.46 | GGB | 202560.88 | 2907.56 | 2778.2113 |  |  |  | 1 | 1 |  |  |  |  | 136032.85 | 2778.2113 | 136032.85 | 2778.2113 | 9.5148 | [5 empty] | 109.8677 | 2778.2113 |  | 104.98
15.04.2008 23:00 | 3600 | 2 | 762.8 | GGB | 767.033 | 777.023 | 772.527 | 268.07 | GGB | 10829.6 | GGB | 9.78 | GGB | 1012.13 | GGB | 62.25 | GGB | 172654 | GGB | 140473.74 | GGB | 0 | 0 | 3030 | 3600 | 3013.88 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 202597.93 | GGB | 202600.35 | 3013.88 | 2690.3818 |  |  |  | 1 | 1 |  |  |  |  | 140473.74 | 2690.3818 | 140473.74 | 2690.3818 | 9.5751 | [5 empty] | 117.6031 | 2690.3818 |  | 104.98
15.04.2008 24:00 | 3600 | 2 | 763.21 | GGB | 764.469 | 774.797 | 768.864 | 267.91 | GGB | 10901 | GGB | 9.8 | GGB | 1012.41 | GGB | 62.44 | GGB | 171929.97 | GGB | 139843.55 | GGB | 0 | 0 | 3048 | 3600 | 3032.34 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 202637.54 | GGB | 202639.96 | 3032.34 | 2702.5058 |  |  |  | 1 | 1 |  |  |  |  | 139843.55 | 2702.5058 | 139843.55 | 2702.5058 | 9.5412 | [5 empty] | 117.7926 | 2702.5058 |  | 104.98
16.04.2008 01:00 | 3600 | 2 | 762.66 | GGB | 763.37 | 773.719 | 767.766 | 268.47 | GGB | 10931.7 | GGB | 9.8 | GGB | 1012.8 | GGB | 62.22 | GGB | 172946.69 | GGB | 140820.07 | GGB | 0 | 0 | 3090 | 3600 | 3074.32 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 202677.44 | GGB | 202679.85 | 3074.32 | 2683.7652 |  |  |  | 0 | 1 | [14 empty] | 120.2572 | 2683.7652 |  | 104.98
16.04.2008 02:00 | 3600 | 2 | 762.92 | GGB | 763.37 | 773.578 | 767.766 | 268.76 | GGB | 10951.2 | GGB | 9.8 | GGB | 1012.98 | GGB | 62.13 | GGB | 173239.38 | GGB | 141120.06 | GGB | 0 | 0 | 3087 | 3600 | 3071 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 202717.48 | GGB | 202719.89 | 3071 | 2678.0601 |  |  |  | 0 | 1 | [14 empty] | 120.3833 | 2678.0601 |  | 104.98
16.04.2008 03:00 | 3600 | 2 | 762.33 | GGB | 763.37 | 773.133 | 767.766 | 270.18 | GGB | 10955.1 | GGB | 9.8 | GGB | 1013.02 | GGB | 61.52 | GGB | 174988.91 | GGB | 142811.87 | GGB | 0 | 0 | 3119 | 3600 | 3103.59 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 202758.17 | GGB | 202760.58 | 3103.59 | 2646.3346 |  |  |  | 0 | 1 | [14 empty] | 123.1193 | 2646.3346 |  | 104.98
16.04.2008 04:00 | 3600 | 2 | 763.68 | GGB | 764.835 | 774.281 | 768.864 | 270.63 | GGB | 10960.8 | GGB | 9.82 | GGB | 1012.41 | GGB | 60.99 | GGB | 175970.41 | GGB | 143753.91 | GGB | 0 | 0 | 3054 | 3600 | 3038.11 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 202798.67 | GGB | 202801.08 | 3038.11 | 2628.9928 |  |  |  | 1 | 1 |  |  |  |  | 143753.91 | 2628.9928 | 143753.91 | 2628.9928 | 9.3316 | [5 empty] | 121.3167 | 2628.9928 |  | 104.98
16.04.2008 05:00 | 3600 | 2 | 763.42 | GGB | 764.469 | 774.469 | 768.864 | 268.32 | GGB | 10970.5 | GGB | 9.81 | GGB | 1011.74 | GGB | 61.75 | GGB | 173148.05 | GGB | 141032.29 | GGB | 0 | 0 | 3058 | 3600 | 3042.76 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 202838.85 | GGB | 202841.26 | 3042.76 | 2679.7267 |  |  |  | 1 | 1 |  |  |  |  | 141032.29 | 2679.7267 | 141032.29 | 2679.7267 | 9.4059 | [5 empty] | 119.2021 | 2679.7267 |  | 104.98
16.04.2008 06:00 | 3600 | 2 | 762.6 | GGB | 762.271 | 772.523 | 767.766 | 268.83 | GGB | 10966.6 | GGB | 9.8 | GGB | 1011.36 | GGB | 61.69 | GGB | 173626.7 | GGB | 141393.78 | GGB | 0 | 0 | 3105 | 3600 | 3089.34 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 202879.38 | GGB | 202881.79 | 3089.34 | 2672.8757 |  |  |  | 0 | 1 | [14 empty] | 121.3371 | 2672.8757 |  | 104.98
16.04.2008 07:00 | 3600 | 2 | 762.61 | GGB | 763.37 | 773.367 | 767.766 | 269.17 | GGB | 10983.2 | GGB | 9.8 | GGB | 1011.02 | GGB | 61.66 | GGB | 173994.21 | GGB | 141660.61 | GGB | 0 | 0 | 3111 | 3600 | 3094.79 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 202919.56 | GGB | 202921.97 | 3094.79 | 2667.8411 |  |  |  | 0 | 1 | [14 empty] | 121.7805 | 2667.8411 |  | 104.98
16.04.2008 08:00 | 3600 | 2 | 763.26 | GGB | 763.37 | 774.703 | 768.864 | 268.86 | GGB | 10989 | GGB | 9.81 | GGB | 1010.82 | GGB | 61.69 | GGB | 173822.56 | GGB | 141480.11 | GGB | 0 | 0 | 3087 | 3600 | 3070.91 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 202959.64 | GGB | 202962.05 | 3070.91 | 2671.2447 |  |  |  | 0 | 1 | [14 empty] | 120.6869 | 2671.2447 |  | 104.98
16.04.2008 09:00 | 3600 | 2 | 762.68 | GGB | 764.469 | 774.422 | 769.963 | 269.06 | GGB | 10978 | GGB | 9.8 | GGB | 1010.86 | GGB | 61.64 | GGB | 174171.36 | GGB | 141788.22 | GGB | 0 | 0 | 3110 | 3600 | 3094.74 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 203000.06 | GGB | 203002.48 | 3094.74 | 2665.44 |  |  |  | 1 | 1 |  |  |  |  | 141788.22 | 2665.44 | 141788.22 | 2665.44 | 9.3477 | [5 empty] | 121.8882 | 2665.44 |  | 104.98
16.04.2008 10:00 | 3600 | 2 | 763.35 | GGB | 763.37 | 773.602 | 768.864 | 268.2 | GGB | 10955.6 | GGB | 9.82 | GGB | 1010.79 | GGB | 61.7 | GGB | 173524.36 | GGB | 141227.45 | GGB | 0 | 0 | 3038 | 3600 | 3022.11 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 203040.33 | GGB | 203042.75 | 3022.11 | 2676.0237 |  |  |  | 0 | 1 | [14 empty] | 118.5569 | 2676.0237 |  | 104.98
16.04.2008 11:00 | 3600 | 2 | 763.28 | GGB | 767.033 | 776.953 | 772.527 | 267.18 | GGB | 10875.1 | GGB | 9.82 | GGB | 1010.53 | GGB | 61.72 | GGB | 172877.37 | GGB | 140656.22 | GGB | 0 | 0 | 2974 | 3600 | 2958.15 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 203080.68 | GGB | 203083.1 | 2958.15 | 2686.8915 |  |  |  | 1 | 1 |  |  |  |  | 140656.22 | 2686.8915 | 140656.22 | 2686.8915 | 9.3662 | [5 empty] | 115.5784 | 2686.8915 |  | 104.98
16.04.2008 12:00 | 3600 | 2 | 764.61 | GGB | 764.469 | 773.836 | 768.864 | 262.65 | GGB | 10798.5 | GGB | 9.83 | GGB | 1008.57 | GGB | 63.07 | GGB | 168504.62 | GGB | 136284.38 | GGB | 0 | 0 | 2874 | 3600 | 2858.05 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 203120.84 | GGB | 203123.26 | 2858.05 | 2773.0838 |  |  |  | 1 | 1 |  |  |  |  | 136284.38 | 2773.0838 | 136284.38 | 2773.0838 | 9.4106 | [5 empty] | 108.1965 | 2773.0838 |  | 104.98
16.04.2008 13:00 | 3600 | 2 | 764.6 | GGB | 765.934 | 776.156 | 771.429 | 261.52 | GGB | 10736.7 | GGB | 9.81 | GGB | 1007.36 | GGB | 63.3 | GGB | 167525.32 | GGB | 135235.89 | GGB | 0 | 0 | 2872 | 3600 | 2856.3 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 203160.8 | GGB | 203163.22 | 2856.3 | 2794.5836 |  |  |  | 1 | 1 |  |  |  |  | 135235.89 | 2794.5836 | 135235.89 | 2794.5836 | 9.4577 | [5 empty] | 107.2984 | 2794.5836 |  | 104.98
16.04.2008 14:00 | 3600 | 2 | 764.15 | GGB | 764.469 | 775.219 | 770.33 | 261.03 | GGB | 10683.7 | GGB | 9.8 | GGB | 1006.74 | GGB | 63.46 | GGB | 166682.46 | GGB | 134409.81 | GGB | 0 | 0 | 2865 | 3600 | 2849.31 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 203200.53 | GGB | 203202.95 | 2849.31 | 2811.7591 |  |  |  | 1 | 1 |  |  |  |  | 134409.81 | 2811.7591 | 134409.81 | 2811.7591 | 9.5124 | [5 empty] | 106.382 | 2811.7591 |  | 104.98
16.04.2008 15:00 | 3600 | 2 | 764.58 | GGB | 763.37 | 773.883 | 768.864 | 261.12 | GGB | 10689.1 | GGB | 9.81 | GGB | 1005.82 | GGB | 63.48 | GGB | 166910.23 | GGB | 134460.76 | GGB | 0 | 0 | 2837 | 3600 | 2821.13 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 203239.93 | GGB | 203242.35 | 2821.13 | 2810.6936 |  |  |  | 0 | 1 | [14 empty] | 105.3698 | 2810.6936 |  | 104.98
16.04.2008 16:00 | 3600 | 2 | 764.31 | GGB | 763.37 | 774.07 | 768.864 | 262.38 | GGB | 10730 | GGB | 9.8 | GGB | 1005.47 | GGB | 62.94 | GGB | 168628.96 | GGB | 136019.05 | GGB | 0 | 0 | 2872 | 3600 | 2856.58 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 203279.35 | GGB | 203281.78 | 2856.58 | 2778.4932 |  |  |  | 0 | 1 | [14 empty] | 107.9304 | 2778.4932 |  | 104.98
16.04.2008 17:00 | 3600 | 2 | 763.5 | GGB | 763.37 | 774 | 768.864 | 263.25 | GGB | 10754.3 | GGB | 9.79 | GGB | 1005.46 | GGB | 62.69 | GGB | 169679.78 | GGB | 136966.61 | GGB | 0 | 0 | 2918 | 3600 | 2902.87 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 203318.96 | GGB | 203321.39 | 2902.87 | 2759.271 |  |  |  | 0 | 1 | [14 empty] | 110.4434 | 2759.271 |  | 104.98
16.04.2008 18:00 | 3600 | 2 | 763.69 | GGB | 764.469 | 773.93 | 768.864 | 263.64 | GGB | 10796.1 | GGB | 9.81 | GGB | 1005.49 | GGB | 62.64 | GGB | 170070.4 | GGB | 137307.17 | GGB | 0 | 0 | 2920 | 3600 | 2904.55 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 203358.59 | GGB | 203361.01 | 2904.55 | 2752.4273 |  |  |  | 1 | 1 |  |  |  |  | 137307.17 | 2752.4273 | 137307.17 | 2752.4273 | 9.5388 | [5 empty] | 110.7821 | 2752.4273 |  | 104.98
16.04.2008 19:00 | 3600 | 2 | 761.58 | GGB | 762.271 | 772.266 | 767.766 | 266.09 | GGB | 10854.3 | GGB | 9.78 | GGB | 1005.83 | GGB | 61.67 | GGB | 172474.64 | GGB | 139694.92 | GGB | 0 | 0 | 3049 | 3600 | 3033.71 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 203398.36 | GGB | 203400.78 | 3033.71 | 2705.3811 |  |  |  | 0 | 1 | [14 empty] | 117.7205 | 2705.3811 |  | 104.98
16.04.2008 20:00 | 3600 | 2 | 761.44 | GGB | 763.37 | 772.523 | 768.864 | 268.36 | GGB | 10953.2 | GGB | 9.79 | GGB | 1006.56 | GGB | 60.9 | GGB | 174665.41 | GGB | 141900.12 | GGB | 0 | 0 | 3112 | 3600 | 3096.05 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 203438.43 | GGB | 203440.85 | 3096.05 | 2663.3381 |  |  |  | 0 | 1 | [14 empty] | 122.0361 | 2663.3381 |  | 104.98
16.04.2008 21:00 | 3600 | 2 | 761.6 | GGB | 763.37 | 772.477 | 767.766 | 269.41 | GGB | 11006.5 | GGB | 9.8 | GGB | 1007.7 | GGB | 60.84 | GGB | 175496.17 | GGB | 142763.54 | GGB | 0 | 0 | 3125 | 3600 | 3109.66 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 203478.88 | GGB | 203481.3 | 3109.66 | 2647.2305 |  |  |  | 0 | 1 | [14 empty] | 123.3184 | 2647.2305 |  | 104.98
16.04.2008 22:00 | 3600 | 2 | 761.73 | GGB | 762.271 | 771.281 | 766.667 | 269.35 | GGB | 11036.1 | GGB | 9.8 | GGB | 1008.22 | GGB | 60.64 | GGB | 175698.63 | GGB | 143084.25 | GGB | 0 | 0 | 3118 | 3600 | 3102.13 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 203519.3 | GGB | 203521.73 | 3102.13 | 2641.297 |  |  |  | 0 | 1 | [14 empty] | 123.2961 | 2641.297 |  | 104.98
16.04.2008 23:00 | 3600 | 2 | 761.17 | GGB | 764.469 | 773.578 | 768.864 | 270.66 | GGB | 11047.8 | GGB | 9.8 | GGB | 1008.32 | GGB | 60.55 | GGB | 176584.4 | GGB | 143862.45 | GGB | 0 | 0 | 3175 | 3600 | 3159.37 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 203559.47 | GGB | 203561.9 | 3159.37 | 2627.0093 |  |  |  | 1 | 1 |  |  |  |  | 143862.45 | 2627.0093 | 143862.45 | 2627.0093 | 9.4082 | [5 empty] | 126.2541 | 2627.0093 |  | 104.98
16.04.2008 24:00 | 3600 | 2 | 761.25 | GGB | 763.37 | 771.586 | 767.766 | 271.08 | GGB | 11062.4 | GGB | 9.8 | GGB | 1008.21 | GGB | 60.54 | GGB | 176838.58 | GGB | 144056.47 | GGB | 0 | 0 | 3171 | 3600 | 3155.36 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 203599.3 | GGB | 203601.73 | 3155.36 | 2623.4712 |  |  |  | 0 | 1 | [14 empty] | 126.2639 | 2623.4712 |  | 104.98
17.04.2008 01:00 | 3600 | 2 | 761 | GGB | 763.37 | 772.898 | 767.766 | 271.58 | GGB | 11073.4 | GGB | 9.8 | GGB | 1007.67 | GGB | 60.34 | GGB | 177335.93 | GGB | 144470.15 | GGB | 0 | 0 | 3192 | 3600 | 3175.71 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 203639.34 | GGB | 203641.77 | 3175.71 | 2615.9591 |  |  |  | 0 | 1 | [14 empty] | 127.4431 | 2615.9591 |  | 104.98
17.04.2008 02:00 | 3600 | 2 | 761.16 | GGB | 763.37 | 772.805 | 767.766 | 272.03 | GGB | 11094.1 | GGB | 9.8 | GGB | 1007.13 | GGB | 60.26 | GGB | 177596.71 | GGB | 144640.71 | GGB | 0 | 0 | 3192 | 3600 | 3175.75 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 203680.53 | GGB | 203682.96 | 3175.75 | 2612.8743 |  |  |  | 0 | 1 | [14 empty] | 127.5952 | 2612.8743 |  | 104.98
17.04.2008 03:00 | 3600 | 2 | 761.2 | GGB | 763.37 | 772.805 | 767.766 | 272.12 | GGB | 11099.9 | GGB | 9.8 | GGB | 1006.6 | GGB | 60.17 | GGB | 177741.96 | GGB | 144723.68 | GGB | 0 | 0 | 3193 | 3600 | 3177.05 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 203721.12 | GGB | 203723.55 | 3177.05 | 2611.3764 |  |  |  | 0 | 1 | [14 empty] | 127.7207 | 2611.3764 |  | 104.98
17.04.2008 04:00 | 3600 | 2 | 761.21 | GGB | 763.37 | 771.867 | 767.766 | 272.1 | GGB | 11099.4 | GGB | 9.8 | GGB | 1006.57 | GGB | 60.17 | GGB | 177633.02 | GGB | 144629.84 | GGB | 0 | 0 | 3193 | 3600 | 3177.43 | GGB | 100 | GGB | 40.84 | GGB | 40.84 | GGB | 203761.96 | GGB | 203764.39 | 3177.43 | 2613.0707 |  |  |  | 0 | 1 | [14 empty] | 127.6531 | 2613.0707 |  | 104.98
17.04.2008 05:00 | 3600 | 2 | 761.38 | GGB | 763.37 | 771.914 | 767.766 | 272.23 | GGB | 11104.7 | GGB | 9.81 | GGB | 1006.09 | GGB | 60.08 | GGB | 177636.33 | GGB | 144600.53 | GGB | 0 | 0 | 3184 | 3600 | 3168.18 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 203802.9 | GGB | 203805.33 | 3168.18 | 2613.6004 |  |  |  | 0 | 1 | [14 empty] | 127.2557 | 2613.6004 |  | 104.98
17.04.2008 06:00 | 3600 | 2 | 761.19 | GGB | 763.37 | 772.898 | 768.864 | 272.33 | GGB | 11105.9 | GGB | 9.81 | GGB | 1005.22 | GGB | 60 | GGB | 177882.8 | GGB | 144711.27 | GGB | 0 | 0 | 3195 | 3600 | 3179.19 | GGB | 100 | GGB | 41.13 | GGB | 41.13 | GGB | 203844.03 | GGB | 203846.46 | 3179.19 | 2611.6003 |  |  |  | 0 | 1 | [14 empty] | 127.7957 | 2611.6003 |  | 104.98
17.04.2008 07:00 | 3600 | 2 | 761.14 | GGB | 763.37 | 773.086 | 768.132 | 272.42 | GGB | 11108.1 | GGB | 9.81 | GGB | 1004.97 | GGB | 59.9 | GGB | 177920.21 | GGB | 144749.99 | GGB | 0 | 0 | 3203 | 3600 | 3186.95 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 203885.19 | GGB | 203887.61 | 3186.95 | 2610.9017 |  |  |  | 0 | 1 | [14 empty] | 128.1419 | 2610.9017 |  | 104.98
17.04.2008 08:00 | 3600 | 2 | 761.42 | GGB | 764.469 | 773.086 | 769.597 | 273.78 | GGB | 11084.4 | GGB | 9.8 | GGB | 1005.11 | GGB | 59.18 | GGB | 179596.03 | GGB | 146451.52 | GGB | 0 | 0 | 3188 | 3600 | 3172.34 | GGB | 100 | GGB | 40.96 | GGB | 40.96 | GGB | 203926.15 | GGB | 203928.57 | 3172.34 | 2580.5673 |  |  |  | 1 | 1 |  |  |  |  | 146451.52 | 2580.5673 | 146451.52 | 2580.5673 | 9.2268 | [5 empty] | 129.0539 | 2580.5673 |  | 104.98
17.04.2008 09:00 | 3600 | 2 | 761.57 | GGB | 762.271 | 770.906 | 767.033 | 271.99 | GGB | 11108.8 | GGB | 9.81 | GGB | 1004.87 | GGB | 59.67 | GGB | 177348.04 | GGB | 144367.83 | GGB | 0 | 0 | 3192 | 3600 | 3176.07 | GGB | 100 | GGB | 40.68 | GGB | 40.68 | GGB | 203966.83 | GGB | 203969.25 | 3176.07 | 2617.8131 |  |  |  | 0 | 1 | [14 empty] | 127.3673 | 2617.8131 |  | 104.98
17.04.2008 10:00 | 3600 | 2 | 761.23 | GGB | 763.37 | 773.18 | 768.132 | 271.73 | GGB | 11096.4 | GGB | 9.81 | GGB | 1004.84 | GGB | 59.78 | GGB | 176820.98 | GGB | 143889.33 | GGB | 0 | 0 | 3202 | 3600 | 3186.29 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 204007.68 | GGB | 204010.1 | 3186.29 | 2626.5186 |  |  |  | 0 | 1 | [14 empty] | 127.3536 | 2626.5186 |  | 104.98
17.04.2008 11:00 | 3600 | 2 | 760.68 | GGB | 761.172 | 770.906 | 765.934 | 271.78 | GGB | 11086.6 | GGB | 9.8 | GGB | 1004.81 | GGB | 59.59 | GGB | 176971.72 | GGB | 144088.25 | GGB | 0 | 0 | 3221 | 3600 | 3205.25 | GGB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 204048.46 | GGB | 204050.88 | 3205.25 | 2622.8926 |  |  |  | 0 | 1 | [14 empty] | 128.2886 | 2622.8926 |  | 104.98
17.04.2008 12:00 | 3600 | 2 | 760.63 | GGB | 762.271 | 771.984 | 767.033 | 273.28 | GGB | 11061.8 | GGB | 9.8 | GGB | 1004.54 | GGB | 58.73 | GGB | 179217.51 | GGB | 146255.35 | GGB | 0 | 0 | 3207 | 3600 | 3190.68 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 204089.68 | GGB | 204092.1 | 3190.68 | 2584.0286 |  |  |  | 0 | 1 | [14 empty] | 129.6261 | 2584.0286 |  | 104.98
17.04.2008 13:00 | 3600 | 2 | 761.48 | GGB | 763.37 | 772.898 | 768.132 | 271.35 | GGB | 11098.6 | GGB | 9.81 | GGB | 1003.94 | GGB | 59.51 | GGB | 176606.41 | GGB | 143699.71 | GGB | 0 | 0 | 3191 | 3600 | 3175.38 | GGB | 100 | GGB | 41.01 | GGB | 41.01 | GGB | 204130.69 | GGB | 204133.11 | 3175.38 | 2629.9844 |  |  |  | 0 | 1 | [14 empty] | 126.7503 | 2629.9844 |  | 104.98
17.04.2008 14:00 | 3600 | 2 | 761.44 | GGB | 762.271 | 771.961 | 767.033 | 270.99 | GGB | 11094.4 | GGB | 9.82 | GGB | 1003.41 | GGB | 59.76 | GGB | 176531.59 | GGB | 143456.51 | GGB | 0 | 0 | 3180 | 3600 | 3164.67 | GGB | 100 | GGB | 41.56 | GGB | 41.56 | GGB | 204172.25 | GGB | 204174.67 | 3164.67 | 2634.443 |  |  |  | 0 | 1 | [14 empty] | 126.109 | 2634.443 |  | 104.98
17.04.2008 15:00 | 3600 | 2 | 760.91 | GGB | 762.271 | 771.961 | 768.132 | 270.51 | GGB | 11066 | GGB | 9.8 | GGB | 1002.8 | GGB | 59.97 | GGB | 176222.39 | GGB | 143027.15 | GGB | 0 | 0 | 3203 | 3600 | 3187.26 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 204213.53 | GGB | 204215.95 | 3187.26 | 2642.3515 |  |  |  | 0 | 1 | [14 empty] | 126.6291 | 2642.3515 |  | 104.98
17.04.2008 16:00 | 3600 | 2 | 760.42 | GGB | 762.271 | 772.148 | 767.033 | 270.72 | GGB | 11062.2 | GGB | 9.8 | GGB | 1002.39 | GGB | 59.79 | GGB | 176583.3 | GGB | 143340.23 | GGB | 0 | 0 | 3236 | 3600 | 3220.6 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 204254.59 | GGB | 204257.01 | 3220.6 | 2636.5801 |  |  |  | 0 | 1 | [14 empty] | 128.2338 | 2636.5801 |  | 104.98
17.04.2008 17:00 | 3600 | 2 | 761.21 | GGB | 762.271 | 771.117 | 767.033 | 270.14 | GGB | 11082.1 | GGB | 9.81 | GGB | 1002.23 | GGB | 59.73 | GGB | 176617.41 | GGB | 143370.35 | GGB | 0 | 0 | 3195 | 3600 | 3178.99 | GGB | 100 | GGB | 40.92 | GGB | 40.92 | GGB | 204295.5 | GGB | 204297.93 | 3178.99 | 2636.0262 |  |  |  | 0 | 1 | [14 empty] | 126.6036 | 2636.0262 |  | 104.98
17.04.2008 18:00 | 3600 | 2 | 760.72 | GGB | 763.37 | 773.203 | 768.132 | 270.51 | GGB | 11100 | GGB | 9.81 | GGB | 1002.18 | GGB | 59.32 | GGB | 177257.81 | GGB | 144061.66 | GGB | 0 | 0 | 3231 | 3600 | 3215.41 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 204336.15 | GGB | 204338.58 | 3215.41 | 2623.3767 |  |  |  | 0 | 1 | [14 empty] | 128.6715 | 2623.3767 |  | 104.98
17.04.2008 19:00 | 3600 | 2 | 760.47 | GGB | 762.271 | 771.305 | 765.934 | 270.56 | GGB | 11088.1 | GGB | 9.8 | GGB | 1001.93 | GGB | 59.34 | GGB | 177291.92 | GGB | 144043.68 | GGB | 0 | 0 | 3230 | 3600 | 3214.33 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 204376.44 | GGB | 204378.87 | 3214.33 | 2623.7041 |  |  |  | 0 | 1 | [14 empty] | 128.6122 | 2623.7041 |  | 104.98
17.04.2008 20:00 | 3600 | 2 | 759.95 | GGB | 761.172 | 770.32 | 765.934 | 272.34 | GGB | 11088.2 | GGB | 9.79 | GGB | 1001.87 | GGB | 59.33 | GGB | 178179.89 | GGB | 144761.41 | GGB | 0 | 0 | 3275 | 3600 | 3259.12 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 204416.82 | GGB | 204419.25 | 3259.12 | 2610.6958 |  |  |  | 0 | 1 | [14 empty] | 131.0541 | 2610.6958 |  | 104.98
17.04.2008 21:00 | 3600 | 2 | 760.47 | GGB | 762.271 | 771.211 | 765.934 | 273.57 | GGB | 11116.7 | GGB | 9.8 | GGB | 1001.85 | GGB | 59.61 | GGB | 178671.74 | GGB | 145037.22 | GGB | 0 | 0 | 3273 | 3600 | 3256.62 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 204457.33 | GGB | 204459.75 | 3256.62 | 2605.7311 |  |  |  | 0 | 1 | [14 empty] | 131.2031 | 2605.7311 |  | 104.98
17.04.2008 22:00 | 3600 | 2 | 761.39 | GGB | 761.172 | 770.883 | 764.835 | 272.62 | GGB | 11124.9 | GGB | 9.82 | GGB | 1001.75 | GGB | 59.94 | GGB | 178350.45 | GGB | 144618.87 | GGB | 0 | 0 | 3220 | 3600 | 3204.61 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 204496.28 | GGB | 204498.71 | 3204.61 | 2613.2689 |  |  |  | 0 | 1 | [14 empty] | 128.7353 | 2613.2689 |  | 104.98
17.04.2008 23:00 | 3600 | 2 | 760.59 | GGB | 762.271 | 771.047 | 767.033 | 272.98 | GGB | 11095.7 | GGB | 9.8 | GGB | 1001.72 | GGB | 60.02 | GGB | 177945.52 | GGB | 144249.04 | GGB | 0 | 0 | 3263 | 3600 | 3246.71 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 204535.86 | GGB | 204538.29 | 3246.71 | 2619.9689 |  |  |  | 0 | 1 | [14 empty] | 130.093 | 2619.9689 |  | 104.98
17.04.2008 24:00 | 3600 | 2 | 761.12 | GGB | 763.37 | 772.898 | 767.033 | 272.95 | GGB | 11080.2 | GGB | 9.81 | GGB | 1001.47 | GGB | 59.86 | GGB | 177921.31 | GGB | 144263.04 | GGB | 0 | 0 | 3218 | 3600 | 3202.35 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 204576.34 | GGB | 204578.77 | 3202.35 | 2619.7147 |  |  |  | 0 | 1 | [14 empty] | 128.328 | 2619.7147 |  | 104.98
18.04.2008 01:00 | 3600 | 2 | 760.96 | GGB | 763.37 | 773.063 | 768.132 | 271.83 | GGB | 11064.9 | GGB | 9.81 | GGB | 1001.27 | GGB | 60.34 | GGB | 176575.6 | GGB | 142938.1 | GGB | 0 | 0 | 3209 | 3600 | 3193.52 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 204617.17 | GGB | 204619.6 | 3193.52 | 2643.9976 |  |  |  | 0 | 1 | [14 empty] | 126.7988 | 2643.9976 |  | 104.98
18.04.2008 02:00 | 3600 | 2 | 761.03 | GGB | 763.37 | 773.016 | 766.667 | 271.8 | GGB | 11053.6 | GGB | 9.81 | GGB | 1000.76 | GGB | 60.54 | GGB | 176499.68 | GGB | 142717.76 | GGB | 0 | 0 | 3208 | 3600 | 3191.9 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 204658.01 | GGB | 204660.43 | 3191.9 | 2648.0797 |  |  |  | 0 | 1 | [14 empty] | 126.5391 | 2648.0797 |  | 104.98
18.04.2008 03:00 | 3600 | 2 | 760.65 | GGB | 761.172 | 770.93 | 766.3 | 272.11 | GGB | 11048.6 | GGB | 9.8 | GGB | 1000.77 | GGB | 60.54 | GGB | 176698.84 | GGB | 142880.44 | GGB | 0 | 0 | 3232 | 3600 | 3216.33 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 204698.78 | GGB | 204701.2 | 3216.33 | 2645.0646 |  |  |  | 0 | 1 | [14 empty] | 127.653 | 2645.0646 |  | 104.98
18.04.2008 04:00 | 3600 | 2 | 760.86 | GGB | 762.271 | 772.008 | 767.766 | 272.4 | GGB | 11049.8 | GGB | 9.8 | GGB | 1000.21 | GGB | 60.57 | GGB | 176842.98 | GGB | 142906.37 | GGB | 0 | 0 | 3220 | 3600 | 3204.61 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 204739.45 | GGB | 204741.87 | 3204.61 | 2644.5847 |  |  |  | 0 | 1 | [14 empty] | 127.2109 | 2644.5847 |  | 104.98
18.04.2008 05:00 | 3600 | 2 | 760.78 | GGB | 762.271 | 771 | 766.667 | 272.45 | GGB | 11045.5 | GGB | 9.8 | GGB | 1000.12 | GGB | 60.5 | GGB | 176803.37 | GGB | 142889.79 | GGB | 0 | 0 | 3224 | 3600 | 3208.13 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 204780.06 | GGB | 204782.48 | 3208.13 | 2644.8916 |  |  |  | 0 | 1 | [14 empty] | 127.3358 | 2644.8916 |  | 104.98
18.04.2008 06:00 | 3600 | 2 | 760.97 | GGB | 761.538 | 770.953 | 766.667 | 272.78 | GGB | 11048.9 | GGB | 9.8 | GGB | 999.84 | GGB | 60.51 | GGB | 176848.48 | GGB | 142882.05 | GGB | 0 | 0 | 3223 | 3600 | 3207.32 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 204820.58 | GGB | 204823 | 3207.32 | 2645.0348 |  |  |  | 0 | 1 | [14 empty] | 127.2968 | 2645.0348 |  | 104.98
18.04.2008 07:00 | 3600 | 2 | 760.76 | GGB | 761.538 | 770.836 | 766.667 | 272.69 | GGB | 11045.7 | GGB | 9.81 | GGB | 999.57 | GGB | 60.61 | GGB | 176874.89 | GGB | 142819.56 | GGB | 0 | 0 | 3225 | 3600 | 3209.38 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 204861.07 | GGB | 204863.49 | 3209.38 | 2646.1922 |  |  |  | 0 | 1 | [14 empty] | 127.3228 | 2646.1922 |  | 104.98
18.04.2008 08:00 | 3600 | 2 | 761.13 | GGB | 762.637 | 771.984 | 767.766 | 272.23 | GGB | 11050.3 | GGB | 9.81 | GGB | 999.49 | GGB | 60.76 | GGB | 176593.21 | GGB | 142517.32 | GGB | 0 | 0 | 3207 | 3600 | 3190.81 | GGB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 204901.97 | GGB | 204904.4 | 3190.81 | 2651.804 |  |  |  | 0 | 1 | [14 empty] | 126.3182 | 2651.804 |  | 104.98
18.04.2008 09:00 | 3600 | 2 | 761.08 | GGB | 761.538 | 771.047 | 766.667 | 271.66 | GGB | 11032.6 | GGB | 9.81 | GGB | 999.57 | GGB | 60.85 | GGB | 176114.56 | GGB | 142106.81 | GGB | 0 | 0 | 3203 | 3209 | 3187.15 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 204941.2 | GGB | 204943.63 | 3187.15 | 2659.4644 |  |  |  | 0 | 1 | [14 empty] | 125.8099 | 2659.4644 |  | 104.98
18.04.2008 10:00 | 3600 | 2 | 761.57 | GGB | 764.102 | 773.086 | 768.864 | 271.17 | GGB | 11028.7 | GGB | 9.82 | GGB | 999.82 | GGB | 60.95 | GGB | 175770.15 | GGB | 141819.95 | GGB | 0 | 0 | 3184 | 3600 | 3168.44 | GGB | 100 | GGB | 41.22 | GGB | 41.22 | GGB | 204982.42 | GGB | 204984.85 | 3168.44 | 2664.8437 |  |  |  | 1 | 1 |  |  |  |  | 141819.95 | 2664.8437 | 141819.95 | 2664.8437 | 9.1686 | [5 empty] | 124.8189 | 2664.8437 |  | 104.98
18.04.2008 11:00 | 3600 | 2 | 761.25 | GGB | 763.004 | 772.172 | 767.766 | 270.4 | GGB | 10990 | GGB | 9.81 | GGB | 999.08 | GGB | 61.13 | GGB | 174882.18 | GGB | 140925.97 | GGB | 0 | 0 | 3167 | 3600 | 3150.87 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 205022.44 | GGB | 205024.87 | 3150.87 | 2681.7484 |  |  |  | 0 | 1 | [14 empty] | 123.3443 | 2681.7484 |  | 104.98
18.04.2008 12:00 | 3600 | 2 | 761.76 | GGB | 763.004 | 772.031 | 767.766 | 269.25 | GGB | 10948.3 | GGB | 9.82 | GGB | 998.9 | GGB | 61.61 | GGB | 173691.62 | GGB | 139736.82 | GGB | 0 | 0 | 3122 | 3600 | 3105.89 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 205063.43 | GGB | 205065.86 | 3105.89 | 2704.5699 |  |  |  | 0 | 1 | [14 empty] | 120.5576 | 2704.5699 |  | 104.98
18.04.2008 13:00 | 3600 | 2 | 761.88 | GGB | 763.004 | 772.875 | 767.766 | 268.48 | GGB | 10906.1 | GGB | 9.81 | GGB | 998.65 | GGB | 61.98 | GGB | 172809.14 | GGB | 138838.49 | GGB | 0 | 0 | 3101 | 3600 | 3085.7 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 205103.22 | GGB | 205105.65 | 3085.7 | 2722.0694 |  |  |  | 0 | 1 | [14 empty] | 119.0039 | 2722.0694 |  | 104.98
18.04.2008 14:00 | 3600 | 2 | 762.35 | GGB | 763.004 | 772.781 | 767.766 | 268.09 | GGB | 10871.4 | GGB | 9.81 | GGB | 998.35 | GGB | 62.26 | GGB | 172024.6 | GGB | 138051.31 | GGB | 0 | 0 | 3077 | 3600 | 3061.54 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 205142.61 | GGB | 205145.04 | 3061.54 | 2737.5908 |  |  |  | 0 | 1 | [14 empty] | 117.4027 | 2737.5908 |  | 104.98
18.04.2008 15:00 | 3600 | 2 | 762.01 | GGB | 763.004 | 771.656 | 767.766 | 267.97 | GGB | 10851 | GGB | 9.8 | GGB | 998.34 | GGB | 62.09 | GGB | 171709.91 | GGB | 137867.69 | GGB | 0 | 0 | 3090 | 3600 | 3074.64 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 205181.97 | GGB | 205184.4 | 3074.64 | 2741.2369 |  |  |  | 0 | 1 | [14 empty] | 117.7482 | 2741.2369 |  | 104.98
18.04.2008 16:00 | 3600 | 2 | 762.28 | GGB | 762.637 | 771.938 | 767.033 | 267.67 | GGB | 10840.3 | GGB | 9.81 | GGB | 998.2 | GGB | 62.47 | GGB | 171309.38 | GGB | 137371.69 | GGB | 0 | 0 | 3072 | 3600 | 3055.8 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 205221.35 | GGB | 205223.79 | 3055.8 | 2751.1345 |  |  |  | 0 | 1 | [14 empty] | 116.6057 | 2751.1345 |  | 104.98
18.04.2008 17:00 | 3600 | 2 | 762.04 | GGB | 763.004 | 771.797 | 767.033 | 268.25 | GGB | 10864.1 | GGB | 9.8 | GGB | 998.29 | GGB | 62.14 | GGB | 172189.65 | GGB | 138227.21 | GGB | 0 | 0 | 3105 | 3600 | 3089.38 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 205261.26 | GGB | 205263.7 | 3089.38 | 2734.1071 |  |  |  | 0 | 1 | [14 empty] | 118.6212 | 2734.1071 |  | 104.98
18.04.2008 18:00 | 3600 | 2 | 761.91 | GGB | 761.538 | 772.078 | 767.033 | 268.73 | GGB | 10873.8 | GGB | 9.8 | GGB | 998.78 | GGB | 62.11 | GGB | 172289.78 | GGB | 138386.12 | GGB | 0 | 0 | 3113 | 3600 | 3097.34 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 205301.42 | GGB | 205303.86 | 3097.34 | 2730.9675 |  |  |  | 0 | 1 | [14 empty] | 119.0636 | 2730.9675 |  | 104.98
18.04.2008 19:00 | 3600 | 2 | 761.52 | GGB | 762.637 | 771.891 | 765.934 | 269.13 | GGB | 10887.3 | GGB | 9.8 | GGB | 998.93 | GGB | 61.75 | GGB | 172754.13 | GGB | 138928.91 | GGB | 0 | 0 | 3140 | 3600 | 3124.54 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 205341.98 | GGB | 205344.42 | 3124.54 | 2720.2977 |  |  |  | 0 | 1 | [14 empty] | 120.5803 | 2720.2977 |  | 104.98
18.04.2008 20:00 | 3600 | 2 | 762.09 | GGB | 760.44 | 770.742 | 765.934 | 269.43 | GGB | 10900.3 | GGB | 9.81 | GGB | 999.32 | GGB | 62.1 | GGB | 172659.5 | GGB | 138762.18 | GGB | 0 | 0 | 3122 | 3600 | 3106.31 | GGB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 205381.71 | GGB | 205384.15 | 3106.31 | 2723.5663 |  |  |  | 0 | 1 | [14 empty] | 119.7329 | 2723.5663 |  | 104.98
18.04.2008 21:00 | 3600 | 2 | 761.51 | GGB | 762.637 | 772.922 | 768.132 | 270.02 | GGB | 10912 | GGB | 9.81 | GGB | 999.57 | GGB | 62 | GGB | 173375.82 | GGB | 139412.93 | GGB | 0 | 0 | 3148 | 3600 | 3132.25 | GGB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 205421.95 | GGB | 205424.39 | 3132.25 | 2710.8533 |  |  |  | 0 | 1 | [14 empty] | 121.2989 | 2710.8533 |  | 104.98
18.04.2008 22:00 | 3600 | 2 | 761.87 | GGB | 763.004 | 772.57 | 767.033 | 270.15 | GGB | 10919.8 | GGB | 9.81 | GGB | 999.73 | GGB | 61.68 | GGB | 173679.51 | GGB | 139813.62 | GGB | 0 | 0 | 3141 | 3600 | 3125.35 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 205462.77 | GGB | 205465.21 | 3125.35 | 2703.0843 |  |  |  | 0 | 1 | [14 empty] | 121.3796 | 2703.0843 |  | 104.98
18.04.2008 23:00 | 3600 | 2 | 760.99 | GGB | 762.637 | 771.516 | 767.033 | 270.25 | GGB | 10923 | GGB | 9.8 | GGB | 1000.72 | GGB | 61.74 | GGB | 173523.26 | GGB | 139802.47 | GGB | 0 | 0 | 3185 | 3600 | 3168.92 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 205502.54 | GGB | 205504.97 | 3168.92 | 2703.2999 |  |  |  | 0 | 1 | [14 empty] | 123.0619 | 2703.2999 |  | 104.98
18.04.2008 24:00 | 3600 | 2 | 761.11 | GGB | 761.538 | 770.297 | 765.934 | 271.06 | GGB | 10949.9 | GGB | 9.8 | GGB | 1000.88 | GGB | 61.87 | GGB | 174247.29 | GGB | 140353.48 | GGB | 0 | 0 | 3185 | 3600 | 3169.17 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 205542.83 | GGB | 205545.26 | 3169.17 | 2692.6871 |  |  |  | 0 | 1 | [14 empty] | 123.5567 | 2692.6871 |  | 104.98
19.04.2008 01:00 | 3600 | 2 | 761.37 | GGB | 762.637 | 772.453 | 767.033 | 271.28 | GGB | 10969.6 | GGB | 9.81 | GGB | 1000.76 | GGB | 61.78 | GGB | 174663.21 | GGB | 140711.12 | GGB | 0 | 0 | 3188 | 3600 | 3171.92 | GGB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 205583.3 | GGB | 205585.73 | 3171.92 | 2685.8432 |  |  |  | 0 | 1 | [14 empty] | 123.979 | 2685.8432 |  | 104.98
19.04.2008 02:00 | 3600 | 2 | 761.24 | GGB | 762.637 | 772.148 | 767.033 | 271.7 | GGB | 10978 | GGB | 9.81 | GGB | 1001.01 | GGB | 61.54 | GGB | 175465.36 | GGB | 141491.67 | GGB | 0 | 0 | 3187 | 3600 | 3170.86 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 205623.7 | GGB | 205626.13 | 3170.86 | 2671.0265 |  |  |  | 0 | 1 | [14 empty] | 124.6251 | 2671.0265 |  | 104.98
19.04.2008 03:00 | 3600 | 2 | 761.35 | GGB | 761.538 | 771.07 | 767.033 | 271.69 | GGB | 10978.2 | GGB | 9.8 | GGB | 1000.97 | GGB | 61.44 | GGB | 175305.81 | GGB | 141400.43 | GGB | 0 | 0 | 3195 | 3600 | 3178.7 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 205663.77 | GGB | 205666.2 | 3178.7 | 2672.75 |  |  |  | 0 | 1 | [14 empty] | 124.8527 | 2672.75 |  | 104.98
19.04.2008 04:00 | 3600 | 2 | 761.34 | GGB | 762.637 | 772.078 | 767.033 | 271.95 | GGB | 10998.1 | GGB | 9.81 | GGB | 1001.32 | GGB | 61.33 | GGB | 175600.7 | GGB | 141734.47 | GGB | 0 | 0 | 3198 | 3600 | 3182.31 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 205703.46 | GGB | 205705.89 | 3182.31 | 2666.4509 |  |  |  | 0 | 1 | [14 empty] | 125.2897 | 2666.4509 |  | 104.98
19.04.2008 05:00 | 3600 | 2 | 761.12 | GGB | 762.637 | 772.242 | 768.132 | 272.33 | GGB | 11004.1 | GGB | 9.8 | GGB | 1001.7 | GGB | 61.25 | GGB | 176021.03 | GGB | 142160.4 | GGB | 0 | 0 | 3211 | 3600 | 3194.93 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 205743.29 | GGB | 205745.72 | 3194.93 | 2658.4619 |  |  |  | 0 | 1 | [14 empty] | 126.1646 | 2658.4619 |  | 104.98
19.04.2008 06:00 | 3600 | 2 | 761.84 | GGB | 762.637 | 772.172 | 767.033 | 272.69 | GGB | 10999 | GGB | 9.81 | GGB | 1001.86 | GGB | 61 | GGB | 176862.79 | GGB | 142971.23 | GGB | 0 | 0 | 3184 | 3600 | 3168.3 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 205783.2 | GGB | 205785.63 | 3168.3 | 2643.385 |  |  |  | 0 | 1 | [14 empty] | 125.8266 | 2643.385 |  | 104.98
19.04.2008 07:00 | 3600 | 2 | 761.07 | GGB | 761.538 | 771.117 | 765.934 | 272.22 | GGB | 11015.4 | GGB | 9.8 | GGB | 1001.98 | GGB | 61.21 | GGB | 176109.06 | GGB | 142290.25 | GGB | 0 | 0 | 3218 | 3600 | 3202.64 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 205823.21 | GGB | 205825.64 | 3202.64 | 2656.0358 |  |  |  | 0 | 1 | [14 empty] | 126.5846 | 2656.0358 |  | 104.98
19.04.2008 08:00 | 3600 | 2 | 761.22 | GGB | 761.538 | 772.195 | 766.667 | 272.4 | GGB | 11029 | GGB | 9.81 | GGB | 1002.41 | GGB | 61.19 | GGB | 176151.97 | GGB | 142394.83 | GGB | 0 | 0 | 3214 | 3600 | 3197.86 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 205863.35 | GGB | 205865.78 | 3197.86 | 2654.0851 |  |  |  | 0 | 1 | [14 empty] | 126.4885 | 2654.0851 |  | 104.98
19.04.2008 09:00 | 3600 | 2 | 761.31 | GGB | 762.637 | 772.43 | 766.667 | 272.76 | GGB | 11034.1 | GGB | 9.8 | GGB | 1002.54 | GGB | 61.16 | GGB | 176345.63 | GGB | 142584.19 | GGB | 0 | 0 | 3219 | 3600 | 3203.41 | GGB | 100 | GGB | 40.37 | GGB | 40.37 | GGB | 205903.72 | GGB | 205906.15 | 3203.41 | 2650.5603 |  |  |  | 0 | 1 | [14 empty] | 126.8766 | 2650.5603 |  | 104.98
19.04.2008 10:00 | 3600 | 2 | 761.76 | GGB | 762.637 | 771.469 | 766.3 | 272.12 | GGB | 11033.4 | GGB | 9.81 | GGB | 1003.11 | GGB | 61.33 | GGB | 175721.74 | GGB | 142087.19 | GGB | 0 | 0 | 3184 | 3600 | 3167.98 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 205944.15 | GGB | 205946.58 | 3167.98 | 2659.8316 |  |  |  | 0 | 1 | [14 empty] | 125.0359 | 2659.8316 |  | 104.98
19.04.2008 11:00 | 3600 | 2 | 761.5 | GGB | 764.102 | 773.531 | 768.864 | 271.36 | GGB | 10998 | GGB | 9.82 | GGB | 1003.42 | GGB | 61.89 | GGB | 175101.15 | GGB | 141389.63 | GGB | 0 | 0 | 3149 | 3600 | 3133.57 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 205984.53 | GGB | 205986.96 | 3133.57 | 2672.9542 |  |  |  | 1 | 1 |  |  |  |  | 141389.63 | 2672.9542 | 141389.63 | 2672.9542 | 9.3593 | [5 empty] | 123.0706 | 2672.9542 |  | 104.98
19.04.2008 12:00 | 3600 | 2 | 762.11 | GGB | 764.102 | 772.57 | 768.864 | 270.43 | GGB | 10963.3 | GGB | 9.82 | GGB | 1003.68 | GGB | 62.1 | GGB | 174143.85 | GGB | 140565.31 | GGB | 0 | 0 | 3114 | 3600 | 3097.92 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 206024.88 | GGB | 206027.31 | 3097.92 | 2688.6292 |  |  |  | 1 | 1 |  |  |  |  | 140565.31 | 2688.6292 | 140565.31 | 2688.6292 | 9.3662 | [5 empty] | 120.9611 | 2688.6292 |  | 104.98
19.04.2008 13:00 | 3600 | 2 | 762.57 | GGB | 763.004 | 773.648 | 767.766 | 269.67 | GGB | 10935.9 | GGB | 9.82 | GGB | 1003.44 | GGB | 62.32 | GGB | 173336.21 | GGB | 139790.28 | GGB | 0 | 0 | 3087 | 3600 | 3071.1 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 206065.18 | GGB | 206067.61 | 3071.1 | 2703.5356 |  |  |  | 0 | 1 | [14 empty] | 119.2528 | 2703.5356 |  | 104.98
19.04.2008 14:00 | 3600 | 2 | 764 | GGB | 763.004 | 772.195 | 767.766 | 268.15 | GGB | 10859.5 | GGB | 9.83 | GGB | 1002.96 | GGB | 63.24 | GGB | 171026.6 | GGB | 137484.15 | GGB | 0 | 0 | 2983 | 3600 | 2967.11 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 206105.3 | GGB | 206107.73 | 2967.11 | 2748.8841 |  |  |  | 0 | 1 | [14 empty] | 113.3141 | 2748.8841 |  | 104.98
19.04.2008 15:00 | 3600 | 2 | 760.99 | GGB | 765.201 | 775.594 | 770.33 | 268.18 | GGB | 10771.7 | GGB | 9.77 | GGB | 1002.8 | GGB | 63.32 | GGB | 171386.41 | GGB | 137718.93 | GGB | 0 | 0 | 3133 | 3600 | 3117.42 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 206145.34 | GGB | 206147.77 | 3117.42 | 2744.1979 |  |  |  | 1 | 1 |  |  |  |  | 137718.93 | 2744.1979 | 137718.93 | 2744.1979 | 9.4388 | [5 empty] | 119.2577 | 2744.1979 |  | 104.98
19.04.2008 16:00 | 3600 | 2 | 763.5 | GGB | 765.201 | 774.609 | 770.33 | 267.82 | GGB | 10864 | GGB | 9.82 | GGB | 1002.85 | GGB | 63.08 | GGB | 171548.16 | GGB | 137951.07 | GGB | 0 | 0 | 3023 | 3600 | 3006.91 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 206185.51 | GGB | 206187.94 | 3006.91 | 2739.5801 |  |  |  | 1 | 1 |  |  |  |  | 137951.07 | 2739.5801 | 137951.07 | 2739.5801 | 9.4082 | [5 empty] | 115.224 | 2739.5801 |  | 104.98
19.04.2008 17:00 | 3600 | 2 | 763.46 | GGB | 763.004 | 772.453 | 768.498 | 266.99 | GGB | 10869.2 | GGB | 9.81 | GGB | 1002.86 | GGB | 62.78 | GGB | 171657.09 | GGB | 138165.25 | GGB | 0 | 0 | 3020 | 3600 | 3004.25 | GGB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 206225.85 | GGB | 206228.28 | 3004.25 | 2735.3332 |  |  |  | 0 | 1 | [14 empty] | 115.3008 | 2735.3332 |  | 104.98
19.04.2008 18:00 | 3600 | 2 | 762.06 | GGB | 760.44 | 770.625 | 765.934 | 267.31 | GGB | 10815.4 | GGB | 9.79 | GGB | 1002.88 | GGB | 61.86 | GGB | 172935.68 | GGB | 139580.55 | GGB | 0 | 0 | 3035 | 3600 | 3019.41 | GGB | 100 | GGB | 40.53 | GGB | 40.53 | GGB | 206266.38 | GGB | 206268.81 | 3019.41 | 2707.5979 |  |  |  | 0 | 1 | [14 empty] | 117.0697 | 2707.5979 |  | 104.98
19.04.2008 19:00 | 3600 | 2 | 763.99 | GGB | 763.004 | 772.805 | 767.766 | 266.18 | GGB | 10886.9 | GGB | 9.83 | GGB | 1002.84 | GGB | 62.01 | GGB | 171219.16 | GGB | 138127.71 | GGB | 0 | 0 | 2963 | 3600 | 2947.1 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 206306.77 | GGB | 206309.19 | 2947.1 | 2736.0766 |  |  |  | 0 | 1 | [14 empty] | 113.0767 | 2736.0766 |  | 104.98
19.04.2008 20:00 | 3600 | 2 | 761.96 | GGB | 763.004 | 772.781 | 768.864 | 266.99 | GGB | 10871.5 | GGB | 9.8 | GGB | 1002.8 | GGB | 61.9 | GGB | 172086.22 | GGB | 138866.42 | GGB | 0 | 0 | 3064 | 3600 | 3048.05 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 206347.12 | GGB | 206349.55 | 3048.05 | 2721.5219 |  |  |  | 0 | 1 | [14 empty] | 117.5755 | 2721.5219 |  | 104.98
19.04.2008 21:00 | 3600 | 2 | 762.02 | GGB | 763.004 | 772.781 | 767.766 | 267.34 | GGB | 10896 | GGB | 9.8 | GGB | 1003.01 | GGB | 61.78 | GGB | 172505.45 | GGB | 139284.74 | GGB | 0 | 0 | 3059 | 3600 | 3042.99 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 206387.48 | GGB | 206389.91 | 3042.99 | 2713.3482 |  |  |  | 0 | 1 | [14 empty] | 117.7339 | 2713.3482 |  | 104.98
19.04.2008 22:00 | 3600 | 2 | 762.42 | GGB | 763.004 | 772.781 | 768.864 | 267.67 | GGB | 10927.6 | GGB | 9.81 | GGB | 1003.55 | GGB | 61.33 | GGB | 173554.07 | GGB | 140396.14 | GGB | 0 | 0 | 3053 | 3600 | 3036.84 | GGB | 100 | GGB | 40.52 | GGB | 40.52 | GGB | 206428 | GGB | 206430.43 | 3036.84 | 2691.8689 |  |  |  | 0 | 1 | [14 empty] | 118.4335 | 2691.8689 |  | 104.98
19.04.2008 23:00 | 3600 | 2 | 762.13 | GGB | 763.004 | 772.547 | 767.766 | 268.41 | GGB | 10923.7 | GGB | 9.8 | GGB | 1003.86 | GGB | 61.22 | GGB | 173808.25 | GGB | 140691.36 | GGB | 0 | 0 | 3081 | 3600 | 3065.2 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 206468.27 | GGB | 206470.7 | 3065.2 | 2686.2204 |  |  |  | 0 | 1 | [14 empty] | 119.7909 | 2686.2204 |  | 104.98
19.04.2008 24:00 | 3600 | 2 | 761.78 | GGB | 763.004 | 772.711 | 767.766 | 268.4 | GGB | 10944.1 | GGB | 9.8 | GGB | 1003.65 | GGB | 61.19 | GGB | 173727.93 | GGB | 140607.83 | GGB | 0 | 0 | 3094 | 3600 | 3077.98 | GGB | 100 | GGB | 40.23 | GGB | 40.23 | GGB | 206508.5 | GGB | 206510.93 | 3077.98 | 2687.8162 |  |  |  | 0 | 1 | [14 empty] | 120.2189 | 2687.8162 |  | 104.98
20.04.2008 01:00 | 3600 | 2 | 761.64 | GGB | 763.004 | 772.57 | 767.766 | 268.74 | GGB | 10956 | GGB | 9.8 | GGB | 1003.71 | GGB | 61.07 | GGB | 174111.94 | GGB | 140976.36 | GGB | 0 | 0 | 3104 | 3600 | 3087.98 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 206548.61 | GGB | 206551.04 | 3087.98 | 2680.7899 |  |  |  | 0 | 1 | [14 empty] | 120.9256 | 2680.7899 |  | 104.98
20.04.2008 02:00 | 3600 | 2 | 761.8 | GGB | 761.538 | 771.891 | 766.667 | 269.16 | GGB | 10967.1 | GGB | 9.81 | GGB | 1003.63 | GGB | 61.04 | GGB | 174447.55 | GGB | 141252.64 | GGB | 0 | 0 | 3095 | 3600 | 3079.01 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 206588.86 | GGB | 206591.29 | 3079.01 | 2675.5465 |  |  |  | 0 | 1 | [14 empty] | 120.8106 | 2675.5465 |  | 104.98
20.04.2008 03:00 | 3600 | 2 | 761.78 | GGB | 763.004 | 772.781 | 767.766 | 269.3 | GGB | 10983.1 | GGB | 9.8 | GGB | 1003.36 | GGB | 60.84 | GGB | 174842.57 | GGB | 141617.62 | GGB | 0 | 0 | 3130 | 3600 | 3114.33 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 206628.95 | GGB | 206631.38 | 3114.33 | 2668.651 |  |  |  | 0 | 1 | [14 empty] | 122.5122 | 2668.651 |  | 104.98
20.04.2008 04:00 | 3600 | 2 | 761.78 | GGB | 764.102 | 774 | 768.864 | 270.33 | GGB | 10980.4 | GGB | 9.8 | GGB | 1003.58 | GGB | 60.53 | GGB | 176247.7 | GGB | 142919.52 | GGB | 0 | 0 | 3118 | 3600 | 3102.22 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 206669.01 | GGB | 206671.45 | 3102.22 | 2644.3414 |  |  |  | 1 | 1 |  |  |  |  | 142919.52 | 2644.3414 | 142919.52 | 2644.3414 | 9.4317 | [5 empty] | 123.1577 | 2644.3414 |  | 104.98
20.04.2008 05:00 | 3600 | 2 | 761.65 | GGB | 764.102 | 773.133 | 767.766 | 269.64 | GGB | 11009.4 | GGB | 9.8 | GGB | 1003.54 | GGB | 60.74 | GGB | 175113.25 | GGB | 141906.53 | GGB | 0 | 0 | 3136 | 3600 | 3119.77 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 206709.06 | GGB | 206711.49 | 3119.77 | 2663.2178 |  |  |  | 1 | 1 |  |  |  |  | 141906.53 | 2663.2178 | 141906.53 | 2663.2178 | 9.4388 | [5 empty] | 122.9766 | 2663.2178 |  | 104.98
20.04.2008 06:00 | 3600 | 2 | 761.12 | GGB | 763.004 | 772.055 | 766.667 | 270.37 | GGB | 11024.5 | GGB | 9.8 | GGB | 1003.87 | GGB | 60.43 | GGB | 175999.02 | GGB | 142801.13 | GGB | 0 | 0 | 3160 | 3600 | 3144 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 206749.18 | GGB | 206751.61 | 3144 | 2646.5337 |  |  |  | 0 | 1 | [14 empty] | 124.713 | 2646.5337 |  | 104.98
20.04.2008 07:00 | 3600 | 2 | 760.75 | GGB | 761.538 | 771.938 | 766.667 | 271.5 | GGB | 11059 | GGB | 9.8 | GGB | 1004.29 | GGB | 60.18 | GGB | 177142.27 | GGB | 143898.96 | GGB | 0 | 0 | 3197 | 3600 | 3181.06 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 206789.43 | GGB | 206791.86 | 3181.06 | 2626.3428 |  |  |  | 0 | 1 | [14 empty] | 127.1531 | 2626.3428 |  | 104.98
20.04.2008 08:00 | 3600 | 2 | 761.5 | GGB | 763.004 | 771.867 | 767.766 | 271.24 | GGB | 11078.1 | GGB | 9.81 | GGB | 1004.61 | GGB | 60.24 | GGB | 176937.61 | GGB | 143753.07 | GGB | 0 | 0 | 3167 | 3600 | 3151.63 | GGB | 100 | GGB | 40.29 | GGB | 40.29 | GGB | 206829.71 | GGB | 206832.15 | 3151.63 | 2629.0082 |  |  |  | 0 | 1 | [14 empty] | 125.849 | 2629.0082 |  | 104.98
20.04.2008 09:00 | 3600 | 2 | 761.99 | GGB | 762.637 | 773.133 | 767.766 | 269.98 | GGB | 11049.6 | GGB | 9.82 | GGB | 1004.83 | GGB | 60.46 | GGB | 175978.12 | GGB | 142910.88 | GGB | 0 | 0 | 3125 | 3600 | 3109 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 206869.91 | GGB | 206872.35 | 3109 | 2644.5012 |  |  |  | 0 | 1 | [14 empty] | 123.4194 | 2644.5012 |  | 104.98
20.04.2008 10:00 | 3600 | 2 | 762.88 | GGB | 765.201 | 774.141 | 769.963 | 270.39 | GGB | 10980.3 | GGB | 9.82 | GGB | 1005.02 | GGB | 60.18 | GGB | 177032.24 | GGB | 143914.45 | GGB | 0 | 0 | 3063 | 3600 | 3047.22 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 206910.25 | GGB | 206912.68 | 3047.22 | 2626.0601 |  |  |  | 1 | 1 |  |  |  |  | 143914.45 | 2626.0601 | 143914.45 | 2626.0601 | 9.3709 | [5 empty] | 121.8164 | 2626.0601 |  | 104.98
20.04.2008 11:00 | 3600 | 2 | 764.24 | GGB | 766.667 | 776.438 | 771.429 | 267.81 | GGB | 10941.7 | GGB | 9.84 | GGB | 1005.26 | GGB | 61.02 | GGB | 173942.49 | GGB | 141079.19 | GGB | 0 | 0 | 2981 | 3600 | 2964.92 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 206950.33 | GGB | 206952.77 | 2964.92 | 2678.8359 |  |  |  | 1 | 1 |  |  |  |  | 141079.19 | 2678.8359 | 141079.19 | 2678.8359 | 9.427 | [5 empty] | 116.1913 | 2678.8359 |  | 104.98
20.04.2008 12:00 | 3600 | 2 | 763.38 | GGB | 764.102 | 774.211 | 769.963 | 265.45 | GGB | 10867.6 | GGB | 9.81 | GGB | 1004.76 | GGB | 61.8 | GGB | 171182.84 | GGB | 138450.93 | GGB | 0 | 0 | 2993 | 3600 | 2977.47 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 206990.21 | GGB | 206992.65 | 2977.47 | 2729.6891 |  |  |  | 1 | 1 |  |  |  |  | 138450.93 | 2729.6891 | 138450.93 | 2729.6891 | 9.4766 | [5 empty] | 114.5093 | 2729.6891 |  | 104.98
20.04.2008 13:00 | 3600 | 2 | 763.99 | GGB | 764.102 | 775.219 | 770.33 | 264.59 | GGB | 10836 | GGB | 9.81 | GGB | 1004.29 | GGB | 62.15 | GGB | 170389.5 | GGB | 137599.27 | GGB | 0 | 0 | 2940 | 3600 | 2924.11 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 207029.98 | GGB | 207032.42 | 2924.11 | 2746.5843 |  |  |  | 1 | 1 |  |  |  |  | 137599.27 | 2746.5843 | 137599.27 | 2746.5843 | 9.5028 | [5 empty] | 111.7654 | 2746.5843 |  | 104.98
20.04.2008 14:00 | 3600 | 2 | 763.72 | GGB | 765.201 | 775.031 | 769.963 | 264.09 | GGB | 10802 | GGB | 9.8 | GGB | 1004.2 | GGB | 62.21 | GGB | 169929.56 | GGB | 137192.84 | GGB | 0 | 0 | 2945 | 3600 | 2928.94 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 207069.57 | GGB | 207072.01 | 2928.94 | 2754.721 |  |  |  | 1 | 1 |  |  |  |  | 137192.84 | 2754.721 | 137192.84 | 2754.721 | 9.546 | [5 empty] | 111.6193 | 2754.721 |  | 104.98
20.04.2008 15:00 | 3600 | 2 | 764.15 | GGB | 765.201 | 776.953 | 771.429 | 264.01 | GGB | 10811.5 | GGB | 9.81 | GGB | 1004.46 | GGB | 62.37 | GGB | 169707.29 | GGB | 136982.94 | GGB | 0 | 0 | 2921 | 3600 | 2905.61 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 207108.94 | GGB | 207111.38 | 2905.61 | 2758.9421 |  |  |  | 1 | 1 |  |  |  |  | 136982.94 | 2758.9421 | 136982.94 | 2758.9421 | 9.5994 | [5 empty] | 110.5608 | 2758.9421 |  | 104.98
20.04.2008 16:00 | 3600 | 2 | 763.59 | GGB | 765.201 | 775.617 | 770.33 | 264.05 | GGB | 10793.4 | GGB | 9.8 | GGB | 1004.45 | GGB | 62.42 | GGB | 169760.11 | GGB | 137002.85 | GGB | 0 | 0 | 2945 | 3600 | 2928.97 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 207148.12 | GGB | 207150.56 | 2928.97 | 2758.5412 |  |  |  | 1 | 1 |  |  |  |  | 137002.85 | 2758.5412 | 137002.85 | 2758.5412 | 9.6459 | [5 empty] | 111.4659 | 2758.5412 |  | 104.98
20.04.2008 17:00 | 3600 | 2 | 763.81 | GGB | 765.201 | 775.617 | 770.696 | 264.03 | GGB | 10794 | GGB | 9.8 | GGB | 1004.6 | GGB | 62.49 | GGB | 169620.37 | GGB | 136882.05 | GGB | 0 | 0 | 2931 | 3600 | 2915.45 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 207187.24 | GGB | 207189.68 | 2915.45 | 2760.9756 |  |  |  | 1 | 1 |  |  |  |  | 136882.05 | 2760.9756 | 136882.05 | 2760.9756 | 9.6607 | [5 empty] | 110.8535 | 2760.9756 |  | 104.98
20.04.2008 18:00 | 3600 | 2 | 763.83 | GGB | 764.102 | 774.586 | 768.498 | 264.36 | GGB | 10798.7 | GGB | 9.8 | GGB | 1004.9 | GGB | 62.32 | GGB | 169843.73 | GGB | 137170.19 | GGB | 0 | 0 | 2939 | 3600 | 2923.27 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 207226.27 | GGB | 207228.72 | 2923.27 | 2755.1759 |  |  |  | 1 | 1 |  |  |  |  | 137170.19 | 2755.1759 | 137170.19 | 2755.1759 | 9.6805 | [5 empty] | 111.3849 | 2755.1759 |  | 104.98
20.04.2008 19:00 | 3600 | 2 | 763.76 | GGB | 764.102 | 773.531 | 769.597 | 264.64 | GGB | 10809.8 | GGB | 9.8 | GGB | 1005.23 | GGB | 62.21 | GGB | 170225.55 | GGB | 137572.53 | GGB | 0 | 0 | 2954 | 3600 | 2938.33 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 207265.3 | GGB | 207267.74 | 2938.33 | 2747.1182 |  |  |  | 1 | 1 |  |  |  |  | 137572.53 | 2747.1182 | 137572.53 | 2747.1182 | 9.6855 | [5 empty] | 112.2871 | 2747.1182 |  | 104.98
20.04.2008 20:00 | 3600 | 2 | 763.64 | GGB | 763.004 | 773.625 | 768.498 | 265.1 | GGB | 10830.2 | GGB | 9.81 | GGB | 1006.07 | GGB | 62.28 | GGB | 170456.62 | GGB | 137844.7 | GGB | 0 | 0 | 2963 | 3600 | 2947.52 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 207304.79 | GGB | 207307.24 | 2947.52 | 2741.6941 |  |  |  | 0 | 1 | [14 empty] | 112.8611 | 2741.6941 |  | 104.98
20.04.2008 21:00 | 3600 | 2 | 763.07 | GGB | 763.004 | 773.813 | 768.132 | 265.82 | GGB | 10847.6 | GGB | 9.8 | GGB | 1006.57 | GGB | 62.26 | GGB | 171033.2 | GGB | 138389.45 | GGB | 0 | 0 | 3005 | 3600 | 2989.58 | GGB | 100 | GGB | 42.6 | GGB | 42.6 | GGB | 207347.4 | GGB | 207349.84 | 2989.58 | 2730.9018 |  |  |  | 0 | 1 | [14 empty] | 114.924 | 2730.9018 |  | 104.98
20.04.2008 22:00 | 3600 | 2 | 762.76 | GGB | 761.538 | 771.609 | 767.033 | 266.2 | GGB | 10888.5 | GGB | 9.8 | GGB | 1006.9 | GGB | 61.78 | GGB | 172118.13 | GGB | 139511.78 | GGB | 0 | 0 | 3024 | 3600 | 3008.13 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 207387.79 | GGB | 207390.23 | 3008.13 | 2708.9325 |  |  |  | 0 | 1 | [14 empty] | 116.5749 | 2708.9325 |  | 104.98
20.04.2008 23:00 | 3600 | 2 | 762.42 | GGB | 765.201 | 774.984 | 769.597 | 267.72 | GGB | 10909 | GGB | 9.8 | GGB | 1007.27 | GGB | 61.27 | GGB | 173211.87 | GGB | 140661.93 | GGB | 0 | 0 | 3060 | 3600 | 3044.12 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 207427.49 | GGB | 207429.94 | 3044.12 | 2686.7824 |  |  |  | 1 | 1 |  |  |  |  | 140661.93 | 2686.7824 | 140661.93 | 2686.7824 | 9.5172 | [5 empty] | 118.9422 | 2686.7824 |  | 104.98
20.04.2008 24:00 | 3600 | 2 | 762.43 | GGB | 763.004 | 773.789 | 768.498 | 268.36 | GGB | 10938.1 | GGB | 9.8 | GGB | 1007.62 | GGB | 61.26 | GGB | 173839.06 | GGB | 141226.06 | GGB | 0 | 0 | 3071 | 3600 | 3054.9 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 207467.45 | GGB | 207469.89 | 3054.9 | 2676.05 |  |  |  | 0 | 1 | [14 empty] | 119.8421 | 2676.05 |  | 104.98
21.04.2008 01:00 | 3600 | 2 | 762.18 | GGB | 763.004 | 773.719 | 768.132 | 268.76 | GGB | 10956.5 | GGB | 9.8 | GGB | 1007.78 | GGB | 61.11 | GGB | 174122.95 | GGB | 141542.59 | GGB | 0 | 0 | 3086 | 3600 | 3069.81 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 207507.66 | GGB | 207510.1 | 3069.81 | 2670.0656 |  |  |  | 0 | 1 | [14 empty] | 120.6969 | 2670.0656 |  | 104.98
21.04.2008 02:00 | 3600 | 2 | 762.24 | GGB | 763.004 | 773.461 | 768.498 | 270.49 | GGB | 10942.9 | GGB | 9.8 | GGB | 1008.18 | GGB | 60.49 | GGB | 176510.68 | GGB | 143807.32 | GGB | 0 | 0 | 3078 | 3600 | 3061.89 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 207548.1 | GGB | 207550.55 | 3061.89 | 2628.0164 |  |  |  | 0 | 1 | [14 empty] | 122.3117 | 2628.0164 |  | 104.98
21.04.2008 03:00 | 3600 | 2 | 762.96 | GGB | 763.004 | 773.813 | 768.498 | 270.27 | GGB | 10988.7 | GGB | 9.81 | GGB | 1008.2 | GGB | 60.32 | GGB | 176154.17 | GGB | 143592.77 | GGB | 0 | 0 | 3056 | 3600 | 3040.19 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 207588.37 | GGB | 207590.82 | 3040.19 | 2631.9431 |  |  |  | 0 | 1 | [14 empty] | 121.2637 | 2631.9431 |  | 104.98
21.04.2008 04:00 | 3600 | 2 | 761.93 | GGB | 763.004 | 772.922 | 767.033 | 269.6 | GGB | 11003 | GGB | 9.8 | GGB | 1008.48 | GGB | 60.68 | GGB | 175299.21 | GGB | 142782.95 | GGB | 0 | 0 | 3116 | 3600 | 3100.49 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 207628.68 | GGB | 207631.12 | 3100.49 | 2646.8707 |  |  |  | 0 | 1 | [14 empty] | 122.9714 | 2646.8707 |  | 104.98
21.04.2008 05:00 | 3600 | 2 | 761.92 | GGB | 764.102 | 773.977 | 768.132 | 269.99 | GGB | 11016.7 | GGB | 9.8 | GGB | 1008.7 | GGB | 60.63 | GGB | 175745.95 | GGB | 143199.46 | GGB | 0 | 0 | 3129 | 3600 | 3112.79 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 207669.06 | GGB | 207671.51 | 3112.79 | 2639.172 |  |  |  | 1 | 1 |  |  |  |  | 143199.46 | 2639.172 | 143199.46 | 2639.172 | 9.357 | [5 empty] | 123.8194 | 2639.172 |  | 104.98
21.04.2008 06:00 | 3600 | 2 | 761.82 | GGB | 763.004 | 772.781 | 768.132 | 270.43 | GGB | 11033.8 | GGB | 9.8 | GGB | 1009.3 | GGB | 60.58 | GGB | 176133.26 | GGB | 143619.75 | GGB | 0 | 0 | 3137 | 3600 | 3120.98 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 207709.5 | GGB | 207711.94 | 3120.98 | 2631.4487 |  |  |  | 0 | 1 | [14 empty] | 124.5095 | 2631.4487 |  | 104.98
21.04.2008 07:00 | 3600 | 2 | 762.4 | GGB | 764.102 | 773.672 | 769.597 | 270.41 | GGB | 11044.5 | GGB | 9.81 | GGB | 1009.38 | GGB | 60.58 | GGB | 176033.13 | GGB | 143548.56 | GGB | 0 | 0 | 3123 | 3600 | 3107.62 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 207749.93 | GGB | 207752.37 | 3107.62 | 2632.7537 |  |  |  | 1 | 1 |  |  |  |  | 143548.56 | 2632.7537 | 143548.56 | 2632.7537 | 9.3477 | [5 empty] | 123.9151 | 2632.7537 |  | 104.98
21.04.2008 08:00 | 3600 | 2 | 761.82 | GGB | 764.102 | 773.719 | 768.498 | 271.4 | GGB | 11004.8 | GGB | 9.8 | GGB | 1009.98 | GGB | 60.33 | GGB | 177409.66 | GGB | 144865.91 | GGB | 0 | 0 | 3125 | 3600 | 3109.66 | GGB | 100 | GGB | 40.54 | GGB | 40.54 | GGB | 207790.47 | GGB | 207792.91 | 3109.66 | 2608.8125 |  |  |  | 1 | 1 |  |  |  |  | 144865.91 | 2608.8125 | 144865.91 | 2608.8125 | 9.3223 | [5 empty] | 125.1344 | 2608.8125 |  | 104.98
21.04.2008 09:00 | 3600 | 2 | 762.92 | GGB | 763.004 | 772.828 | 768.132 | 271.67 | GGB | 10997.2 | GGB | 9.81 | GGB | 1010.23 | GGB | 59.84 | GGB | 177662.73 | GGB | 145324.33 | GGB | 0 | 0 | 3074 | 3600 | 3058.48 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 207830.83 | GGB | 207833.27 | 3058.48 | 2600.5831 |  |  |  | 0 | 1 | [14 empty] | 123.4643 | 2600.5831 |  | 104.98
21.04.2008 10:00 | 3600 | 2 | 764.19 | GGB | 764.102 | 775.055 | 769.597 | 268.76 | GGB | 10998.4 | GGB | 9.83 | GGB | 1010.37 | GGB | 61.28 | GGB | 174113.04 | GGB | 141823.31 | GGB | 0 | 0 | 3018 | 3600 | 3002.07 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 207870.88 | GGB | 207873.32 | 3002.07 | 2664.7806 |  |  |  | 1 | 1 |  |  |  |  | 141823.31 | 2664.7806 | 141823.31 | 2664.7806 | 9.4364 | [5 empty] | 118.2676 | 2664.7806 |  | 104.98
21.04.2008 11:00 | 3600 | 2 | 764.11 | GGB | 764.102 | 775.195 | 769.597 | 267.53 | GGB | 10924 | GGB | 9.82 | GGB | 1010.58 | GGB | 61.66 | GGB | 172750.83 | GGB | 140588.11 | GGB | 0 | 0 | 2991 | 3600 | 2975.62 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 207911.53 | GGB | 207913.97 | 2975.62 | 2688.1932 |  |  |  | 1 | 1 |  |  |  |  | 140588.11 | 2688.1932 | 140588.11 | 2688.1932 | 9.2971 | [5 empty] | 116.2047 | 2688.1932 |  | 104.98
21.04.2008 12:00 | 3600 | 2 | 764.29 | GGB | 766.3 | 776.086 | 771.795 | 267.17 | GGB | 10905.6 | GGB | 9.81 | GGB | 1010.54 | GGB | 61.81 | GGB | 172600.08 | GGB | 140395.96 | GGB | 0 | 0 | 2977 | 3600 | 2961.21 | GGB | 100 | GGB | 40.86 | GGB | 40.86 | GGB | 207952.39 | GGB | 207954.83 | 2961.21 | 2691.8723 |  |  |  | 1 | 1 |  |  |  |  | 140395.96 | 2691.8723 | 140395.96 | 2691.8723 | 9.2493 | [5 empty] | 115.4839 | 2691.8723 |  | 104.98
21.04.2008 13:00 | 3600 | 2 | 764.5 | GGB | 764.102 | 774.656 | 769.597 | 265.82 | GGB | 10857.6 | GGB | 9.81 | GGB | 1010.08 | GGB | 62.16 | GGB | 171438.12 | GGB | 139238.38 | GGB | 0 | 0 | 2936 | 3600 | 2920.33 | GGB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 207992.66 | GGB | 207995.1 | 2920.33 | 2714.2516 |  |  |  | 1 | 1 |  |  |  |  | 139238.38 | 2714.2516 | 139238.38 | 2714.2516 | 9.3849 | [5 empty] | 112.9506 | 2714.2516 |  | 104.98
21.04.2008 14:00 | 3600 | 2 | 764.62 | GGB | 763.004 | 773.531 | 768.498 | 264.98 | GGB | 10830.2 | GGB | 9.81 | GGB | 1009.11 | GGB | 62.56 | GGB | 170859.35 | GGB | 138472.43 | GGB | 0 | 0 | 2918 | 3600 | 2902.5 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 208032.03 | GGB | 208034.47 | 2902.5 | 2729.2653 |  |  |  | 0 | 1 | [14 empty] | 111.6434 | 2729.2653 |  | 104.98
21.04.2008 15:00 | 3600 | 2 | 764.55 | GGB | 765.201 | 776.625 | 771.429 | 266.03 | GGB | 10795.3 | GGB | 9.81 | GGB | 1008.99 | GGB | 62.02 | GGB | 172288.68 | GGB | 139840.31 | GGB | 0 | 0 | 2904 | 3600 | 2887.94 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 208071.4 | GGB | 208073.84 | 2887.94 | 2702.5684 |  |  |  | 1 | 1 |  |  |  |  | 139840.31 | 2702.5684 | 139840.31 | 2702.5684 | 9.5994 | [5 empty] | 112.1807 | 2702.5684 |  | 104.98
21.04.2008 16:00 | 3600 | 2 | 764.78 | GGB | 765.201 | 775.734 | 770.33 | 266.03 | GGB | 10764.9 | GGB | 9.8 | GGB | 1008.8 | GGB | 62.06 | GGB | 172363.51 | GGB | 139856.4 | GGB | 0 | 0 | 2881 | 3600 | 2865.75 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 208110.73 | GGB | 208113.17 | 2865.75 | 2702.2575 |  |  |  | 1 | 1 |  |  |  |  | 139856.4 | 2702.2575 | 139856.4 | 2702.2575 | 9.6092 | [5 empty] | 111.3315 | 2702.2575 |  | 104.98
21.04.2008 17:00 | 3600 | 2 | 765.22 | GGB | 764.102 | 774.516 | 769.963 | 264.14 | GGB | 10795.8 | GGB | 9.82 | GGB | 1008.03 | GGB | 62.4 | GGB | 170199.14 | GGB | 137853.89 | GGB | 0 | 0 | 2865 | 3600 | 2849.82 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 208150.4 | GGB | 208152.84 | 2849.82 | 2741.5113 |  |  |  | 1 | 1 |  |  |  |  | 137853.89 | 2741.5113 | 137853.89 | 2741.5113 | 9.5268 | [5 empty] | 109.1274 | 2741.5113 |  | 104.98
21.04.2008 18:00 | 3600 | 2 | 764.79 | GGB | 766.667 | 777.961 | 772.161 | 263.78 | GGB | 10789 | GGB | 9.81 | GGB | 1007.84 | GGB | 62.81 | GGB | 169787.62 | GGB | 137326.15 | GGB | 0 | 0 | 2899 | 3600 | 2883.37 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 208190.57 | GGB | 208193.01 | 2883.37 | 2752.0469 |  |  |  | 1 | 1 |  |  |  |  | 137326.15 | 2752.0469 | 137326.15 | 2752.0469 | 9.4082 | [5 empty] | 109.9895 | 2752.0469 |  | 104.98
21.04.2008 19:00 | 3600 | 2 | 763.9 | GGB | 765.201 | 774.797 | 769.597 | 265.37 | GGB | 10754.4 | GGB | 9.79 | GGB | 1008.27 | GGB | 62.04 | GGB | 171904.67 | GGB | 139417.03 | GGB | 0 | 0 | 2926 | 3600 | 2910.6 | GGB | 100 | GGB | 40.81 | GGB | 40.81 | GGB | 208231.38 | GGB | 208233.82 | 2910.6 | 2710.7736 |  |  |  | 1 | 1 |  |  |  |  | 139417.03 | 2710.7736 | 139417.03 | 2710.7736 | 9.2607 | [5 empty] | 112.7187 | 2710.7736 |  | 104.98
21.04.2008 20:00 | 3600 | 2 | 764.56 | GGB | 766.3 | 775.594 | 771.795 | 266.27 | GGB | 10806.5 | GGB | 9.81 | GGB | 1008.54 | GGB | 61.59 | GGB | 172560.47 | GGB | 140178.28 | GGB | 0 | 0 | 2904 | 3600 | 2888.73 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 208271.82 | GGB | 208274.26 | 2888.73 | 2696.0525 |  |  |  | 1 | 1 |  |  |  |  | 140178.28 | 2696.0525 | 140178.28 | 2696.0525 | 9.3454 | [5 empty] | 112.4826 | 2696.0525 |  | 104.98
21.04.2008 21:00 | 3600 | 2 | 763.24 | GGB | 764.102 | 773.367 | 768.498 | 266.61 | GGB | 10877.4 | GGB | 9.79 | GGB | 1009.13 | GGB | 61.48 | GGB | 172806.94 | GGB | 140503.83 | GGB | 0 | 0 | 2999 | 3600 | 2983.15 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 208311.31 | GGB | 208313.76 | 2983.15 | 2689.8057 |  |  |  | 1 | 1 |  |  |  |  | 140503.83 | 2689.8057 | 140503.83 | 2689.8057 | 9.5678 | [5 empty] | 116.4289 | 2689.8057 |  | 104.98
21.04.2008 22:00 | 3600 | 2 | 761.79 | GGB | 762.637 | 772.641 | 767.033 | 269.39 | GGB | 10921.9 | GGB | 9.77 | GGB | 1010.11 | GGB | 60.43 | GGB | 175963.81 | GGB | 143662.45 | GGB | 0 | 0 | 3087 | 3600 | 3071.01 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 208351.16 | GGB | 208353.6 | 3071.01 | 2630.6665 |  |  |  | 0 | 1 | [14 empty] | 122.5525 | 2630.6665 |  | 104.98
21.04.2008 23:00 | 3600 | 2 | 762.82 | GGB | 764.102 | 774.117 | 769.597 | 271.14 | GGB | 11028.7 | GGB | 9.81 | GGB | 1010.58 | GGB | 59.44 | GGB | 178638.73 | GGB | 146346.31 | GGB | 0 | 0 | 3089 | 3600 | 3073.55 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 208391.34 | GGB | 208393.78 | 3073.55 | 2582.4225 |  |  |  | 1 | 1 |  |  |  |  | 146346.31 | 2582.4225 | 146346.31 | 2582.4225 | 9.4059 | [5 empty] | 124.9452 | 2582.4225 |  | 104.98
21.04.2008 24:00 | 3600 | 2 | 761.63 | GGB | 765.201 | 774.141 | 769.597 | 271.46 | GGB | 11096.1 | GGB | 9.8 | GGB | 1011.07 | GGB | 59.66 | GGB | 177800.28 | GGB | 145634.47 | GGB | 0 | 0 | 3179 | 3600 | 3163.32 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 208431.38 | GGB | 208433.82 | 3163.32 | 2595.045 |  |  |  | 1 | 1 |  |  |  |  | 145634.47 | 2595.045 | 145634.47 | 2595.045 | 9.4388 | [5 empty] | 127.969 | 2595.045 |  | 104.98
22.04.2008 01:00 | 3600 | 2 | 761.36 | GGB | 763.004 | 773.039 | 768.132 | 272.37 | GGB | 11132.9 | GGB | 9.8 | GGB | 1011.2 | GGB | 59.59 | GGB | 178823.59 | GGB | 146521.66 | GGB | 0 | 0 | 3220 | 3600 | 3203.8 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 208471.73 | GGB | 208474.17 | 3203.8 | 2579.332 |  |  |  | 0 | 1 | [14 empty] | 130.3961 | 2579.332 |  | 104.98
22.04.2008 02:00 | 3600 | 2 | 761.25 | GGB | 761.538 | 771.844 | 767.033 | 273.09 | GGB | 11164.7 | GGB | 9.8 | GGB | 1011.91 | GGB | 59.42 | GGB | 179438.68 | GGB | 147205.38 | GGB | 0 | 0 | 3235 | 3600 | 3218.79 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 208512.36 | GGB | 208514.8 | 3218.79 | 2567.3518 |  |  |  | 0 | 1 | [14 empty] | 131.6176 | 2567.3518 |  | 104.98
22.04.2008 03:00 | 3600 | 2 | 760.47 | GGB | 761.538 | 770.977 | 767.033 | 274.65 | GGB | 11156.4 | GGB | 9.79 | GGB | 1011.75 | GGB | 58.63 | GGB | 181294.95 | GGB | 149058.71 | GGB | 0 | 0 | 3278 | 3600 | 3262.07 | GGB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 208553.34 | GGB | 208555.78 | 3262.07 | 2535.4305 |  |  |  | 0 | 1 | [14 empty] | 135.0667 | 2535.4305 |  | 104.98
22.04.2008 04:00 | 3600 | 2 | 760.84 | GGB | 761.538 | 771.375 | 765.934 | 276.2 | GGB | 11189.5 | GGB | 9.8 | GGB | 1011.83 | GGB | 58.11 | GGB | 183097.3 | GGB | 150789.08 | GGB | 0 | 0 | 3260 | 3600 | 3244.49 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 208594.75 | GGB | 208597.19 | 3244.49 | 2506.3353 |  |  |  | 0 | 1 | [14 empty] | 135.8982 | 2506.3353 |  | 104.98
22.04.2008 05:00 | 3600 | 2 | 760.56 | GGB | 760.44 | 769.383 | 765.934 | 276.39 | GGB | 11277.7 | GGB | 9.8 | GGB | 1012.16 | GGB | 58.51 | GGB | 182739.69 | GGB | 150363.85 | GGB | 0 | 0 | 3337 | 3600 | 3321.18 | GNB | 100 | GGB | 41.34 | GGB | 41.34 | GGB | 208636.09 | GGB | 208638.53 | 3321.18 | 2513.4233 |  |  |  | 0 | 1 | [14 empty] | 138.7182 | 2513.4233 |  | 104.98
22.04.2008 06:00 | 3600 | 2 | 760.27 | GGB | 761.538 | 770.438 | 765.934 | 277.7 | GGB | 11285.3 | GGB | 9.79 | GGB | 1012.31 | GGB | 58.76 | GGB | 183052.19 | GGB | 150527.3 | GGB | 0 | 0 | 3394 | 3600 | 3378.16 | GNB | 100 | GGB | 41.39 | GGB | 41.39 | GGB | 208677.48 | GGB | 208679.92 | 3378.16 | 2510.6941 |  |  |  | 0 | 1 | [14 empty] | 141.2515 | 2510.6941 |  | 104.98
22.04.2008 07:00 | 3600 | 2 | 760.74 | GGB | 762.637 | 771.609 | 767.033 | 278.34 | GGB | 11317 | GGB | 9.81 | GGB | 1012.71 | GGB | 58.87 | GGB | 183468.12 | GGB | 150881.41 | GGB | 0 | 0 | 3385 | 3600 | 3369.03 | GNB | 100 | GGB | 41.32 | GGB | 41.32 | GGB | 208718.8 | GGB | 208721.24 | 3369.03 | 2504.8016 |  |  |  | 0 | 1 | [14 empty] | 141.2011 | 2504.8016 |  | 104.98
22.04.2008 08:00 | 3600 | 2 | 761.07 | GGB | 761.538 | 771.563 | 766.667 | 277.93 | GGB | 11279.3 | GGB | 9.82 | GGB | 1013.65 | GGB | 59.31 | GGB | 182506.42 | GGB | 150029.07 | GGB | 0 | 0 | 3340 | 3600 | 3323.56 | GNB | 100 | GGB | 41.38 | GGB | 41.38 | GGB | 208760.18 | GGB | 208762.62 | 3323.56 | 2519.0318 |  |  |  | 0 | 1 | [14 empty] | 138.5085 | 2519.0318 |  | 104.98
22.04.2008 09:00 | 3600 | 2 | 763.42 | GGB | 765.201 | 774.914 | 770.33 | 276.28 | GGB | 11157.8 | GGB | 9.83 | GGB | 1013.84 | GGB | 59.62 | GGB | 180905.43 | GGB | 148603.12 | GGB | 0 | 0 | 3169 | 3600 | 3153.59 | GGB | 100 | GGB | 41.25 | GGB | 41.25 | GGB | 208801.43 | GGB | 208803.87 | 3153.59 | 2543.2037 |  |  |  | 1 | 1 |  |  |  |  | 148603.12 | 2543.2037 | 148603.12 | 2543.2037 | 9.1619 | [5 empty] | 130.1759 | 2543.2037 |  | 104.98
22.04.2008 10:00 | 3600 | 2 | 764.07 | GGB | 765.201 | 774.961 | 770.33 | 273.34 | GGB | 11030.9 | GGB | 9.82 | GGB | 1013.55 | GGB | 60.51 | GGB | 177859.69 | GGB | 145667.61 | GGB | 0 | 0 | 3063 | 3600 | 3047.29 | GGB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 208842.1 | GGB | 208844.54 | 3047.29 | 2594.4546 |  |  |  | 1 | 1 |  |  |  |  | 145667.61 | 2594.4546 | 145667.61 | 2594.4546 | 9.2925 | [5 empty] | 123.3032 | 2594.4546 |  | 104.98
22.04.2008 11:00 | 3600 | 2 | 764.88 | GGB | 766.3 | 776.344 | 771.429 | 271.26 | GGB | 10959.2 | GGB | 9.83 | GGB | 1012.03 | GGB | 61.25 | GGB | 175573.19 | GGB | 143264.43 | GGB | 0 | 0 | 2988 | 3600 | 2972.05 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 208882.27 | GGB | 208884.71 | 2972.05 | 2637.9751 |  |  |  | 1 | 1 |  |  |  |  | 143264.43 | 2637.9751 | 143264.43 | 2637.9751 | 9.4082 | [5 empty] | 118.2747 | 2637.9751 |  | 104.98
22.04.2008 12:00 | 3600 | 2 | 765.23 | GGB | 767.766 | 777.469 | 772.527 | 267.84 | GGB | 10912.9 | GGB | 9.83 | GGB | 1011.29 | GGB | 62.66 | GGB | 172051.01 | GGB | 139696.93 | GGB | 0 | 0 | 2961 | 3600 | 2945.45 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 208922.12 | GGB | 208924.56 | 2945.45 | 2705.3422 |  |  |  | 1 | 1 |  |  |  |  | 139696.93 | 2705.3422 | 139696.93 | 2705.3422 | 9.4838 | [5 empty] | 114.2973 | 2705.3422 |  | 104.98
22.04.2008 13:00 | 3600 | 2 | 765 | GGB | 765.201 | 775.664 | 771.429 | 266.9 | GGB | 10876 | GGB | 9.81 | GGB | 1011 | GGB | 62.45 | GGB | 171631.78 | GGB | 139404.92 | GGB | 0 | 0 | 2950 | 3600 | 2934.07 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 208961.88 | GGB | 208964.31 | 2934.07 | 2711.0091 |  |  |  | 1 | 1 |  |  |  |  | 139404.92 | 2711.0091 | 139404.92 | 2711.0091 | 9.5076 | [5 empty] | 113.6177 | 2711.0091 |  | 104.98
22.04.2008 14:00 | 3600 | 2 | 764.65 | GGB | 764.102 | 774.633 | 769.963 | 266.01 | GGB | 10837.7 | GGB | 9.8 | GGB | 1010.58 | GGB | 62.65 | GGB | 170993.59 | GGB | 138747.47 | GGB | 0 | 0 | 2953 | 3600 | 2937.07 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 209001.74 | GGB | 209004.18 | 2937.07 | 2723.8551 |  |  |  | 1 | 1 |  |  |  |  | 138747.47 | 2723.8551 | 138747.47 | 2723.8551 | 9.479 | [5 empty] | 113.1975 | 2723.8551 |  | 104.98
22.04.2008 15:00 | 3600 | 2 | 765.16 | GGB | 766.3 | 776.766 | 772.527 | 265.3 | GGB | 10825.3 | GGB | 9.81 | GGB | 1010.09 | GGB | 62.77 | GGB | 170418.11 | GGB | 138160.82 | GGB | 0 | 0 | 2913 | 3600 | 2897.35 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 209042.12 | GGB | 209044.56 | 2897.35 | 2735.4209 |  |  |  | 1 | 1 |  |  |  |  | 138160.82 | 2735.4209 | 138160.82 | 2735.4209 | 9.3593 | [5 empty] | 111.1945 | 2735.4209 |  | 104.98
22.04.2008 16:00 | 3600 | 2 | 765.4 | GGB | 764.102 | 774.492 | 770.33 | 264.84 | GGB | 10796.1 | GGB | 9.81 | GGB | 1009.74 | GGB | 63.17 | GGB | 169844.83 | GGB | 137486.04 | GGB | 0 | 0 | 2885 | 3600 | 2869.78 | GGB | 100 | GGB | 41.26 | GGB | 41.26 | GGB | 209083.39 | GGB | 209085.82 | 2869.78 | 2748.8464 |  |  |  | 1 | 1 |  |  |  |  | 137486.04 | 2748.8464 | 137486.04 | 2748.8464 | 9.1597 | [5 empty] | 109.5985 | 2748.8464 |  | 104.98
22.04.2008 17:00 | 3600 | 2 | 765.19 | GGB | 765.201 | 775.57 | 769.963 | 265.62 | GGB | 10746.9 | GGB | 9.8 | GGB | 1009.22 | GGB | 62.72 | GGB | 171269.77 | GGB | 138751.41 | GGB | 0 | 0 | 2879 | 3600 | 2863.13 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 209124.09 | GGB | 209126.53 | 2863.13 | 2723.7777 |  |  |  | 1 | 1 |  |  |  |  | 138751.41 | 2723.7777 | 138751.41 | 2723.7777 | 9.2834 | [5 empty] | 110.3509 | 2723.7777 |  | 104.98
22.04.2008 18:00 | 3600 | 2 | 765.44 | GGB | 765.201 | 775.195 | 771.429 | 265.27 | GGB | 10749.6 | GGB | 9.81 | GGB | 1008.82 | GGB | 62.77 | GGB | 170501.74 | GGB | 138055.91 | GGB | 0 | 0 | 2855 | 3600 | 2839.61 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 209164.66 | GGB | 209167.1 | 2839.61 | 2737.4996 |  |  |  | 1 | 1 |  |  |  |  | 138055.91 | 2737.4996 | 138055.91 | 2737.4996 | 9.3155 | [5 empty] | 108.8958 | 2737.4996 |  | 104.98
22.04.2008 19:00 | 3600 | 2 | 765.58 | GGB | 764.102 | 774.07 | 768.864 | 266.07 | GGB | 10733.3 | GGB | 9.8 | GGB | 1009 | GGB | 62.6 | GGB | 171655.99 | GGB | 139084.6 | GGB | 0 | 0 | 2851 | 3600 | 2835.91 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 209204.55 | GGB | 209206.99 | 2835.91 | 2717.2527 |  |  |  | 1 | 1 |  |  |  |  | 139084.6 | 2717.2527 | 139084.6 | 2717.2527 | 9.4743 | [5 empty] | 109.5643 | 2717.2527 |  | 104.98
22.04.2008 20:00 | 3600 | 2 | 765.38 | GGB | 765.201 | 775.477 | 771.429 | 266.16 | GGB | 10755.5 | GGB | 9.81 | GGB | 1008.99 | GGB | 62.38 | GGB | 172302.99 | GGB | 139699.85 | GGB | 0 | 0 | 2878 | 3600 | 2862.83 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 209244.43 | GGB | 209246.87 | 2862.83 | 2705.2857 |  |  |  | 1 | 1 |  |  |  |  | 139699.85 | 2705.2857 | 139699.85 | 2705.2857 | 9.4766 | [5 empty] | 111.0936 | 2705.2857 |  | 104.98
22.04.2008 21:00 | 3600 | 2 | 763.86 | GGB | 766.3 | 775.57 | 770.33 | 267.82 | GGB | 10792.8 | GGB | 9.78 | GGB | 1010.08 | GGB | 61.71 | GGB | 173850.06 | GGB | 141387.38 | GGB | 0 | 0 | 2951 | 3600 | 2935.74 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 209284.51 | GGB | 209286.95 | 2935.74 | 2672.9967 |  |  |  | 1 | 1 |  |  |  |  | 141387.38 | 2672.9967 | 141387.38 | 2672.9967 | 9.4293 | [5 empty] | 115.2991 | 2672.9967 |  | 104.98
22.04.2008 22:00 | 3600 | 2 | 763.85 | GGB | 764.102 | 773.672 | 768.864 | 269.15 | GGB | 10917.6 | GGB | 9.8 | GGB | 1011.63 | GGB | 61.07 | GGB | 175343.22 | GGB | 143097.5 | GGB | 0 | 0 | 3000 | 3600 | 2984.15 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 209324.06 | GGB | 209326.5 | 2984.15 | 2641.0524 |  |  |  | 1 | 1 |  |  |  |  | 143097.5 | 2641.0524 | 143097.5 | 2641.0524 | 9.5557 | [5 empty] | 118.6179 | 2641.0524 |  | 104.98
22.04.2008 23:00 | 3600 | 2 | 763 | GGB | 764.102 | 773.953 | 768.864 | 270.02 | GGB | 10971.4 | GGB | 9.79 | GGB | 1011.49 | GGB | 60.8 | GGB | 175193.58 | GGB | 143068.05 | GGB | 0 | 0 | 3075 | 3600 | 3059.13 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 209363.33 | GGB | 209365.78 | 3059.13 | 2641.5961 |  |  |  | 1 | 1 |  |  |  |  | 143068.05 | 2641.5961 | 143068.05 | 2641.5961 | 9.6214 | [5 empty] | 121.5733 | 2641.5961 |  | 104.98
22.04.2008 24:00 | 3600 | 2 | 762.82 | GGB | 764.102 | 772.805 | 768.864 | 271.19 | GGB | 11030 | GGB | 9.8 | GGB | 1012.28 | GGB | 60.7 | GGB | 176247.7 | GGB | 144084.75 | GGB | 0 | 0 | 3106 | 3600 | 3089.95 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 209402.79 | GGB | 209405.23 | 3089.95 | 2622.9563 |  |  |  | 1 | 1 |  |  |  |  | 144084.75 | 2622.9563 | 144084.75 | 2622.9563 | 9.5799 | [5 empty] | 123.6707 | 2622.9563 |  | 104.98
23.04.2008 01:00 | 3600 | 2 | 762.25 | GGB | 764.102 | 773.461 | 768.864 | 272.82 | GGB | 11042.3 | GGB | 9.79 | GGB | 1012.93 | GGB | 60.29 | GGB | 178629.93 | GGB | 146307.05 | GGB | 0 | 0 | 3137 | 3600 | 3121.38 | GGB | 100 | GGB | 40.77 | GGB | 40.77 | GGB | 209443.55 | GGB | 209446 | 3121.38 | 2583.1154 |  |  |  | 1 | 1 |  |  |  |  | 146307.05 | 2583.1154 | 146307.05 | 2583.1154 | 9.2698 | [5 empty] | 126.8555 | 2583.1154 |  | 104.98
23.04.2008 02:00 | 3600 | 2 | 762.51 | GGB | 761.538 | 770.227 | 766.3 | 274.67 | GGB | 11072.3 | GGB | 9.79 | GGB | 1013.76 | GGB | 59.61 | GGB | 180622.64 | GGB | 148365.05 | GGB | 0 | 0 | 3152 | 3600 | 3136.48 | GGB | 100 | GGB | 41.35 | GGB | 41.35 | GGB | 209484.9 | GGB | 209487.35 | 3136.48 | 2547.2846 |  |  |  | 0 | 1 | [14 empty] | 129.2622 | 2547.2846 |  | 104.98
23.04.2008 03:00 | 3600 | 2 | 762.78 | GGB | 766.3 | 775.688 | 771.429 | 276.23 | GGB | 11138.6 | GGB | 9.81 | GGB | 1014.18 | GGB | 59.27 | GGB | 181631.65 | GGB | 149406 | GGB | 0 | 0 | 3169 | 3600 | 3153.34 | GGB | 100 | GGB | 41.58 | GGB | 41.58 | GGB | 209526.48 | GGB | 209528.93 | 3153.34 | 2529.537 |  |  |  | 1 | 1 |  |  |  |  | 149406 | 2529.537 | 149406 | 2529.537 | 9.0892 | [5 empty] | 130.8689 | 2529.537 |  | 104.98
23.04.2008 04:00 | 3600 | 2 | 762.27 | GGB | 761.538 | 772.242 | 766.3 | 276.18 | GGB | 11179.3 | GGB | 9.8 | GGB | 1014.33 | GGB | 59.52 | GGB | 181053.97 | GGB | 148840.44 | GGB | 0 | 0 | 3219 | 3600 | 3202.86 | GGB | 100 | GGB | 41.25 | GGB | 41.25 | GGB | 209567.74 | GGB | 209570.18 | 3202.86 | 2539.1486 |  |  |  | 0 | 1 | [14 empty] | 132.4209 | 2539.1486 |  | 104.98
23.04.2008 05:00 | 3600 | 2 | 761.69 | GGB | 762.637 | 772.477 | 767.033 | 276.16 | GGB | 11219.8 | GGB | 9.8 | GGB | 1014.7 | GGB | 59.54 | GGB | 181024.27 | GGB | 148861.1 | GGB | 0 | 0 | 3279 | 3600 | 3262.66 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 209607.75 | GGB | 209610.19 | 3262.66 | 2538.7962 |  |  |  | 0 | 1 | [14 empty] | 134.912 | 2538.7962 |  | 104.98
23.04.2008 06:00 | 3600 | 2 | 761.4 | GGB | 762.637 | 771.516 | 766.667 | 276.74 | GGB | 11245.9 | GGB | 9.8 | GGB | 1014.69 | GGB | 59.26 | GGB | 181967.26 | GGB | 149759.51 | GGB | 0 | 0 | 3297 | 3600 | 3281.33 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 209647.97 | GGB | 209650.41 | 3281.33 | 2523.5659 |  |  |  | 0 | 1 | [14 empty] | 136.5029 | 2523.5659 |  | 104.98
23.04.2008 07:00 | 3600 | 2 | 761.28 | GGB | 761.538 | 771.281 | 766.3 | 278.38 | GGB | 11231.5 | GGB | 9.79 | GGB | 1015.02 | GGB | 58.17 | GGB | 184690.59 | GGB | 152554.38 | GGB | 0 | 0 | 3287 | 3600 | 3270.99 | GGB | 100 | GGB | 41.23 | GGB | 41.23 | GGB | 209689.2 | GGB | 209691.64 | 3270.99 | 2477.333 |  |  |  | 0 | 1 | [14 empty] | 138.6122 | 2477.333 |  | 104.98
23.04.2008 08:00 | 3600 | 2 | 762.66 | GGB | 763.004 | 772.359 | 767.766 | 277.83 | GGB | 11245.8 | GGB | 9.82 | GGB | 1015.62 | GGB | 58.15 | GGB | 183715.69 | GGB | 151845.82 | GGB | 0 | 0 | 3220 | 3600 | 3204.07 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 209730.62 | GGB | 209733.05 | 3204.07 | 2488.893 |  |  |  | 0 | 1 | [14 empty] | 135.1457 | 2488.893 |  | 104.98
23.04.2008 09:00 | 3600 | 2 | 762.55 | GGB | 764.102 | 774.422 | 768.864 | 276.94 | GGB | 11213.8 | GGB | 9.81 | GGB | 1016 | GGB | 58.38 | GGB | 182954.26 | GGB | 151170.65 | GGB | 0 | 0 | 3199 | 3600 | 3183.32 | GGB | 100 | GGB | 41.28 | GGB | 41.28 | GGB | 209771.9 | GGB | 209774.33 | 3183.32 | 2500.0091 |  |  |  | 1 | 1 |  |  |  |  | 151170.65 | 2500.0091 | 151170.65 | 2500.0091 | 9.1552 | [5 empty] | 133.6735 | 2500.0091 |  | 104.98
23.04.2008 10:00 | 3600 | 2 | 763.68 | GGB | 765.201 | 774.516 | 769.963 | 275.55 | GGB | 11179.3 | GGB | 9.83 | GGB | 1015.98 | GGB | 58.82 | GGB | 181501.81 | GGB | 149769.18 | GGB | 0 | 0 | 3145 | 3600 | 3128.75 | GGB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 209812.89 | GGB | 209815.32 | 3128.75 | 2523.403 |  |  |  | 1 | 1 |  |  |  |  | 149769.18 | 2523.403 | 149769.18 | 2523.403 | 9.22 | [5 empty] | 130.164 | 2523.403 |  | 104.98
23.04.2008 11:00 | 3600 | 2 | 764.01 | GGB | 766.3 | 775.875 | 771.429 | 273.7 | GGB | 11105.7 | GGB | 9.82 | GGB | 1015.15 | GGB | 59.38 | GGB | 179925.03 | GGB | 148094.67 | GGB | 0 | 0 | 3090 | 3600 | 3074.33 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 209853.83 | GGB | 209856.26 | 3074.33 | 2551.9352 |  |  |  | 1 | 1 |  |  |  |  | 148094.67 | 2551.9352 | 148094.67 | 2551.9352 | 9.2313 | [5 empty] | 126.47 | 2551.9352 |  | 104.98
23.04.2008 12:00 | 3600 | 2 | 764.9 | GGB | 766.3 | 776.133 | 771.429 | 271.67 | GGB | 11038.4 | GGB | 9.83 | GGB | 1014.82 | GGB | 60.04 | GGB | 177901.51 | GGB | 146092.69 | GGB | 0 | 0 | 3007 | 3600 | 2991.43 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 209894.66 | GGB | 209897.09 | 2991.43 | 2586.9056 |  |  |  | 1 | 1 |  |  |  |  | 146092.69 | 2586.9056 | 146092.69 | 2586.9056 | 9.2561 | [5 empty] | 121.3961 | 2586.9056 |  | 104.98
23.04.2008 13:00 | 3600 | 2 | 765.22 | GGB | 765.201 | 775.125 | 771.429 | 269.74 | GGB | 10958.1 | GGB | 9.82 | GGB | 1014.1 | GGB | 60.6 | GGB | 176462.27 | GGB | 144563.81 | GGB | 0 | 0 | 2950 | 3600 | 2934.74 | GGB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 209935.29 | GGB | 209937.72 | 2934.74 | 2614.2642 |  |  |  | 1 | 1 |  |  |  |  | 144563.81 | 2614.2642 | 144563.81 | 2614.2642 | 9.3017 | [5 empty] | 117.8492 | 2614.2642 |  | 104.98
23.04.2008 14:00 | 3600 | 2 | 764.79 | GGB | 765.201 | 774.844 | 769.963 | 269.2 | GGB | 10906.7 | GGB | 9.81 | GGB | 1013.73 | GGB | 60.73 | GGB | 175814.17 | GGB | 143926.42 | GGB | 0 | 0 | 2957 | 3600 | 2940.97 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 209975.87 | GGB | 209978.3 | 2940.97 | 2625.8417 |  |  |  | 1 | 1 |  |  |  |  | 143926.42 | 2625.8417 | 143926.42 | 2625.8417 | 9.3132 | [5 empty] | 117.5787 | 2625.8417 |  | 104.98
23.04.2008 15:00 | 3600 | 2 | 765.72 | GGB | 765.201 | 776.719 | 771.429 | 267.35 | GGB | 10936.2 | GGB | 9.82 | GGB | 1013.49 | GGB | 61.48 | GGB | 173339.51 | GGB | 141547.43 | GGB | 0 | 0 | 2914 | 3600 | 2898.71 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 210015.96 | GGB | 210018.39 | 2898.71 | 2669.9743 |  |  |  | 1 | 1 |  |  |  |  | 141547.43 | 2669.9743 | 141547.43 | 2669.9743 | 9.427 | [5 empty] | 113.9736 | 2669.9743 |  | 104.98
23.04.2008 16:00 | 3600 | 2 | 765.02 | GGB | 765.201 | 775.664 | 769.963 | 266.67 | GGB | 10895.6 | GGB | 9.81 | GGB | 1013.01 | GGB | 61.81 | GGB | 172613.28 | GGB | 140749.07 | GGB | 0 | 0 | 2938 | 3600 | 2921.93 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 210056.03 | GGB | 210058.46 | 2921.93 | 2685.119 |  |  |  | 1 | 1 |  |  |  |  | 140749.07 | 2685.119 | 140749.07 | 2685.119 | 9.4317 | [5 empty] | 114.2386 | 2685.119 |  | 104.98
23.04.2008 17:00 | 3600 | 2 | 765.73 | GGB | 763.004 | 774.094 | 768.864 | 267.09 | GGB | 10863.8 | GGB | 9.81 | GGB | 1012.82 | GGB | 61.97 | GGB | 172964.29 | GGB | 140939.11 | GGB | 0 | 0 | 2887 | 3600 | 2871.62 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 210096.11 | GGB | 210098.54 | 2871.62 | 2681.4984 |  |  |  | 0 | 1 | [14 empty] | 112.4232 | 2681.4984 |  | 104.98
23.04.2008 18:00 | 3600 | 2 | 765.18 | GGB | 766.3 | 776.742 | 772.527 | 267.99 | GGB | 10840.3 | GGB | 9.81 | GGB | 1012.82 | GGB | 61.44 | GGB | 174270.39 | GGB | 142231.89 | GGB | 0 | 0 | 2903 | 3600 | 2887.23 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 210136.44 | GGB | 210138.87 | 2887.23 | 2657.1256 |  |  |  | 1 | 1 |  |  |  |  | 142231.89 | 2657.1256 | 142231.89 | 2657.1256 | 9.3709 | [5 empty] | 114.0712 | 2657.1256 |  | 104.98
23.04.2008 19:00 | 3600 | 2 | 765.64 | GGB | 766.667 | 776.859 | 772.527 | 267.57 | GGB | 10863.7 | GGB | 9.81 | GGB | 1012.93 | GGB | 61.63 | GGB | 173356.01 | GGB | 141417.68 | GGB | 0 | 0 | 2902 | 3600 | 2886.17 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 210176.92 | GGB | 210179.36 | 2886.17 | 2672.424 |  |  |  | 1 | 1 |  |  |  |  | 141417.68 | 2672.424 | 141417.68 | 2672.424 | 9.3339 | [5 empty] | 113.3765 | 2672.424 |  | 104.98
23.04.2008 20:00 | 3600 | 2 | 764.51 | GGB | 764.102 | 775.008 | 770.33 | 267.79 | GGB | 10878 | GGB | 9.79 | GGB | 1013.45 | GGB | 61.83 | GGB | 172908.17 | GGB | 141043.12 | GGB | 0 | 0 | 2954 | 3600 | 2938.38 | GGB | 100 | GGB | 40.41 | GGB | 40.41 | GGB | 210217.34 | GGB | 210219.77 | 2938.38 | 2679.521 |  |  |  | 1 | 1 |  |  |  |  | 141043.12 | 2679.521 | 141043.12 | 2679.521 | 9.3523 | [5 empty] | 115.1217 | 2679.521 |  | 104.98
23.04.2008 21:00 | 3600 | 2 | 763.9 | GGB | 764.102 | 774.961 | 768.864 | 270.43 | GGB | 10896.5 | GGB | 9.78 | GGB | 1014.47 | GGB | 60.63 | GGB | 176197.08 | GGB | 144387.49 | GGB | 0 | 0 | 2991 | 3600 | 2975.49 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 210257.85 | GGB | 210260.28 | 2975.49 | 2617.4567 |  |  |  | 1 | 1 |  |  |  |  | 144387.49 | 2617.4567 | 144387.49 | 2617.4567 | 9.3293 | [5 empty] | 119.3399 | 2617.4567 |  | 104.98
23.04.2008 22:00 | 3600 | 2 | 763.95 | GGB | 765.201 | 774.891 | 769.963 | 271.93 | GGB | 10966.9 | GGB | 9.79 | GGB | 1015.53 | GGB | 60.26 | GGB | 177743.06 | GGB | 145966.42 | GGB | 0 | 0 | 3021 | 3600 | 3004.92 | GGB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 210298.01 | GGB | 210300.44 | 3004.92 | 2589.1434 |  |  |  | 1 | 1 |  |  |  |  | 145966.42 | 2589.1434 | 145966.42 | 2589.1434 | 9.4106 | [5 empty] | 121.8382 | 2589.1434 |  | 104.98
23.04.2008 23:00 | 3600 | 2 | 763.29 | GGB | 764.102 | 775.477 | 770.33 | 272.73 | GGB | 11072.2 | GGB | 9.8 | GGB | 1016.39 | GGB | 60.2 | GGB | 178529.8 | GGB | 146765.59 | GGB | 0 | 0 | 3100 | 3600 | 3084.15 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 210337.46 | GGB | 210339.89 | 3084.15 | 2575.045 |  |  |  | 1 | 1 |  |  |  |  | 146765.59 | 2575.045 | 146765.59 | 2575.045 | 9.5799 | [5 empty] | 125.7353 | 2575.045 |  | 104.98
23.04.2008 24:00 | 3600 | 2 | 762.62 | GGB | 764.102 | 774.234 | 768.864 | 273.06 | GGB | 11121.8 | GGB | 9.8 | GGB | 1016.61 | GGB | 60.08 | GGB | 178281.12 | GGB | 146641.74 | GGB | 0 | 0 | 3171 | 3600 | 3154.95 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 210377.62 | GGB | 210380.06 | 3154.95 | 2577.2198 |  |  |  | 1 | 1 |  |  |  |  | 146641.74 | 2577.2198 | 146641.74 | 2577.2198 | 9.4082 | [5 empty] | 128.5132 | 2577.2198 |  | 104.98
24.04.2008 01:00 | 3600 | 2 | 762.15 | GGB | 761.538 | 771.961 | 766.3 | 275.11 | GGB | 11148.1 | GGB | 9.79 | GGB | 1017.95 | GGB | 59.92 | GGB | 180332.15 | GGB | 148597.07 | GGB | 0 | 0 | 3218 | 3600 | 3201.98 | GGB | 100 | GGB | 41.82 | GGB | 41.82 | GGB | 210419.45 | GGB | 210421.88 | 3201.98 | 2543.3072 |  |  |  | 0 | 1 | [14 empty] | 132.168 | 2543.3072 |  | 104.98
24.04.2008 02:00 | 3600 | 2 | 762.37 | GGB | 764.102 | 774.234 | 768.864 | 277.35 | GGB | 11183 | GGB | 9.8 | GGB | 1018.89 | GGB | 59.05 | GGB | 182798.01 | GGB | 151164.97 | GGB | 0 | 0 | 3223 | 3600 | 3207.19 | GGB | 100 | GGB | 42.07 | GGB | 42.07 | GGB | 210461.51 | GGB | 210463.95 | 3207.19 | 2500.103 |  |  |  | 1 | 1 |  |  |  |  | 151164.97 | 2500.103 | 151164.97 | 2500.103 | 8.9833 | [5 empty] | 134.6708 | 2500.103 |  | 104.98
24.04.2008 03:00 | 3600 | 2 | 762.23 | GGB | 762.637 | 773.273 | 767.766 | 276.75 | GGB | 11262.5 | GGB | 9.8 | GGB | 1019.59 | GGB | 59.51 | GGB | 181363.17 | GGB | 149874.99 | GGB | 0 | 0 | 3274 | 3600 | 3258.32 | GGB | 100 | GGB | 41.66 | GGB | 41.66 | GGB | 210503.17 | GGB | 210505.61 | 3258.32 | 2521.6215 |  |  |  | 0 | 1 | [14 empty] | 135.6502 | 2521.6215 |  | 104.98
24.04.2008 04:00 | 3600 | 2 | 760.9 | GGB | 762.637 | 771.914 | 766.667 | 278.61 | GGB | 11311.7 | GGB | 9.79 | GGB | 1020.01 | GGB | 59.13 | GGB | 183478.02 | GGB | 151854.18 | GGB | 0 | 0 | 3376 | 3600 | 3360.49 | GNB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 210543.3 | GGB | 210545.74 | 3360.49 | 2488.756 |  |  |  | 0 | 1 | [14 empty] | 141.7512 | 2488.756 |  | 104.98
24.04.2008 05:00 | 3600 | 2 | 761.03 | GGB | 764.102 | 773.086 | 768.864 | 280.05 | GGB | 11376 | GGB | 9.8 | GGB | 1020.41 | GGB | 58.74 | GGB | 185110.92 | GGB | 153446.72 | GNB | 0 | 0 | 3405 | 3600 | 3389.33 | GNB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 210583.46 | GGB | 210585.9 | 3389.33 | 2462.9265 |  |  |  | 1 | 1 |  |  |  |  | 153446.72 | 2462.9265 |  | 2462.9265 | 9.4106 | [5 empty] | 144.4671 | 2462.9265 |  | 104.98
24.04.2008 06:00 | 3600 | 2 | 761.14 | GGB | 763.004 | 771.984 | 766.667 | 281.27 | GGB | 11447.3 | GGB | 9.81 | GGB | 1020.83 | GGB | 58.44 | GGB | 186626.09 | GGB | 154905.66 | GNB | 0 | 0 | 3427 | 3600 | 3410.61 | GNB | 100 | GGB | 42.59 | GGB | 42.59 | GGB | 210626.05 | GGB | 210628.49 | 3410.61 | 2439.7301 |  |  |  | 0 | 1 | [14 empty] | 146.7563 | 2439.7301 |  | 104.98
24.04.2008 07:00 | 3600 | 2 | 759.75 | GGB | 762.637 | 772.242 | 766.3 | 283.32 | GNB | 11426.5 | GGB | 9.78 | GGB | 1021.41 | GGB | 57.62 | GGB | 189305.41 | GGB | 157612.33 | GGB | 0 | 0 | 3515 | 3600 | 3498 | GKB | 100 | GGB | 41.88 | GGB | 41.88 | GGB | 210667.93 | GGB | 210670.37 | 3498 | 2397.8327 |  |  |  | 0 | 1 | [14 empty] | 153.1466 | 2397.8327 |  | 104.98
24.04.2008 08:00 | 3600 | 2 | 761.76 | GGB | 765.201 | 774.445 | 768.864 | 282.59 | GGB | 11430.5 | GGB | 9.81 | GGB | 1022.16 | GGB | 57.71 | GGB | 188645.21 | GGB | 157132.2 | GNB | 0 | 0 | 3410 | 3600 | 3394.26 | GNB | 100 | GGB | 41.73 | GGB | 41.73 | GGB | 210709.66 | GGB | 210712.1 | 3394.26 | 2405.1595 |  |  |  | 1 | 1 |  |  |  |  | 157132.2 | 2405.1595 |  | 2405.1595 | 9.0565 | [5 empty] | 148.1521 | 2405.1595 |  | 104.98
24.04.2008 09:00 | 3600 | 2 | 763.13 | GGB | 764.102 | 772.406 | 768.132 | 278.56 | GGB | 11362.1 | GGB | 9.83 | GGB | 1022.42 | GGB | 58.9 | GGB | 183808.12 | GGB | 152596.86 | GGB | 0 | 0 | 3297 | 3600 | 3280.74 | GGB | 100 | GGB | 42.15 | GGB | 42.15 | GGB | 210751.81 | GGB | 210754.25 | 3280.74 | 2476.6434 |  |  |  | 1 | 1 |  |  |  |  | 152596.86 | 2476.6434 | 152596.86 | 2476.6434 | 8.9663 | [5 empty] | 139.0641 | 2476.6434 |  | 104.98
24.04.2008 10:00 | 3600 | 2 | 763.23 | GGB | 764.102 | 774.492 | 768.498 | 274.64 | GGB | 11221.5 | GGB | 9.81 | GGB | 1022.06 | GGB | 59.97 | GGB | 179796.29 | GGB | 148732.39 | GGB | 0 | 0 | 3247 | 3600 | 3231.4 | GGB | 100 | GGB | 41.64 | GGB | 41.64 | GGB | 210793.45 | GGB | 210795.89 | 3231.4 | 2540.9933 |  |  |  | 1 | 1 |  |  |  |  | 148732.39 | 2540.9933 | 148732.39 | 2540.9933 | 9.0761 | [5 empty] | 133.5038 | 2540.9933 |  | 104.98
24.04.2008 11:00 | 3600 | 2 | 763.28 | GGB | 765.201 | 774.563 | 769.963 | 272.13 | GGB | 11113.9 | GGB | 9.8 | GGB | 1021.51 | GGB | 60.62 | GGB | 177181.89 | GGB | 146207.7 | GGB | 0 | 0 | 3182 | 3600 | 3166.23 | GGB | 100 | GGB | 41.65 | GGB | 41.65 | GGB | 210835.1 | GGB | 210837.54 | 3166.23 | 2584.8707 |  |  |  | 1 | 1 |  |  |  |  | 146207.7 | 2584.8707 | 146207.7 | 2584.8707 | 9.0739 | [5 empty] | 128.5909 | 2584.8707 |  | 104.98
24.04.2008 12:00 | 3600 | 2 | 764.71 | GGB | 765.201 | 774.609 | 769.963 | 270.24 | GGB | 11036.2 | GGB | 9.81 | GGB | 1021.01 | GGB | 61.49 | GGB | 174789.75 | GGB | 143783.45 | GGB | 0 | 0 | 3074 | 3600 | 3058.16 | GGB | 100 | GGB | 41.29 | GGB | 41.29 | GGB | 210876.39 | GGB | 210878.83 | 3058.16 | 2628.4527 |  |  |  | 1 | 1 |  |  |  |  | 143783.45 | 2628.4527 | 143783.45 | 2628.4527 | 9.153 | [5 empty] | 122.1424 | 2628.4527 |  | 104.98
24.04.2008 13:00 | 3600 | 2 | 764.29 | GGB | 764.102 | 774.352 | 768.864 | 269.16 | GGB | 10956 | GGB | 9.79 | GGB | 1020.49 | GGB | 62.07 | GGB | 173854.47 | GGB | 142697.57 | GGB | 0 | 0 | 3053 | 3600 | 3037.22 | GGB | 100 | GGB | 41.41 | GGB | 41.41 | GGB | 210917.8 | GGB | 210920.24 | 3037.22 | 2648.4543 |  |  |  | 1 | 1 |  |  |  |  | 142697.57 | 2648.4543 | 142697.57 | 2648.4543 | 9.1265 | [5 empty] | 120.39 | 2648.4543 |  | 104.98
24.04.2008 14:00 | 3600 | 2 | 764.62 | GGB | 765.201 | 776.438 | 770.33 | 268.63 | GGB | 10938.6 | GGB | 9.8 | GGB | 1020.12 | GGB | 62.33 | GGB | 173510.06 | GGB | 142250.35 | GGB | 0 | 0 | 3018 | 3600 | 3002.69 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 210957.84 | GGB | 210960.28 | 3002.69 | 2656.7808 |  |  |  | 1 | 1 |  |  |  |  | 142250.35 | 2656.7808 | 142250.35 | 2656.7808 | 9.4388 | [5 empty] | 118.6483 | 2656.7808 |  | 104.98
24.04.2008 15:00 | 3600 | 2 | 764.99 | GGB | 765.201 | 776.508 | 770.33 | 267.61 | GGB | 10895.2 | GGB | 9.8 | GGB | 1019.13 | GGB | 62.69 | GGB | 172573.67 | GGB | 141196.26 | GGB | 0 | 0 | 2981 | 3600 | 2965.82 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 210997.97 | GGB | 211000.41 | 2965.82 | 2676.6148 |  |  |  | 1 | 1 |  |  |  |  | 141196.26 | 2676.6148 | 141196.26 | 2676.6148 | 9.4176 | [5 empty] | 116.323 | 2676.6148 |  | 104.98
24.04.2008 16:00 | 3600 | 2 | 765.17 | GGB | 765.201 | 775.641 | 771.429 | 266.95 | GGB | 10861.7 | GGB | 9.79 | GGB | 1018.28 | GGB | 62.88 | GGB | 172059.81 | GGB | 140576.64 | GGB | 0 | 0 | 2956 | 3600 | 2940.81 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 211038.04 | GGB | 211040.49 | 2940.81 | 2688.4125 |  |  |  | 1 | 1 |  |  |  |  | 140576.64 | 2688.4125 | 140576.64 | 2688.4125 | 9.4293 | [5 empty] | 114.8359 | 2688.4125 |  | 104.98
24.04.2008 17:00 | 3600 | 2 | 765.38 | GGB | 765.201 | 775.734 | 770.33 | 266.14 | GGB | 10822.4 | GGB | 9.79 | GGB | 1017.33 | GGB | 63.1 | GGB | 171152.04 | GGB | 139616.05 | GGB | 0 | 0 | 2932 | 3600 | 2916.26 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 211078.11 | GGB | 211080.56 | 2916.26 | 2706.9094 |  |  |  | 1 | 1 |  |  |  |  | 139616.05 | 2706.9094 | 139616.05 | 2706.9094 | 9.4317 | [5 empty] | 113.0991 | 2706.9094 |  | 104.98
24.04.2008 18:00 | 3600 | 2 | 765.43 | GGB | 766.3 | 776.742 | 771.429 | 265.77 | GGB | 10815.5 | GGB | 9.79 | GGB | 1016.88 | GGB | 63.1 | GGB | 170836.24 | GGB | 139297.21 | GGB | 0 | 0 | 2922 | 3600 | 2906.52 | GGB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 211119.06 | GGB | 211121.51 | 2906.52 | 2713.1053 |  |  |  | 1 | 1 |  |  |  |  | 139297.21 | 2713.1053 | 139297.21 | 2713.1053 | 9.229 | [5 empty] | 112.4639 | 2713.1053 |  | 104.98
24.04.2008 19:00 | 3600 | 2 | 765.18 | GGB | 765.201 | 775.711 | 770.33 | 265.69 | GGB | 10791.7 | GGB | 9.78 | GGB | 1016.71 | GGB | 63.3 | GGB | 170388.4 | GGB | 138825.24 | GGB | 0 | 0 | 2928 | 3600 | 2911.92 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 211158.98 | GGB | 211161.43 | 2911.92 | 2722.3292 |  |  |  | 1 | 1 |  |  |  |  | 138825.24 | 2722.3292 | 138825.24 | 2722.3292 | 9.4671 | [5 empty] | 112.2911 | 2722.3292 |  | 104.98
24.04.2008 20:00 | 3600 | 2 | 765.27 | GGB | 765.201 | 775.547 | 770.33 | 265.76 | GGB | 10791.1 | GGB | 9.78 | GGB | 1016.56 | GGB | 63.03 | GGB | 170347.69 | GGB | 138881.24 | GGB | 0 | 0 | 2921 | 3600 | 2904.92 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 211198.94 | GGB | 211201.4 | 2904.92 | 2721.2315 |  |  |  | 1 | 1 |  |  |  |  | 138881.24 | 2721.2315 | 138881.24 | 2721.2315 | 9.4553 | [5 empty] | 112.0664 | 2721.2315 |  | 104.98
24.04.2008 21:00 | 3600 | 2 | 764.96 | GGB | 764.102 | 775.219 | 768.864 | 266.65 | GGB | 10810.4 | GGB | 9.78 | GGB | 1017.13 | GGB | 62.77 | GGB | 170791.12 | GGB | 139428.17 | GGB | 0 | 0 | 2939 | 3600 | 2923.58 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 211238.93 | GGB | 211241.39 | 2923.58 | 2710.557 |  |  |  | 1 | 1 |  |  |  |  | 139428.17 | 2710.557 | 139428.17 | 2710.557 | 9.4506 | [5 empty] | 113.2304 | 2710.557 |  | 104.98
24.04.2008 22:00 | 3600 | 2 | 763.98 | GGB | 764.102 | 774.047 | 768.864 | 268.24 | GGB | 10858.2 | GGB | 9.77 | GGB | 1018.19 | GGB | 62.36 | GGB | 172747.53 | GGB | 141346.12 | GGB | 0 | 0 | 3017 | 3600 | 3001.57 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 211279.12 | GGB | 211281.58 | 3001.57 | 2673.777 |  |  |  | 1 | 1 |  |  |  |  | 141346.12 | 2673.777 | 141346.12 | 2673.777 | 9.4035 | [5 empty] | 117.8501 | 2673.777 |  | 104.98
24.04.2008 23:00 | 3600 | 2 | 761.95 | GGB | 764.102 | 773.883 | 768.864 | 272.79 | GGB | 10887.7 | GGB | 9.74 | GGB | 1018.89 | GGB | 60.96 | GGB | 177315.03 | GGB | 145789.8 | GGB | 0 | 0 | 3130 | 3600 | 3114.13 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 211320.27 | GGB | 211322.73 | 3114.13 | 2592.2801 |  |  |  | 1 | 1 |  |  |  |  | 145789.8 | 2592.2801 | 145789.8 | 2592.2801 | 9.1842 | [5 empty] | 126.1134 | 2592.2801 |  | 104.98
24.04.2008 24:00 | 3600 | 2 | 763.5 | GGB | 763.004 | 773.93 | 768.864 | 272.47 | GGB | 11040.8 | GGB | 9.79 | GGB | 1019.19 | GGB | 61.26 | GGB | 176535.99 | GGB | 145064.97 | GGB | 0 | 0 | 3124 | 3600 | 3108.61 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 211360.16 | GGB | 211362.63 | 3108.61 | 2605.2327 |  |  |  | 0 | 1 | [14 empty] | 125.264 | 2605.2327 |  | 104.98
25.04.2008 01:00 | 3600 | 2 | 762.5 | GGB | 763.004 | 772.898 | 766.667 | 273.01 | GGB | 11046.4 | GGB | 9.78 | GGB | 1019.59 | GGB | 61.26 | GGB | 177233.6 | GGB | 145691.99 | GGB | 0 | 0 | 3182 | 3600 | 3166.06 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 211400.13 | GGB | 211402.59 | 3166.06 | 2594.0204 |  |  |  | 0 | 1 | [14 empty] | 128.1304 | 2594.0204 |  | 104.98
25.04.2008 02:00 | 3600 | 2 | 762.53 | GGB | 762.637 | 771.984 | 767.766 | 273.93 | GGB | 11091.6 | GGB | 9.78 | GGB | 1019.95 | GGB | 60.86 | GGB | 178267.92 | GGB | 146768.72 | GGB | 0 | 0 | 3206 | 3600 | 3190.15 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 211440.42 | GGB | 211442.89 | 3190.15 | 2574.9901 |  |  |  | 0 | 1 | [14 empty] | 130.0595 | 2574.9901 |  | 104.98
25.04.2008 03:00 | 3600 | 2 | 761.73 | GGB | 762.637 | 772.195 | 767.766 | 274.87 | GGB | 11127 | GGB | 9.78 | GGB | 1020.4 | GGB | 60.53 | GGB | 179241.72 | GGB | 147783.93 | GGB | 0 | 0 | 3248 | 3600 | 3232.01 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 211481.31 | GGB | 211483.78 | 3232.01 | 2557.3011 |  |  |  | 0 | 1 | [14 empty] | 132.6775 | 2557.3011 |  | 104.98
25.04.2008 04:00 | 3600 | 2 | 760.75 | GGB | 762.637 | 772.148 | 766.667 | 277.39 | GGB | 11184.3 | GGB | 9.76 | GGB | 1020.54 | GGB | 60.03 | GGB | 181577.74 | GGB | 149955.81 | GGB | 0 | 0 | 3351 | 3600 | 3334.71 | GNB | 100 | GGB | 41.57 | GGB | 41.57 | GGB | 211522.89 | GGB | 211525.35 | 3334.71 | 2520.2625 |  |  |  | 0 | 1 | [14 empty] | 138.9053 | 2520.2625 |  | 104.98
25.04.2008 05:00 | 3600 | 2 | 760.62 | GGB | 761.538 | 772.172 | 766.667 | 279.96 | GGB | 11289.7 | GGB | 9.77 | GGB | 1020.98 | GGB | 59.55 | GGB | 183840.03 | GGB | 152105.85 | GGB | 0 | 0 | 3414 | 3600 | 3397.95 | GNB | 100 | GGB | 42.68 | GGB | 42.68 | GGB | 211565.57 | GGB | 211568.03 | 3397.95 | 2484.6382 |  |  |  | 0 | 1 | [14 empty] | 143.5689 | 2484.6382 |  | 104.98
25.04.2008 06:00 | 3600 | 2 | 761.2 | GGB | 761.538 | 770.766 | 765.934 | 280.9 | GGB | 11322.8 | GGB | 9.79 | GGB | 1021.39 | GGB | 58.92 | GGB | 185299.08 | GGB | 153669.97 | GNB | 0 | 0 | 3400 | 3600 | 3384.31 | GNB | 100 | GGB | 41.49 | GGB | 41.49 | GGB | 211607.05 | GGB | 211609.52 | 3384.31 | 2459.3484 |  |  |  | 0 | 1 | [14 empty] | 144.463 | 2459.3484 |  | 104.98
25.04.2008 07:00 | 3600 | 2 | 759.96 | GGB | 761.538 | 771.891 | 765.934 | 281.43 | GGB | 11369.1 | GGB | 9.77 | GGB | 1021.71 | GGB | 58.78 | GGB | 185970.28 | GGB | 154337.79 | GNB | 0 | 0 | 3498 | 3600 | 3481.77 | GNB | 100 | GGB | 41.48 | GGB | 41.48 | GGB | 211648.54 | GGB | 211651 | 3481.77 | 2448.7068 |  |  |  | 0 | 1 | [14 empty] | 149.2691 | 2448.7068 |  | 104.98
25.04.2008 08:00 | 3600 | 2 | 761.56 | GGB | 763.004 | 772.898 | 768.132 | 280.71 | GGB | 11403.7 | GGB | 9.81 | GGB | 1022.15 | GGB | 58.98 | GGB | 185464.13 | GGB | 153889.84 | GNB | 0 | 0 | 3432 | 3600 | 3415.77 | GNB | 100 | GGB | 41.48 | GGB | 41.48 | GGB | 211690.01 | GGB | 211692.48 | 3415.77 | 2455.8346 |  |  |  | 0 | 1 | [14 empty] | 146.0145 | 2455.8346 |  | 104.98
25.04.2008 09:00 | 3600 | 2 | 763.48 | GGB | 764.102 | 773.836 | 769.597 | 277.34 | GGB | 11257 | GGB | 9.82 | GGB | 1022.15 | GGB | 59.6 | GGB | 182269.85 | GGB | 150957.53 | GGB | 0 | 0 | 3270 | 3207 | 3254.36 | GGB | 100 | GGB | 41.4 | GGB | 41.4 | GGB | 211731.41 | GGB | 211733.88 | 3254.36 | 2503.5386 |  |  |  | 1 | 1 |  |  |  |  | 150957.53 | 2503.5386 | 150957.53 | 2503.5386 | 9.1287 | [5 empty] | 136.4639 | 2503.5386 |  | 104.98
25.04.2008 10:00 | 3600 | 2 | 765.23 | GGB | 766.3 | 776.766 | 772.161 | 272.98 | GGB | 11107 | GGB | 9.83 | GGB | 1021.76 | GGB | 60.47 | GGB | 178241.51 | GGB | 147183.31 | GGB | 0 | 0 | 3083 | 3600 | 3067.64 | GGB | 100 | GGB | 40.49 | GGB | 40.49 | GGB | 211771.9 | GGB | 211774.37 | 3067.64 | 2567.7368 |  |  |  | 1 | 1 |  |  |  |  | 147183.31 | 2567.7368 | 147183.31 | 2567.7368 | 9.3339 | [5 empty] | 125.4182 | 2567.7368 |  | 104.98
25.04.2008 11:00 | 3600 | 2 | 765.23 | GGB | 765.201 | 775.102 | 770.696 | 269.26 | GGB | 10999.9 | GGB | 9.81 | GGB | 1021.08 | GGB | 61.77 | GGB | 174104.24 | GGB | 143111.37 | GGB | 0 | 0 | 3034 | 3600 | 3018.5 | GGB | 100 | GGB | 41.19 | GGB | 41.19 | GGB | 211813.09 | GGB | 211815.56 | 3018.5 | 2640.7965 |  |  |  | 1 | 1 |  |  |  |  | 143111.37 | 2640.7965 | 143111.37 | 2640.7965 | 9.1752 | [5 empty] | 119.9949 | 2640.7965 |  | 104.98
25.04.2008 12:00 | 3600 | 2 | 765.12 | GGB | 765.201 | 775.195 | 770.696 | 267.62 | GGB | 10905.3 | GGB | 9.8 | GGB | 1020.8 | GGB | 62.4 | GGB | 172244.67 | GGB | 141280.1 | GGB | 0 | 0 | 2991 | 3600 | 2975.69 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 211853.11 | GGB | 211855.59 | 2975.69 | 2675.0264 |  |  |  | 1 | 1 |  |  |  |  | 141280.1 | 2675.0264 | 141280.1 | 2675.0264 | 9.4411 | [5 empty] | 116.7794 | 2675.0264 |  | 104.98
25.04.2008 13:00 | 3600 | 2 | 765.45 | GGB | 765.201 | 775.406 | 770.696 | 266.2 | GGB | 10852 | GGB | 9.8 | GGB | 1019.66 | GGB | 62.84 | GGB | 170980.38 | GGB | 139901.54 | GGB | 0 | 0 | 2942 | 3600 | 2926.74 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 211892.83 | GGB | 211895.31 | 2926.74 | 2701.3856 |  |  |  | 1 | 1 |  |  |  |  | 139901.54 | 2701.3856 | 139901.54 | 2701.3856 | 9.5148 | [5 empty] | 113.7376 | 2701.3856 |  | 104.98
25.04.2008 14:00 | 3600 | 2 | 765.65 | GGB | 765.201 | 775.336 | 770.696 | 265.2 | GGB | 10802.2 | GGB | 9.79 | GGB | 1018.47 | GGB | 63.29 | GGB | 169961.47 | GGB | 138718.79 | GGB | 0 | 0 | 2913 | 3600 | 2897.44 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 211932.48 | GGB | 211934.95 | 2897.44 | 2724.4182 |  |  |  | 1 | 1 |  |  |  |  | 138718.79 | 2724.4182 | 138718.79 | 2724.4182 | 9.534 | [5 empty] | 111.647 | 2724.4182 |  | 104.98
25.04.2008 15:00 | 3600 | 2 | 765.73 | GGB | 766.3 | 777.328 | 771.795 | 264.56 | GGB | 10765.7 | GGB | 9.79 | GGB | 1017.65 | GGB | 63.48 | GGB | 169603.86 | GGB | 138239.77 | GGB | 0 | 0 | 2904 | 3600 | 2888.1 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 211971.99 | GGB | 211974.46 | 2888.1 | 2733.8587 |  |  |  | 1 | 1 |  |  |  |  | 138239.77 | 2733.8587 | 138239.77 | 2733.8587 | 9.5654 | [5 empty] | 110.9029 | 2733.8587 |  | 104.98
25.04.2008 16:00 | 3600 | 2 | 766.05 | GGB | 765.201 | 776.18 | 770.696 | 265.17 | GGB | 10701.1 | GGB | 9.78 | GGB | 1016.78 | GGB | 63.31 | GGB | 170634.88 | GGB | 139030.78 | GGB | 0 | 0 | 2853 | 3600 | 2837.04 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 212011.44 | GGB | 212013.92 | 2837.04 | 2718.3045 |  |  |  | 1 | 1 |  |  |  |  | 139030.78 | 2718.3045 | 139030.78 | 2718.3045 | 9.5775 | [5 empty] | 109.5655 | 2718.3045 |  | 104.98
25.04.2008 17:00 | 3600 | 2 | 766.26 | GGB | 766.3 | 777.117 | 772.161 | 264.15 | GGB | 10716.4 | GGB | 9.8 | GGB | 1016.46 | GGB | 63.5 | GGB | 169463.02 | GGB | 137953.57 | GGB | 0 | 0 | 2844 | 3600 | 2828.65 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 212050.75 | GGB | 212053.23 | 2828.65 | 2739.5304 |  |  |  | 1 | 1 |  |  |  |  | 137953.57 | 2739.5304 | 137953.57 | 2739.5304 | 9.614 | [5 empty] | 108.3951 | 2739.5304 |  | 104.98
25.04.2008 18:00 | 3600 | 2 | 765.75 | GGB | 765.201 | 777.07 | 771.795 | 263.68 | GGB | 10723.6 | GGB | 9.79 | GGB | 1016.12 | GGB | 63.75 | GGB | 168845.73 | GGB | 137305.41 | GGB | 0 | 0 | 2864 | 3600 | 2848.78 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 212090.65 | GGB | 212093.13 | 2848.78 | 2752.4626 |  |  |  | 1 | 1 |  |  |  |  | 137305.41 | 2752.4626 | 137305.41 | 2752.4626 | 9.4719 | [5 empty] | 108.6536 | 2752.4626 |  | 104.98
25.04.2008 19:00 | 3600 | 2 | 765.54 | GGB | 765.201 | 775.922 | 770.696 | 263.77 | GGB | 10725.2 | GGB | 9.78 | GGB | 1016.17 | GGB | 63.76 | GGB | 168763.2 | GGB | 137239.18 | GGB | 0 | 0 | 2884 | 3600 | 2868.25 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 212130.03 | GGB | 212132.51 | 2868.25 | 2753.7909 |  |  |  | 1 | 1 |  |  |  |  | 137239.18 | 2753.7909 | 137239.18 | 2753.7909 | 9.597 | [5 empty] | 109.3434 | 2753.7909 |  | 104.98
25.04.2008 20:00 | 3600 | 2 | 765.54 | GGB | 765.201 | 776.133 | 770.696 | 264.02 | GGB | 10734.2 | GGB | 9.78 | GGB | 1016.26 | GGB | 63.65 | GGB | 168802.81 | GGB | 137328.03 | GGB | 0 | 0 | 2893 | 3600 | 2877.43 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 212169.01 | GGB | 212171.49 | 2877.43 | 2752.0092 |  |  |  | 1 | 1 |  |  |  |  | 137328.03 | 2752.0092 | 137328.03 | 2752.0092 | 9.6954 | [5 empty] | 109.7644 | 2752.0092 |  | 104.98
25.04.2008 21:00 | 3600 | 2 | 764.8 | GGB | 763.004 | 773.977 | 768.132 | 265.52 | GGB | 10767.5 | GGB | 9.77 | GGB | 1016.92 | GGB | 63.21 | GGB | 170057.2 | GGB | 138620.67 | GGB | 0 | 0 | 2939 | 3600 | 2923.16 | GGB | 100 | GGB | 39.02 | GGB | 39.02 | GGB | 212208.03 | GGB | 212210.51 | 2923.16 | 2726.3467 |  |  |  | 0 | 1 | [14 empty] | 112.5584 | 2726.3467 |  | 104.98
25.04.2008 22:00 | 3600 | 2 | 761.71 | GGB | 762.637 | 773.508 | 768.132 | 270.74 | GGB | 10875 | GGB | 9.74 | GGB | 1018.17 | GGB | 62.44 | GGB | 174188.97 | GGB | 142487.26 | GGB | 0 | 0 | 3155 | 3600 | 3139.6 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 212247.2 | GGB | 212249.69 | 3139.6 | 2652.3634 |  |  |  | 0 | 1 | [14 empty] | 124.2647 | 2652.3634 |  | 104.98
25.04.2008 23:00 | 3600 | 2 | 761.66 | GGB | 762.637 | 772.43 | 767.033 | 273.62 | GGB | 11013.6 | GGB | 9.76 | GGB | 1019.2 | GGB | 61.73 | GGB | 176911.2 | GGB | 145168.57 | GGB | 0 | 0 | 3217 | 3600 | 3201.23 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 212286.47 | GGB | 212288.96 | 3201.23 | 2603.3734 |  |  |  | 0 | 1 | [14 empty] | 129.0883 | 2603.3734 |  | 104.98
25.04.2008 24:00 | 3600 | 2 | 761.76 | GGB | 761.538 | 772.289 | 767.033 | 275.3 | GGB | 11101.4 | GGB | 9.77 | GGB | 1019.9 | GGB | 61.09 | GGB | 179000.74 | GGB | 147264.28 | GGB | 0 | 0 | 3261 | 3600 | 3244.87 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 212325.93 | GGB | 212328.42 | 3244.87 | 2566.325 |  |  |  | 0 | 1 | [14 empty] | 132.7371 | 2566.325 |  | 104.98
26.04.2008 01:00 | 3600 | 2 | 761.91 | GGB | 764.102 | 773.297 | 768.132 | 276.64 | GGB | 11176.3 | GGB | 9.78 | GGB | 1020.51 | GGB | 60.6 | GGB | 180568.73 | GGB | 148863.15 | GGB | 0 | 0 | 3307 | 3600 | 3291.37 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 212365.75 | GGB | 212368.24 | 3291.37 | 2538.7613 |  |  |  | 1 | 1 |  |  |  |  | 148863.15 | 2538.7613 | 148863.15 | 2538.7613 | 9.4909 | [5 empty] | 136.101 | 2538.7613 |  | 104.98
26.04.2008 02:00 | 3600 | 2 | 761.22 | GGB | 762.637 | 771.117 | 767.033 | 277.32 | GGB | 11201.4 | GGB | 9.77 | GGB | 1020.93 | GGB | 60.25 | GGB | 181616.25 | GGB | 149946.16 | GGB | 0 | 0 | 3353 | 3600 | 3336.67 | GNB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 212405.78 | GGB | 212408.27 | 3336.67 | 2520.4247 |  |  |  | 0 | 1 | [14 empty] | 138.978 | 2520.4247 |  | 104.98
26.04.2008 03:00 | 3600 | 2 | 761.02 | GGB | 761.538 | 771.305 | 765.934 | 278.7 | GGB | 11268.3 | GGB | 9.78 | GGB | 1021.47 | GGB | 59.87 | GGB | 183057.69 | GGB | 151386.66 | GGB | 0 | 0 | 3398 | 3600 | 3381.77 | GNB | 100 | GGB | 41.33 | GGB | 41.33 | GGB | 212447.1 | GGB | 212449.6 | 3381.77 | 2496.4419 |  |  |  | 0 | 1 | [14 empty] | 142.2097 | 2496.4419 |  | 104.98
26.04.2008 04:00 | 3600 | 2 | 760.69 | GGB | 762.637 | 771.328 | 767.033 | 279.71 | GGB | 11312.1 | GGB | 9.78 | GGB | 1022.08 | GGB | 59.45 | GGB | 184203.14 | GGB | 152617.61 | GGB | 0 | 0 | 3444 | 3600 | 3428.43 | GNB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 212487.57 | GGB | 212490.07 | 3428.43 | 2476.3066 |  |  |  | 0 | 1 | [14 empty] | 145.3441 | 2476.3066 |  | 104.98
26.04.2008 05:00 | 3600 | 2 | 760.6 | GGB | 761.538 | 771.422 | 767.033 | 280.23 | GGB | 11350.5 | GGB | 9.78 | GGB | 1022.79 | GGB | 59.1 | GGB | 184882.05 | GGB | 153447.77 | GNB | 0 | 0 | 3458 | 3600 | 3442.21 | GNB | 100 | GGB | 40.47 | GGB | 40.47 | GGB | 212528.04 | GGB | 212530.54 | 3442.21 | 2462.9097 |  |  |  | 0 | 1 | [14 empty] | 146.7221 | 2462.9097 |  | 104.98
26.04.2008 06:00 | 3600 | 2 | 760.41 | GGB | 761.538 | 771.375 | 765.934 | 280.83 | GGB | 11380.1 | GGB | 9.78 | GGB | 1023.22 | GGB | 58.85 | GGB | 185834.94 | GGB | 154420.71 | GNB | 0 | 0 | 3497 | 3600 | 3481.28 | GNB | 100 | GGB | 40.67 | GGB | 40.67 | GGB | 212568.7 | GGB | 212571.21 | 3481.28 | 2447.3919 |  |  |  | 0 | 1 | [14 empty] | 149.3283 | 2447.3919 |  | 104.98
26.04.2008 07:00 | 3600 | 2 | 760.8 | GGB | 762.637 | 772.688 | 767.033 | 281.03 | GGB | 11414 | GGB | 9.79 | GGB | 1023.53 | GGB | 58.68 | GGB | 186195.85 | GGB | 154850.36 | GNB | 0 | 0 | 3486 | 3600 | 3469.82 | GNB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 212609.61 | GGB | 212612.12 | 3469.82 | 2440.6014 |  |  |  | 0 | 1 | [14 empty] | 149.2508 | 2440.6014 |  | 104.98
26.04.2008 08:00 | 3600 | 2 | 761.9 | GGB | 764.102 | 773.813 | 768.498 | 279.77 | GGB | 11398.4 | GGB | 9.81 | GGB | 1023.98 | GGB | 59.02 | GGB | 185095.52 | GGB | 153842.3 | GNB | 0 | 0 | 3422 | 3600 | 3405.72 | GNB | 100 | GGB | 40.98 | GGB | 40.98 | GGB | 212650.59 | GGB | 212653.1 | 3405.72 | 2456.5935 |  |  |  | 1 | 1 |  |  |  |  | 153842.3 | 2456.5935 |  | 2456.5935 | 9.2223 | [5 empty] | 145.5399 | 2456.5935 |  | 104.98
26.04.2008 09:00 | 3600 | 2 | 764.32 | GGB | 766.3 | 776.016 | 770.696 | 275.19 | GGB | 11274.2 | GGB | 9.84 | GGB | 1024.17 | GGB | 60.27 | GGB | 179981.15 | GGB | 149056.57 | GGB | 0 | 0 | 3248 | 3600 | 3231.92 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 212691.33 | GGB | 212693.84 | 3231.92 | 2535.4669 |  |  |  | 1 | 1 |  |  |  |  | 149056.57 | 2535.4669 | 149056.57 | 2535.4669 | 9.2766 | [5 empty] | 133.8164 | 2535.4669 |  | 104.98
26.04.2008 10:00 | 3600 | 2 | 765.44 | GGB | 765.201 | 775.102 | 770.696 | 269.7 | GGB | 11048.2 | GGB | 9.83 | GGB | 1023.59 | GGB | 61.84 | GGB | 174019.52 | GGB | 143362.67 | GGB | 0 | 0 | 3058 | 3600 | 3041.95 | GGB | 100 | GGB | 41.53 | GGB | 41.53 | GGB | 212732.86 | GGB | 212735.37 | 3041.95 | 2636.1674 |  |  |  | 1 | 1 |  |  |  |  | 143362.67 | 2636.1674 | 143362.67 | 2636.1674 | 9.1001 | [5 empty] | 121.1395 | 2636.1674 |  | 104.98
26.04.2008 11:00 | 3600 | 2 | 765.93 | GGB | 766.667 | 777.375 | 771.795 | 266.67 | GGB | 10886.8 | GGB | 9.81 | GGB | 1022.85 | GGB | 62.87 | GGB | 170972.68 | GGB | 140320.23 | GGB | 0 | 0 | 2969 | 3600 | 2952.96 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 212773.25 | GGB | 212775.76 | 2952.96 | 2693.3251 |  |  |  | 1 | 1 |  |  |  |  | 140320.23 | 2693.3251 | 140320.23 | 2693.3251 | 9.357 | [5 empty] | 115.1 | 2693.3251 |  | 104.98
26.04.2008 12:00 | 3600 | 2 | 766.04 | GGB | 766.667 | 778.266 | 772.161 | 265.63 | GGB | 10819.2 | GGB | 9.8 | GGB | 1022.02 | GGB | 63.39 | GGB | 170021.99 | GGB | 139212.82 | GGB | 0 | 0 | 2933 | 3600 | 2917.24 | GGB | 100 | GGB | 40.31 | GGB | 40.31 | GGB | 212813.56 | GGB | 212816.07 | 2917.24 | 2714.75 |  |  |  | 1 | 1 |  |  |  |  | 139212.82 | 2714.75 | 139212.82 | 2714.75 | 9.3755 | [5 empty] | 112.8103 | 2714.75 |  | 104.98
26.04.2008 13:00 | 3600 | 2 | 766.03 | GGB | 765.201 | 776.18 | 770.696 | 264.48 | GGB | 10762.4 | GGB | 9.79 | GGB | 1021.32 | GGB | 63.87 | GGB | 168750 | GGB | 137879.5 | GGB | 0 | 0 | 2911 | 3600 | 2895.69 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 212853.52 | GGB | 212856.03 | 2895.69 | 2741.0021 |  |  |  | 1 | 1 |  |  |  |  | 137879.5 | 2741.0021 | 137879.5 | 2741.0021 | 9.4577 | [5 empty] | 110.9045 | 2741.0021 |  | 104.98
26.04.2008 14:00 | 3600 | 2 | 766.54 | GGB | 765.201 | 776.391 | 770.696 | 264.05 | GGB | 10742.6 | GGB | 9.79 | GGB | 1020.64 | GGB | 64.2 | GGB | 168273.55 | GGB | 137265.04 | GGB | 0 | 0 | 2875 | 3600 | 2859.86 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 212893.33 | GGB | 212895.84 | 2859.86 | 2753.2721 |  |  |  | 1 | 1 |  |  |  |  | 137265.04 | 2753.2721 | 137265.04 | 2753.2721 | 9.4933 | [5 empty] | 109.0441 | 2753.2721 |  | 104.98
26.04.2008 15:00 | 3600 | 2 | 766.68 | GGB | 767.766 | 777.563 | 773.26 | 263.38 | GGB | 10714.5 | GGB | 9.8 | GGB | 1020.3 | GGB | 64.42 | GGB | 167812.51 | GGB | 136751.97 | GGB | 0 | 0 | 2851 | 3600 | 2835.6 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 212932.98 | GGB | 212935.49 | 2835.6 | 2763.6019 |  |  |  | 1 | 1 |  |  |  |  | 136751.97 | 2763.6019 | 136751.97 | 2763.6019 | 9.5316 | [5 empty] | 107.715 | 2763.6019 |  | 104.98
26.04.2008 16:00 | 3600 | 2 | 766.93 | GGB | 766.667 | 778.664 | 773.26 | 262.79 | GGB | 10672.7 | GGB | 9.79 | GGB | 1019.79 | GGB | 64.8 | GGB | 167080.79 | GGB | 135933.98 | GGB | 0 | 0 | 2813 | 3600 | 2797.57 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 212972.42 | GGB | 212974.94 | 2797.57 | 2780.232 |  |  |  | 1 | 1 |  |  |  |  | 135933.98 | 2780.232 | 135933.98 | 2780.232 | 9.5799 | [5 empty] | 105.6347 | 2780.232 |  | 104.98
26.04.2008 17:00 | 3600 | 2 | 766.41 | GGB | 766.3 | 777.469 | 771.795 | 262.36 | GGB | 10636.2 | GGB | 9.78 | GGB | 1019.02 | GGB | 64.89 | GGB | 166702.27 | GGB | 135487.98 | GGB | 0 | 0 | 2832 | 3600 | 2816.1 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 213011.65 | GGB | 213014.16 | 2816.1 | 2789.384 |  |  |  | 1 | 1 |  |  |  |  | 135487.98 | 2789.384 | 135487.98 | 2789.384 | 9.6361 | [5 empty] | 105.9855 | 2789.384 |  | 104.98
26.04.2008 18:00 | 3600 | 2 | 766.86 | GGB | 766.667 | 777.469 | 773.26 | 262.25 | GGB | 10645 | GGB | 9.79 | GGB | 1018.55 | GGB | 64.96 | GGB | 166513.01 | GGB | 135243.59 | GGB | 0 | 0 | 2811 | 3600 | 2795.52 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 213050.83 | GGB | 213053.34 | 2795.52 | 2794.4245 |  |  |  | 1 | 1 |  |  |  |  | 135243.59 | 2794.4245 | 135243.59 | 2794.4245 | 9.6459 | [5 empty] | 105.0212 | 2794.4245 |  | 104.98
26.04.2008 19:00 | 3600 | 2 | 766.53 | GGB | 766.3 | 777.164 | 771.795 | 262.2 | GGB | 10629.7 | GGB | 9.78 | GGB | 1018.48 | GGB | 64.92 | GGB | 166487.7 | GGB | 135231.23 | GGB | 0 | 0 | 2820 | 3600 | 2804.8 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 213089.57 | GGB | 213092.08 | 2804.8 | 2794.6799 |  |  |  | 1 | 1 |  |  |  |  | 135231.23 | 2794.6799 | 135231.23 | 2794.6799 | 9.7555 | [5 empty] | 105.3602 | 2794.6799 |  | 104.98
26.04.2008 20:00 | 3600 | 2 | 766.59 | GGB | 765.201 | 775.852 | 770.696 | 262.51 | GGB | 10647.6 | GGB | 9.78 | GGB | 1018.65 | GGB | 64.76 | GGB | 166739.68 | GGB | 135520.78 | GGB | 0 | 0 | 2825 | 3600 | 2809.78 | GGB | 100 | GGB | 38.52 | GGB | 38.52 | GGB | 213128.08 | GGB | 213130.6 | 2809.78 | 2788.7089 |  |  |  | 1 | 1 |  |  |  |  | 135520.78 | 2788.7089 | 135520.78 | 2788.7089 | 9.8112 | [5 empty] | 105.7732 | 2788.7089 |  | 104.98
26.04.2008 21:00 | 3600 | 2 | 765.71 | GGB | 764.102 | 775.172 | 769.597 | 263.72 | GGB | 10688.1 | GGB | 9.77 | GGB | 1018.96 | GGB | 64.31 | GGB | 167761.89 | GGB | 136574.08 | GGB | 0 | 0 | 2878 | 3600 | 2862.35 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 213167.75 | GGB | 213170.27 | 2862.35 | 2767.2015 |  |  |  | 1 | 1 |  |  |  |  | 136574.08 | 2767.2015 | 136574.08 | 2767.2015 | 9.5268 | [5 empty] | 108.5897 | 2767.2015 |  | 104.98
26.04.2008 22:00 | 3600 | 2 | 763.11 | GGB | 764.102 | 774.023 | 768.498 | 269.04 | GGB | 10819.4 | GGB | 9.74 | GGB | 1020.52 | GGB | 63.34 | GGB | 172326.1 | GGB | 140913.43 | GGB | 0 | 0 | 3088 | 3600 | 3072.49 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 213206.52 | GGB | 213209.04 | 3072.49 | 2681.9871 |  |  |  | 1 | 1 |  |  |  |  | 140913.43 | 2681.9871 | 140913.43 | 2681.9871 | 9.7479 | [5 empty] | 120.2653 | 2681.9871 |  | 104.98
26.04.2008 23:00 | 3600 | 2 | 762.71 | GGB | 762.637 | 773.063 | 767.033 | 271.7 | GGB | 10933.3 | GGB | 9.76 | GGB | 1021.65 | GGB | 62.68 | GGB | 174789.75 | GGB | 143366.37 | GGB | 0 | 0 | 3158 | 3600 | 3142.56 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 213245.26 | GGB | 213247.79 | 3142.56 | 2636.0994 |  |  |  | 0 | 1 | [14 empty] | 125.1493 | 2636.0994 |  | 104.98
26.04.2008 24:00 | 3600 | 2 | 763.05 | GGB | 762.637 | 772.758 | 767.033 | 272.86 | GGB | 11014.1 | GGB | 9.77 | GGB | 1022.35 | GGB | 62.15 | GGB | 176135.47 | GGB | 144796 | GGB | 0 | 0 | 3171 | 3600 | 3155.55 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 213284.08 | GGB | 213286.61 | 3155.55 | 2610.0721 |  |  |  | 0 | 1 | [14 empty] | 126.9197 | 2610.0721 |  | 104.98
27.04.2008 01:00 | 3600 | 2 | 762.29 | GGB | 763.004 | 772.641 | 767.033 | 275.01 | GGB | 11090.7 | GGB | 9.77 | GGB | 1022.87 | GGB | 61.6 | GGB | 178428.57 | GGB | 147000.24 | GGB | 0 | 0 | 3254 | 3600 | 3238.59 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 213323.31 | GGB | 213325.84 | 3238.59 | 2570.9346 |  |  |  | 0 | 1 | [14 empty] | 132.2426 | 2570.9346 |  | 104.98
27.04.2008 02:00 | 3600 | 2 | 761.65 | GGB | 762.637 | 772.5 | 767.033 | 276.72 | GGB | 11162.6 | GGB | 9.77 | GGB | 1023.18 | GGB | 61.06 | GGB | 180427.88 | GGB | 148928.41 | GGB | 0 | 0 | 3324 | 3600 | 3307.71 | GNB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 213362.79 | GGB | 213365.31 | 3307.71 | 2537.6488 |  |  |  | 0 | 1 | [14 empty] | 136.8367 | 2537.6488 |  | 104.98
27.04.2008 03:00 | 3600 | 2 | 761.88 | GGB | 762.637 | 772.336 | 767.033 | 277.7 | GGB | 11212 | GGB | 9.78 | GGB | 1023.37 | GGB | 60.78 | GGB | 181480.91 | GGB | 149953.57 | GGB | 0 | 0 | 3350 | 3600 | 3334.07 | GNB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 213402.39 | GGB | 213404.91 | 3334.07 | 2520.3001 |  |  |  | 0 | 1 | [14 empty] | 138.8766 | 2520.3001 |  | 104.98
27.04.2008 04:00 | 3600 | 2 | 761.39 | GGB | 762.637 | 772.172 | 767.033 | 278.76 | GGB | 11258 | GGB | 9.78 | GGB | 1023.64 | GGB | 60.42 | GGB | 182730.89 | GGB | 151189.36 | GGB | 0 | 0 | 3398 | 3600 | 3382.24 | GNB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 213442.2 | GGB | 213444.72 | 3382.24 | 2499.6997 |  |  |  | 0 | 1 | [14 empty] | 142.0441 | 2499.6997 |  | 104.98
27.04.2008 05:00 | 3600 | 2 | 762.77 | GGB | 765.201 | 775.43 | 769.597 | 278.38 | GGB | 11306 | GGB | 9.81 | GGB | 1024.27 | GGB | 60.25 | GGB | 182549.33 | GGB | 151208.26 | GGB | 0 | 0 | 3356 | 3600 | 3340 | GNB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 213482.22 | GGB | 213484.74 | 3340 | 2499.3873 |  |  |  | 1 | 1 |  |  |  |  | 151208.26 | 2499.3873 | 151208.26 | 2499.3873 | 9.4435 | [5 empty] | 140.2877 | 2499.3873 |  | 104.98
27.04.2008 06:00 | 3600 | 2 | 760.74 | GGB | 762.637 | 772.008 | 767.033 | 278.9 | GGB | 11271 | GGB | 9.77 | GGB | 1024.34 | GGB | 59.98 | GGB | 183105 | GGB | 151805.7 | GGB | 0 | 0 | 3449 | 3600 | 3433.31 | GNB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 213522.55 | GGB | 213525.07 | 3433.31 | 2489.5508 |  |  |  | 0 | 1 | [14 empty] | 144.7767 | 2489.5508 |  | 104.98
27.04.2008 07:00 | 3600 | 2 | 762.07 | GGB | 762.637 | 771.938 | 767.033 | 277.89 | GGB | 11280.6 | GGB | 9.79 | GGB | 1024.35 | GGB | 60.02 | GGB | 182207.13 | GGB | 151042.35 | GGB | 0 | 0 | 3378 | 3600 | 3361.76 | GNB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 213563.52 | GGB | 213566.04 | 3361.76 | 2502.1327 |  |  |  | 0 | 1 | [14 empty] | 141.0467 | 2502.1327 |  | 104.98
27.04.2008 08:00 | 3600 | 2 | 762.38 | GGB | 764.102 | 774.094 | 768.132 | 277.47 | GGB | 11276 | GGB | 9.8 | GGB | 1024.52 | GGB | 60.18 | GGB | 181655.86 | GGB | 150538.06 | GGB | 0 | 0 | 3360 | 3600 | 3344.07 | GNB | 100 | GGB | 41.04 | GGB | 41.04 | GGB | 213604.57 | GGB | 213607.08 | 3344.07 | 2510.5146 |  |  |  | 1 | 1 |  |  |  |  | 150538.06 | 2510.5146 | 150538.06 | 2510.5146 | 9.2088 | [5 empty] | 139.8361 | 2510.5146 |  | 104.98
27.04.2008 09:00 | 3600 | 2 | 764.22 | GGB | 765.201 | 775.172 | 769.597 | 274.54 | GGB | 11211.9 | GGB | 9.82 | GGB | 1024.57 | GGB | 60.84 | GGB | 178566.11 | GGB | 147692.32 | GGB | 0 | 0 | 3238 | 3600 | 3222.11 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 213645.27 | GGB | 213647.79 | 3222.11 | 2558.8873 |  |  |  | 1 | 1 |  |  |  |  | 147692.32 | 2558.8873 | 147692.32 | 2558.8873 | 9.2834 | [5 empty] | 132.1891 | 2558.8873 |  | 104.98
27.04.2008 10:00 | 3600 | 2 | 764.74 | GGB | 765.201 | 775.148 | 769.597 | 270.93 | GGB | 11071.2 | GGB | 9.82 | GGB | 1024.5 | GGB | 62.04 | GGB | 174822.76 | GGB | 144067.82 | GGB | 0 | 0 | 3128 | 3600 | 3112.04 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 213685.67 | GGB | 213688.19 | 3112.04 | 2623.2645 |  |  |  | 1 | 1 |  |  |  |  | 144067.82 | 2623.2645 | 144067.82 | 2623.2645 | 9.3547 | [5 empty] | 124.5402 | 2623.2645 |  | 104.98
27.04.2008 11:00 | 3600 | 2 | 764.81 | GGB | 765.201 | 776.297 | 770.696 | 268.75 | GGB | 10957 | GGB | 9.8 | GGB | 1023.99 | GGB | 62.85 | GGB | 172440.53 | GGB | 141692.59 | GGB | 0 | 0 | 3077 | 3336 | 3060.83 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 213725.78 | GGB | 213728.29 | 3060.83 | 2667.239 |  |  |  | 1 | 1 |  |  |  |  | 141692.59 | 2667.239 | 141692.59 | 2667.239 | 9.4246 | [5 empty] | 120.4714 | 2667.239 |  | 104.98
27.04.2008 12:00 | 3600 | 2 | 765.49 | GGB | 766.3 | 776.109 | 770.696 | 266.39 | GGB | 10860.4 | GGB | 9.81 | GGB | 1022.34 | GGB | 63.55 | GGB | 169714.99 | GGB | 138938.85 | GGB | 0 | 0 | 2993 | 3600 | 2977.3 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 213765.65 | GGB | 213768.16 | 2977.3 | 2720.1031 |  |  |  | 1 | 1 |  |  |  |  | 138938.85 | 2720.1031 | 138938.85 | 2720.1031 | 9.479 | [5 empty] | 114.9063 | 2720.1031 |  | 104.98
27.04.2008 13:00 | 3600 | 2 | 766.05 | GGB | 766.3 | 777.258 | 770.696 | 264.97 | GGB | 10781.6 | GGB | 9.8 | GGB | 1020.98 | GGB | 64.08 | GGB | 168378.08 | GGB | 137441.08 | GGB | 0 | 0 | 2938 | 3600 | 2922.8 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 213805.22 | GGB | 213807.74 | 2922.8 | 2749.7456 |  |  |  | 1 | 1 |  |  |  |  | 137441.08 | 2749.7456 | 137441.08 | 2749.7456 | 9.5485 | [5 empty] | 111.5869 | 2749.7456 |  | 104.98
27.04.2008 14:00 | 3600 | 2 | 766.08 | GGB | 765.201 | 776.109 | 771.429 | 264.38 | GGB | 10728 | GGB | 9.79 | GGB | 1020.08 | GGB | 64.51 | GGB | 167826.81 | GGB | 136698.43 | GGB | 0 | 0 | 2916 | 3600 | 2900.68 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 213845.8 | GGB | 213848.32 | 2900.68 | 2764.6843 |  |  |  | 1 | 1 |  |  |  |  | 136698.43 | 2764.6843 | 136698.43 | 2764.6843 | 9.3132 | [5 empty] | 110.144 | 2764.6843 |  | 104.98
27.04.2008 15:00 | 3600 | 2 | 766.56 | GGB | 765.201 | 775.945 | 770.33 | 263.57 | GGB | 10711.3 | GGB | 9.79 | GGB | 1019.38 | GGB | 65 | GGB | 167044.47 | GGB | 135771.63 | GGB | 0 | 0 | 2889 | 3600 | 2873.71 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 213885.14 | GGB | 213887.66 | 2873.71 | 2783.5565 |  |  |  | 1 | 1 |  |  |  |  | 135771.63 | 2783.5565 | 135771.63 | 2783.5565 | 9.6067 | [5 empty] | 108.3801 | 2783.5565 |  | 104.98
27.04.2008 16:00 | 3600 | 2 | 766.33 | GGB | 765.201 | 777.047 | 770.33 | 263.16 | GGB | 10680.1 | GGB | 9.79 | GGB | 1018.34 | GGB | 65.09 | GGB | 166618.64 | GGB | 135249.68 | GGB | 0 | 0 | 2891 | 3600 | 2874.99 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 213924.38 | GGB | 213926.9 | 2874.99 | 2794.2987 |  |  |  | 1 | 1 |  |  |  |  | 135249.68 | 2794.2987 | 135249.68 | 2794.2987 | 9.6312 | [5 empty] | 108.0115 | 2794.2987 |  | 104.98
27.04.2008 17:00 | 3600 | 2 | 765.74 | GGB | 767.766 | 778.008 | 772.527 | 262.62 | GGB | 10657.5 | GGB | 9.78 | GGB | 1017.47 | GGB | 65.07 | GGB | 166551.52 | GGB | 135086.29 | GGB | 0 | 0 | 2913 | 3600 | 2897.28 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 213963.45 | GGB | 213965.97 | 2897.28 | 2797.6784 |  |  |  | 1 | 1 |  |  |  |  | 135086.29 | 2797.6784 | 135086.29 | 2797.6784 | 9.6731 | [5 empty] | 108.7174 | 2797.6784 |  | 104.98
27.04.2008 18:00 | 3600 | 2 | 766.37 | GGB | 765.201 | 776.977 | 771.429 | 262.26 | GGB | 10688.8 | GGB | 9.79 | GGB | 1017.45 | GGB | 64.94 | GGB | 166612.04 | GGB | 135184.56 | GGB | 0 | 0 | 2883 | 3600 | 2867.73 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 214002.64 | GGB | 214005.16 | 2867.73 | 2795.6447 |  |  |  | 1 | 1 |  |  |  |  | 135184.56 | 2795.6447 | 135184.56 | 2795.6447 | 9.6435 | [5 empty] | 107.6869 | 2795.6447 |  | 104.98
27.04.2008 19:00 | 3600 | 2 | 765.75 | GGB | 764.102 | 775.102 | 769.963 | 262.46 | GGB | 10697 | GGB | 9.78 | GGB | 1017.14 | GGB | 64.56 | GGB | 167109.39 | GGB | 135702.63 | GGB | 0 | 0 | 2916 | 3600 | 2899.97 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 214041.89 | GGB | 214044.41 | 2899.97 | 2784.9718 |  |  |  | 1 | 1 |  |  |  |  | 135702.63 | 2784.9718 | 135702.63 | 2784.9718 | 9.6287 | [5 empty] | 109.3149 | 2784.9718 |  | 104.98
27.04.2008 20:00 | 3600 | 2 | 765.66 | GGB | 764.102 | 775.781 | 769.963 | 262.53 | GGB | 10725.9 | GGB | 9.78 | GGB | 1016.59 | GGB | 64.04 | GGB | 167411.99 | GGB | 136081.61 | GGB | 0 | 0 | 2914 | 3600 | 2898.59 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 214081.22 | GGB | 214083.74 | 2898.59 | 2777.2158 |  |  |  | 1 | 1 |  |  |  |  | 136081.61 | 2777.2158 | 136081.61 | 2777.2158 | 9.6092 | [5 empty] | 109.568 | 2777.2158 |  | 104.98
27.04.2008 21:00 | 3600 | 2 | 764.88 | GGB | 764.102 | 774.539 | 769.963 | 263.66 | GGB | 10762 | GGB | 9.78 | GGB | 1016.92 | GGB | 63.5 | GGB | 168430.9 | GGB | 137174.57 | GGB | 0 | 0 | 2966 | 3600 | 2950.55 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 214120.69 | GGB | 214123.21 | 2950.55 | 2755.0879 |  |  |  | 1 | 1 |  |  |  |  | 137174.57 | 2755.0879 | 137174.57 | 2755.0879 | 9.5751 | [5 empty] | 112.4279 | 2755.0879 |  | 104.98
27.04.2008 22:00 | 3600 | 2 | 763.74 | GGB | 762.637 | 773.531 | 767.766 | 265.75 | GGB | 10807.3 | GGB | 9.76 | GGB | 1018.18 | GGB | 63.04 | GGB | 170398.3 | GGB | 139139.06 | GGB | 0 | 0 | 3051 | 3600 | 3035.51 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 214160.28 | GGB | 214162.8 | 3035.51 | 2716.1891 |  |  |  | 0 | 1 | [14 empty] | 117.3217 | 2716.1891 |  | 104.98
27.04.2008 23:00 | 3600 | 2 | 762.48 | GGB | 762.637 | 773.531 | 767.766 | 268.71 | GGB | 10928.2 | GGB | 9.76 | GGB | 1018.89 | GGB | 62.09 | GGB | 173617.89 | GGB | 142270.86 | GGB | 0 | 0 | 3151 | 3600 | 3134.94 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 214200.16 | GGB | 214202.69 | 3134.94 | 2656.3978 |  |  |  | 0 | 1 | [14 empty] | 123.8918 | 2656.3978 |  | 104.98
27.04.2008 24:00 | 3600 | 2 | 762.12 | GGB | 761.538 | 772.172 | 766.667 | 271.58 | GGB | 11014.6 | GGB | 9.76 | GGB | 1019.11 | GGB | 61.78 | GGB | 175947.31 | GGB | 144345.67 | GGB | 0 | 0 | 3225 | 3600 | 3208.92 | GGB | 100 | GGB | 40.97 | GGB | 40.97 | GGB | 214241.13 | GGB | 214243.66 | 3208.92 | 2618.215 |  |  |  | 0 | 1 | [14 empty] | 128.6649 | 2618.215 |  | 104.98
28.04.2008 01:00 | 3600 | 2 | 761.59 | GGB | 761.538 | 771.023 | 766.3 | 273.59 | GGB | 11062.2 | GGB | 9.76 | GGB | 1019.56 | GGB | 60.96 | GGB | 178612.33 | GGB | 146956 | GGB | 0 | 0 | 3284 | 3600 | 3267.75 | GGB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 214281.35 | GGB | 214283.88 | 3267.75 | 2571.7085 |  |  |  | 0 | 1 | [14 empty] | 133.3932 | 2571.7085 |  | 104.98
28.04.2008 02:00 | 3600 | 2 | 762.4 | GGB | 764.102 | 773.32 | 768.864 | 275.04 | GGB | 11145.6 | GGB | 9.79 | GGB | 1019.25 | GGB | 60.31 | GGB | 180454.29 | GGB | 148714.41 | GGB | 0 | 0 | 3273 | 3600 | 3256.76 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 214321.65 | GGB | 214324.18 | 3256.76 | 2541.3005 |  |  |  | 1 | 1 |  |  |  |  | 148714.41 | 2541.3005 | 148714.41 | 2541.3005 | 9.3779 | [5 empty] | 134.5353 | 2541.3005 |  | 104.98
28.04.2008 03:00 | 3600 | 2 | 761.5 | GGB | 761.538 | 770.977 | 766.667 | 274.55 | GGB | 11175.6 | GGB | 9.78 | GGB | 1019.19 | GGB | 60.4 | GGB | 179648.84 | GGB | 148004.44 | GGB | 0 | 0 | 3331 | 3600 | 3315.5 | GNB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 214362.05 | GGB | 214364.58 | 3315.5 | 2553.491 |  |  |  | 0 | 1 | [14 empty] | 136.308 | 2553.491 |  | 104.98
28.04.2008 04:00 | 3600 | 2 | 761.19 | GGB | 764.102 | 773.016 | 767.766 | 276.93 | GGB | 11185.6 | GGB | 9.78 | GGB | 1019.31 | GGB | 59.3 | GGB | 182904.74 | GGB | 151199.29 | GGB | 0 | 0 | 3359 | 3600 | 3343.09 | GNB | 100 | GGB | 40.64 | GGB | 40.64 | GGB | 214402.68 | GGB | 214405.22 | 3343.09 | 2499.5355 |  |  |  | 1 | 1 |  |  |  |  | 151199.29 | 2499.5355 | 151199.29 | 2499.5355 | 9.2994 | [5 empty] | 140.4091 | 2499.5355 |  | 104.98
28.04.2008 05:00 | 3600 | 2 | 761.21 | GGB | 761.538 | 772.008 | 766.667 | 275.91 | GGB | 11249.6 | GGB | 9.78 | GGB | 1019.32 | GGB | 59.55 | GGB | 181584.34 | GGB | 149998.63 | GGB | 0 | 0 | 3386 | 3600 | 3370.17 | GNB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 214443.23 | GGB | 214445.77 | 3370.17 | 2519.543 |  |  |  | 0 | 1 | [14 empty] | 140.4225 | 2519.543 |  | 104.98
28.04.2008 06:00 | 3600 | 2 | 760.81 | GGB | 761.538 | 772.383 | 766.667 | 277.31 | GGB | 11231.3 | GGB | 9.78 | GGB | 1019.26 | GGB | 58.76 | GGB | 183652.97 | GGB | 152057.85 | GGB | 0 | 0 | 3385 | 3600 | 3369.13 | GNB | 100 | GGB | 40.78 | GGB | 40.78 | GGB | 214484.01 | GGB | 214486.55 | 3369.13 | 2485.4225 |  |  |  | 0 | 1 | [14 empty] | 142.3063 | 2485.4225 |  | 104.98
28.04.2008 07:00 | 3600 | 2 | 761.15 | GGB | 762.637 | 772.383 | 766.667 | 277.9 | GGB | 11263.5 | GGB | 9.79 | GGB | 1019.52 | GGB | 58.26 | GGB | 184811.63 | GGB | 153286.41 | GNB | 0 | 0 | 3378 | 3600 | 3361.54 | GNB | 100 | GGB | 40.63 | GGB | 40.63 | GGB | 214524.64 | GGB | 214527.18 | 3361.54 | 2465.5023 |  |  |  | 0 | 1 | [14 empty] | 143.1329 | 2465.5023 |  | 104.98
28.04.2008 08:00 | 3600 | 2 | 762 | GGB | 764.102 | 773.367 | 768.864 | 275.21 | GGB | 11299.3 | GGB | 9.81 | GGB | 1019.23 | GGB | 59.04 | GGB | 181633.85 | GGB | 150254.44 | GGB | 0 | 0 | 3358 | 3600 | 3342.05 | GNB | 100 | GGB | 40.34 | GGB | 40.34 | GGB | 214564.98 | GGB | 214567.52 | 3342.05 | 2515.2535 |  |  |  | 1 | 1 |  |  |  |  | 150254.44 | 2515.2535 | 150254.44 | 2515.2535 | 9.3686 | [5 empty] | 139.4883 | 2515.2535 |  | 104.98
28.04.2008 09:00 | 3600 | 2 | 763.46 | GGB | 765.201 | 774.68 | 769.963 | 272.19 | GGB | 11151.8 | GGB | 9.82 | GGB | 1019.14 | GGB | 59.99 | GGB | 178376.85 | GGB | 147130.03 | GGB | 0 | 0 | 3227 | 3600 | 3211.1 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 214605.28 | GGB | 214607.82 | 3211.1 | 2568.6666 |  |  |  | 1 | 1 |  |  |  |  | 147130.03 | 2568.6666 | 147130.03 | 2568.6666 | 9.3779 | [5 empty] | 131.2359 | 2568.6666 |  | 104.98
28.04.2008 10:00 | 3600 | 2 | 765.17 | GGB | 765.201 | 775.617 | 769.963 | 268.6 | GGB | 10972.3 | GGB | 9.82 | GGB | 1018.62 | GGB | 60.97 | GGB | 174520.17 | GGB | 143451.65 | GGB | 0 | 0 | 3038 | 3600 | 3022.16 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 214645.29 | GGB | 214647.83 | 3022.16 | 2634.5323 |  |  |  | 1 | 1 |  |  |  |  | 143451.65 | 2634.5323 | 143451.65 | 2634.5323 | 9.4458 | [5 empty] | 120.4261 | 2634.5323 |  | 104.98
28.04.2008 11:00 | 3600 | 2 | 766 | GGB | 766.3 | 776.836 | 771.429 | 265.04 | GGB | 10806.5 | GGB | 9.81 | GGB | 1017.39 | GGB | 62.17 | GGB | 170750.41 | GGB | 139682.61 | GGB | 0 | 0 | 2924 | 3600 | 2907.94 | GGB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 214686.03 | GGB | 214688.57 | 2907.94 | 2705.6195 |  |  |  | 1 | 1 |  |  |  |  | 139682.61 | 2705.6195 | 139682.61 | 2705.6195 | 9.2766 | [5 empty] | 112.8302 | 2705.6195 |  | 104.98
28.04.2008 12:00 | 3600 | 2 | 766.54 | GGB | 765.201 | 776.766 | 771.429 | 262.7 | GGB | 10676 | GGB | 9.8 | GGB | 1015.78 | GGB | 63.12 | GGB | 168358.28 | GGB | 137117.37 | GGB | 0 | 0 | 2839 | 3600 | 2823.1 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 214725.32 | GGB | 214727.85 | 2823.1 | 2756.2372 |  |  |  | 1 | 1 |  |  |  |  | 137117.37 | 2756.2372 | 137117.37 | 2756.2372 | 9.6214 | [5 empty] | 107.5267 | 2756.2372 |  | 104.98
28.04.2008 13:00 | 3600 | 2 | 767.01 | GGB | 767.766 | 778.008 | 773.626 | 261.39 | GGB | 10610.8 | GGB | 9.79 | GGB | 1014.42 | GGB | 63.48 | GGB | 167589.14 | GGB | 136161.4 | GGB | 0 | 0 | 2788 | 3600 | 2772.68 | GGB | 100 | GGB | 39 | GGB | 39 | GGB | 214764.31 | GGB | 214766.85 | 2772.68 | 2772.68 |  |  |  | 1 | 1 |  |  |  |  | 136161.4 | 2772.68 | 136161.4 | 2772.68 | 9.6803 | [5 empty] | 104.87 |  |  | #VALUE!
28.04.2008 14:00 | 3600 | 2 | 766.91 | GGB | 765.201 | 777.141 | 771.429 | 260.71 | GGB | 10580.1 | GGB | 9.79 | GGB | 1013.66 | GGB | 63.63 | GGB | 166843.11 | GGB | 135393.69 | GGB | 0 | 0 | 2770 | 3600 | 2754.54 | GGB | 100 | GGB | 38.88 | GGB | 38.88 | GGB | 214803.19 | GGB | 214805.73 | 2754.54 | 2754.54 |  |  |  | 1 | 1 |  |  |  |  | 135393.69 | 2754.54 | 135393.69 | 2754.54 | 9.5923 | [5 empty] | 103.5965 |  |  | #VALUE!
28.04.2008 15:00 | 3600 | 2 | 767.2 | GGB | 766.3 | 778.008 | 772.527 | 258.1 | GGB | 10565.4 | GGB | 9.79 | GGB | 1012.37 | GGB | 64.69 | GGB | 164099.97 | GGB | 132581.77 | GGB | 0 | 0 | 2744 | 3600 | 2728.62 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 214841.74 | GGB | 214844.28 | 2728.62 | 2728.62 |  |  |  | 1 | 1 |  |  |  |  | 132581.77 | 2728.62 | 132581.77 | 2728.62 | 9.3843 | [5 empty] | 100.4904 |  |  | #VALUE!
28.04.2008 16:00 | 3600 | 2 | 766.95 | GGB | 765.201 | 777.07 | 772.527 | 257.25 | GGB | 10526.3 | GGB | 9.78 | GGB | 1010.98 | GGB | 64.87 | GGB | 163560.81 | GGB | 131895.07 | GGB | 0 | 0 | 2736 | 3600 | 2720.57 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 214880.13 | GGB | 214882.67 | 2720.57 | 2720.57 |  |  |  | 1 | 1 |  |  |  |  | 131895.07 | 2720.57 | 131895.07 | 2720.57 | 9.347 | [5 empty] | 99.6749 |  |  | #VALUE!
28.04.2008 17:00 | 3600 | 2 | 767.12 | GGB | 766.3 | 777.914 | 772.527 | 258.9 | GGB | 10495.4 | GGB | 9.78 | GGB | 1010.47 | GGB | 64.31 | GGB | 165703.16 | GGB | 133776.57 | GGB | 0 | 0 | 2726 | 3600 | 2710.21 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 214918.67 | GGB | 214921.21 | 2710.21 | 2710.21 |  |  |  | 1 | 1 |  |  |  |  | 133776.57 | 2710.21 | 133776.57 | 2710.21 | 9.4074 | [5 empty] | 100.7118 |  |  | #VALUE!
28.04.2008 18:00 | 3600 | 2 | 767.24 | GGB | 766.667 | 777.82 | 772.527 | 257.99 | GGB | 10516.1 | GGB | 9.79 | GGB | 1010.03 | GGB | 64.65 | GGB | 164454.28 | GGB | 132574.6 | GGB | 0 | 0 | 2714 | 3600 | 2698.69 | GGB | 100 | GGB | 38.41 | GGB | 38.41 | GGB | 214957.09 | GGB | 214959.62 | 2698.69 | 2698.69 |  |  |  | 1 | 1 |  |  |  |  | 132574.6 | 2698.69 | 132574.6 | 2698.69 | 9.3147 | [5 empty] | 99.3827 |  |  | #VALUE!
28.04.2008 19:00 | 3600 | 2 | 766.85 | GGB | 765.201 | 776.836 | 771.429 | 257.42 | GGB | 10505.9 | GGB | 9.78 | GGB | 1009.76 | GGB | 64.91 | GGB | 163652.13 | GGB | 131794.06 | GGB | 0 | 0 | 2730 | 3600 | 2714.35 | GGB | 100 | GGB | 38.35 | GGB | 38.35 | GGB | 214995.43 | GGB | 214997.97 | 2714.35 | 2714.35 |  |  |  | 1 | 1 |  |  |  |  | 131794.06 | 2714.35 | 131794.06 | 2714.35 | 9.3282 | [5 empty] | 99.3709 |  |  | #VALUE!
28.04.2008 20:00 | 3600 | 2 | 766.6 | GGB | 765.201 | 776.836 | 771.429 | 259.68 | GGB | 10512.9 | GGB | 9.78 | GGB | 1009.58 | GGB | 64.1 | GGB | 166279.74 | GGB | 134209.1 | GGB | 0 | 0 | 2734 | 3600 | 2718.75 | GGB | 100 | GGB | 38.61 | GGB | 38.61 | GGB | 215034.04 | GGB | 215036.58 | 2718.75 | 2718.75 |  |  |  | 1 | 1 |  |  |  |  | 134209.1 | 2718.75 | 134209.1 | 2718.75 | 9.4504 | [5 empty] | 101.3558 |  |  | #VALUE!
28.04.2008 21:00 | 3600 | 2 | 765.64 | GGB | 764.102 | 774.609 | 769.963 | 261.25 | GGB | 10563.4 | GGB | 9.77 | GGB | 1010.18 | GGB | 63.55 | GGB | 167190.82 | GGB | 135243.76 | GGB | 0 | 0 | 2807 | 3600 | 2791.12 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 215072.7 | GGB | 215075.24 | 2791.12 | 2791.12 |  |  |  | 1 | 1 |  |  |  |  | 135243.76 | 2791.12 | 135243.76 | 2791.12 | 9.7641 | [5 empty] | 104.856 |  |  | #VALUE!
28.04.2008 22:00 | 3600 | 2 | 764.62 | GGB | 763.004 | 773.789 | 768.864 | 262.96 | GGB | 10701.4 | GGB | 9.77 | GGB | 1011 | GGB | 63.53 | GGB | 167912.64 | GGB | 135946.51 | GGB | 0 | 0 | 2922 | 3600 | 2905.91 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 215111.24 | GGB | 215113.78 | 2905.91 | 2779.9757 |  |  |  | 0 | 1 | [14 empty] | 109.7356 | 2779.9757 |  | 104.98
28.04.2008 23:00 | 3600 | 2 | 763.13 | GGB | 761.538 | 771.516 | 766.3 | 265.39 | GGB | 10766 | GGB | 9.76 | GGB | 1011.08 | GGB | 62.41 | GGB | 171433.72 | GGB | 139269.42 | GGB | 0 | 0 | 3024 | 3600 | 3008.5 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 215149.83 | GGB | 215152.37 | 3008.5 | 2713.6467 |  |  |  | 0 | 1 | [14 empty] | 116.3867 | 2713.6467 |  | 104.98
28.04.2008 24:00 | 3600 | 2 | 763.47 | GGB | 764.102 | 774.727 | 768.864 | 268.89 | GGB | 10862.6 | GGB | 9.78 | GGB | 1011.1 | GGB | 61.54 | GGB | 174583.99 | GGB | 142200.63 | GGB | 0 | 0 | 3071 | 3600 | 3055.46 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 215188.53 | GGB | 215191.07 | 3055.46 | 2657.7097 |  |  |  | 1 | 1 |  |  |  |  | 142200.63 | 2657.7097 | 142200.63 | 2657.7097 | 9.7656 | [5 empty] | 120.6912 | 2657.7097 |  | 104.98
29.04.2008 01:00 | 3600 | 2 | 762.72 | GGB | 761.538 | 772.641 | 766.667 | 268.76 | GGB | 10934.5 | GGB | 9.78 | GGB | 1011.71 | GGB | 61.69 | GGB | 174122.95 | GGB | 141848.94 | GGB | 0 | 0 | 3128 | 3600 | 3111.91 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 215227.23 | GGB | 215229.77 | 3111.91 | 2664.2991 |  |  |  | 0 | 1 | [14 empty] | 122.617 | 2664.2991 |  | 104.98
29.04.2008 02:00 | 3600 | 2 | 762.54 | GGB | 764.102 | 774.797 | 768.864 | 271.06 | GGB | 10953.9 | GGB | 9.78 | GGB | 1012.23 | GGB | 60.75 | GGB | 177271.01 | GGB | 144891.92 | GGB | 0 | 0 | 3149 | 3600 | 3133.26 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 215266.3 | GGB | 215268.84 | 3133.26 | 2608.3442 |  |  |  | 1 | 1 |  |  |  |  | 144891.92 | 2608.3442 | 144891.92 | 2608.3442 | 9.6731 | [5 empty] | 126.1067 | 2608.3442 |  | 104.98
29.04.2008 03:00 | 3600 | 2 | 762.64 | GGB | 764.102 | 773.859 | 768.864 | 271.77 | GGB | 10978.7 | GGB | 9.78 | GGB | 1012.42 | GGB | 60.13 | GGB | 178184.29 | GGB | 145937.1 | GGB | 0 | 0 | 3146 | 3600 | 3130.11 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 215305.4 | GGB | 215307.95 | 3130.11 | 2589.6636 |  |  |  | 1 | 1 |  |  |  |  | 145937.1 | 2589.6636 | 145937.1 | 2589.6636 | 9.6632 | [5 empty] | 126.8887 | 2589.6636 |  | 104.98
29.04.2008 04:00 | 3600 | 2 | 761.65 | GGB | 761.538 | 772.758 | 766.667 | 272.32 | GGB | 11054.6 | GGB | 9.77 | GGB | 1012.52 | GGB | 60.22 | GGB | 178390.06 | GGB | 146082.49 | GGB | 0 | 0 | 3240 | 3600 | 3223.68 | GGB | 100 | GGB | 39.27 | GGB | 39.27 | GGB | 215344.68 | GGB | 215347.22 | 3223.68 | 2587.0862 |  |  |  | 0 | 1 | [14 empty] | 130.812 | 2587.0862 |  | 104.98
29.04.2008 05:00 | 3600 | 2 | 761.28 | GGB | 761.538 | 771.422 | 766.3 | 273.1 | GGB | 11104.9 | GGB | 9.78 | GGB | 1012.18 | GGB | 60.31 | GGB | 178861 | GGB | 146377.15 | GGB | 0 | 0 | 3299 | 3600 | 3283.05 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 215384.14 | GGB | 215386.68 | 3283.05 | 2581.8784 |  |  |  | 0 | 1 | [14 empty] | 133.4899 | 2581.8784 |  | 104.98
29.04.2008 06:00 | 3600 | 2 | 761.15 | GGB | 763.004 | 772.406 | 768.864 | 275.14 | GGB | 11115.7 | GGB | 9.77 | GGB | 1012.29 | GGB | 59.54 | GGB | 181351.07 | GGB | 148775.48 | GGB | 0 | 0 | 3317 | 3600 | 3301.39 | GGB | 100 | GGB | 39.65 | GGB | 39.65 | GGB | 215423.79 | GGB | 215426.33 | 3301.39 | 2540.2573 |  |  |  | 0 | 1 | [14 empty] | 136.435 | 2540.2573 |  | 104.98
29.04.2008 07:00 | 3600 | 2 | 762.68 | GGB | 762.637 | 772.43 | 767.766 | 273.2 | GGB | 11161.3 | GGB | 9.8 | GGB | 1012.13 | GGB | 59.85 | GGB | 179193.3 | GGB | 146845.47 | GGB | 0 | 0 | 3263 | 3600 | 3247.03 | GGB | 100 | GGB | 42.49 | GGB | 42.49 | GGB | 215466.27 | GGB | 215468.82 | 3247.03 | 2573.6443 |  |  |  | 0 | 1 | [14 empty] | 132.4477 | 2573.6443 |  | 104.98
29.04.2008 08:00 | 3600 | 2 | 763.86 | GGB | 765.201 | 775.805 | 769.963 | 271.59 | GGB | 11066.3 | GGB | 9.82 | GGB | 1012.3 | GGB | 59.62 | GGB | 178726.76 | GGB | 146591.72 | GGB | 0 | 0 | 3130 | 3600 | 3114.56 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 215506.11 | GGB | 215508.65 | 3114.56 | 2578.0992 |  |  |  | 1 | 1 |  |  |  |  | 146591.72 | 2578.0992 | 146591.72 | 2578.0992 | 9.4885 | [5 empty] | 126.8246 | 2578.0992 |  | 104.98
29.04.2008 09:00 | 3600 | 2 | 765.28 | GGB | 766.3 | 776.836 | 771.429 | 267.15 | GGB | 10926 | GGB | 9.83 | GGB | 1011.88 | GGB | 60.59 | GGB | 174215.38 | GGB | 142414.13 | GGB | 0 | 0 | 2991 | 3600 | 2975.05 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 215545.29 | GGB | 215547.83 | 2975.05 | 2653.7254 |  |  |  | 1 | 1 |  |  |  |  | 142414.13 | 2653.7254 | 142414.13 | 2653.7254 | 9.6459 | [5 empty] | 117.6914 | 2653.7254 |  | 104.98
29.04.2008 10:00 | 3600 | 2 | 765.81 | GGB | 765.201 | 775.922 | 770.33 | 262.35 | GGB | 10730.6 | GGB | 9.81 | GGB | 1011.17 | GGB | 61.9 | GGB | 169368.39 | GGB | 137813.41 | GGB | 0 | 0 | 2866 | 3600 | 2850.6 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 215584.92 | GGB | 215587.46 | 2850.6 | 2742.3166 |  |  |  | 1 | 1 |  |  |  |  | 137813.41 | 2742.3166 | 137813.41 | 2742.3166 | 9.5364 | [5 empty] | 109.1253 | 2742.3166 |  | 104.98
29.04.2008 11:00 | 3600 | 2 | 766.06 | GGB | 766.3 | 777.023 | 772.161 | 260.05 | GGB | 10634.4 | GGB | 9.8 | GGB | 1009.98 | GGB | 62.88 | GGB | 166540.52 | GGB | 134960.25 | GGB | 0 | 0 | 2826 | 3600 | 2810.18 | GGB | 100 | GGB | 39.38 | GGB | 39.38 | GGB | 215624.3 | GGB | 215626.84 | 2810.18 | 2800.2912 |  |  |  | 1 | 1 |  |  |  |  | 134960.25 | 2800.2912 | 134960.25 | 2800.2912 | 9.597 | [5 empty] | 105.3507 | 2800.2912 |  | 104.98
29.04.2008 12:00 | 3600 | 2 | 765.99 | GGB | 765.201 | 776.016 | 770.696 | 258.29 | GGB | 10580.8 | GGB | 9.79 | GGB | 1008.19 | GGB | 63.65 | GGB | 164760.17 | GGB | 132974.95 | GGB | 0 | 0 | 2813 | 3600 | 2797.67 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 215663.37 | GGB | 215665.91 | 2797.67 | 2797.67 |  |  |  | 1 | 1 |  |  |  |  | 132974.95 | 2797.67 | 132974.95 | 2797.67 | 9.5219 | [5 empty] | 103.3389 |  |  | #VALUE!
29.04.2008 13:00 | 3600 | 2 | 766.59 | GGB | 765.201 | 777 | 772.161 | 258.82 | GGB | 10524.1 | GGB | 9.79 | GGB | 1007.51 | GGB | 63.24 | GGB | 165669.05 | GGB | 133781.03 | GGB | 0 | 0 | 2762 | 3600 | 2746.26 | GGB | 100 | GGB | 38.22 | GGB | 38.22 | GGB | 215701.59 | GGB | 215704.13 | 2746.26 | 2746.26 |  |  |  | 1 | 1 |  |  |  |  | 133781.03 | 2746.26 | 133781.03 | 2746.26 | 9.6127 | [5 empty] | 102.0549 |  |  | #VALUE!
29.04.2008 14:00 | 3600 | 2 | 767.08 | GGB | 766.3 | 776.789 | 772.161 | 257.68 | GGB | 10515.6 | GGB | 9.79 | GGB | 1006.83 | GGB | 63.47 | GGB | 164595.12 | GGB | 132734.46 | GGB | 0 | 0 | 2733 | 3600 | 2717.61 | GGB | 100 | GGB | 36.95 | GGB | 36.95 | GGB | 215738.53 | GGB | 215741.08 | 2717.61 | 2717.61 |  |  |  | 1 | 1 |  |  |  |  | 132734.46 | 2717.61 | 132734.46 | 2717.61 | 9.7624 | [5 empty] | 100.2001 |  |  | #VALUE!
29.04.2008 15:00 | 3600 | 2 | 766.23 | GGB | 765.201 | 776.953 | 770.696 | 256.74 | GGB | 10525.5 | GGB | 9.78 | GGB | 1006.48 | GGB | 64.11 | GGB | 162965.52 | GGB | 131124.78 | GGB | 0 | 0 | 2779 | 3600 | 2763.83 | GGB | 100 | GGB | 39.57 | GGB | 39.57 | GGB | 215778.1 | GGB | 215780.65 | 2763.83 | 2763.83 |  |  |  | 1 | 1 |  |  |  |  | 131124.78 | 2763.83 | 131124.78 | 2763.83 | 9.1586 | [5 empty] | 100.6685 |  |  | #VALUE!
29.04.2008 16:00 | 3600 | 2 | 765.73 | GGB | 765.201 | 775.852 | 770.696 | 258.53 | GGB | 10539.2 | GGB | 9.77 | GGB | 1006.47 | GGB | 63.52 | GGB | 164721.66 | GGB | 132767.82 | GGB | 0 | 0 | 2812 | 3600 | 2796.11 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 215817.87 | GGB | 215820.42 | 2796.11 | 2796.11 |  |  |  | 1 | 1 |  |  |  |  | 132767.82 | 2796.11 | 132767.82 | 2796.11 | 9.3345 | [5 empty] | 103.1204 |  |  | #VALUE!
29.04.2008 17:00 | 3600 | 2 | 765.65 | GGB | 764.102 | 775.852 | 769.597 | 260.49 | GGB | 10565.8 | GGB | 9.78 | GGB | 1006.34 | GGB | 62.58 | GGB | 166758.39 | GGB | 134768.15 | GGB | 0 | 0 | 2821 | 3600 | 2805.88 | GGB | 100 | GGB | 38.68 | GGB | 38.68 | GGB | 215856.56 | GGB | 215859.1 | 2805.88 | 2804.2828 |  |  |  | 1 | 1 |  |  |  |  | 134768.15 | 2804.2828 | 134768.15 | 2804.2828 | 9.7706 | [5 empty] | 105.0398 | 2804.2828 |  | 104.98
29.04.2008 18:00 | 3600 | 2 | 765.47 | GGB | 765.201 | 775.852 | 770.696 | 260.31 | GGB | 10607 | GGB | 9.79 | GGB | 1006.45 | GGB | 62.63 | GGB | 166203.82 | GGB | 134314.59 | GGB | 0 | 0 | 2835 | 3600 | 2819.03 | GGB | 100 | GGB | 37.36 | GGB | 37.36 | GGB | 215893.92 | GGB | 215896.46 | 2819.03 | 2813.7524 |  |  |  | 1 | 1 |  |  |  |  | 134314.59 | 2813.7524 | 134314.59 | 2813.7524 | 10.1158 | [5 empty] | 105.1769 | 2813.7524 |  | 104.98
29.04.2008 19:00 | 3600 | 2 | 765.28 | GGB | 765.201 | 776.063 | 769.597 | 259.34 | GGB | 10619.1 | GGB | 9.79 | GGB | 1006.12 | GGB | 63.29 | GGB | 164746.97 | GGB | 132831.96 | GGB | 0 | 0 | 2864 | 3600 | 2848.63 | GGB | 100 | GGB | 37.63 | GGB | 37.63 | GGB | 215931.55 | GGB | 215934.09 | 2848.63 | 2845.1587 |  |  |  | 1 | 1 |  |  |  |  | 132831.96 | 2845.1587 | 132831.96 | 2845.1587 | 10.0433 | [5 empty] | 105.1081 | 2845.1587 |  | 104.98
29.04.2008 20:00 | 3600 | 2 | 764.76 | GGB | 764.102 | 775.992 | 769.597 | 260.88 | GGB | 10613 | GGB | 9.77 | GGB | 1006.62 | GGB | 62.98 | GGB | 166453.59 | GGB | 134400.94 | GGB | 0 | 0 | 2898 | 3600 | 2881.94 | GGB | 100 | GGB | 39.04 | GGB | 39.04 | GGB | 215970.59 | GGB | 215973.13 | 2881.94 | 2811.9446 |  |  |  | 1 | 1 |  |  |  |  | 134400.94 | 2811.9446 | 134400.94 | 2811.9446 | 9.6805 | [5 empty] | 107.5932 | 2811.9446 |  | 104.98
29.04.2008 21:00 | 3600 | 2 | 764.93 | GGB | 763.004 | 773.602 | 768.498 | 260.94 | GGB | 10655.3 | GGB | 9.78 | GGB | 1007.21 | GGB | 63.42 | GGB | 165885.82 | GGB | 133842.96 | GGB | 0 | 0 | 2911 | 3600 | 2895.67 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 216009.57 | GGB | 216012.12 | 2895.67 | 2823.6674 |  |  |  | 0 | 1 | [14 empty] | 107.657 | 2823.6674 |  | 104.98
29.04.2008 22:00 | 3600 | 2 | 764.51 | GGB | 764.102 | 774.891 | 768.498 | 262.88 | GGB | 10657.7 | GGB | 9.78 | GGB | 1008.06 | GGB | 62.7 | GGB | 168665.27 | GGB | 136492.5 | GGB | 0 | 0 | 2921 | 3600 | 2905.2 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 216048.82 | GGB | 216051.37 | 2905.2 | 2768.8554 |  |  |  | 1 | 1 |  |  |  |  | 136492.5 | 2768.8554 | 136492.5 | 2768.8554 | 9.6287 | [5 empty] | 110.1494 | 2768.8554 |  | 104.98
29.04.2008 23:00 | 3600 | 2 | 764.35 | GGB | 763.004 | 774 | 768.498 | 262.84 | GGB | 10717 | GGB | 9.78 | GGB | 1008.54 | GGB | 62.43 | GGB | 168233.94 | GGB | 136318.97 | GGB | 0 | 0 | 2953 | 3600 | 2937.56 | GGB | 100 | GGB | 37.59 | GGB | 37.59 | GGB | 216086.4 | GGB | 216088.96 | 2937.56 | 2772.3801 |  |  |  | 0 | 1 | [14 empty] | 111.2348 | 2772.3801 |  | 104.98
29.04.2008 24:00 | 3600 | 2 | 764.04 | GGB | 763.004 | 774.211 | 768.498 | 263.25 | GGB | 10752.1 | GGB | 9.78 | GGB | 1008.79 | GGB | 62.76 | GGB | 168330.77 | GGB | 136298.32 | GGB | 0 | 0 | 3000 | 3600 | 2984.5 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 216124.69 | GGB | 216127.25 | 2984.5 | 2772.8001 |  |  |  | 0 | 1 | [14 empty] | 112.9951 | 2772.8001 |  | 104.98
30.04.2008 01:00 | 3600 | 2 | 763.44 | GGB | 764.102 | 774.305 | 768.132 | 264.88 | GGB | 10793 | GGB | 9.77 | GGB | 1008.84 | GGB | 62.63 | GGB | 169531.24 | GGB | 137330.46 | GGB | 0 | 0 | 3064 | 3600 | 3048.56 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 216164.05 | GGB | 216166.61 | 3048.56 | 2751.9605 |  |  |  | 1 | 1 |  |  |  |  | 137330.46 | 2751.9605 | 137330.46 | 2751.9605 | 9.6018 | [5 empty] | 116.2945 | 2751.9605 |  | 104.98
30.04.2008 02:00 | 3600 | 2 | 763.49 | GGB | 764.102 | 774.164 | 768.498 | 265.44 | GGB | 10835.2 | GGB | 9.78 | GGB | 1008.96 | GGB | 62.28 | GGB | 170400.5 | GGB | 138195.8 | GGB | 0 | 0 | 3073 | 3600 | 3057.12 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 216203.43 | GGB | 216206 | 3057.12 | 2734.7286 |  |  |  | 1 | 1 |  |  |  |  | 138195.8 | 2734.7286 | 138195.8 | 2734.7286 | 9.5945 | [5 empty] | 117.3559 | 2734.7286 |  | 104.98
30.04.2008 03:00 | 3600 | 2 | 762.92 | GGB | 764.102 | 774.281 | 769.597 | 266.26 | GGB | 10849.4 | GGB | 9.78 | GGB | 1008.96 | GGB | 62.33 | GGB | 171028.8 | GGB | 138682.5 | GGB | 0 | 0 | 3100 | 3600 | 3084.22 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 216242.91 | GGB | 216245.48 | 3084.22 | 2725.1311 |  |  |  | 1 | 1 |  |  |  |  | 138682.5 | 2725.1311 | 138682.5 | 2725.1311 | 9.5726 | [5 empty] | 118.8132 | 2725.1311 |  | 104.98
30.04.2008 04:00 | 3600 | 2 | 762.78 | GGB | 764.102 | 774.281 | 769.597 | 268.51 | GGB | 10853.6 | GGB | 9.78 | GGB | 1008.9 | GGB | 61.33 | GGB | 173911.68 | GGB | 141434.72 | GGB | 0 | 0 | 3106 | 3600 | 3090.34 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 216282.6 | GGB | 216285.17 | 3090.34 | 2672.102 |  |  |  | 1 | 1 |  |  |  |  | 141434.72 | 2672.102 | 141434.72 | 2672.102 | 9.522 | [5 empty] | 121.4115 | 2672.102 |  | 104.98
30.04.2008 05:00 | 3600 | 2 | 762.79 | GGB | 762.637 | 773.156 | 768.132 | 267.72 | GGB | 10911 | GGB | 9.78 | GGB | 1008.56 | GGB | 61.79 | GGB | 172687.01 | GGB | 140198.71 | GGB | 0 | 0 | 3125 | 3600 | 3109.6 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 216322.19 | GGB | 216324.76 | 3109.6 | 2695.6596 |  |  |  | 0 | 1 | [14 empty] | 121.1005 | 2695.6596 |  | 104.98
30.04.2008 06:00 | 3600 | 2 | 762.78 | GGB | 762.637 | 773.156 | 768.132 | 268.26 | GGB | 10931 | GGB | 9.79 | GGB | 1008.63 | GGB | 61.64 | GGB | 173253.68 | GGB | 140730.7 | GGB | 0 | 0 | 3143 | 3600 | 3127.65 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 216361.82 | GGB | 216364.39 | 3127.65 | 2685.4695 |  |  |  | 0 | 1 | [14 empty] | 122.2657 | 2685.4695 |  | 104.98
30.04.2008 07:00 | 3600 | 2 | 763.29 | GGB | 764.102 | 773.156 | 768.132 | 267.88 | GGB | 10940.1 | GGB | 9.79 | GGB | 1008.54 | GGB | 61.7 | GGB | 173065.52 | GGB | 140542.11 | GGB | 0 | 0 | 3136 | 3600 | 3120.58 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 216401.76 | GGB | 216404.32 | 3120.58 | 2689.073 |  |  |  | 1 | 1 |  |  |  |  | 140542.11 | 2689.073 | 140542.11 | 2689.073 | 9.4648 | [5 empty] | 121.8258 | 2689.073 |  | 104.98
30.04.2008 08:00 | 3600 | 2 | 763.88 | GGB | 763.004 | 773.156 | 768.132 | 265.71 | GGB | 10895.1 | GGB | 9.8 | GGB | 1008.4 | GGB | 62.03 | GGB | 171026.6 | GGB | 138730.01 | GGB | 0 | 0 | 3075 | 3600 | 3059.61 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 216441.82 | GGB | 216444.38 | 3059.61 | 2724.1979 |  |  |  | 0 | 1 | [14 empty] | 117.9055 | 2724.1979 |  | 104.98
30.04.2008 09:00 | 3600 | 2 | 763.63 | GGB | 763.004 | 774.141 | 768.498 | 265.55 | GGB | 10857.2 | GGB | 9.79 | GGB | 1008.3 | GGB | 62.35 | GGB | 170518.24 | GGB | 138172.04 | GGB | 0 | 0 | 3084 | 3600 | 3067.89 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 216482.01 | GGB | 216484.58 | 3067.89 | 2735.1988 |  |  |  | 0 | 1 | [14 empty] | 117.7491 | 2735.1988 |  | 104.98
30.04.2008 10:00 | 3600 | 2 | 763.14 | GGB | 764.102 | 773.016 | 768.132 | 265.65 | GGB | 10844 | GGB | 9.78 | GGB | 1008.43 | GGB | 62.11 | GGB | 170276.17 | GGB | 138093.59 | GGB | 0 | 0 | 3104 | 3600 | 3088.23 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 216521.28 | GGB | 216523.84 | 3088.23 | 2736.7527 |  |  |  | 1 | 1 |  |  |  |  | 138093.59 | 2736.7527 | 138093.59 | 2736.7527 | 9.6263 | [5 empty] | 118.4624 | 2736.7527 |  | 104.98
30.04.2008 11:00 | 3600 | 2 | 762.55 | GGB | 761.538 | 771.727 | 767.033 | 266.35 | GGB | 10834.4 | GGB | 9.78 | GGB | 1008.81 | GGB | 62.24 | GGB | 170978.18 | GGB | 138659.4 | GGB | 0 | 0 | 3113 | 3600 | 3097.52 | GGB | 100 | GGB | 37.89 | GGB | 37.89 | GGB | 216559.17 | GGB | 216561.73 | 3097.52 | 2725.5851 |  |  |  | 0 | 1 | [14 empty] | 119.3056 | 2725.5851 |  | 104.98
30.04.2008 12:00 | 3600 | 2 | 762.72 | GGB | 763.004 | 773.531 | 767.033 | 268.05 | GGB | 10841.9 | GGB | 9.78 | GGB | 1009.59 | GGB | 61.2 | GGB | 173056.72 | GGB | 140890.85 | GGB | 0 | 0 | 3114 | 3600 | 3098.02 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 216597.66 | GGB | 216600.22 | 3098.02 | 2682.4169 |  |  |  | 0 | 1 | [14 empty] | 121.2452 | 2682.4169 |  | 104.98
30.04.2008 13:00 | 3600 | 2 | 763.68 | GGB | 765.201 | 775.852 | 770.696 | 266.24 | GGB | 10887.5 | GGB | 9.81 | GGB | 1009.38 | GGB | 62.18 | GGB | 170599.67 | GGB | 138455.3 | GGB | 0 | 0 | 3102 | 3600 | 3086.67 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 216637.2 | GGB | 216639.76 | 3086.67 | 2729.603 |  |  |  | 1 | 1 |  |  |  |  | 138455.3 | 2729.603 | 138455.3 | 2729.603 | 9.5581 | [5 empty] | 118.7127 | 2729.603 |  | 104.98
30.04.2008 14:00 | 3600 | 2 | 763.96 | GGB | 764.102 | 774.328 | 768.498 | 264.72 | GGB | 10812.3 | GGB | 9.79 | GGB | 1008.84 | GGB | 62.64 | GGB | 169281.46 | GGB | 137125.24 | GGB | 0 | 0 | 3045 | 3600 | 3029.48 | GGB | 100 | GGB | 41.78 | GGB | 41.78 | GGB | 216678.98 | GGB | 216681.54 | 3029.48 | 2756.079 |  |  |  | 1 | 1 |  |  |  |  | 137125.24 | 2756.079 | 137125.24 | 2756.079 | 9.0457 | [5 empty] | 115.3939 | 2756.079 |  | 104.98
30.04.2008 15:00 | 3600 | 2 | 763.58 | GGB | 764.102 | 774.352 | 768.498 | 265.78 | GGB | 10748.5 | GGB | 9.78 | GGB | 1008.66 | GGB | 62.12 | GGB | 170916.56 | GGB | 138637.62 | GGB | 0 | 0 | 3039 | 3600 | 3023.23 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 216717.58 | GGB | 216720.14 | 3023.23 | 2726.0133 |  |  |  | 1 | 1 |  |  |  |  | 138637.62 | 2726.0133 | 138637.62 | 2726.0133 | 9.7909 | [5 empty] | 116.4259 | 2726.0133 |  | 104.98
30.04.2008 16:00 | 3600 | 2 | 764.17 | GGB | 764.102 | 774.539 | 768.498 | 264.64 | GGB | 10772.4 | GGB | 9.8 | GGB | 1008.64 | GGB | 62.66 | GGB | 169106.51 | GGB | 136945.96 | GGB | 0 | 0 | 3015 | 3600 | 2999.15 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 216755.97 | GGB | 216758.53 | 2999.15 | 2759.6871 |  |  |  | 1 | 1 |  |  |  |  | 136945.96 | 2759.6871 | 136945.96 | 2759.6871 | 9.8444 | [5 empty] | 114.0893 | 2759.6871 |  | 104.98
30.04.2008 17:00 | 3600 | 2 | 764.08 | GGB | 764.102 | 774.539 | 768.498 | 263.83 | GGB | 10754.6 | GGB | 9.79 | GGB | 1008.71 | GGB | 63.47 | GGB | 167886.23 | GGB | 135641.26 | GGB | 0 | 0 | 3030 | 3600 | 3014.23 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 216794.35 | GGB | 216796.91 | 3014.23 | 2786.2319 |  |  |  | 1 | 1 |  |  |  |  | 135641.26 | 2786.2319 | 135641.26 | 2786.2319 | 9.847 | [5 empty] | 113.5705 | 2786.2319 |  | 104.98
30.04.2008 18:00 | 3600 | 2 | 764.37 | GGB | 764.102 | 774.422 | 769.597 | 263.5 | GGB | 10736.6 | GGB | 9.79 | GGB | 1008.67 | GGB | 63.7 | GGB | 167454.9 | GGB | 135195.03 | GGB | 0 | 0 | 3005 | 3600 | 2989.82 | GGB | 100 | GGB | 38.38 | GGB | 38.38 | GGB | 216832.73 | GGB | 216835.29 | 2989.82 | 2795.4282 |  |  |  | 1 | 1 |  |  |  |  | 135195.03 | 2795.4282 | 135195.03 | 2795.4282 | 9.847 | [5 empty] | 112.2802 | 2795.4282 |  | 104.98
30.04.2008 19:00 | 3600 | 2 | 764.03 | GGB | 764.102 | 773.555 | 768.498 | 263.52 | GGB | 10722.5 | GGB | 9.78 | GGB | 1009.01 | GGB | 63.74 | GGB | 167141.3 | GGB | 134969.71 | GGB | 0 | 0 | 3009 | 3600 | 2993.8 | GGB | 100 | GGB | 38.37 | GGB | 38.37 | GGB | 216871.1 | GGB | 216873.66 | 2993.8 | 2800.0949 |  |  |  | 1 | 1 |  |  |  |  | 134969.71 | 2800.0949 | 134969.71 | 2800.0949 | 9.8496 | [5 empty] | 112.2423 | 2800.0949 |  | 104.98
30.04.2008 20:00 | 3600 | 2 | 764.28 | GGB | 764.102 | 774.891 | 769.597 | 263.29 | GGB | 10721.5 | GGB | 9.79 | GGB | 1008.95 | GGB | 63.89 | GGB | 166960.85 | GGB | 134755.93 | GGB | 0 | 0 | 2990 | 3600 | 2974.37 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 216909.53 | GGB | 216912.08 | 2974.37 | 2804.5371 |  |  |  | 1 | 1 |  |  |  |  | 134755.93 | 2804.5371 | 134755.93 | 2804.5371 | 9.8368 | [5 empty] | 111.3372 | 2804.5371 |  | 104.98
30.04.2008 21:00 | 3600 | 2 | 764.09 | GGB | 764.102 | 774.867 | 769.597 | 263.74 | GGB | 10727.7 | GGB | 9.78 | GGB | 1009.3 | GGB | 63.76 | GGB | 167334.96 | GGB | 135157.79 | GGB | 0 | 0 | 3016 | 3600 | 3000.3 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 216948.43 | GGB | 216950.98 | 3000.3 | 2796.1984 |  |  |  | 1 | 1 |  |  |  |  | 135157.79 | 2796.1984 | 135157.79 | 2796.1984 | 9.7154 | [5 empty] | 112.6428 | 2796.1984 |  | 104.98
30.04.2008 22:00 | 3600 | 2 | 763.27 | GGB | 764.102 | 774.68 | 769.597 | 265.16 | GGB | 10761.9 | GGB | 9.77 | GGB | 1009.64 | GGB | 63.58 | GGB | 168592.65 | GGB | 136291.37 | GGB | 0 | 0 | 3070 | 3600 | 3053.78 | GGB | 100 | GGB | 38.99 | GGB | 38.99 | GGB | 216987.42 | GGB | 216989.97 | 3053.78 | 2772.9415 |  |  |  | 1 | 1 |  |  |  |  | 136291.37 | 2772.9415 | 136291.37 | 2772.9415 | 9.6929 | [5 empty] | 115.6122 | 2772.9415 |  | 104.98
30.04.2008 23:00 | 3600 | 2 | 763.71 | GGB | 764.102 | 774.82 | 769.597 | 265.74 | GGB | 10818.9 | GGB | 9.79 | GGB | 1009.97 | GGB | 63.32 | GGB | 169339.78 | GGB | 137045.7 | GGB | 0 | 0 | 3073 | 3600 | 3056.84 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 217026.58 | GGB | 217029.14 | 3056.84 | 2757.6786 |  |  |  | 1 | 1 |  |  |  |  | 137045.7 | 2757.6786 | 137045.7 | 2757.6786 | 9.6484 | [5 empty] | 116.3685 | 2757.6786 |  | 104.98
30.04.2008 24:00 | 3600 | 2 | 763.18 | GGB | 761.538 | 772.5 | 767.766 | 265.98 | GGB | 10821.8 | GGB | 9.78 | GGB | 1010.56 | GGB | 63.13 | GGB | 169639.07 | GGB | 137448.59 | GGB | 0 | 0 | 3109 | 3600 | 3092.94 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 217065.88 | GGB | 217068.43 | 3092.94 | 2749.5953 |  |  |  | 0 | 1 | [14 empty] | 118.089 | 2749.5953 |  | 104.98
01.05.2008 01:00 | 3600 | 2 | 762.75 | GGB | 764.102 | 774.68 | 768.864 | 267.34 | GGB | 10875.7 | GGB | 9.78 | GGB | 1010.67 | GGB | 62.71 | GGB | 171054.11 | GGB | 138781.93 | GGB | 0 | 0 | 3159 | 3600 | 3143.51 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 217105.31 | GGB | 217107.86 | 3143.51 | 2723.1787 |  |  |  | 1 | 1 |  |  |  |  | 138781.93 | 2723.1787 | 138781.93 | 2723.1787 | 9.5848 | [5 empty] | 121.184 | 2723.1787 |  | 104.98
01.05.2008 02:00 | 3600 | 2 | 762.55 | GGB | 763.004 | 773.648 | 768.864 | 267.96 | GGB | 10904.4 | GGB | 9.78 | GGB | 1011.25 | GGB | 62.53 | GGB | 171927.77 | GGB | 139645.73 | GGB | 0 | 0 | 3182 | 3600 | 3166.59 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 217144.77 | GGB | 217147.32 | 3166.59 | 2706.3341 |  |  |  | 0 | 1 | [14 empty] | 122.8335 | 2706.3341 |  | 104.98
01.05.2008 03:00 | 3600 | 2 | 761.76 | GGB | 761.538 | 771.609 | 766.667 | 269.16 | GGB | 10929.3 | GGB | 9.77 | GGB | 1011.66 | GGB | 62.38 | GGB | 173104.03 | GGB | 140721.82 | GGB | 0 | 0 | 3221 | 3600 | 3204.99 | GGB | 100 | GGB | 39.61 | GGB | 39.61 | GGB | 217184.37 | GGB | 217186.93 | 3204.99 | 2685.6389 |  |  |  | 0 | 1 | [14 empty] | 125.2811 | 2685.6389 |  | 104.98
01.05.2008 04:00 | 3600 | 2 | 762.86 | GGB | 763.004 | 772.547 | 766.667 | 269.61 | GGB | 10969.7 | GGB | 9.79 | GGB | 1011.7 | GGB | 62.16 | GGB | 173576.08 | GGB | 141203.85 | GGB | 0 | 0 | 3200 | 3600 | 3183.79 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 217223.99 | GGB | 217226.55 | 3183.79 | 2676.4709 |  |  |  | 0 | 1 | [14 empty] | 124.8787 | 2676.4709 |  | 104.98
01.05.2008 05:00 | 3600 | 2 | 762.91 | GGB | 764.102 | 774.398 | 768.498 | 269.29 | GGB | 10977.6 | GGB | 9.79 | GGB | 1011.74 | GGB | 62.14 | GGB | 173324.1 | GGB | 141010.52 | GGB | 0 | 0 | 3187 | 3600 | 3171.49 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 217263.63 | GGB | 217266.19 | 3171.49 | 2680.1405 |  |  |  | 1 | 1 |  |  |  |  | 141010.52 | 2680.1405 | 141010.52 | 2680.1405 | 9.534 | [5 empty] | 124.226 | 2680.1405 |  | 104.98
01.05.2008 06:00 | 3600 | 2 | 761.89 | GGB | 763.004 | 773.344 | 768.132 | 269.37 | GGB | 10970.5 | GGB | 9.78 | GGB | 1011.73 | GGB | 61.92 | GGB | 173777.44 | GGB | 141474.08 | GGB | 0 | 0 | 3224 | 3600 | 3208.52 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 217303.34 | GGB | 217305.9 | 3208.52 | 2671.3586 |  |  |  | 0 | 1 | [14 empty] | 126.0896 | 2671.3586 |  | 104.98
01.05.2008 07:00 | 3600 | 2 | 762.1 | GGB | 763.004 | 773.133 | 767.033 | 269.59 | GGB | 10998.7 | GGB | 9.79 | GGB | 1011.77 | GGB | 61.65 | GGB | 174263.79 | GGB | 141988.76 | GGB | 0 | 0 | 3229 | 3600 | 3213.53 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 217343.08 | GGB | 217345.65 | 3213.53 | 2661.6755 |  |  |  | 0 | 1 | [14 empty] | 126.7459 | 2661.6755 |  | 104.98
01.05.2008 08:00 | 3600 | 2 | 762.85 | GGB | 763.004 | 774.047 | 768.498 | 268.89 | GGB | 10981.4 | GGB | 9.8 | GGB | 1012 | GGB | 61.99 | GGB | 173434.14 | GGB | 141200.62 | GGB | 0 | 0 | 3199 | 3600 | 3182.96 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 217382.84 | GGB | 217385.41 | 3182.96 | 2676.5322 |  |  |  | 0 | 1 | [14 empty] | 124.8433 | 2676.5322 |  | 104.98
01.05.2008 09:00 | 3600 | 2 | 763.29 | GGB | 764.102 | 774.797 | 768.498 | 267.81 | GGB | 10942.6 | GGB | 9.8 | GGB | 1012.27 | GGB | 62.3 | GGB | 172081.82 | GGB | 140007.92 | GGB | 0 | 0 | 3162 | 3600 | 3145.82 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 217423.66 | GGB | 217426.23 | 3145.82 | 2699.333 |  |  |  | 1 | 1 |  |  |  |  | 140007.92 | 2699.333 | 140007.92 | 2699.333 | 9.2584 | [5 empty] | 122.3444 | 2699.333 |  | 104.98
01.05.2008 10:00 | 3600 | 2 | 763.62 | GGB | 764.102 | 774.164 | 769.597 | 266.84 | GGB | 10892.2 | GGB | 9.79 | GGB | 1012.2 | GGB | 62.6 | GGB | 170813.13 | GGB | 138839.6 | GGB | 0 | 0 | 3131 | 3600 | 3115.59 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 217463.29 | GGB | 217465.86 | 3115.59 | 2722.0476 |  |  |  | 1 | 1 |  |  |  |  | 138839.6 | 2722.0476 | 138839.6 | 2722.0476 | 9.5364 | [5 empty] | 120.1576 | 2722.0476 |  | 104.98
01.05.2008 11:00 | 3600 | 2 | 763.46 | GGB | 764.102 | 774.352 | 769.597 | 266.18 | GGB | 10864.9 | GGB | 9.79 | GGB | 1012.19 | GGB | 63 | GGB | 170093.51 | GGB | 138089.03 | GGB | 0 | 0 | 3097 | 3600 | 3080.78 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 217502.96 | GGB | 217505.52 | 3080.78 | 2736.843 |  |  |  | 1 | 1 |  |  |  |  | 138089.03 | 2736.843 | 138089.03 | 2736.843 | 9.5292 | [5 empty] | 118.1728 | 2736.843 |  | 104.98
01.05.2008 12:00 | 3600 | 2 | 763.57 | GGB | 764.102 | 774.352 | 768.498 | 264.82 | GGB | 10803.7 | GGB | 9.79 | GGB | 1011.54 | GGB | 63.49 | GGB | 168745.6 | GGB | 136709.73 | GGB | 0 | 0 | 3040 | 3600 | 3024.11 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 217542.45 | GGB | 217545.01 | 3024.11 | 2764.4558 |  |  |  | 1 | 1 |  |  |  |  | 136709.73 | 2764.4558 | 136709.73 | 2764.4558 | 9.5702 | [5 empty] | 114.8404 | 2764.4558 |  | 104.98
01.05.2008 13:00 | 3600 | 2 | 763.86 | GGB | 765.201 | 774.352 | 769.597 | 264.02 | GGB | 10778.5 | GGB | 9.8 | GGB | 1011.06 | GGB | 63.61 | GGB | 168219.64 | GGB | 136169.63 | GGB | 0 | 0 | 3017 | 3600 | 3001.19 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 217581.91 | GGB | 217584.47 | 3001.19 | 2775.4206 |  |  |  | 1 | 1 |  |  |  |  | 136169.63 | 2775.4206 | 136169.63 | 2775.4206 | 9.5775 | [5 empty] | 113.5197 | 2775.4206 |  | 104.98
01.05.2008 14:00 | 3600 | 2 | 763.91 | GGB | 764.102 | 774.352 | 769.597 | 263.23 | GGB | 10736.6 | GGB | 9.79 | GGB | 1010.76 | GGB | 63.88 | GGB | 167389.98 | GGB | 135351.11 | GGB | 0 | 0 | 2994 | 3600 | 2978.61 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 217621.24 | GGB | 217623.81 | 2978.61 | 2792.2047 |  |  |  | 1 | 1 |  |  |  |  | 135351.11 | 2792.2047 | 135351.11 | 2792.2047 | 9.6067 | [5 empty] | 111.9884 | 2792.2047 |  | 104.98
01.05.2008 15:00 | 3600 | 2 | 764.15 | GGB | 765.201 | 775.289 | 769.597 | 262.69 | GGB | 10723.6 | GGB | 9.79 | GGB | 1010.77 | GGB | 64.11 | GGB | 166704.47 | GGB | 134704.04 | GGB | 0 | 0 | 2977 | 3600 | 2961.54 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 217660.48 | GGB | 217663.05 | 2961.54 | 2805.6174 |  |  |  | 1 | 1 |  |  |  |  | 134704.04 | 2805.6174 | 134704.04 | 2805.6174 | 9.6312 | [5 empty] | 110.8143 | 2805.6174 |  | 104.98
01.05.2008 16:00 | 3600 | 2 | 764.2 | GGB | 765.201 | 775.289 | 769.597 | 262.41 | GGB | 10703.5 | GGB | 9.79 | GGB | 1010.27 | GGB | 64.26 | GGB | 166704.47 | GGB | 134577.67 | GGB | 0 | 0 | 2969 | 3600 | 2953.1 | GGB | 100 | GGB | 39.16 | GGB | 39.16 | GGB | 217699.64 | GGB | 217702.21 | 2953.1 | 2808.2519 |  |  |  | 1 | 1 |  |  |  |  | 134577.67 | 2808.2519 | 134577.67 | 2808.2519 | 9.6509 | [5 empty] | 110.3948 | 2808.2519 |  | 104.98
01.05.2008 17:00 | 3600 | 2 | 764.25 | GGB | 764.102 | 774.117 | 769.597 | 262.06 | GGB | 10670.8 | GGB | 9.78 | GGB | 1009.71 | GGB | 64.48 | GGB | 166158.7 | GGB | 133975.33 | GGB | 0 | 0 | 2959 | 3600 | 2943.15 | GGB | 100 | GGB | 38.73 | GGB | 38.73 | GGB | 217738.37 | GGB | 217740.94 | 2943.15 | 2820.8775 |  |  |  | 1 | 1 |  |  |  |  | 133975.33 | 2820.8775 | 133975.33 | 2820.8775 | 9.758 | [5 empty] | 109.5304 | 2820.8775 |  | 104.98
01.05.2008 18:00 | 3600 | 2 | 764.47 | GGB | 763.004 | 773.133 | 767.033 | 261.76 | GGB | 10662 | GGB | 9.79 | GGB | 1009.45 | GGB | 64.58 | GGB | 165924.33 | GGB | 133711.14 | GGB | 0 | 0 | 2936 | 3600 | 2919.98 | GGB | 100 | GGB | 38.55 | GGB | 38.55 | GGB | 217776.92 | GGB | 217779.49 | 2919.98 | 2826.4511 |  |  |  | 0 | 1 | [14 empty] | 108.4538 | 2826.4511 |  | 104.98
01.05.2008 19:00 | 3600 | 2 | 764.5 | GGB | 764.102 | 775.148 | 768.498 | 261.63 | GGB | 10656.9 | GGB | 9.79 | GGB | 1009.24 | GGB | 64.71 | GGB | 165985.95 | GGB | 133682.08 | GGB | 0 | 0 | 2939 | 3600 | 2923.18 | GGB | 100 | GGB | 38.26 | GGB | 38.26 | GGB | 217815.18 | GGB | 217817.75 | 2923.18 | 2827.0655 |  |  |  | 1 | 1 |  |  |  |  | 133682.08 | 2827.0655 | 133682.08 | 2827.0655 | 9.8779 | [5 empty] | 108.5491 | 2827.0655 |  | 104.98
01.05.2008 20:00 | 3600 | 2 | 763.89 | GGB | 763.004 | 774.234 | 768.498 | 262.44 | GGB | 10686.7 | GGB | 9.78 | GGB | 1009.16 | GGB | 64.33 | GGB | 166719.88 | GGB | 134414.14 | GGB | 0 | 0 | 2986 | 3600 | 2969.9 | GGB | 100 | GGB | 38.35 | GGB | 38.35 | GGB | 217853.52 | GGB | 217856.1 | 2969.9 | 2811.6685 |  |  |  | 0 | 1 | [14 empty] | 110.8879 | 2811.6685 |  | 104.98
01.05.2008 21:00 | 3600 | 2 | 762.16 | GGB | 763.004 | 773.109 | 767.033 | 264.74 | GGB | 10748.5 | GGB | 9.77 | GGB | 1010.08 | GGB | 63.77 | GGB | 168473.81 | GGB | 136179.28 | GGB | 0 | 0 | 3082 | 3600 | 3066.02 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 217892.43 | GGB | 217895.01 | 3066.02 | 2775.224 |  |  |  | 0 | 1 | [14 empty] | 115.9801 | 2775.224 |  | 104.98
01.05.2008 22:00 | 3600 | 2 | 762.11 | GGB | 761.538 | 771.727 | 767.033 | 266.53 | GGB | 10819.5 | GGB | 9.77 | GGB | 1011.29 | GGB | 63.41 | GGB | 170130.92 | GGB | 137829.41 | GGB | 0 | 0 | 3127 | 3600 | 3111.6 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 217931.86 | GGB | 217934.44 | 3111.6 | 2741.9982 |  |  |  | 0 | 1 | [14 empty] | 119.1306 | 2741.9982 |  | 104.98
01.05.2008 23:00 | 3600 | 2 | 761.67 | GGB | 762.637 | 771.703 | 767.033 | 267.58 | GGB | 10894.9 | GGB | 9.78 | GGB | 1011.35 | GGB | 62.58 | GGB | 172153.34 | GGB | 139822.66 | GGB | 0 | 0 | 3172 | 3600 | 3155.83 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 217971.16 | GGB | 217973.73 | 3155.83 | 2702.9095 |  |  |  | 0 | 1 | [14 empty] | 122.5713 | 2702.9095 |  | 104.98
01.05.2008 24:00 | 3600 | 2 | 761.46 | GGB | 762.637 | 772.406 | 767.033 | 268.78 | GGB | 10920.8 | GGB | 9.78 | GGB | 1011.48 | GGB | 62.45 | GGB | 172694.71 | GGB | 140334.33 | GGB | 0 | 0 | 3190 | 3600 | 3174.01 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 218010.37 | GGB | 218012.95 | 3174.01 | 2693.0545 |  |  |  | 0 | 1 | [14 empty] | 123.7285 | 2693.0545 |  | 104.98
02.05.2008 01:00 | 3600 | 2 | 761.7 | GGB | 762.637 | 773.273 | 768.132 | 269.39 | GGB | 10956.7 | GGB | 9.79 | GGB | 1011.4 | GGB | 62.28 | GGB | 173458.34 | GGB | 141014.12 | GGB | 0 | 0 | 3198 | 3600 | 3181.99 | GGB | 100 | GGB | 39.41 | GGB | 39.41 | GGB | 218049.78 | GGB | 218052.36 | 3181.99 | 2680.072 |  |  |  | 0 | 1 | [14 empty] | 124.6404 | 2680.072 |  | 104.98
02.05.2008 02:00 | 3600 | 2 | 762.15 | GGB | 762.637 | 772.195 | 767.033 | 268.54 | GGB | 10939.9 | GGB | 9.79 | GGB | 1011.27 | GGB | 62.34 | GGB | 172802.54 | GGB | 140436.48 | GGB | 0 | 0 | 3182 | 3600 | 3166.48 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 218089.24 | GGB | 218091.82 | 3166.48 | 2691.0956 |  |  |  | 0 | 1 | [14 empty] | 123.5248 | 2691.0956 |  | 104.98
02.05.2008 03:00 | 3600 | 2 | 761.77 | GGB | 762.637 | 772.031 | 767.033 | 268.38 | GGB | 10938.6 | GGB | 9.79 | GGB | 1011.09 | GGB | 62.36 | GGB | 172816.85 | GGB | 140415.12 | GGB | 0 | 0 | 3189 | 3600 | 3173.56 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 218128.73 | GGB | 218131.31 | 3173.56 | 2691.505 |  |  |  | 0 | 1 | [14 empty] | 123.7822 | 2691.505 |  | 104.98
02.05.2008 04:00 | 3600 | 2 | 761.88 | GGB | 763.004 | 773.32 | 768.132 | 268.22 | GGB | 10934.2 | GGB | 9.79 | GGB | 1011.08 | GGB | 62.41 | GGB | 172585.78 | GGB | 140207.94 | GGB | 0 | 0 | 3184 | 3600 | 3168.67 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 218168.26 | GGB | 218170.84 | 3168.67 | 2695.4822 |  |  |  | 0 | 1 | [14 empty] | 123.4091 | 2695.4822 |  | 104.98
02.05.2008 05:00 | 3600 | 2 | 762.13 | GGB | 761.538 | 772.313 | 767.033 | 267.26 | GGB | 10932 | GGB | 9.79 | GGB | 1010.65 | GGB | 61.39 | GGB | 171872.76 | GGB | 139995.01 | GGB | 0 | 0 | 3171 | 3600 | 3154.78 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 218208.16 | GGB | 218210.74 | 3154.78 | 2699.5819 |  |  |  | 0 | 1 | [14 empty] | 122.6815 | 2699.5819 |  | 104.98
02.05.2008 06:00 | 3600 | 2 | 761.42 | GGB | 762.637 | 772.266 | 768.132 | 267.84 | GGB | 10914.5 | GGB | 9.78 | GGB | 1011.07 | GGB | 61.84 | GGB | 172070.82 | GGB | 140025.87 | GGB | 0 | 0 | 3214 | 3600 | 3197.85 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 218248.26 | GGB | 218250.84 | 3197.85 | 2698.987 |  |  |  | 0 | 1 | [14 empty] | 124.3838 | 2698.987 |  | 104.98
02.05.2008 07:00 | 3600 | 2 | 761.72 | GGB | 762.637 | 773.344 | 767.033 | 268.33 | GGB | 10924.8 | GGB | 9.78 | GGB | 1011.23 | GGB | 62.32 | GGB | 172191.85 | GGB | 139943.14 | GGB | 0 | 0 | 3203 | 3600 | 3187.14 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 218288.27 | GGB | 218290.85 | 3187.14 | 2700.5825 |  |  |  | 0 | 1 | [14 empty] | 123.894 | 2700.5825 |  | 104.98
02.05.2008 08:00 | 3600 | 2 | 762.23 | GGB | 765.201 | 774.914 | 769.597 | 269.17 | GGB | 10914.6 | GGB | 9.79 | GGB | 1011.82 | GGB | 62.12 | GGB | 173493.55 | GGB | 141171.07 | GGB | 0 | 0 | 3181 | 3600 | 3165.32 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 218327.77 | GGB | 218330.35 | 3165.32 | 2677.0924 |  |  |  | 1 | 1 |  |  |  |  | 141171.07 | 2677.0924 | 141171.07 | 2677.0924 | 9.5678 | [5 empty] | 124.1254 | 2677.0924 |  | 104.98
02.05.2008 09:00 | 3600 | 2 | 761.68 | GGB | 762.637 | 772.898 | 768.132 | 268.97 | GGB | 10924.8 | GGB | 9.78 | GGB | 1012.58 | GGB | 62.24 | GGB | 172626.49 | GGB | 140520.62 | GGB | 0 | 0 | 3226 | 3208 | 3210.54 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 218367.08 | GGB | 218369.66 | 3210.54 | 2689.4843 |  |  |  | 0 | 1 | [14 empty] | 125.3186 | 2689.4843 |  | 104.98
02.05.2008 10:00 | 3600 | 2 | 762.36 | GGB | 763.004 | 773.766 | 768.132 | 267.95 | GGB | 10926.3 | GGB | 9.79 | GGB | 1013.27 | GGB | 62.4 | GGB | 171479.94 | GGB | 139615.19 | GGB | 0 | 0 | 3186 | 3600 | 3169.88 | GGB | 100 | GGB | 39.19 | GGB | 39.19 | GGB | 218406.27 | GGB | 218408.85 | 3169.88 | 2706.9261 |  |  |  | 0 | 1 | [14 empty] | 122.9343 | 2706.9261 |  | 104.98
02.05.2008 11:00 | 3600 | 2 | 761.96 | GGB | 764.102 | 773.625 | 768.132 | 267.79 | GGB | 10913.3 | GGB | 9.79 | GGB | 1013.72 | GGB | 62.14 | GGB | 171134.43 | GGB | 139501.53 | GGB | 0 | 0 | 3208 | 3600 | 3192.26 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 218445.83 | GGB | 218448.41 | 3192.26 | 2709.1316 |  |  |  | 1 | 1 |  |  |  |  | 139501.53 | 2709.1316 | 139501.53 | 2709.1316 | 9.5533 | [5 empty] | 123.7014 | 2709.1316 |  | 104.98
02.05.2008 12:00 | 3600 | 2 | 762.78 | GGB | 764.102 | 773.555 | 768.132 | 266.92 | GGB | 10884.5 | GGB | 9.8 | GGB | 1013.11 | GGB | 63.39 | GGB | 170216.75 | GGB | 138154.44 | GGB | 0 | 0 | 3158 | 3600 | 3141.77 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 218485.27 | GGB | 218487.85 | 3141.77 | 2735.5473 |  |  |  | 1 | 1 |  |  |  |  | 138154.44 | 2735.5473 | 138154.44 | 2735.5473 | 9.5824 | [5 empty] | 120.5693 | 2735.5473 |  | 104.98
02.05.2008 13:00 | 3600 | 2 | 762.65 | GGB | 764.102 | 774.703 | 769.597 | 265.74 | GGB | 10833 | GGB | 9.79 | GGB | 1012.71 | GGB | 63.86 | GGB | 169154.92 | GGB | 137049.63 | GGB | 0 | 0 | 3149 | 3600 | 3132.91 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 218524.04 | GGB | 218526.63 | 3132.91 | 2757.5996 |  |  |  | 1 | 1 |  |  |  |  | 137049.63 | 2757.5996 | 137049.63 | 2757.5996 | 9.7454 | [5 empty] | 119.2678 | 2757.5996 |  | 104.98
02.05.2008 14:00 | 3600 | 2 | 763.47 | GGB | 764.102 | 774.516 | 769.597 | 264.84 | GGB | 10773.2 | GGB | 9.79 | GGB | 1011.76 | GGB | 64.28 | GGB | 168002.87 | GGB | 135818.36 | GGB | 0 | 0 | 3076 | 3600 | 3059.89 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 218562.9 | GGB | 218565.49 | 3059.89 | 2782.5988 |  |  |  | 1 | 1 |  |  |  |  | 135818.36 | 2782.5988 | 135818.36 | 2782.5988 | 9.7254 | [5 empty] | 115.4415 | 2782.5988 |  | 104.98
02.05.2008 15:00 | 3600 | 2 | 764.71 | GGB | 764.102 | 774.539 | 769.597 | 263.65 | GGB | 10696.2 | GGB | 9.8 | GGB | 1011.09 | GGB | 64.54 | GGB | 167432.89 | GGB | 135163.14 | GGB | 0 | 0 | 2984 | 3600 | 2967.97 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 218601.65 | GGB | 218604.24 | 2967.97 | 2796.0877 |  |  |  | 1 | 1 |  |  |  |  | 135163.14 | 2796.0877 | 135163.14 | 2796.0877 | 9.753 | [5 empty] | 111.4334 | 2796.0877 |  | 104.98
02.05.2008 16:00 | 3600 | 2 | 762.42 | GGB | 760.44 | 771.563 | 765.934 | 263.08 | GGB | 10689.1 | GGB | 9.76 | GGB | 1010.43 | GGB | 63.89 | GGB | 167043.37 | GGB | 135019.02 | GGB | 0 | 0 | 3093 | 3600 | 3077.6 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 218640.45 | GGB | 218643.04 | 3077.6 | 2799.0723 |  |  |  | 0 | 1 | [14 empty] | 115.4263 | 2799.0723 |  | 104.98
02.05.2008 17:00 | 3600 | 2 | 762.38 | GGB | 764.102 | 773.461 | 768.498 | 266.85 | GGB | 10828.7 | GGB | 9.78 | GGB | 1012.3 | GGB | 63.36 | GGB | 169985.68 | GGB | 137868.62 | GGB | 0 | 0 | 3178 | 3600 | 3162.2 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 218679.75 | GGB | 218682.34 | 3162.2 | 2741.2184 |  |  |  | 1 | 1 |  |  |  |  | 137868.62 | 2741.2184 | 137868.62 | 2741.2184 | 9.6165 | [5 empty] | 121.1023 | 2741.2184 |  | 104.98
02.05.2008 18:00 | 3600 | 2 | 763.19 | GGB | 764.102 | 774.352 | 769.597 | 266.83 | GGB | 10850.6 | GGB | 9.79 | GGB | 1012.71 | GGB | 63.59 | GGB | 169529.04 | GGB | 137464.2 | GGB | 0 | 0 | 3136 | 3600 | 3120.07 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 218719.05 | GGB | 218721.64 | 3120.07 | 2749.2831 |  |  |  | 1 | 1 |  |  |  |  | 137464.2 | 2749.2831 | 137464.2 | 2749.2831 | 9.6165 | [5 empty] | 119.1383 | 2749.2831 |  | 104.98
02.05.2008 19:00 | 3600 | 2 | 763.22 | GGB | 764.102 | 773.227 | 768.132 | 265.76 | GGB | 10822.3 | GGB | 9.79 | GGB | 1012.8 | GGB | 63.98 | GGB | 168594.85 | GGB | 136557.44 | GGB | 0 | 0 | 3120 | 3600 | 3103.93 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 218758.26 | GGB | 218760.84 | 3103.93 | 2767.5387 |  |  |  | 1 | 1 |  |  |  |  | 136557.44 | 2767.5387 | 136557.44 | 2767.5387 | 9.641 | [5 empty] | 117.7402 | 2767.5387 |  | 104.98
02.05.2008 20:00 | 3600 | 2 | 763.26 | GGB | 764.102 | 773.063 | 768.132 | 265.42 | GGB | 10804.7 | GGB | 9.79 | GGB | 1012.92 | GGB | 64.19 | GGB | 168229.54 | GGB | 136195.16 | GGB | 0 | 0 | 3117 | 3600 | 3101.71 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 218797.9 | GGB | 218800.48 | 3101.71 | 2774.9004 |  |  |  | 1 | 1 |  |  |  |  | 136195.16 | 2774.9004 | 136195.16 | 2774.9004 | 9.534 | [5 empty] | 117.3439 | 2774.9004 |  | 104.98
02.05.2008 21:00 | 3600 | 2 | 763.28 | GGB | 763.004 | 773.18 | 768.498 | 265.43 | GGB | 10794.2 | GGB | 9.79 | GGB | 1013.27 | GGB | 64.42 | GGB | 168035.88 | GGB | 135989.15 | GGB | 0 | 0 | 3121 | 3600 | 3104.92 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 218837.62 | GGB | 218840.2 | 3104.92 | 2779.1041 |  |  |  | 0 | 1 | [14 empty] | 117.2876 | 2779.1041 |  | 104.98
02.05.2008 22:00 | 3600 | 2 | 762.59 | GGB | 764.102 | 774.188 | 768.498 | 266.3 | GGB | 10808.9 | GGB | 9.78 | GGB | 1013.72 | GGB | 64.12 | GGB | 168719.19 | GGB | 136725.63 | GGB | 0 | 0 | 3153 | 3600 | 3136.95 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 218875.68 | GGB | 218878.26 | 3136.95 | 2764.1343 |  |  |  | 1 | 1 |  |  |  |  | 136725.63 | 2764.1343 | 136725.63 | 2764.1343 | 9.9298 | [5 empty] | 119.1393 | 2764.1343 |  | 104.98
02.05.2008 23:00 | 3600 | 2 | 761.94 | GGB | 762.637 | 772.781 | 767.033 | 267.12 | GGB | 10844.9 | GGB | 9.77 | GGB | 1013.9 | GGB | 63.63 | GGB | 170633.78 | GGB | 138501.93 | GGB | 0 | 0 | 3195 | 3600 | 3179.44 | GGB | 100 | GGB | 37.65 | GGB | 37.65 | GGB | 218913.33 | GGB | 218915.91 | 3179.44 | 2728.684 |  |  |  | 0 | 1 | [14 empty] | 122.3218 | 2728.684 |  | 104.98
02.05.2008 24:00 | 3600 | 2 | 762.9 | GGB | 763.004 | 773.672 | 768.132 | 267.88 | GGB | 10878.5 | GGB | 9.79 | GGB | 1014.21 | GGB | 63.52 | GGB | 170706.4 | GGB | 138648.47 | GGB | 0 | 0 | 3174 | 3600 | 3158.26 | GGB | 100 | GGB | 38.4 | GGB | 38.4 | GGB | 218951.73 | GGB | 218954.31 | 3158.26 | 2725.8 |  |  |  | 0 | 1 | [14 empty] | 121.6355 | 2725.8 |  | 104.98
03.05.2008 01:00 | 3600 | 2 | 761.92 | GGB | 762.637 | 772.594 | 767.033 | 268.32 | GGB | 10875.7 | GGB | 9.78 | GGB | 1014.47 | GGB | 63.63 | GGB | 171145.43 | GGB | 138996.07 | GGB | 0 | 0 | 3221 | 3600 | 3204.72 | GGB | 100 | GGB | 40.89 | GGB | 40.89 | GGB | 218992.61 | GGB | 218995.2 | 3204.72 | 2718.9833 |  |  |  | 0 | 1 | [14 empty] | 123.7343 | 2718.9833 |  | 104.98
03.05.2008 02:00 | 3600 | 2 | 761.78 | GGB | 761.538 | 771.516 | 765.934 | 269.54 | GGB | 10909.1 | GGB | 9.78 | GGB | 1015.07 | GGB | 63.24 | GGB | 172196.26 | GGB | 140094.59 | GGB | 0 | 0 | 3236 | 3600 | 3220.38 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 219032.74 | GGB | 219035.33 | 3220.38 | 2697.6631 |  |  |  | 0 | 1 | [14 empty] | 125.3216 | 2697.6631 |  | 104.98
03.05.2008 03:00 | 3600 | 2 | 761.34 | GGB | 761.538 | 772.57 | 767.033 | 270.81 | GGB | 10951.1 | GGB | 9.77 | GGB | 1015.25 | GGB | 63.12 | GGB | 173934.79 | GGB | 141586.53 | GGB | 0 | 0 | 3293 | 3600 | 3276.83 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 219072.22 | GGB | 219074.81 | 3276.83 | 2669.237 |  |  |  | 0 | 1 | [14 empty] | 128.8764 | 2669.237 |  | 104.98
03.05.2008 04:00 | 3600 | 2 | 761.53 | GGB | 761.538 | 771.516 | 765.934 | 271.35 | GGB | 10993.7 | GGB | 9.78 | GGB | 1015.42 | GGB | 62.48 | GGB | 174829.36 | GGB | 142607.54 | GGB | 0 | 0 | 3283 | 3600 | 3266.91 | GGB | 100 | GGB | 38.78 | GGB | 38.78 | GGB | 219111 | GGB | 219113.59 | 3266.91 | 2650.1264 |  |  |  | 0 | 1 | [14 empty] | 129.4128 | 2650.1264 |  | 104.98
03.05.2008 05:00 | 3600 | 2 | 761.46 | GGB | 761.538 | 772.523 | 767.033 | 272.16 | GGB | 11038.9 | GGB | 9.78 | GGB | 1015.85 | GGB | 62.2 | GGB | 176059.54 | GGB | 143793.61 | GGB | 0 | 0 | 3303 | 3600 | 3286.65 | GGB | 100 | GGB | 38.29 | GGB | 38.29 | GGB | 219149.29 | GGB | 219151.88 | 3286.65 | 2628.267 |  |  |  | 0 | 1 | [14 empty] | 131.2776 | 2628.267 |  | 104.98
03.05.2008 06:00 | 3600 | 2 | 761.3 | GGB | 762.637 | 772.664 | 768.132 | 272.09 | GGB | 11053.8 | GGB | 9.78 | GGB | 1016.11 | GGB | 61.79 | GGB | 176279.61 | GGB | 144186.3 | GGB | 0 | 0 | 3310 | 3600 | 3293.68 | GGB | 100 | GGB | 39.98 | GGB | 39.98 | GGB | 219189.27 | GGB | 219191.86 | 3293.68 | 2621.1089 |  |  |  | 0 | 1 | [14 empty] | 131.9176 | 2621.1089 |  | 104.98
03.05.2008 07:00 | 3600 | 2 | 761.87 | GGB | 762.637 | 772.711 | 768.132 | 271.64 | GGB | 11062.9 | GGB | 9.8 | GGB | 1016.39 | GGB | 61.98 | GGB | 176120.06 | GGB | 144014.75 | GGB | 0 | 0 | 3288 | 3600 | 3272.18 | GGB | 100 | GGB | 41.15 | GGB | 41.15 | GGB | 219230.43 | GGB | 219233.01 | 3272.18 | 2624.2312 |  |  |  | 0 | 1 | [14 empty] | 130.9006 | 2624.2312 |  | 104.98
03.05.2008 08:00 | 3600 | 2 | 762.37 | GGB | 763.004 | 772.688 | 768.132 | 270.46 | GGB | 11039.6 | GGB | 9.8 | GGB | 1017.07 | GGB | 62.28 | GGB | 174795.25 | GGB | 142898.81 | GGB | 0 | 0 | 3257 | 3600 | 3241.31 | GGB | 100 | GGB | 41.07 | GGB | 41.07 | GGB | 219271.49 | GGB | 219274.08 | 3241.31 | 2644.7246 |  |  |  | 0 | 1 | [14 empty] | 128.6609 | 2644.7246 |  | 104.98
03.05.2008 09:00 | 3600 | 2 | 763.16 | GGB | 764.102 | 773.836 | 768.132 | 268.84 | GGB | 10991.3 | GGB | 9.8 | GGB | 1017.21 | GGB | 62.65 | GGB | 173056.72 | GGB | 141341.07 | GGB | 0 | 0 | 3198 | 3600 | 3182.31 | GGB | 100 | GGB | 40.57 | GGB | 40.57 | GGB | 219312.07 | GGB | 219314.65 | 3182.31 | 2673.8725 |  |  |  | 1 | 1 |  |  |  |  | 141341.07 | 2673.8725 | 141341.07 | 2673.8725 | 9.3155 | [5 empty] | 124.942 | 2673.8725 |  | 104.98
03.05.2008 10:00 | 3600 | 2 | 763.95 | GGB | 764.102 | 774.867 | 769.597 | 266.45 | GGB | 10900.8 | GGB | 9.81 | GGB | 1017.7 | GGB | 63.53 | GGB | 169949.37 | GGB | 138503.76 | GGB | 0 | 0 | 3123 | 3600 | 3107.6 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 219351.85 | GGB | 219354.43 | 3107.6 | 2728.6479 |  |  |  | 1 | 1 |  |  |  |  | 138503.76 | 2728.6479 | 138503.76 | 2728.6479 | 9.5005 | [5 empty] | 119.5595 | 2728.6479 |  | 104.98
03.05.2008 11:00 | 3600 | 2 | 764.45 | GGB | 766.3 | 777 | 770.696 | 264.79 | GGB | 10770.9 | GGB | 9.8 | GGB | 1016.74 | GGB | 64.36 | GGB | 168225.14 | GGB | 136634.75 | GGB | 0 | 0 | 3040 | 3600 | 3024.45 | GGB | 100 | GGB | 39.62 | GGB | 39.62 | GGB | 219391.47 | GGB | 219394.05 | 3024.45 | 2765.9728 |  |  |  | 1 | 1 |  |  |  |  | 136634.75 | 2765.9728 | 136634.75 | 2765.9728 | 9.5388 | [5 empty] | 114.7903 | 2765.9728 |  | 104.98
03.05.2008 12:00 | 3600 | 2 | 764.5 | GGB | 764.102 | 775.758 | 769.597 | 262.61 | GGB | 10699.8 | GGB | 9.79 | GGB | 1016.21 | GGB | 65.09 | GGB | 166021.16 | GGB | 134485.26 | GGB | 0 | 0 | 2987 | 3600 | 2971.71 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 219430.94 | GGB | 219433.52 | 2971.71 | 2810.1816 |  |  |  | 1 | 1 |  |  |  |  | 134485.26 | 2810.1816 | 134485.26 | 2810.1816 | 9.5751 | [5 empty] | 111.0142 | 2810.1816 |  | 104.98
03.05.2008 13:00 | 3600 | 2 | 764.42 | GGB | 764.102 | 775.828 | 769.597 | 263.66 | GGB | 10641.6 | GGB | 9.78 | GGB | 1016.25 | GGB | 64.67 | GGB | 167542.93 | GGB | 135890.01 | GGB | 0 | 0 | 2974 | 3600 | 2958.77 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 219470.53 | GGB | 219473.11 | 2958.77 | 2781.1316 |  |  |  | 1 | 1 |  |  |  |  | 135890.01 | 2781.1316 | 135890.01 | 2781.1316 | 9.546 | [5 empty] | 111.6854 | 2781.1316 |  | 104.98
03.05.2008 14:00 | 3600 | 2 | 764.95 | GGB | 765.201 | 775.57 | 770.696 | 261.9 | GGB | 10664.7 | GGB | 9.79 | GGB | 1015.62 | GGB | 65.29 | GGB | 165141.99 | GGB | 133614.8 | GGB | 0 | 0 | 2943 | 3600 | 2927.84 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 219510.58 | GGB | 219513.16 | 2927.84 | 2828.4891 |  |  |  | 1 | 1 |  |  |  |  | 133614.8 | 2828.4891 | 133614.8 | 2828.4891 | 9.4364 | [5 empty] | 108.6674 | 2828.4891 |  | 104.98
03.05.2008 15:00 | 3600 | 2 | 765.18 | GGB | 765.201 | 775.57 | 770.696 | 261.27 | GGB | 10640.3 | GGB | 9.79 | GGB | 1015.05 | GGB | 65.56 | GGB | 165155.19 | GGB | 133445.6 | GGB | 0 | 0 | 2938 | 3600 | 2922.86 | GGB | 100 | GGB | 37.77 | GGB | 37.77 | GGB | 219548.35 | GGB | 219550.93 | 2922.86 | 2832.0754 |  |  |  | 1 | 1 |  |  |  |  | 133445.6 | 2832.0754 | 133445.6 | 2832.0754 | 10.006 | [5 empty] | 108.3452 | 2832.0754 |  | 104.98
03.05.2008 16:00 | 3600 | 2 | 762.73 | GGB | 764.102 | 774.586 | 769.597 | 264.28 | GGB | 10741.9 | GGB | 9.76 | GGB | 1016.09 | GGB | 63.34 | GGB | 168160.22 | GGB | 136906.82 | GGB | 0 | 0 | 3097 | 3600 | 3081.26 | GGB | 100 | GGB | 36.95 | GGB | 36.95 | GGB | 219585.3 | GGB | 219587.88 | 3081.26 | 2760.4761 |  |  |  | 1 | 1 |  |  |  |  | 136906.82 | 2760.4761 | 136906.82 | 2760.4761 | 10.2281 | [5 empty] | 117.1793 | 2760.4761 |  | 104.98
03.05.2008 17:00 | 3600 | 2 | 762.32 | GGB | 759.341 | 769.031 | 763.37 | 266.48 | GGB | 10800.8 | GGB | 9.76 | GGB | 1017.48 | GGB | 62.48 | GGB | 170160.63 | GGB | 139082.67 | GGB | 0 | 0 | 3145 | 3600 | 3129.02 | GGB | 100 | GGB | 36.86 | GGB | 36.86 | GGB | 219622.16 | GGB | 219624.74 | 3129.02 | 2717.2904 |  |  |  | 0 | 1 | [14 empty] | 120.8868 | 2717.2904 |  | 104.98
03.05.2008 18:00 | 3600 | 2 | 764.24 | GGB | 766.3 | 777.797 | 771.795 | 267.66 | GGB | 10857.6 | GGB | 9.81 | GGB | 1017.8 | GGB | 62.88 | GGB | 170975.98 | GGB | 139624.91 | GGB | 0 | 0 | 3083 | 3600 | 3066.79 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 219660.76 | GGB | 219663.34 | 3066.79 | 2706.7376 |  |  |  | 1 | 1 |  |  |  |  | 139624.91 | 2706.7376 | 139624.91 | 2706.7376 | 9.7909 | [5 empty] | 118.9445 | 2706.7376 |  | 104.98
03.05.2008 19:00 | 3600 | 2 | 763.25 | GGB | 763.004 | 773.531 | 768.132 | 265.73 | GGB | 10827.5 | GGB | 9.78 | GGB | 1017.3 | GGB | 63.78 | GGB | 168967.87 | GGB | 137550.31 | GGB | 0 | 0 | 3110 | 3600 | 3094.64 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 219700.82 | GGB | 219703.39 | 3094.64 | 2747.562 |  |  |  | 0 | 1 | [14 empty] | 118.2413 | 2747.562 |  | 104.98
03.05.2008 20:00 | 3600 | 2 | 762.91 | GGB | 763.004 | 774.633 | 768.132 | 266.59 | GGB | 10831.5 | GGB | 9.78 | GGB | 1017.71 | GGB | 63.73 | GGB | 169179.13 | GGB | 137798.81 | GGB | 0 | 0 | 3137 | 3600 | 3121.48 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 219740.18 | GGB | 219742.75 | 3121.48 | 2742.6071 |  |  |  | 0 | 1 | [14 empty] | 119.4823 | 2742.6071 |  | 104.98
03.05.2008 21:00 | 3600 | 2 | 762.34 | GGB | 762.637 | 772.406 | 767.033 | 268.32 | GGB | 10808.7 | GGB | 9.77 | GGB | 1018.46 | GGB | 63.54 | GGB | 171038.7 | GGB | 139495.77 | GGB | 0 | 0 | 3161 | 3600 | 3145.37 | GGB | 100 | GGB | 41.06 | GGB | 41.06 | GGB | 219781.23 | GGB | 219783.81 | 3145.37 | 2709.2434 |  |  |  | 0 | 1 | [14 empty] | 121.8794 | 2709.2434 |  | 104.98
03.05.2008 22:00 | 3600 | 2 | 763.78 | GGB | 763.004 | 773.484 | 767.033 | 268.62 | GGB | 10879.8 | GGB | 9.8 | GGB | 1019.4 | GGB | 63.39 | GGB | 171260.97 | GGB | 139864.94 | GGB | 0 | 0 | 3133 | 3600 | 3117.39 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 219819.51 | GGB | 219822.09 | 3117.39 | 2702.0925 |  |  |  | 0 | 1 | [14 empty] | 121.1149 | 2702.0925 |  | 104.98
03.05.2008 23:00 | 3600 | 2 | 762.52 | GGB | 763.004 | 773.508 | 767.033 | 268.71 | GGB | 10905.4 | GGB | 9.78 | GGB | 1019.86 | GGB | 63.53 | GGB | 171134.43 | GGB | 139769.61 | GGB | 0 | 0 | 3202 | 3600 | 3186.09 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 219859.93 | GGB | 219862.51 | 3186.09 | 2703.9354 |  |  |  | 0 | 1 | [14 empty] | 123.6996 | 2703.9354 |  | 104.98
03.05.2008 24:00 | 3600 | 2 | 762.58 | GGB | 763.004 | 773.273 | 767.766 | 269.35 | GGB | 10926.7 | GGB | 9.78 | GGB | 1019.52 | GGB | 63.4 | GGB | 171861.75 | GGB | 140371.16 | GGB | 0 | 0 | 3217 | 3600 | 3201.47 | GGB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 219900.55 | GGB | 219903.13 | 3201.47 | 2692.3479 |  |  |  | 0 | 1 | [14 empty] | 124.8317 | 2692.3479 |  | 104.98
04.05.2008 01:00 | 3600 | 2 | 762.26 | GGB | 764.102 | 773.203 | 767.766 | 269.73 | GGB | 10940.5 | GGB | 9.78 | GGB | 1019.69 | GGB | 63.23 | GGB | 172362.41 | GGB | 140872.93 | GGB | 0 | 0 | 3234 | 3600 | 3218.08 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 219940.09 | GGB | 219942.67 | 3218.08 | 2682.7581 |  |  |  | 1 | 1 |  |  |  |  | 140872.93 | 2682.7581 | 140872.93 | 2682.7581 | 9.5581 | [5 empty] | 125.9279 | 2682.7581 |  | 104.98
04.05.2008 02:00 | 3600 | 2 | 761.69 | GGB | 763.004 | 773.227 | 767.766 | 270.89 | GGB | 10972.1 | GGB | 9.78 | GGB | 1019.7 | GGB | 62.87 | GGB | 173716.92 | GGB | 142131.63 | GGB | 0 | 0 | 3265 | 3600 | 3249.01 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 219979.51 | GGB | 219982.1 | 3249.01 | 2659 |  |  |  | 0 | 1 | [14 empty] | 128.2742 | 2659 |  | 104.98
04.05.2008 03:00 | 3600 | 2 | 761.61 | GGB | 762.637 | 772.945 | 767.033 | 271.97 | GGB | 11017 | GGB | 9.77 | GGB | 1019.93 | GGB | 62.48 | GGB | 175112.15 | GGB | 143473.47 | GGB | 0 | 0 | 3295 | 3600 | 3279.1 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 220019.06 | GGB | 220021.64 | 3279.1 | 2634.1316 |  |  |  | 0 | 1 | [14 empty] | 130.6844 | 2634.1316 |  | 104.98
04.05.2008 04:00 | 3600 | 2 | 761.37 | GGB | 762.637 | 772.922 | 767.033 | 273.32 | GGB | 11066.8 | GGB | 9.78 | GGB | 1020.18 | GGB | 62.07 | GGB | 176666.93 | GGB | 144963.24 | GGB | 0 | 0 | 3323 | 3600 | 3307.31 | GNB | 100 | GGB | 39.73 | GGB | 39.73 | GGB | 220058.79 | GGB | 220061.37 | 3307.31 | 2607.0609 |  |  |  | 0 | 1 | [14 empty] | 133.1773 | 2607.0609 |  | 104.98
04.05.2008 05:00 | 3600 | 2 | 761.67 | GGB | 761.538 | 771.586 | 767.033 | 273.93 | GGB | 11100.9 | GGB | 9.78 | GGB | 1020.54 | GGB | 61.74 | GGB | 177475.68 | GGB | 145819.7 | GGB | 0 | 0 | 3327 | 3600 | 3310.8 | GNB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 220098.67 | GGB | 220101.25 | 3310.8 | 2591.7486 |  |  |  | 0 | 1 | [14 empty] | 134.1055 | 2591.7486 |  | 104.98
04.05.2008 06:00 | 3600 | 2 | 761.05 | GGB | 764.102 | 773.742 | 769.597 | 275.49 | GGB | 11108.7 | GGB | 9.78 | GGB | 1020.86 | GGB | 60.83 | GGB | 179791.89 | GGB | 148168.93 | GGB | 0 | 0 | 3365 | 3600 | 3349.44 | GNB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 220138.69 | GGB | 220141.27 | 3349.44 | 2550.6562 |  |  |  | 1 | 1 |  |  |  |  | 148168.93 | 2550.6562 | 148168.93 | 2550.6562 | 9.4435 | [5 empty] | 137.8564 | 2550.6562 |  | 104.98
04.05.2008 07:00 | 3600 | 2 | 762.21 | GGB | 763.004 | 773.789 | 768.132 | 273.46 | GGB | 11149.7 | GGB | 9.8 | GGB | 1021.59 | GGB | 61.24 | GGB | 177495.48 | GGB | 146204.04 | GGB | 0 | 0 | 3313 | 3600 | 3297.51 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 220178.72 | GGB | 220181.3 | 3297.51 | 2584.9354 |  |  |  | 0 | 1 | [14 empty] | 133.9192 | 2584.9354 |  | 104.98
04.05.2008 08:00 | 3600 | 2 | 761.78 | GGB | 764.102 | 772.898 | 768.132 | 272.48 | GGB | 11117.6 | GGB | 9.8 | GGB | 1021.34 | GGB | 61.31 | GGB | 176754.96 | GGB | 145526.79 | GGB | 0 | 0 | 3311 | 3600 | 3294.8 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 220218.83 | GGB | 220221.41 | 3294.8 | 2596.9651 |  |  |  | 1 | 1 |  |  |  |  | 145526.79 | 2596.9651 | 145526.79 | 2596.9651 | 9.4223 | [5 empty] | 133.1894 | 2596.9651 |  | 104.98
04.05.2008 09:00 | 3600 | 2 | 763.1 | GGB | 764.102 | 774.094 | 768.132 | 270.57 | GGB | 11017.3 | GGB | 9.81 | GGB | 1021.13 | GGB | 61.86 | GGB | 174667.61 | GGB | 143542.78 | GGB | 0 | 0 | 3212 | 3600 | 3195.88 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 220258.89 | GGB | 220261.48 | 3195.88 | 2632.8597 |  |  |  | 1 | 1 |  |  |  |  | 143542.78 | 2632.8597 | 143542.78 | 2632.8597 | 9.4317 | [5 empty] | 127.4293 | 2632.8597 |  | 104.98
04.05.2008 10:00 | 3600 | 2 | 764.73 | GGB | 764.102 | 775.031 | 769.597 | 267.77 | GGB | 10935.4 | GGB | 9.82 | GGB | 1021.22 | GGB | 63.06 | GGB | 171146.53 | GGB | 140161.78 | GGB | 0 | 0 | 3103 | 3600 | 3087.41 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 220298.95 | GGB | 220301.53 | 3087.41 | 2696.3699 |  |  |  | 1 | 1 |  |  |  |  | 140161.78 | 2696.3699 | 140161.78 | 2696.3699 | 9.4364 | [5 empty] | 120.2047 | 2696.3699 |  | 104.98
04.05.2008 11:00 | 3600 | 2 | 764.93 | GGB | 765.201 | 776.203 | 770.696 | 264.03 | GGB | 10797.3 | GGB | 9.81 | GGB | 1020.34 | GGB | 64.7 | GGB | 166813.4 | GGB | 135833.07 | GGB | 0 | 0 | 3042 | 3600 | 3025.88 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 220338.99 | GGB | 220341.57 | 3025.88 | 2782.2974 |  |  |  | 1 | 1 |  |  |  |  | 135833.07 | 2782.2974 | 135833.07 | 2782.2974 | 9.4388 | [5 empty] | 114.1707 | 2782.2974 |  | 104.98
04.05.2008 12:00 | 3600 | 2 | 765.21 | GGB | 765.201 | 775.969 | 770.696 | 262.25 | GGB | 10694.7 | GGB | 9.8 | GGB | 1019.43 | GGB | 65.45 | GGB | 164915.32 | GGB | 133868.86 | GGB | 0 | 0 | 2973 | 3600 | 2957.18 | GGB | 100 | GGB | 40.85 | GGB | 40.85 | GGB | 220379.84 | GGB | 220382.42 | 2957.18 | 2823.1211 |  |  |  | 1 | 1 |  |  |  |  | 133868.86 | 2823.1211 | 133868.86 | 2823.1211 | 9.2516 | [5 empty] | 109.9651 | 2823.1211 |  | 104.98
04.05.2008 13:00 | 3600 | 2 | 765.27 | GGB | 764.102 | 775.875 | 770.696 | 261.28 | GGB | 10624.6 | GGB | 9.79 | GGB | 1018.47 | GGB | 65.85 | GGB | 164087.87 | GGB | 132914.19 | GGB | 0 | 0 | 2937 | 3600 | 2921.79 | GGB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 220420.09 | GGB | 220422.67 | 2921.79 | 2843.3984 |  |  |  | 1 | 1 |  |  |  |  | 132914.19 | 2843.3984 | 132914.19 | 2843.3984 | 9.3895 | [5 empty] | 107.8743 | 2843.3984 |  | 104.98
04.05.2008 14:00 | 3600 | 2 | 765.07 | GGB | 767.766 | 778.078 | 773.26 | 264.19 | GGB | 10626.9 | GGB | 9.77 | GGB | 1018.42 | GGB | 64.79 | GGB | 167319.56 | GGB | 135951.36 | GGB | 0 | 0 | 2950 | 3600 | 2934.03 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 220459.85 | GGB | 220462.43 | 2934.03 | 2779.8766 |  |  |  | 1 | 1 |  |  |  |  | 135951.36 | 2779.8766 | 135951.36 | 2779.8766 | 9.5052 | [5 empty] | 110.8015 | 2779.8766 |  | 104.98
04.05.2008 15:00 | 3600 | 2 | 766.38 | GGB | 765.201 | 775.781 | 769.597 | 261.76 | GGB | 10635.4 | GGB | 9.8 | GGB | 1018.23 | GGB | 65.48 | GGB | 164806.39 | GGB | 133611.23 | GGB | 0 | 0 | 2870 | 3600 | 2853.96 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 220498.74 | GGB | 220501.32 | 2853.96 | 2828.5646 |  |  |  | 1 | 1 |  |  |  |  | 133611.23 | 2828.5646 | 133611.23 | 2828.5646 | 9.7179 | [5 empty] | 105.9225 | 2828.5646 |  | 104.98
04.05.2008 16:00 | 3600 | 2 | 766.38 | GGB | 764.102 | 775.406 | 769.597 | 260.58 | GGB | 10617.5 | GGB | 9.79 | GGB | 1017.74 | GGB | 65.63 | GGB | 163773.17 | GGB | 132650.19 | GGB | 0 | 0 | 2876 | 3600 | 2860.01 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 220537.64 | GGB | 220540.22 | 2860.01 | 2849.0574 |  |  |  | 1 | 1 |  |  |  |  | 132650.19 | 2849.0574 | 132650.19 | 2849.0574 | 9.7154 | [5 empty] | 105.3836 | 2849.0574 |  | 104.98
04.05.2008 17:00 | 3600 | 2 | 764.3 | GGB | 763.004 | 774.234 | 768.498 | 262.38 | GGB | 10636.3 | GGB | 9.76 | GGB | 1018.32 | GGB | 64.98 | GGB | 164822.89 | GGB | 133833.7 | GGB | 0 | 0 | 2986 | 3600 | 2970.21 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 220576.23 | GGB | 220578.81 | 2970.21 | 2823.8627 |  |  |  | 0 | 1 | [14 empty] | 110.4206 | 2823.8627 |  | 104.98
04.05.2008 18:00 | 3600 | 2 | 764.93 | GGB | 767.766 | 778.664 | 772.161 | 264.87 | GGB | 10749.2 | GGB | 9.8 | GGB | 1018.99 | GGB | 64.57 | GGB | 166913.53 | GGB | 135783.7 | GGB | 0 | 0 | 3023 | 3600 | 3007.41 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 220614.87 | GGB | 220617.45 | 3007.41 | 2783.309 |  |  |  | 1 | 1 |  |  |  |  | 135783.7 | 2783.309 | 135783.7 | 2783.309 | 9.7807 | [5 empty] | 113.4326 | 2783.309 |  | 104.98
04.05.2008 19:00 | 3600 | 2 | 763.93 | GGB | 765.201 | 776.531 | 770.696 | 264.47 | GGB | 10729.5 | GGB | 9.77 | GGB | 1019.07 | GGB | 64.99 | GGB | 166366.67 | GGB | 135183.74 | GGB | 0 | 0 | 3070 | 3600 | 3054.04 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 220653.45 | GGB | 220656.03 | 3054.04 | 2795.6617 |  |  |  | 1 | 1 |  |  |  |  | 135183.74 | 2795.6617 | 135183.74 | 2795.6617 | 9.796 | [5 empty] | 114.6824 | 2795.6617 |  | 104.98
04.05.2008 20:00 | 3600 | 2 | 763.87 | GGB | 762.637 | 774.328 | 768.132 | 265.7 | GGB | 10704.1 | GGB | 9.78 | GGB | 1018.85 | GGB | 64.63 | GGB | 167990.77 | GGB | 136617.58 | GGB | 0 | 0 | 3071 | 3600 | 3055.69 | GGB | 100 | GGB | 38.69 | GGB | 38.69 | GGB | 220692.14 | GGB | 220694.72 | 3055.69 | 2766.3204 |  |  |  | 0 | 1 | [14 empty] | 115.9614 | 2766.3204 |  | 104.98
04.05.2008 21:00 | 3600 | 2 | 764.25 | GGB | 764.102 | 774.352 | 769.597 | 264.4 | GGB | 10741.6 | GGB | 9.79 | GGB | 1018.96 | GGB | 65.23 | GGB | 166097.08 | GGB | 134854.1 | GGB | 0 | 0 | 3055 | 3600 | 3038.91 | GGB | 100 | GGB | 38.31 | GGB | 38.31 | GGB | 220730.45 | GGB | 220733.03 | 3038.91 | 2802.4954 |  |  |  | 1 | 1 |  |  |  |  | 134854.1 | 2802.4954 | 134854.1 | 2802.4954 | 9.865 | [5 empty] | 113.836 | 2802.4954 |  | 104.98
04.05.2008 22:00 | 3600 | 2 | 764.03 | GGB | 763.004 | 774.445 | 768.498 | 265.26 | GGB | 10778.2 | GGB | 9.78 | GGB | 1019.71 | GGB | 65.12 | GGB | 167622.15 | GGB | 136235.85 | GGB | 0 | 0 | 3100 | 3600 | 3083.77 | GGB | 100 | GGB | 38.25 | GGB | 38.25 | GGB | 220768.7 | GGB | 220771.28 | 3083.77 | 2774.0716 |  |  |  | 0 | 1 | [14 empty] | 116.7 | 2774.0716 |  | 104.98
04.05.2008 23:00 | 3600 | 2 | 763.32 | GGB | 765.201 | 775.688 | 770.696 | 266.79 | GGB | 10798 | GGB | 9.78 | GGB | 1019.93 | GGB | 64.7 | GGB | 168150.31 | GGB | 136865.16 | GGB | 0 | 0 | 3152 | 3600 | 3135.9 | GGB | 100 | GGB | 38.27 | GGB | 38.27 | GGB | 220806.97 | GGB | 220809.55 | 3135.9 | 2761.3163 |  |  |  | 1 | 1 |  |  |  |  | 136865.16 | 2761.3163 | 136865.16 | 2761.3163 | 9.8753 | [5 empty] | 119.221 | 2761.3163 |  | 104.98
04.05.2008 24:00 | 3600 | 2 | 763.02 | GGB | 763.004 | 773.648 | 768.132 | 267.77 | GGB | 10823.6 | GGB | 9.77 | GGB | 1020.34 | GGB | 64.58 | GGB | 169159.32 | GGB | 137789.21 | GGB | 0 | 0 | 3175 | 3600 | 3159.04 | GGB | 100 | GGB | 38.3 | GGB | 38.3 | GGB | 220845.27 | GGB | 220847.85 | 3159.04 | 2742.7982 |  |  |  | 0 | 1 | [14 empty] | 120.9116 | 2742.7982 |  | 104.98
05.05.2008 01:00 | 3600 | 2 | 762.69 | GGB | 762.637 | 772.969 | 767.033 | 269.07 | GGB | 10874.8 | GGB | 9.78 | GGB | 1020.73 | GGB | 64.23 | GGB | 170536.95 | GGB | 139107.4 | GGB | 0 | 0 | 3209 | 3600 | 3192.93 | GGB | 100 | GGB | 39.11 | GGB | 39.11 | GGB | 220884.39 | GGB | 220886.96 | 3192.93 | 2716.8073 |  |  |  | 0 | 1 | [14 empty] | 123.3778 | 2716.8073 |  | 104.98
05.05.2008 02:00 | 3600 | 2 | 762.3 | GGB | 761.538 | 771.914 | 767.033 | 270.42 | GGB | 10924.4 | GGB | 9.77 | GGB | 1020.6 | GGB | 63.71 | GGB | 172053.21 | GGB | 140543.5 | GGB | 0 | 0 | 3244 | 3600 | 3228.44 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 220924.39 | GGB | 220926.96 | 3228.44 | 2689.0465 |  |  |  | 0 | 1 | [14 empty] | 126.0378 | 2689.0465 |  | 104.98
05.05.2008 03:00 | 3600 | 2 | 762.96 | GGB | 765.201 | 776.133 | 770.696 | 271.25 | GGB | 11002.4 | GGB | 9.8 | GGB | 1020.88 | GGB | 63.23 | GGB | 173732.33 | GGB | 142159.19 | GGB | 0 | 0 | 3253 | 3600 | 3236.74 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 220964.22 | GGB | 220966.8 | 3236.74 | 2658.4845 |  |  |  | 1 | 1 |  |  |  |  | 142159.19 | 2658.4845 | 142159.19 | 2658.4845 | 9.4861 | [5 empty] | 127.8145 | 2658.4845 |  | 104.98
05.05.2008 04:00 | 3600 | 2 | 761.13 | GGB | 764.102 | 774.023 | 768.132 | 272.32 | GGB | 11009.1 | GGB | 9.76 | GGB | 1021.17 | GGB | 62.63 | GGB | 175572.09 | GGB | 143964.03 | GGB | 0 | 0 | 3346 | 3600 | 3330.16 | GNB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 221003.44 | GGB | 221006.02 | 3330.16 | 2625.1557 |  |  |  | 1 | 1 |  |  |  |  | 143964.03 | 2625.1557 | 143964.03 | 2625.1557 | 9.6361 | [5 empty] | 133.1731 | 2625.1557 |  | 104.98
05.05.2008 05:00 | 3600 | 2 | 761.21 | GGB | 761.538 | 771.961 | 767.033 | 274.3 | GGB | 11044.8 | GGB | 9.77 | GGB | 1021.36 | GGB | 61.79 | GGB | 178255.82 | GGB | 146557.03 | GGB | 0 | 0 | 3353 | 3600 | 3337.26 | GNB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 221042.35 | GGB | 221044.93 | 3337.26 | 2578.7095 |  |  |  | 0 | 1 | [14 empty] | 135.8608 | 2578.7095 |  | 104.98
05.05.2008 06:00 | 3600 | 2 | 762.87 | GGB | 764.102 | 774.141 | 769.963 | 274.04 | GGB | 11126.2 | GGB | 9.81 | GGB | 1021.27 | GGB | 61.41 | GGB | 177868.5 | GGB | 146392.9 | GGB | 0 | 0 | 3288 | 3600 | 3271.77 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 221081.32 | GGB | 221083.9 | 3271.77 | 2581.6006 |  |  |  | 1 | 1 |  |  |  |  | 146392.9 | 2581.6006 | 146392.9 | 2581.6006 | 9.6979 | [5 empty] | 133.0455 | 2581.6006 |  | 104.98
05.05.2008 07:00 | 3600 | 2 | 762.02 | GGB | 761.538 | 770.695 | 766.3 | 272.55 | GGB | 11079.9 | GGB | 9.78 | GGB | 1021.45 | GGB | 61.69 | GGB | 176395.14 | GGB | 145083.22 | GGB | 0 | 0 | 3309 | 3600 | 3293.06 | GGB | 100 | GGB | 39.13 | GGB | 39.13 | GGB | 221120.44 | GGB | 221123.03 | 3293.06 | 2604.905 |  |  |  | 0 | 1 | [14 empty] | 132.7133 | 2604.905 |  | 104.98
05.05.2008 08:00 | 3600 | 2 | 763.03 | GGB | 765.201 | 775.031 | 768.864 | 272.33 | GGB | 11103.6 | GGB | 9.81 | GGB | 1021.73 | GGB | 61.93 | GGB | 175907.7 | GGB | 144617.6 | GGB | 0 | 0 | 3279 | 3600 | 3262.8 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 221161.05 | GGB | 221163.64 | 3262.8 | 2613.2919 |  |  |  | 1 | 1 |  |  |  |  | 144617.6 | 2613.2919 | 144617.6 | 2613.2919 | 9.3063 | [5 empty] | 131.0718 | 2613.2919 |  | 104.98
05.05.2008 09:00 | 3600 | 2 | 763.78 | GGB | 764.102 | 774.68 | 768.864 | 269.52 | GGB | 11006.1 | GGB | 9.81 | GGB | 1021.29 | GGB | 62.66 | GGB | 172693.61 | GGB | 141606.71 | GGB | 0 | 0 | 3196 | 3600 | 3179.88 | GGB | 100 | GGB | 43.19 | GGB | 43.19 | GGB | 221204.24 | GGB | 221206.83 | 3179.88 | 2668.8566 |  |  |  | 1 | 1 |  |  |  |  | 141606.71 | 2668.8566 | 141606.71 | 2668.8566 | 8.7504 | [5 empty] | 125.0812 | 2668.8566 |  | 104.98
05.05.2008 10:00 | 3600 | 2 | 764.26 | GGB | 765.201 | 775.898 | 769.597 | 267.27 | GGB | 10857.3 | GGB | 9.8 | GGB | 1020.76 | GGB | 63.58 | GGB | 170216.75 | GGB | 139118.25 | GGB | 0 | 0 | 3117 | 3600 | 3101.2 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 221244.39 | GGB | 221246.98 | 3101.2 | 2716.5954 |  |  |  | 1 | 1 |  |  |  |  | 139118.25 | 2716.5954 | 139118.25 | 2716.5954 | 9.4129 | [5 empty] | 119.8426 | 2716.5954 |  | 104.98
05.05.2008 11:00 | 3600 | 2 | 765.51 | GGB | 764.102 | 774.867 | 769.597 | 264.4 | GGB | 10768 | GGB | 9.81 | GGB | 1019.9 | GGB | 64.62 | GGB | 167010.36 | GGB | 135962.3 | GGB | 0 | 0 | 3012 | 3600 | 2996.73 | GGB | 100 | GGB | 38.36 | GGB | 38.36 | GGB | 221282.75 | GGB | 221285.34 | 2996.73 | 2779.6529 |  |  |  | 1 | 1 |  |  |  |  | 135962.3 | 2779.6529 | 135962.3 | 2779.6529 | 9.8521 | [5 empty] | 113.1784 | 2779.6529 |  | 104.98
05.05.2008 12:00 | 3600 | 2 | 765.53 | GGB | 765.201 | 776.953 | 770.696 | 262.71 | GGB | 10698.2 | GGB | 9.8 | GGB | 1019.21 | GGB | 65.32 | GGB | 164956.03 | GGB | 133923.04 | GGB | 0 | 0 | 2983 | 3600 | 2966.96 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 221321.21 | GGB | 221323.8 | 2966.96 | 2821.979 |  |  |  | 1 | 1 |  |  |  |  | 133923.04 | 2821.979 | 133923.04 | 2821.979 | 9.8265 | [5 empty] | 110.3734 | 2821.979 |  | 104.98
05.05.2008 13:00 | 3600 | 2 | 765.56 | GGB | 765.201 | 776.953 | 770.696 | 261.44 | GGB | 10637.5 | GGB | 9.79 | GGB | 1018.5 | GGB | 65.88 | GGB | 164049.36 | GGB | 132873.02 | GGB | 0 | 0 | 2962 | 3600 | 2946.39 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 221360.29 | GGB | 221362.88 | 2946.39 | 2844.2794 |  |  |  | 1 | 1 |  |  |  |  | 132873.02 | 2844.2794 | 132873.02 | 2844.2794 | 9.6706 | [5 empty] | 108.7488 | 2844.2794 |  | 104.98
05.05.2008 14:00 | 3600 | 2 | 765.64 | GGB | 765.201 | 777.047 | 770.696 | 260.9 | GGB | 10605.8 | GGB | 9.78 | GGB | 1017.45 | GGB | 66.03 | GGB | 163809.48 | GGB | 132487.04 | GGB | 0 | 0 | 2939 | 3600 | 2922.94 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 221399.3 | GGB | 221401.89 | 2922.94 | 2852.5658 |  |  |  | 1 | 1 |  |  |  |  | 132487.04 | 2852.5658 | 132487.04 | 2852.5658 | 9.688 | [5 empty] | 107.5699 | 2852.5658 |  | 104.98
05.05.2008 15:00 | 3600 | 2 | 766.38 | GGB | 765.201 | 776.93 | 770.696 | 259.84 | GGB | 10586.9 | GGB | 9.79 | GGB | 1016.59 | GGB | 66.21 | GGB | 163200.99 | GGB | 131810.13 | GGB | 0 | 0 | 2899 | 3600 | 2882.97 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 221438.24 | GGB | 221440.83 | 2882.97 | 2867.2151 |  |  |  | 1 | 1 |  |  |  |  | 131810.13 | 2867.2151 | 131810.13 | 2867.2151 | 9.7054 | [5 empty] | 105.5568 | 2867.2151 |  | 104.98
05.05.2008 16:00 | 3600 | 2 | 765.9 | GGB | 766.3 | 776.977 | 771.795 | 261.28 | GGB | 10563.5 | GGB | 9.78 | GGB | 1016.09 | GGB | 65.28 | GGB | 165018.75 | GGB | 133581 | GGB | 0 | 0 | 2905 | 3600 | 2889.72 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 221477.11 | GGB | 221479.69 | 2889.72 | 2829.2048 |  |  |  | 1 | 1 |  |  |  |  | 133581 | 2829.2048 | 133581 | 2829.2048 | 9.7254 | [5 empty] | 107.2255 | 2829.2048 |  | 104.98
05.05.2008 17:00 | 3600 | 2 | 766.24 | GGB | 765.201 | 775.992 | 770.696 | 259.47 | GGB | 10573.9 | GGB | 9.79 | GGB | 1015.6 | GGB | 65.89 | GGB | 162957.82 | GGB | 131610.2 | GGB | 0 | 0 | 2872 | 3600 | 2856.31 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 221516.9 | GGB | 221519.48 | 2856.31 | 2856.31 |  |  |  | 1 | 1 |  |  |  |  | 131610.2 | 2856.31 | 131610.2 | 2856.31 | 9.4476 | [5 empty] | 104.4221 |  |  | #VALUE!
05.05.2008 18:00 | 3600 | 2 | 765.75 | GGB | 765.201 | 775.945 | 770.696 | 259.92 | GGB | 10547.9 | GGB | 9.77 | GGB | 1015.28 | GGB | 65.44 | GGB | 163987.74 | GGB | 132576.56 | GGB | 0 | 0 | 2869 | 3600 | 2853.05 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 221555.61 | GGB | 221558.19 | 2853.05 | 2850.6397 |  |  |  | 1 | 1 |  |  |  |  | 132576.56 | 2850.6397 | 132576.56 | 2850.6397 | 9.7631 | [5 empty] | 105.0688 | 2850.6397 |  | 104.98
05.05.2008 19:00 | 3600 | 2 | 764.96 | GGB | 764.102 | 775.945 | 769.597 | 261.5 | GGB | 10640.4 | GGB | 9.77 | GGB | 1015.42 | GGB | 64.72 | GGB | 165515.01 | GGB | 134113.62 | GGB | 0 | 0 | 2956 | 3600 | 2940.19 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 221594.61 | GGB | 221597.2 | 2940.19 | 2817.9688 |  |  |  | 1 | 1 |  |  |  |  | 134113.62 | 2817.9688 | 134113.62 | 2817.9688 | 9.688 | [5 empty] | 109.5332 | 2817.9688 |  | 104.98
05.05.2008 20:00 | 3600 | 2 | 764.31 | GGB | 763.004 | 773.719 | 768.498 | 264.12 | GGB | 10704.8 | GGB | 9.77 | GGB | 1016.3 | GGB | 63.76 | GGB | 168069.99 | GGB | 136692.08 | GGB | 0 | 0 | 3013 | 3600 | 2997.22 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 221633.81 | GGB | 221636.4 | 2997.22 | 2764.8127 |  |  |  | 0 | 1 | [14 empty] | 113.8045 | 2764.8127 |  | 104.98
05.05.2008 21:00 | 3600 | 2 | 763.46 | GGB | 764.102 | 774.891 | 768.864 | 266.45 | GGB | 10807.7 | GGB | 9.77 | GGB | 1017.36 | GGB | 63.3 | GGB | 169844.83 | GGB | 138470.03 | GGB | 0 | 0 | 3111 | 3600 | 3095.27 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 221673.17 | GGB | 221675.75 | 3095.27 | 2729.3126 |  |  |  | 1 | 1 |  |  |  |  | 138470.03 | 2729.3126 | 138470.03 | 2729.3126 | 9.6043 | [5 empty] | 119.0561 | 2729.3126 |  | 104.98
05.05.2008 22:00 | 3600 | 2 | 763.6 | GGB | 765.201 | 775.898 | 770.696 | 267.88 | GGB | 10848 | GGB | 9.78 | GGB | 1018.26 | GGB | 62.91 | GGB | 171514.05 | GGB | 140115.01 | GGB | 0 | 0 | 3108 | 3600 | 3092.52 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 221712.7 | GGB | 221715.28 | 3092.52 | 2697.2699 |  |  |  | 1 | 1 |  |  |  |  | 140115.01 | 2697.2699 | 140115.01 | 2697.2699 | 9.5605 | [5 empty] | 120.3635 | 2697.2699 |  | 104.98
05.05.2008 23:00 | 3600 | 2 | 763.23 | GGB | 763.004 | 773.648 | 768.498 | 268.32 | GGB | 10894.8 | GGB | 9.78 | GGB | 1019.03 | GGB | 62.83 | GGB | 171959.68 | GGB | 140620.82 | GGB | 0 | 0 | 3150 | 3600 | 3134.3 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 221752.28 | GGB | 221754.86 | 3134.3 | 2687.5679 |  |  |  | 0 | 1 | [14 empty] | 122.43 | 2687.5679 |  | 104.98
05.05.2008 24:00 | 3600 | 2 | 763.33 | GGB | 765.201 | 775.055 | 769.963 | 269.28 | GGB | 10933.1 | GGB | 9.78 | GGB | 1019.24 | GGB | 61.89 | GGB | 174401.33 | GGB | 143047.81 | GGB | 0 | 0 | 3152 | 3600 | 3135.93 | GGB | 100 | GGB | 39.69 | GGB | 39.69 | GGB | 221791.97 | GGB | 221794.55 | 3135.93 | 2641.9698 |  |  |  | 1 | 1 |  |  |  |  | 143047.81 | 2641.9698 | 143047.81 | 2641.9698 | 9.522 | [5 empty] | 124.6078 | 2641.9698 |  | 104.98
06.05.2008 01:00 | 3600 | 2 | 763.53 | GGB | 763.004 | 773.906 | 767.766 | 268.66 | GGB | 10957.2 | GGB | 9.79 | GGB | 1019.52 | GGB | 62.39 | GGB | 173127.14 | GGB | 141829.23 | GGB | 0 | 0 | 3151 | 3600 | 3135.39 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 221831.27 | GGB | 221833.86 | 3135.39 | 2664.6693 |  |  |  | 0 | 1 | [14 empty] | 123.525 | 2664.6693 |  | 104.98
06.05.2008 02:00 | 3600 | 2 | 761.97 | GGB | 762.637 | 772.969 | 766.667 | 269.96 | GGB | 10983 | GGB | 9.76 | GGB | 1019.81 | GGB | 61.8 | GGB | 174673.12 | GGB | 143387.84 | GGB | 0 | 0 | 3255 | 3600 | 3238.84 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 221870.22 | GGB | 221872.81 | 3238.84 | 2635.7047 |  |  |  | 0 | 1 | [14 empty] | 129.0029 | 2635.7047 |  | 104.98
06.05.2008 03:00 | 3600 | 2 | 761.94 | GGB | 764.102 | 775.172 | 769.963 | 272.53 | GGB | 11051.6 | GGB | 9.78 | GGB | 1020.06 | GGB | 60.95 | GGB | 177471.28 | GGB | 146093.97 | GGB | 0 | 0 | 3292 | 3600 | 3275.88 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 221909.06 | GGB | 221911.64 | 3275.88 | 2586.8829 |  |  |  | 1 | 1 |  |  |  |  | 146093.97 | 2586.8829 | 146093.97 | 2586.8829 | 9.7329 | [5 empty] | 132.9406 | 2586.8829 |  | 104.98
06.05.2008 04:00 | 3600 | 2 | 762.3 | GGB | 763.004 | 773.039 | 767.766 | 271.92 | GGB | 11088.5 | GGB | 9.78 | GGB | 1019.96 | GGB | 60.96 | GGB | 176906.8 | GGB | 145607.08 | GGB | 0 | 0 | 3275 | 3600 | 3259.09 | GGB | 100 | GGB | 38.1 | GGB | 38.1 | GGB | 221947.16 | GGB | 221949.74 | 3259.09 | 2595.5331 |  |  |  | 0 | 1 | [14 empty] | 131.8185 | 2595.5331 |  | 104.98
06.05.2008 05:00 | 3600 | 2 | 761.14 | GGB | 761.538 | 770.906 | 765.201 | 273.73 | GGB | 11138.6 | GGB | 9.77 | GGB | 1020.09 | GGB | 60.21 | GGB | 179348.45 | GGB | 147968.34 | GGB | 0 | 0 | 3364 | 3600 | 3348.25 | GNB | 100 | GGB | 36.41 | GGB | 36.41 | GGB | 221983.57 | GGB | 221986.15 | 3348.25 | 2554.1139 |  |  |  | 0 | 1 | [14 empty] | 137.6208 | 2554.1139 |  | 104.98
06.05.2008 06:00 | 3600 | 2 | 761.26 | GGB | 761.538 | 772.008 | 766.667 | 273.99 | GGB | 11196 | GGB | 9.79 | GGB | 1020.48 | GGB | 59.91 | GGB | 179567.42 | GGB | 148340.35 | GGB | 0 | 0 | 3360 | 3600 | 3344.23 | GNB | 100 | GGB | 46.38 | GGB | 46.38 | GGB | 222029.95 | GGB | 222032.53 | 3344.23 | 2547.7087 |  |  |  | 0 | 1 | [14 empty] | 137.8012 | 2547.7087 |  | 104.98
06.05.2008 07:00 | 3600 | 2 | 761.18 | GGB | 762.637 | 772.008 | 766.667 | 274.33 | GGB | 11202.6 | GGB | 9.78 | GGB | 1020.43 | GGB | 59.54 | GGB | 180096.68 | GGB | 148936.63 | GGB | 0 | 0 | 3377 | 3600 | 3361.45 | GNB | 100 | GGB | 44.44 | GGB | 44.44 | GGB | 222074.38 | GGB | 222076.97 | 3361.45 | 2537.5087 |  |  |  | 0 | 1 | [14 empty] | 139.0675 | 2537.5087 |  | 104.98
06.05.2008 08:00 | 3600 | 2 | 762.09 | GGB | 763.004 | 773.414 | 767.766 | 275.33 | GGB | 11176.6 | GGB | 9.79 | GGB | 1020.99 | GGB | 58.68 | GGB | 181888.03 | GGB | 150890.17 | GGB | 0 | 0 | 3324 | 3600 | 3308.09 | GNB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 222114.12 | GGB | 222116.71 | 3308.09 | 2504.6562 |  |  |  | 0 | 1 | [14 empty] | 138.6551 | 2504.6562 |  | 104.98
06.05.2008 09:00 | 3600 | 2 | 763.03 | GGB | 764.102 | 773.719 | 768.864 | 272.16 | GGB | 11168.1 | GGB | 9.81 | GGB | 1021.22 | GGB | 59.67 | GGB | 178264.62 | GGB | 147478.17 | GGB | 0 | 0 | 3262 | 3600 | 3246.48 | GGB | 100 | GGB | 38.86 | GGB | 38.86 | GGB | 222152.98 | GGB | 222155.57 | 3246.48 | 2562.603 |  |  |  | 1 | 1 |  |  |  |  | 147478.17 | 2562.603 | 147478.17 | 2562.603 | 9.7254 | [5 empty] | 132.9958 | 2562.603 |  | 104.98
06.05.2008 10:00 | 3600 | 2 | 762.1 | GGB | 762.637 | 773.063 | 766.667 | 271.68 | GGB | 11120.3 | GGB | 9.79 | GGB | 1020.97 | GGB | 59.87 | GGB | 177678.14 | GGB | 146865.51 | GGB | 0 | 0 | 3273 | 3600 | 3257.43 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 222192.07 | GGB | 222194.66 | 3257.43 | 2573.2931 |  |  |  | 0 | 1 | [14 empty] | 132.89 | 2573.2931 |  | 104.98
06.05.2008 11:00 | 3600 | 2 | 763.29 | GGB | 765.201 | 776.414 | 769.963 | 270.7 | GGB | 11116.3 | GGB | 9.8 | GGB | 1020.96 | GGB | 60.25 | GGB | 177098.26 | GGB | 146219.74 | GGB | 0 | 0 | 3216 | 3600 | 3199.94 | GGB | 100 | GGB | 40.46 | GGB | 40.46 | GGB | 222232.53 | GGB | 222235.12 | 3199.94 | 2584.6579 |  |  |  | 1 | 1 |  |  |  |  | 146219.74 | 2584.6579 | 146219.74 | 2584.6579 | 9.3408 | [5 empty] | 129.9707 | 2584.6579 |  | 104.98
06.05.2008 12:00 | 3600 | 2 | 763.19 | GGB | 763.004 | 773.906 | 767.766 | 270.15 | GGB | 11086.2 | GGB | 9.79 | GGB | 1020.35 | GGB | 60.42 | GGB | 176717.54 | GGB | 145745.24 | GGB | 0 | 0 | 3204 | 3600 | 3187.79 | GGB | 100 | GGB | 40.83 | GGB | 40.83 | GGB | 222273.36 | GGB | 222275.95 | 3187.79 | 2593.0727 |  |  |  | 0 | 1 | [14 empty] | 129.057 | 2593.0727 |  | 104.98
06.05.2008 13:00 | 3600 | 2 | 763.46 | GGB | 761.538 | 772.594 | 766.667 | 269.49 | GGB | 11066.8 | GGB | 9.79 | GGB | 1020.12 | GGB | 60.64 | GGB | 176166.27 | GGB | 145160.32 | GGB | 0 | 0 | 3172 | 3600 | 3155.76 | GGB | 100 | GGB | 40.17 | GGB | 40.17 | GGB | 222313.53 | GGB | 222316.12 | 3155.76 | 2603.5214 |  |  |  | 0 | 1 | [14 empty] | 127.2475 | 2603.5214 |  | 104.98
06.05.2008 14:00 | 3600 | 2 | 763.71 | GGB | 766.3 | 776.742 | 771.429 | 269.34 | GGB | 11003.5 | GGB | 9.79 | GGB | 1019.78 | GGB | 60.54 | GGB | 176726.35 | GGB | 145615.68 | GGB | 0 | 0 | 3130 | 3600 | 3114.3 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 222353.73 | GGB | 222356.32 | 3114.3 | 2595.3798 |  |  |  | 1 | 1 |  |  |  |  | 145615.68 | 2595.3798 | 145615.68 | 2595.3798 | 9.4012 | [5 empty] | 125.9697 | 2595.3798 |  | 104.98
06.05.2008 15:00 | 3600 | 2 | 764.36 | GGB | 764.102 | 775.664 | 768.864 | 269.17 | GGB | 10957.8 | GGB | 9.79 | GGB | 1019.27 | GGB | 60.52 | GGB | 176813.27 | GGB | 145627.4 | GGB | 0 | 0 | 3068 | 3600 | 3051.8 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 222393.82 | GGB | 222396.41 | 3051.8 | 2595.171 |  |  |  | 1 | 1 |  |  |  |  | 145627.4 | 2595.171 | 145627.4 | 2595.171 | 9.427 | [5 empty] | 123.4516 | 2595.171 |  | 104.98
06.05.2008 16:00 | 3600 | 2 | 764.6 | GGB | 764.102 | 774.633 | 768.864 | 266.71 | GGB | 10966.7 | GGB | 9.8 | GGB | 1018.62 | GGB | 61.24 | GGB | 173995.31 | GGB | 142904.57 | GGB | 0 | 0 | 3064 | 3600 | 3047.88 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 222433.67 | GGB | 222436.27 | 3047.88 | 2644.618 |  |  |  | 1 | 1 |  |  |  |  | 142904.57 | 2644.618 | 142904.57 | 2644.618 | 9.4814 | [5 empty] | 120.9878 | 2644.618 |  | 104.98
06.05.2008 17:00 | 3600 | 2 | 764.47 | GGB | 764.102 | 775.664 | 770.33 | 266.55 | GGB | 10946 | GGB | 9.79 | GGB | 1018.32 | GGB | 61.39 | GGB | 173890.78 | GGB | 142711.87 | GGB | 0 | 0 | 3057 | 3600 | 3040.99 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 222473.48 | GGB | 222476.08 | 3040.99 | 2648.189 |  |  |  | 1 | 1 |  |  |  |  | 142711.87 | 2648.189 | 142711.87 | 2648.189 | 9.4933 | [5 empty] | 120.5515 | 2648.189 |  | 104.98
06.05.2008 18:00 | 3600 | 2 | 764.3 | GGB | 764.102 | 775.43 | 769.963 | 267.18 | GGB | 10913.6 | GGB | 9.78 | GGB | 1018.37 | GGB | 61.06 | GGB | 175027.43 | GGB | 143796.17 | GGB | 0 | 0 | 3044 | 3600 | 3027.89 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 222513.34 | GGB | 222515.94 | 3027.89 | 2628.2202 |  |  |  | 1 | 1 |  |  |  |  | 143796.17 | 2628.2202 | 143796.17 | 2628.2202 | 9.4814 | [5 empty] | 120.9442 | 2628.2202 |  | 104.98
06.05.2008 19:00 | 3600 | 2 | 764.55 | GGB | 763.004 | 773.086 | 767.766 | 267.05 | GGB | 10954.5 | GGB | 9.79 | GGB | 1018.25 | GGB | 61.03 | GGB | 174505.86 | GGB | 143361.7 | GGB | 0 | 0 | 3048 | 3600 | 3032.67 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 222553.11 | GGB | 222555.7 | 3032.67 | 2636.1853 |  |  |  | 0 | 1 | [14 empty] | 120.7691 | 2636.1853 |  | 104.98
06.05.2008 20:00 | 3600 | 2 | 763.43 | GGB | 762.637 | 774.352 | 767.766 | 267.46 | GGB | 10969.4 | GGB | 9.78 | GGB | 1018.44 | GGB | 60.83 | GGB | 174796.35 | GGB | 143714.46 | GGB | 0 | 0 | 3105 | 3600 | 3089.47 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 222592.99 | GGB | 222595.58 | 3089.47 | 2629.7145 |  |  |  | 0 | 1 | [14 empty] | 123.3338 | 2629.7145 |  | 104.98
06.05.2008 21:00 | 3600 | 2 | 763.3 | GGB | 762.637 | 773.039 | 767.766 | 269.42 | GGB | 11006.6 | GGB | 9.78 | GGB | 1018.95 | GGB | 60.67 | GGB | 175800.96 | GGB | 144679.62 | GGB | 0 | 0 | 3140 | 3600 | 3124.72 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 222633.04 | GGB | 222635.63 | 3124.72 | 2612.1716 |  |  |  | 0 | 1 | [14 empty] | 125.5787 | 2612.1716 |  | 104.98
06.05.2008 22:00 | 3600 | 2 | 762.25 | GGB | 761.538 | 772.945 | 766.667 | 272.78 | GGB | 10990.3 | GGB | 9.76 | GGB | 1019.85 | GGB | 60.16 | GGB | 178870.9 | GGB | 147561.82 | GGB | 0 | 0 | 3192 | 3600 | 3175.89 | GGB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 222673.18 | GGB | 222675.77 | 3175.89 | 2561.1503 |  |  |  | 0 | 1 | [14 empty] | 130.1778 | 2561.1503 |  | 104.98
06.05.2008 23:00 | 3600 | 2 | 762.85 | GGB | 761.538 | 771.797 | 766.3 | 273.09 | GGB | 11087.7 | GGB | 9.78 | GGB | 1020.38 | GGB | 60.26 | GGB | 179037.06 | GGB | 147730.83 | GGB | 0 | 0 | 3216 | 3600 | 3199.96 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 222713.18 | GGB | 222715.78 | 3199.96 | 2558.2202 |  |  |  | 0 | 1 | [14 empty] | 131.3147 | 2558.2202 |  | 104.98
06.05.2008 24:00 | 3600 | 2 | 761.73 | GGB | 762.637 | 772.969 | 767.766 | 274.97 | GGB | 11152 | GGB | 9.77 | GGB | 1020.5 | GGB | 60.31 | GGB | 179593.83 | GGB | 148188.71 | GGB | 0 | 0 | 3301 | 3600 | 3285.37 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 222753.27 | GGB | 222755.87 | 3285.37 | 2550.3157 |  |  |  | 0 | 1 | [14 empty] | 135.2374 | 2550.3157 |  | 104.98
07.05.2008 01:00 | 3600 | 2 | 761.69 | GGB | 761.538 | 771.938 | 766.667 | 275.76 | GGB | 11199.3 | GGB | 9.78 | GGB | 1020.45 | GGB | 59.96 | GGB | 180559.92 | GGB | 149132.17 | GGB | 0 | 0 | 3330 | 3600 | 3313.82 | GNB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 222793.49 | GGB | 222796.09 | 3313.82 | 2534.1816 |  |  |  | 0 | 1 | [14 empty] | 137.277 | 2534.1816 |  | 104.98
07.05.2008 02:00 | 3600 | 2 | 761.84 | GGB | 762.637 | 772.992 | 767.766 | 276.52 | GGB | 11235.9 | GGB | 9.79 | GGB | 1020.79 | GGB | 60.09 | GGB | 181364.27 | GGB | 149788.3 | GGB | 0 | 0 | 3348 | 3600 | 3331.64 | GNB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 222833.75 | GGB | 222836.35 | 3331.64 | 2523.0809 |  |  |  | 0 | 1 | [14 empty] | 138.6224 | 2523.0809 |  | 104.98
07.05.2008 03:00 | 3600 | 2 | 761.33 | GGB | 761.538 | 771.891 | 766.667 | 277.55 | GGB | 11249.2 | GGB | 9.78 | GGB | 1020.73 | GGB | 59.99 | GGB | 182053.08 | GGB | 150393.01 | GGB | 0 | 0 | 3392 | 3600 | 3375.71 | GNB | 100 | GGB | 40.25 | GGB | 40.25 | GGB | 222874 | GGB | 222876.6 | 3375.71 | 2512.9359 |  |  |  | 0 | 1 | [14 empty] | 141.0231 | 2512.9359 |  | 104.98
07.05.2008 04:00 | 3600 | 2 | 761.16 | GGB | 762.637 | 772.641 | 767.766 | 278.04 | GGB | 11279.2 | GGB | 9.78 | GGB | 1021.03 | GGB | 59.74 | GGB | 182813.41 | GGB | 151180.87 | GGB | 0 | 0 | 3420 | 3600 | 3404.35 | GNB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 222914.27 | GGB | 222916.87 | 3404.35 | 2499.8401 |  |  |  | 0 | 1 | [14 empty] | 142.9646 | 2499.8401 |  | 104.98
07.05.2008 05:00 | 3600 | 2 | 761.31 | GGB | 761.538 | 771.422 | 766.3 | 278.18 | GGB | 11292 | GGB | 9.78 | GGB | 1020.94 | GGB | 59.63 | GGB | 183030.18 | GGB | 151397.08 | GGB | 0 | 0 | 3419 | 3600 | 3402.72 | GNB | 100 | GGB | 40.27 | GGB | 40.27 | GGB | 222954.54 | GGB | 222957.14 | 3402.72 | 2496.2701 |  |  |  | 0 | 1 | [14 empty] | 143.1005 | 2496.2701 |  | 104.98
07.05.2008 06:00 | 3600 | 2 | 760.82 | GGB | 760.44 | 771.422 | 765.201 | 278.91 | GGB | 11311.5 | GGB | 9.78 | GGB | 1020.98 | GGB | 59.33 | GGB | 183733.3 | GGB | 152121.01 | GGB | 0 | 0 | 3467 | 3600 | 3451.08 | GNB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 222994.92 | GGB | 222997.52 | 3451.08 | 2484.3906 |  |  |  | 0 | 1 | [14 empty] | 145.8283 | 2484.3906 |  | 104.98
07.05.2008 07:00 | 3600 | 2 | 760.68 | GGB | 763.004 | 772.617 | 768.132 | 280.07 | GGB | 11366.2 | GGB | 9.78 | GGB | 1021.09 | GGB | 58.99 | GGB | 184910.66 | GGB | 153270.3 | GNB | 0 | 0 | 3503 | 3600 | 3486.92 | GNB | 100 | GGB | 42.44 | GGB | 42.44 | GGB | 223037.36 | GGB | 223039.96 | 3486.92 | 2465.7615 |  |  |  | 0 | 1 | [14 empty] | 148.4559 | 2465.7615 |  | 104.98
07.05.2008 08:00 | 3600 | 2 | 761.53 | GGB | 762.637 | 772.523 | 767.766 | 278.29 | GGB | 11348.1 | GGB | 9.81 | GGB | 1021.4 | GGB | 59.38 | GGB | 183330.57 | GGB | 151829.38 | GGB | 0 | 0 | 3429 | 3600 | 3412.59 | GNB | 100 | GGB | 41.85 | GGB | 41.85 | GGB | 223079.21 | GGB | 223081.81 | 3412.59 | 2489.1625 |  |  |  | 0 | 1 | [14 empty] | 143.9254 | 2489.1625 |  | 104.98
07.05.2008 09:00 | 3600 | 2 | 762.24 | GGB | 762.637 | 772.266 | 767.766 | 275.8 | GGB | 11257.7 | GGB | 9.81 | GGB | 1020.55 | GGB | 59.97 | GGB | 180762.39 | GGB | 149309.53 | GGB | 0 | 0 | 3362 | 3600 | 3346.04 | GNB | 100 | GGB | 40.99 | GGB | 40.99 | GGB | 223120.2 | GGB | 223122.8 | 3346.04 | 2531.1713 |  |  |  | 0 | 1 | [14 empty] | 138.7766 | 2531.1713 |  | 104.98
07.05.2008 10:00 | 3600 | 2 | 762.89 | GGB | 763.004 | 773.625 | 767.766 | 274.11 | GGB | 11183.2 | GGB | 9.8 | GGB | 1019.56 | GGB | 60.51 | GGB | 179033.75 | GGB | 147500.76 | GGB | 0 | 0 | 3310 | 3600 | 3293.94 | GGB | 100 | GGB | 40.18 | GGB | 40.18 | GGB | 223160.38 | GGB | 223162.98 | 3293.94 | 2562.2105 |  |  |  | 0 | 1 | [14 empty] | 134.9607 | 2562.2105 |  | 104.98
07.05.2008 11:00 | 3600 | 2 | 763.37 | GGB | 764.102 | 774.633 | 768.864 | 273.31 | GGB | 11131.8 | GGB | 9.79 | GGB | 1018.96 | GGB | 61 | GGB | 178245.91 | GGB | 146550.51 | GGB | 0 | 0 | 3271 | 3600 | 3255.52 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 223200.08 | GGB | 223202.68 | 3255.52 | 2578.8242 |  |  |  | 1 | 1 |  |  |  |  | 146550.51 | 2578.8242 | 146550.51 | 2578.8242 | 9.5196 | [5 empty] | 132.5273 | 2578.8242 |  | 104.98
07.05.2008 12:00 | 3600 | 2 | 763.32 | GGB | 764.102 | 774.398 | 769.963 | 273.1 | GGB | 11101.5 | GGB | 9.79 | GGB | 1018.54 | GGB | 61.26 | GGB | 177882.8 | GGB | 146078.09 | GGB | 0 | 0 | 3243 | 3600 | 3227.43 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 223239.94 | GGB | 223242.54 | 3227.43 | 2587.1642 |  |  |  | 1 | 1 |  |  |  |  | 146078.09 | 2587.1642 | 146078.09 | 2587.1642 | 9.4814 | [5 empty] | 130.9602 | 2587.1642 |  | 104.98
07.05.2008 13:00 | 3600 | 2 | 764.51 | GGB | 764.102 | 774.422 | 768.864 | 271.58 | GGB | 11056.8 | GGB | 9.8 | GGB | 1017.75 | GGB | 61.94 | GGB | 176399.55 | GGB | 144452.18 | GGB | 0 | 0 | 3157 | 3600 | 3141.48 | GGB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 223280.27 | GGB | 223282.87 | 3141.48 | 2616.2845 |  |  |  | 1 | 1 |  |  |  |  | 144452.18 | 2616.2845 | 144452.18 | 2616.2845 | 9.3709 | [5 empty] | 126.0538 | 2616.2845 |  | 104.98
07.05.2008 14:00 | 3600 | 2 | 764.39 | GGB | 765.201 | 775.688 | 769.963 | 270.31 | GGB | 11007.2 | GGB | 9.8 | GGB | 1016.98 | GGB | 62.08 | GGB | 175098.95 | GGB | 143217.67 | GGB | 0 | 0 | 3134 | 3600 | 3118.14 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 223320.63 | GGB | 223323.23 | 3118.14 | 2638.8364 |  |  |  | 1 | 1 |  |  |  |  | 143217.67 | 2638.8364 | 143217.67 | 2638.8364 | 9.3639 | [5 empty] | 124.048 | 2638.8364 |  | 104.98
07.05.2008 15:00 | 3600 | 2 | 765.29 | GGB | 766.3 | 776.859 | 771.429 | 268.14 | GGB | 10932.9 | GGB | 9.81 | GGB | 1015.67 | GGB | 62.85 | GGB | 172592.38 | GGB | 140661.77 | GGB | 0 | 0 | 3055 | 3600 | 3039.66 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 223360.78 | GGB | 223363.38 | 3039.66 | 2686.7855 |  |  |  | 1 | 1 |  |  |  |  | 140661.77 | 2686.7855 | 140661.77 | 2686.7855 | 9.4129 | [5 empty] | 118.7678 | 2686.7855 |  | 104.98
07.05.2008 16:00 | 3600 | 2 | 765.28 | GGB | 765.201 | 775.734 | 769.963 | 265.71 | GGB | 10834 | GGB | 9.8 | GGB | 1013.98 | GGB | 63.38 | GGB | 170399.4 | GGB | 138427.08 | GGB | 0 | 0 | 2995 | 3600 | 2978.85 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 223400.68 | GGB | 223403.28 | 2978.85 | 2730.1594 |  |  |  | 1 | 1 |  |  |  |  | 138427.08 | 2730.1594 | 138427.08 | 2730.1594 | 9.4719 | [5 empty] | 114.5426 | 2730.1594 |  | 104.98
07.05.2008 17:00 | 3600 | 2 | 764.81 | GGB | 766.3 | 776.883 | 771.429 | 265.33 | GGB | 10810.7 | GGB | 9.79 | GGB | 1012.85 | GGB | 63.18 | GGB | 169862.44 | GGB | 137917.38 | GGB | 0 | 0 | 3008 | 3600 | 2992.83 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 223440.46 | GGB | 223443.06 | 2992.83 | 2740.2493 |  |  |  | 1 | 1 |  |  |  |  | 137917.38 | 2740.2493 | 137917.38 | 2740.2493 | 9.5005 | [5 empty] | 114.6565 | 2740.2493 |  | 104.98
07.05.2008 18:00 | 3600 | 2 | 764.66 | GGB | 764.102 | 774.422 | 768.864 | 265.12 | GGB | 10803.5 | GGB | 9.78 | GGB | 1012.57 | GGB | 63.14 | GGB | 169662.18 | GGB | 137737.32 | GGB | 0 | 0 | 3015 | 3600 | 2998.98 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 223480.1 | GGB | 223482.7 | 2998.98 | 2743.8315 |  |  |  | 1 | 1 |  |  |  |  | 137737.32 | 2743.8315 | 137737.32 | 2743.8315 | 9.534 | [5 empty] | 114.7421 | 2743.8315 |  | 104.98
07.05.2008 19:00 | 3600 | 2 | 763.35 | GGB | 762.637 | 773.438 | 767.766 | 266.63 | GGB | 10831.7 | GGB | 9.77 | GGB | 1012.72 | GGB | 63.02 | GGB | 170479.73 | GGB | 138470.81 | GGB | 0 | 0 | 3118 | 3600 | 3101.9 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 223519.74 | GGB | 223522.34 | 3101.9 | 2729.2972 |  |  |  | 0 | 1 | [14 empty] | 119.3118 | 2729.2972 |  | 104.98
07.05.2008 20:00 | 3600 | 2 | 764.06 | GGB | 765.201 | 775.547 | 769.963 | 267.17 | GGB | 10876.8 | GGB | 9.79 | GGB | 1012.39 | GGB | 63.08 | GGB | 170650.28 | GGB | 138537.05 | GGB | 0 | 0 | 3102 | 3600 | 3086.7 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 223559.28 | GGB | 223561.87 | 3086.7 | 2727.9923 |  |  |  | 1 | 1 |  |  |  |  | 138537.05 | 2727.9923 | 138537.05 | 2727.9923 | 9.5605 | [5 empty] | 118.784 | 2727.9923 |  | 104.98
07.05.2008 21:00 | 3600 | 2 | 763.22 | GGB | 764.102 | 774.586 | 768.498 | 267.21 | GGB | 10879.5 | GGB | 9.78 | GGB | 1011.79 | GGB | 62.78 | GGB | 171693.4 | GGB | 139427.69 | GGB | 0 | 0 | 3155 | 3600 | 3139.17 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 223598.91 | GGB | 223601.5 | 3139.17 | 2710.5663 |  |  |  | 1 | 1 |  |  |  |  | 139427.69 | 2710.5663 | 139427.69 | 2710.5663 | 9.5364 | [5 empty] | 121.5798 | 2710.5663 |  | 104.98
07.05.2008 22:00 | 3600 | 2 | 763.7 | GGB | 763.004 | 774.539 | 768.498 | 267.13 | GGB | 10903.8 | GGB | 9.79 | GGB | 1012.06 | GGB | 62.75 | GGB | 171671.39 | GGB | 139457.97 | GGB | 0 | 0 | 3142 | 3600 | 3126.11 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 223638.46 | GGB | 223641.06 | 3126.11 | 2709.9778 |  |  |  | 0 | 1 | [14 empty] | 121.1003 | 2709.9778 |  | 104.98
07.05.2008 23:00 | 3600 | 2 | 762.77 | GGB | 762.637 | 773.484 | 768.132 | 268.06 | GGB | 10930.1 | GGB | 9.78 | GGB | 1011.62 | GGB | 62.34 | GGB | 172965.39 | GGB | 140621.25 | GGB | 0 | 0 | 3194 | 3600 | 3177.77 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 223678.16 | GGB | 223680.76 | 3177.77 | 2687.5597 |  |  |  | 0 | 1 | [14 empty] | 124.1283 | 2687.5597 |  | 104.98
07.05.2008 24:00 | 3600 | 2 | 763.57 | GGB | 763.004 | 773.625 | 767.033 | 267.38 | GGB | 10940.3 | GGB | 9.79 | GGB | 1011.41 | GGB | 62.05 | GGB | 172541.76 | GGB | 140367.89 | GGB | 0 | 0 | 3144 | 3600 | 3128.17 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 223717.92 | GGB | 223720.52 | 3128.17 | 2692.4106 |  |  |  | 0 | 1 | [14 empty] | 121.9707 | 2692.4106 |  | 104.98
08.05.2008 01:00 | 3600 | 2 | 762.47 | GGB | 764.102 | 774.727 | 769.597 | 268.25 | GGB | 10971.3 | GGB | 9.78 | GGB | 1012.03 | GGB | 61.2 | GGB | 173438.54 | GGB | 141542.34 | GGB | 0 | 0 | 3218 | 3600 | 3202.35 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 223757.78 | GGB | 223760.38 | 3202.35 | 2670.0703 |  |  |  | 1 | 1 |  |  |  |  | 141542.34 | 2670.0703 | 141542.34 | 2670.0703 | 9.4814 | [5 empty] | 125.9078 | 2670.0703 |  | 104.98
08.05.2008 02:00 | 3600 | 2 | 762.03 | GGB | 761.538 | 772.594 | 767.033 | 268.54 | GGB | 10981.6 | GGB | 9.78 | GGB | 1012.32 | GGB | 61.21 | GGB | 173719.12 | GGB | 141809.04 | GGB | 0 | 0 | 3247 | 3600 | 3231.34 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 223797.67 | GGB | 223800.27 | 3231.34 | 2665.0487 |  |  |  | 0 | 1 | [14 empty] | 127.287 | 2665.0487 |  | 104.98
08.05.2008 03:00 | 3600 | 2 | 761.49 | GGB | 763.004 | 773.742 | 768.132 | 270.37 | GGB | 11029.4 | GGB | 9.77 | GGB | 1012.17 | GGB | 60.67 | GGB | 175475.26 | GGB | 143452.87 | GGB | 0 | 0 | 3296 | 3600 | 3280.55 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 223837.52 | GGB | 223840.12 | 3280.55 | 2634.5099 |  |  |  | 0 | 1 | [14 empty] | 130.7234 | 2634.5099 |  | 104.98
08.05.2008 04:00 | 3600 | 2 | 762.84 | GGB | 764.102 | 773.789 | 768.498 | 269.94 | GGB | 11057.2 | GGB | 9.8 | GGB | 1012.1 | GGB | 60.62 | GGB | 175142.96 | GGB | 143191.55 | GGB | 0 | 0 | 3236 | 3600 | 3220.12 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 223877.19 | GGB | 223879.79 | 3220.12 | 2639.3178 |  |  |  | 1 | 1 |  |  |  |  | 143191.55 | 2639.3178 | 143191.55 | 2639.3178 | 9.5268 | [5 empty] | 128.0817 | 2639.3178 |  | 104.98
08.05.2008 05:00 | 3600 | 2 | 761.7 | GGB | 762.637 | 772.477 | 767.033 | 269.5 | GGB | 11033.9 | GGB | 9.78 | GGB | 1011.93 | GGB | 60.63 | GGB | 175289.31 | GGB | 143284.09 | GGB | 0 | 0 | 3269 | 3600 | 3253.37 | GGB | 100 | GGB | 39.76 | GGB | 39.76 | GGB | 223916.95 | GGB | 223919.55 | 3253.37 | 2637.6132 |  |  |  | 0 | 1 | [14 empty] | 129.4878 | 2637.6132 |  | 104.98
08.05.2008 06:00 | 3600 | 2 | 762.06 | GGB | 761.538 | 771.609 | 765.934 | 270.22 | GGB | 11060.1 | GGB | 9.78 | GGB | 1012.06 | GGB | 60.52 | GGB | 175904.39 | GGB | 143850.97 | GGB | 0 | 0 | 3274 | 3600 | 3258.12 | GGB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 223956.73 | GGB | 223959.33 | 3258.12 | 2627.219 |  |  |  | 0 | 1 | [14 empty] | 130.1899 | 2627.219 |  | 104.98
08.05.2008 07:00 | 3600 | 2 | 761.18 | GGB | 761.538 | 771.68 | 767.033 | 271.23 | GGB | 11052.8 | GGB | 9.77 | GGB | 1012.31 | GGB | 60.53 | GGB | 176353.33 | GGB | 144250.68 | GGB | 0 | 0 | 3315 | 3600 | 3298.81 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 223996.43 | GGB | 223999.03 | 3298.81 | 2619.9391 |  |  |  | 0 | 1 | [14 empty] | 132.1821 | 2619.9391 |  | 104.98
08.05.2008 08:00 | 3600 | 2 | 761.79 | GGB | 761.538 | 771.586 | 765.934 | 271.9 | GGB | 11069.4 | GGB | 9.78 | GGB | 1012.24 | GGB | 60.52 | GGB | 176611.91 | GGB | 144453.7 | GGB | 0 | 0 | 3299 | 3600 | 3282.97 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 224036.09 | GGB | 224038.69 | 3282.97 | 2616.257 |  |  |  | 0 | 1 | [14 empty] | 131.7325 | 2616.257 |  | 104.98
08.05.2008 09:00 | 3600 | 2 | 762.37 | GGB | 764.102 | 773.859 | 769.597 | 272.3 | GGB | 11091.4 | GGB | 9.79 | GGB | 1012.47 | GGB | 60.49 | GGB | 177234.7 | GGB | 145012.21 | GGB | 0 | 0 | 3279 | 3600 | 3263.23 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 224075.68 | GGB | 224078.28 | 3263.23 | 2606.1805 |  |  |  | 1 | 1 |  |  |  |  | 145012.21 | 2606.1805 | 145012.21 | 2606.1805 | 9.546 | [5 empty] | 131.4467 | 2606.1805 |  | 104.98
08.05.2008 10:00 | 3600 | 2 | 763.01 | GGB | 764.102 | 774.984 | 769.597 | 271.32 | GGB | 11090.3 | GGB | 9.8 | GGB | 1013.09 | GGB | 60.92 | GGB | 176489.77 | GGB | 144304.91 | GGB | 0 | 0 | 3242 | 3600 | 3225.63 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 224115.13 | GGB | 224117.74 | 3225.63 | 2618.9545 |  |  |  | 1 | 1 |  |  |  |  | 144304.91 | 2618.9545 | 144304.91 | 2618.9545 | 9.5775 | [5 empty] | 129.2984 | 2618.9545 |  | 104.98
08.05.2008 11:00 | 3600 | 2 | 763.19 | GGB | 762.637 | 772.898 | 768.132 | 269.66 | GGB | 11036.2 | GGB | 9.8 | GGB | 1013.82 | GGB | 61.42 | GGB | 174830.46 | GGB | 142838.91 | GGB | 0 | 0 | 3215 | 3600 | 3199.59 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 224154.59 | GGB | 224157.19 | 3199.59 | 2645.8337 |  |  |  | 0 | 1 | [14 empty] | 126.9517 | 2645.8337 |  | 104.98
08.05.2008 12:00 | 3600 | 2 | 763.74 | GGB | 764.102 | 775.125 | 769.597 | 268.73 | GGB | 10996.7 | GGB | 9.8 | GGB | 1013.87 | GGB | 62 | GGB | 173786.24 | GGB | 141745.3 | GGB | 0 | 0 | 3182 | 3600 | 3166.06 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 224194.6 | GGB | 224197.21 | 3166.06 | 2666.2471 |  |  |  | 1 | 1 |  |  |  |  | 141745.3 | 2666.2471 | 141745.3 | 2666.2471 | 9.4435 | [5 empty] | 124.6595 | 2666.2471 |  | 104.98
08.05.2008 13:00 | 3600 | 2 | 763.75 | GGB | 763.004 | 774.094 | 768.498 | 267.42 | GGB | 10944.4 | GGB | 9.79 | GGB | 1013.27 | GGB | 62.22 | GGB | 172582.47 | GGB | 140586.76 | GGB | 0 | 0 | 3153 | 3600 | 3137.62 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 224234.47 | GGB | 224237.08 | 3137.62 | 2688.219 |  |  |  | 0 | 1 | [14 empty] | 122.53 | 2688.219 |  | 104.98
08.05.2008 14:00 | 3600 | 2 | 764.24 | GGB | 764.102 | 775.242 | 769.597 | 266.28 | GGB | 10908.5 | GGB | 9.8 | GGB | 1012.02 | GGB | 62.52 | GGB | 171632.88 | GGB | 139518.04 | GGB | 0 | 0 | 3107 | 3600 | 3091.58 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 224273.99 | GGB | 224276.6 | 3091.58 | 2708.811 |  |  |  | 1 | 1 |  |  |  |  | 139518.04 | 2708.811 | 139518.04 | 2708.811 | 9.563 | [5 empty] | 119.8142 | 2708.811 |  | 104.98
08.05.2008 15:00 | 3600 | 2 | 764.35 | GGB | 765.201 | 775.664 | 770.696 | 265.48 | GGB | 10859.2 | GGB | 9.79 | GGB | 1011.45 | GGB | 62.83 | GGB | 170750.41 | GGB | 138590.55 | GGB | 0 | 0 | 3072 | 3600 | 3056.4 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 224313.38 | GGB | 224316 | 3056.4 | 2726.9392 |  |  |  | 1 | 1 |  |  |  |  | 138590.55 | 2726.9392 | 138590.55 | 2726.9392 | 9.5921 | [5 empty] | 117.6634 | 2726.9392 |  | 104.98
08.05.2008 16:00 | 3600 | 2 | 764.58 | GGB | 765.201 | 775.453 | 770.696 | 264.3 | GGB | 10813 | GGB | 9.79 | GGB | 1010.71 | GGB | 63.21 | GGB | 169904.25 | GGB | 137649.15 | GGB | 0 | 0 | 3045 | 3600 | 3029.16 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 224352.69 | GGB | 224355.3 | 3029.16 | 2745.5891 |  |  |  | 1 | 1 |  |  |  |  | 137649.15 | 2745.5891 | 137649.15 | 2745.5891 | 9.6165 | [5 empty] | 115.8226 | 2745.5891 |  | 104.98
08.05.2008 17:00 | 3600 | 2 | 763.95 | GGB | 763.004 | 774.75 | 768.498 | 264.76 | GGB | 10803.6 | GGB | 9.78 | GGB | 1010.8 | GGB | 62.81 | GGB | 170169.43 | GGB | 138039 | GGB | 0 | 0 | 3046 | 3600 | 3030.53 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 224391.99 | GGB | 224394.6 | 3030.53 | 2737.835 |  |  |  | 0 | 1 | [14 empty] | 116.2031 | 2737.835 |  | 104.98
08.05.2008 18:00 | 3600 | 2 | 763.84 | GGB | 764.102 | 774.375 | 768.132 | 265.54 | GGB | 10831.5 | GGB | 9.78 | GGB | 1011.07 | GGB | 62.47 | GGB | 170930.87 | GGB | 138837.14 | GGB | 0 | 0 | 3071 | 3600 | 3054.88 | GGB | 100 | GGB | 39.32 | GGB | 39.32 | GGB | 224431.31 | GGB | 224433.92 | 3054.88 | 2722.0958 |  |  |  | 1 | 1 |  |  |  |  | 138837.14 | 2722.0958 | 138837.14 | 2722.0958 | 9.6116 | [5 empty] | 117.8141 | 2722.0958 |  | 104.98
08.05.2008 19:00 | 3600 | 2 | 763.59 | GGB | 766.3 | 776.367 | 771.795 | 267.86 | GGB | 10829 | GGB | 9.78 | GGB | 1011.6 | GGB | 62.02 | GGB | 173209.67 | GGB | 140952.26 | GGB | 0 | 0 | 3076 | 3600 | 3060.56 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 224470.73 | GGB | 224473.34 | 3060.56 | 2681.2482 |  |  |  | 1 | 1 |  |  |  |  | 140952.26 | 2681.2482 | 140952.26 | 2681.2482 | 9.5872 | [5 empty] | 119.8313 | 2681.2482 |  | 104.98
08.05.2008 20:00 | 3600 | 2 | 764.58 | GGB | 764.102 | 774.492 | 769.597 | 266.21 | GGB | 10831.1 | GGB | 9.8 | GGB | 1011.53 | GGB | 62.66 | GGB | 171340.19 | GGB | 139153.1 | GGB | 0 | 0 | 3027 | 3600 | 3011.63 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 224510.01 | GGB | 224512.62 | 3011.63 | 2715.9151 |  |  |  | 1 | 1 |  |  |  |  | 139153.1 | 2715.9151 | 139153.1 | 2715.9151 | 9.6214 | [5 empty] | 116.4105 | 2715.9151 |  | 104.98
08.05.2008 21:00 | 3600 | 2 | 763.36 | GGB | 762.637 | 773.391 | 768.132 | 265.73 | GGB | 10821.7 | GGB | 9.78 | GGB | 1011.43 | GGB | 63.25 | GGB | 170630.48 | GGB | 138319.33 | GGB | 0 | 0 | 3103 | 3600 | 3087.39 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 224549.22 | GGB | 224551.83 | 3087.39 | 2732.2862 |  |  |  | 0 | 1 | [14 empty] | 118.6238 | 2732.2862 |  | 104.98
08.05.2008 22:00 | 3600 | 2 | 763.63 | GGB | 760.44 | 772.172 | 765.934 | 265.71 | GGB | 10838.7 | GGB | 9.78 | GGB | 1011.94 | GGB | 63.31 | GGB | 170465.42 | GGB | 138230.05 | GGB | 0 | 0 | 3115 | 3600 | 3098.84 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 224588.44 | GGB | 224591.05 | 3098.84 | 2734.051 |  |  |  | 0 | 1 | [14 empty] | 118.9869 | 2734.051 |  | 104.98
08.05.2008 23:00 | 3600 | 2 | 762.84 | GGB | 763.004 | 773.555 | 768.498 | 268.23 | GGB | 10902.6 | GGB | 9.78 | GGB | 1012.66 | GGB | 62.73 | GGB | 172770.63 | GGB | 140443.3 | GGB | 0 | 0 | 3203 | 3600 | 3187.13 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 224627.72 | GGB | 224630.33 | 3187.13 | 2690.965 |  |  |  | 0 | 1 | [14 empty] | 124.3364 | 2690.965 |  | 104.98
08.05.2008 24:00 | 3600 | 2 | 762.16 | GGB | 761.538 | 772.453 | 767.033 | 269.81 | GGB | 10943.8 | GGB | 9.77 | GGB | 1013.18 | GGB | 62.39 | GGB | 174261.59 | GGB | 141871.62 | GGB | 0 | 0 | 3245 | 3600 | 3228.69 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 224667.03 | GGB | 224669.64 | 3228.69 | 2663.8732 |  |  |  | 0 | 1 | [14 empty] | 127.2387 | 2663.8732 |  | 104.98
09.05.2008 01:00 | 3600 | 2 | 762.34 | GGB | 765.201 | 775.734 | 769.597 | 270.71 | GGB | 11037.9 | GGB | 9.78 | GGB | 1013.78 | GGB | 61.68 | GGB | 176230.09 | GGB | 143861.91 | GGB | 0 | 0 | 3256 | 3600 | 3239.87 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 224706.56 | GGB | 224709.17 | 3239.87 | 2627.0192 |  |  |  | 1 | 1 |  |  |  |  | 143861.91 | 2627.0192 | 143861.91 | 2627.0192 | 9.5605 | [5 empty] | 129.4705 | 2627.0192 |  | 104.98
09.05.2008 02:00 | 3600 | 2 | 762.72 | GGB | 763.004 | 773.508 | 768.132 | 270.94 | GGB | 11048.5 | GGB | 9.79 | GGB | 1013.9 | GGB | 61.26 | GGB | 176226.79 | GGB | 144057.96 | GGB | 0 | 0 | 3248 | 3600 | 3232.03 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 224746.95 | GGB | 224749.57 | 3232.03 | 2623.4441 |  |  |  | 0 | 1 | [14 empty] | 129.3332 | 2623.4441 |  | 104.98
09.05.2008 03:00 | 3600 | 2 | 762.36 | GGB | 761.538 | 772.43 | 767.033 | 270.66 | GGB | 11050 | GGB | 9.78 | GGB | 1014 | GGB | 61.17 | GGB | 176505.18 | GGB | 144336.45 | GGB | 0 | 0 | 3259 | 3600 | 3243.09 | GGB | 100 | GGB | 41.9 | GGB | 41.9 | GGB | 224788.85 | GGB | 224791.47 | 3243.09 | 2618.3823 |  |  |  | 0 | 1 | [14 empty] | 130.0267 | 2618.3823 |  | 104.98
09.05.2008 04:00 | 3600 | 2 | 762.09 | GGB | 764.102 | 774.563 | 768.132 | 271.48 | GGB | 11082 | GGB | 9.78 | GGB | 1014.2 | GGB | 60.74 | GGB | 177465.77 | GGB | 145338.73 | GGB | 0 | 0 | 3291 | 3600 | 3275.58 | GGB | 100 | GGB | 41 | GGB | 41 | GGB | 224829.85 | GGB | 224832.47 | 3275.58 | 2600.3255 |  |  |  | 1 | 1 |  |  |  |  | 145338.73 | 2600.3255 | 145338.73 | 2600.3255 | 9.2178 | [5 empty] | 132.2413 | 2600.3255 |  | 104.98
09.05.2008 05:00 | 3600 | 2 | 762.02 | GGB | 760.44 | 770.531 | 764.835 | 271.53 | GGB | 11091.8 | GGB | 9.78 | GGB | 1014.41 | GGB | 60.53 | GGB | 177591.21 | GGB | 145564.03 | GGB | 0 | 0 | 3294 | 3600 | 3278.07 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 224869.69 | GGB | 224872.3 | 3278.07 | 2596.3007 |  |  |  | 0 | 1 | [14 empty] | 132.547 | 2596.3007 |  | 104.98
09.05.2008 06:00 | 3600 | 2 | 761.53 | GGB | 761.538 | 771.563 | 767.033 | 272.38 | GGB | 11132.7 | GGB | 9.78 | GGB | 1014.12 | GGB | 60.16 | GGB | 178450.58 | GGB | 146388.65 | GGB | 0 | 0 | 3325 | 3600 | 3309.22 | GNB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 224909.7 | GGB | 224912.32 | 3309.22 | 2581.6756 |  |  |  | 0 | 1 | [14 empty] | 134.5645 | 2581.6756 |  | 104.98
09.05.2008 07:00 | 3600 | 2 | 761.75 | GGB | 762.637 | 772.617 | 768.132 | 272.97 | GGB | 11155.3 | GGB | 9.79 | GGB | 1014.73 | GGB | 60.28 | GGB | 178879.71 | GGB | 146776.3 | GGB | 0 | 0 | 3327 | 3600 | 3310.68 | GNB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 224949.72 | GGB | 224952.33 | 3310.68 | 2574.8571 |  |  |  | 0 | 1 | [14 empty] | 134.9804 | 2574.8571 |  | 104.98
09.05.2008 08:00 | 3600 | 2 | 762.7 | GGB | 761.538 | 771.844 | 767.033 | 272.14 | GGB | 11136.2 | GGB | 9.8 | GGB | 1014.98 | GGB | 60.58 | GGB | 177801.38 | GGB | 145795.59 | GGB | 0 | 0 | 3284 | 3600 | 3267.96 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 224989.66 | GGB | 224992.27 | 3267.96 | 2592.1772 |  |  |  | 0 | 1 | [14 empty] | 132.3484 | 2592.1772 |  | 104.98
09.05.2008 09:00 | 3600 | 2 | 763.2 | GGB | 764.102 | 774 | 768.498 | 271.06 | GGB | 11092.2 | GGB | 9.8 | GGB | 1015.23 | GGB | 60.94 | GGB | 176138.77 | GGB | 144313.37 | GGB | 0 | 0 | 3248 | 3208 | 3232.25 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 225029.47 | GGB | 225032.08 | 3232.25 | 2618.801 |  |  |  | 1 | 1 |  |  |  |  | 144313.37 | 2618.801 | 144313.37 | 2618.801 | 9.4933 | [5 empty] | 129.5714 | 2618.801 |  | 104.98
09.05.2008 10:00 | 3600 | 2 | 764.05 | GGB | 764.102 | 775.125 | 769.597 | 268.85 | GGB | 11015.9 | GGB | 9.8 | GGB | 1015.61 | GGB | 61.92 | GGB | 174138.35 | GGB | 142310.6 | GGB | 0 | 0 | 3170 | 3600 | 3154.56 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 225069.24 | GGB | 225071.85 | 3154.56 | 2655.656 |  |  |  | 1 | 1 |  |  |  |  | 142310.6 | 2655.656 | 142310.6 | 2655.656 | 9.5028 | [5 empty] | 124.702 | 2655.656 |  | 104.98
09.05.2008 11:00 | 3600 | 2 | 764.17 | GGB | 765.201 | 776.414 | 769.597 | 267.24 | GGB | 10953.5 | GGB | 9.79 | GGB | 1015.76 | GGB | 62.15 | GGB | 172602.28 | GGB | 140978.88 | GGB | 0 | 0 | 3127 | 3600 | 3110.98 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 225109.62 | GGB | 225112.23 | 3110.98 | 2680.742 |  |  |  | 1 | 1 |  |  |  |  | 140978.88 | 2680.742 | 140978.88 | 2680.742 | 9.3593 | [5 empty] | 121.8285 | 2680.742 |  | 104.98
09.05.2008 12:00 | 3600 | 2 | 764.56 | GGB | 765.201 | 776.32 | 770.696 | 266.3 | GGB | 10920.1 | GGB | 9.8 | GGB | 1014.72 | GGB | 62.07 | GGB | 172521.96 | GGB | 140802 | GGB | 0 | 0 | 3081 | 3600 | 3065.25 | GGB | 100 | GGB | 40.38 | GGB | 40.38 | GGB | 225149.99 | GGB | 225152.61 | 3065.25 | 2684.1096 |  |  |  | 1 | 1 |  |  |  |  | 140802 | 2684.1096 | 140802 | 2684.1096 | 9.3593 | [5 empty] | 119.887 | 2684.1096 |  | 104.98
09.05.2008 13:00 | 3600 | 2 | 764.67 | GGB | 765.201 | 776.344 | 770.696 | 264.84 | GGB | 10885.1 | GGB | 9.79 | GGB | 1014.24 | GGB | 62.17 | GGB | 170970.48 | GGB | 139427.98 | GGB | 0 | 0 | 3050 | 3600 | 3034.25 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 225190.06 | GGB | 225192.68 | 3034.25 | 2710.5607 |  |  |  | 1 | 1 |  |  |  |  | 139427.98 | 2710.5607 | 139427.98 | 2710.5607 | 9.4317 | [5 empty] | 117.5165 | 2710.5607 |  | 104.98
09.05.2008 14:00 | 3600 | 2 | 764.7 | GGB | 764.102 | 775.477 | 769.597 | 263.81 | GGB | 10850.3 | GGB | 9.79 | GGB | 1014.04 | GGB | 62.27 | GGB | 170516.04 | GGB | 138988.27 | GGB | 0 | 0 | 3023 | 3600 | 3006.97 | GGB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 225229.7 | GGB | 225232.32 | 3006.97 | 2719.1359 |  |  |  | 1 | 1 |  |  |  |  | 138988.27 | 2719.1359 | 138988.27 | 2719.1359 | 9.534 | [5 empty] | 116.0927 | 2719.1359 |  | 104.98
09.05.2008 15:00 | 3600 | 2 | 764.81 | GGB | 764.102 | 774.656 | 769.597 | 262.95 | GGB | 10839.5 | GGB | 9.79 | GGB | 1014.17 | GGB | 62.02 | GGB | 170176.04 | GGB | 138832.71 | GGB | 0 | 0 | 3000 | 3600 | 2984.38 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 225269.35 | GGB | 225271.98 | 2984.38 | 2722.1827 |  |  |  | 1 | 1 |  |  |  |  | 138832.71 | 2722.1827 | 138832.71 | 2722.1827 | 9.5292 | [5 empty] | 115.0915 | 2722.1827 |  | 104.98
09.05.2008 16:00 | 3600 | 2 | 764.92 | GGB | 764.102 | 775.711 | 769.597 | 262.66 | GGB | 10824.3 | GGB | 9.79 | GGB | 1014.07 | GGB | 62.17 | GGB | 170173.84 | GGB | 138756.02 | GGB | 0 | 0 | 2981 | 3600 | 2965.56 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 225309.05 | GGB | 225311.68 | 2965.56 | 2723.6872 |  |  |  | 1 | 1 |  |  |  |  | 138756.02 | 2723.6872 | 138756.02 | 2723.6872 | 9.5196 | [5 empty] | 114.3026 | 2723.6872 |  | 104.98
09.05.2008 17:00 | 3600 | 2 | 765 | GGB | 765.201 | 776.602 | 770.696 | 261.63 | GGB | 10800.6 | GGB | 9.79 | GGB | 1013.55 | GGB | 62.34 | GGB | 169068 | GGB | 137711.06 | GGB | 0 | 0 | 2960 | 3600 | 2944.87 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 225348.51 | GGB | 225351.14 | 2944.87 | 2744.3547 |  |  |  | 1 | 1 |  |  |  |  | 137711.06 | 2744.3547 | 137711.06 | 2744.3547 | 9.5775 | [5 empty] | 112.6503 | 2744.3547 |  | 104.98
09.05.2008 18:00 | 3600 | 2 | 764.86 | GGB | 765.201 | 776.461 | 771.429 | 261.81 | GGB | 10809.3 | GGB | 9.79 | GGB | 1013.65 | GGB | 62.29 | GGB | 169121.91 | GGB | 137790.03 | GGB | 0 | 0 | 2968 | 3600 | 2952.31 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 225387.33 | GGB | 225389.95 | 2952.31 | 2742.7819 |  |  |  | 1 | 1 |  |  |  |  | 137790.03 | 2742.7819 | 137790.03 | 2742.7819 | 9.7379 | [5 empty] | 112.9997 | 2742.7819 |  | 104.98
09.05.2008 19:00 | 3600 | 2 | 764.97 | GGB | 765.201 | 776.203 | 770.33 | 261.09 | GGB | 10796.3 | GGB | 9.79 | GGB | 1013.68 | GGB | 62.28 | GGB | 168349.48 | GGB | 137169.68 | GGB | 0 | 0 | 2959 | 3600 | 2943.43 | GGB | 100 | GGB | 38.42 | GGB | 38.42 | GGB | 225425.75 | GGB | 225428.37 | 2943.43 | 2755.1861 |  |  |  | 1 | 1 |  |  |  |  | 137169.68 | 2755.1861 | 137169.68 | 2755.1861 | 9.8368 | [5 empty] | 112.1526 | 2755.1861 |  | 104.98
09.05.2008 20:00 | 3600 | 2 | 764.49 | GGB | 764.102 | 774.891 | 768.864 | 261.33 | GGB | 10797 | GGB | 9.78 | GGB | 1014.17 | GGB | 62.34 | GGB | 168666.37 | GGB | 137470.81 | GGB | 0 | 0 | 2997 | 3600 | 2981.34 | GGB | 100 | GGB | 39.37 | GGB | 39.37 | GGB | 225465.12 | GGB | 225467.74 | 2981.34 | 2749.1509 |  |  |  | 1 | 1 |  |  |  |  | 137470.81 | 2749.1509 | 137470.81 | 2749.1509 | 9.5994 | [5 empty] | 113.8465 | 2749.1509 |  | 104.98
09.05.2008 21:00 | 3600 | 2 | 764.26 | GGB | 764.102 | 774.891 | 768.864 | 262.45 | GGB | 10826.5 | GGB | 9.78 | GGB | 1014.44 | GGB | 61.77 | GGB | 169327.68 | GGB | 138282.1 | GGB | 0 | 0 | 3024 | 3600 | 3008.51 | GGB | 100 | GGB | 39.99 | GGB | 39.99 | GGB | 225505.11 | GGB | 225507.73 | 3008.51 | 2733.0218 |  |  |  | 1 | 1 |  |  |  |  | 138282.1 | 2733.0218 | 138282.1 | 2733.0218 | 9.4506 | [5 empty] | 115.562 | 2733.0218 |  | 104.98
09.05.2008 22:00 | 3600 | 2 | 764.23 | GGB | 764.102 | 774.82 | 769.597 | 262.6 | GGB | 10846 | GGB | 9.79 | GGB | 1015.04 | GGB | 61.75 | GGB | 169436.61 | GGB | 138461.1 | GGB | 0 | 0 | 3024 | 3600 | 3008.49 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 225544.7 | GGB | 225547.32 | 3008.49 | 2729.4886 |  |  |  | 1 | 1 |  |  |  |  | 138461.1 | 2729.4886 | 138461.1 | 2729.4886 | 9.546 | [5 empty] | 115.7108 | 2729.4886 |  | 104.98
09.05.2008 23:00 | 3600 | 2 | 764.08 | GGB | 764.102 | 774.727 | 768.498 | 262.66 | GGB | 10879.9 | GGB | 9.79 | GGB | 1015.57 | GGB | 61.55 | GGB | 170112.22 | GGB | 139167.67 | GGB | 0 | 0 | 3034 | 3600 | 3018.26 | GGB | 100 | GGB | 39.45 | GGB | 39.45 | GGB | 225584.16 | GGB | 225586.77 | 3018.26 | 2715.6307 |  |  |  | 1 | 1 |  |  |  |  | 139167.67 | 2715.6307 | 139167.67 | 2715.6307 | 9.5799 | [5 empty] | 116.6789 | 2715.6307 |  | 104.98
09.05.2008 24:00 | 3600 | 2 | 762.69 | GGB | 763.004 | 773.648 | 768.132 | 264.99 | GGB | 10907.8 | GGB | 9.77 | GGB | 1016.28 | GGB | 61.74 | GGB | 171741.82 | GGB | 140519.29 | GGB | 0 | 0 | 3158 | 3600 | 3141.74 | GGB | 100 | GGB | 38.64 | GGB | 38.64 | GGB | 225622.79 | GGB | 225625.41 | 3141.74 | 2689.5097 |  |  |  | 0 | 1 | [14 empty] | 122.632 | 2689.5097 |  | 104.98
10.05.2008 01:00 | 3600 | 2 | 762.89 | GGB | 763.004 | 773.836 | 768.498 | 267.03 | GGB | 10918.7 | GGB | 9.78 | GGB | 1016.71 | GGB | 61.08 | GGB | 174210.97 | GGB | 142878.94 | GGB | 0 | 0 | 3157 | 3600 | 3141.59 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 225662.11 | GGB | 225664.72 | 3141.59 | 2645.0924 |  |  |  | 0 | 1 | [14 empty] | 124.6853 | 2645.0924 |  | 104.98
10.05.2008 02:00 | 3600 | 2 | 763.35 | GGB | 762.637 | 772.711 | 768.132 | 266.55 | GGB | 10966.7 | GGB | 9.79 | GGB | 1017.13 | GGB | 61.1 | GGB | 173343.91 | GGB | 142219.72 | GGB | 0 | 0 | 3160 | 3600 | 3143.76 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 225702.24 | GGB | 225704.85 | 3143.76 | 2657.353 |  |  |  | 0 | 1 | [14 empty] | 124.1957 | 2657.353 |  | 104.98
10.05.2008 03:00 | 3600 | 2 | 762.93 | GGB | 763.004 | 774.656 | 768.132 | 266.53 | GGB | 10980.5 | GGB | 9.78 | GGB | 1017.45 | GGB | 61.27 | GGB | 172935.68 | GGB | 141858.53 | GGB | 0 | 0 | 3195 | 3600 | 3179.28 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 225742.33 | GGB | 225744.94 | 3179.28 | 2664.119 |  |  |  | 0 | 1 | [14 empty] | 125.28 | 2664.119 |  | 104.98
10.05.2008 04:00 | 3600 | 2 | 762.14 | GGB | 761.538 | 772.5 | 766.667 | 267.53 | GGB | 11006 | GGB | 9.78 | GGB | 1017.73 | GGB | 61.2 | GGB | 173905.08 | GGB | 142722.37 | GGB | 0 | 0 | 3256 | 3600 | 3239.67 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 225782.42 | GGB | 225785.03 | 3239.67 | 2647.9941 |  |  |  | 0 | 1 | [14 empty] | 128.4371 | 2647.9941 |  | 104.98
10.05.2008 05:00 | 3600 | 2 | 762.9 | GGB | 764.102 | 774.633 | 768.864 | 267.66 | GGB | 11028.8 | GGB | 9.79 | GGB | 1017.92 | GGB | 61.03 | GGB | 174049.22 | GGB | 142942.77 | GGB | 0 | 0 | 3232 | 3600 | 3216.2 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 225822.36 | GGB | 225824.97 | 3216.2 | 2643.9113 |  |  |  | 1 | 1 |  |  |  |  | 142942.77 | 2643.9113 | 142942.77 | 2643.9113 | 9.4624 | [5 empty] | 127.7035 | 2643.9113 |  | 104.98
10.05.2008 06:00 | 3600 | 2 | 762.4 | GGB | 761.538 | 772.477 | 766.667 | 267.75 | GGB | 11023.5 | GGB | 9.78 | GGB | 1018.24 | GGB | 60.82 | GGB | 174215.38 | GGB | 143210.1 | GGB | 0 | 0 | 3255 | 3600 | 3239.03 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 225862.23 | GGB | 225864.85 | 3239.03 | 2638.9759 |  |  |  | 0 | 1 | [14 empty] | 128.8505 | 2638.9759 |  | 104.98
10.05.2008 07:00 | 3600 | 2 | 762.64 | GGB | 762.637 | 773.414 | 767.766 | 268.03 | GGB | 11047.5 | GGB | 9.79 | GGB | 1018.37 | GGB | 60.74 | GGB | 174651.11 | GGB | 143621.78 | GGB | 0 | 0 | 3261 | 3600 | 3245.3 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 225902.12 | GGB | 225904.73 | 3245.3 | 2631.4115 |  |  |  | 0 | 1 | [14 empty] | 129.471 | 2631.4115 |  | 104.98
10.05.2008 08:00 | 3600 | 2 | 763.51 | GGB | 764.102 | 774.492 | 768.864 | 267.17 | GGB | 11029 | GGB | 9.8 | GGB | 1018.63 | GGB | 60.95 | GGB | 173368.12 | GGB | 142512.34 | GGB | 0 | 0 | 3208 | 3600 | 3191.73 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 225942.26 | GGB | 225944.88 | 3191.73 | 2651.8967 |  |  |  | 1 | 1 |  |  |  |  | 142512.34 | 2651.8967 | 142512.34 | 2651.8967 | 9.4129 | [5 empty] | 126.3503 | 2651.8967 |  | 104.98
10.05.2008 09:00 | 3600 | 2 | 764.37 | GGB | 765.201 | 775.5 | 769.963 | 265.09 | GGB | 10965.3 | GGB | 9.8 | GGB | 1018.77 | GGB | 61.75 | GGB | 171205.95 | GGB | 140419.83 | GGB | 0 | 0 | 3128 | 3600 | 3111.82 | GGB | 100 | GGB | 40.08 | GGB | 40.08 | GGB | 225982.34 | GGB | 225984.96 | 3111.82 | 2691.4147 |  |  |  | 1 | 1 |  |  |  |  | 140419.83 | 2691.4147 | 140419.83 | 2691.4147 | 9.4293 | [5 empty] | 121.3781 | 2691.4147 |  | 104.98
10.05.2008 10:00 | 3600 | 2 | 764.81 | GGB | 765.201 | 776.719 | 771.429 | 263.36 | GGB | 10894.8 | GGB | 9.8 | GGB | 1018.66 | GGB | 62.35 | GGB | 169335.38 | GGB | 138621.88 | GGB | 0 | 0 | 3067 | 3600 | 3050.87 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 226022.44 | GGB | 226025.07 | 3050.87 | 2726.3229 |  |  |  | 1 | 1 |  |  |  |  | 138621.88 | 2726.3229 | 138621.88 | 2726.3229 | 9.4223 | [5 empty] | 117.477 | 2726.3229 |  | 104.98
10.05.2008 11:00 | 3600 | 2 | 765.43 | GGB | 765.201 | 776.742 | 769.963 | 261.49 | GGB | 10816.6 | GGB | 9.79 | GGB | 1018.26 | GGB | 62.92 | GGB | 167722.28 | GGB | 137013.81 | GGB | 0 | 0 | 3003 | 3600 | 2987.63 | GGB | 100 | GGB | 39.83 | GGB | 39.83 | GGB | 226062.28 | GGB | 226064.9 | 2987.63 | 2758.3205 |  |  |  | 1 | 1 |  |  |  |  | 137013.81 | 2758.3205 | 137013.81 | 2758.3205 | 9.4885 | [5 empty] | 113.7074 | 2758.3205 |  | 104.98
10.05.2008 12:00 | 3600 | 2 | 765.66 | GGB | 764.102 | 775.805 | 768.864 | 260.49 | GGB | 10767.6 | GGB | 9.79 | GGB | 1017.56 | GGB | 63.3 | GGB | 166649.45 | GGB | 135890.16 | GGB | 0 | 0 | 2974 | 3600 | 2958.43 | GGB | 100 | GGB | 39.66 | GGB | 39.66 | GGB | 226101.94 | GGB | 226104.56 | 2958.43 | 2781.1285 |  |  |  | 1 | 1 |  |  |  |  | 135890.16 | 2781.1285 | 135890.16 | 2781.1285 | 9.5292 | [5 empty] | 111.6726 | 2781.1285 |  | 104.98
10.05.2008 13:00 | 3600 | 2 | 765.7 | GGB | 764.102 | 776.039 | 770.33 | 259.49 | GGB | 10721.2 | GGB | 9.79 | GGB | 1016.39 | GGB | 63.56 | GGB | 165914.43 | GGB | 135031.47 | GGB | 0 | 0 | 2954 | 3600 | 2938.09 | GGB | 100 | GGB | 39.56 | GGB | 39.56 | GGB | 226141.5 | GGB | 226144.12 | 2938.09 | 2798.8142 |  |  |  | 1 | 1 |  |  |  |  | 135031.47 | 2798.8142 | 135031.47 | 2798.8142 | 9.5533 | [5 empty] | 110.2041 | 2798.8142 |  | 104.98
10.05.2008 14:00 | 3600 | 2 | 765.76 | GGB | 766.3 | 777.164 | 771.429 | 258.82 | GGB | 10700.2 | GGB | 9.79 | GGB | 1015.86 | GGB | 63.63 | GGB | 165214.61 | GGB | 134365.6 | GGB | 0 | 0 | 2931 | 3600 | 2915.3 | GGB | 100 | GGB | 39.2 | GGB | 39.2 | GGB | 226180.7 | GGB | 226183.32 | 2915.3 | 2812.6842 |  |  |  | 1 | 1 |  |  |  |  | 134365.6 | 2812.6842 | 134365.6 | 2812.6842 | 9.641 | [5 empty] | 108.81 | 2812.6842 |  | 104.98
10.05.2008 15:00 | 3600 | 2 | 766.29 | GGB | 765.201 | 776.977 | 770.696 | 257.65 | GGB | 10647.6 | GGB | 9.79 | GGB | 1015.18 | GGB | 64.4 | GGB | 163993.24 | GGB | 132976.71 | GGB | 0 | 0 | 2898 | 3600 | 2882.04 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 226219.61 | GGB | 226222.23 | 2882.04 | 2842.0616 |  |  |  | 1 | 1 |  |  |  |  | 132976.71 | 2842.0616 | 132976.71 | 2842.0616 | 9.7129 | [5 empty] | 106.4567 | 2842.0616 |  | 104.98
10.05.2008 16:00 | 3600 | 2 | 766.33 | GGB | 765.201 | 776.086 | 770.696 | 256.54 | GGB | 10603.9 | GGB | 9.79 | GGB | 1014.24 | GGB | 64.51 | GGB | 162956.72 | GGB | 131970.99 | GGB | 0 | 0 | 2877 | 3600 | 2861.08 | GGB | 100 | GGB | 38.71 | GGB | 38.71 | GGB | 226258.32 | GGB | 226260.94 | 2861.08 | 2861.08 |  |  |  | 1 | 1 |  |  |  |  | 131970.99 | 2861.08 | 131970.99 | 2861.08 | 9.7541 | [5 empty] | 104.8832 |  |  | #VALUE!
10.05.2008 17:00 | 3600 | 2 | 766.56 | GGB | 765.201 | 777.047 | 771.795 | 256.02 | GGB | 10578.6 | GGB | 9.79 | GGB | 1013.52 | GGB | 64.58 | GGB | 162462.67 | GGB | 131448.94 | GGB | 0 | 0 | 2845 | 3600 | 2829.88 | GGB | 100 | GGB | 38.6 | GGB | 38.6 | GGB | 226296.91 | GGB | 226299.54 | 2829.88 | 2829.88 |  |  |  | 1 | 1 |  |  |  |  | 131448.94 | 2829.88 | 131448.94 | 2829.88 | 9.6369 | [5 empty] | 103.3291 |  |  | #VALUE!
10.05.2008 18:00 | 3600 | 2 | 766.73 | GGB | 765.201 | 777.141 | 770.696 | 255.79 | GGB | 10557.6 | GGB | 9.78 | GGB | 1013.05 | GGB | 64.9 | GGB | 162353.73 | GGB | 131177.49 | GGB | 0 | 0 | 2826 | 3600 | 2810.89 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 226335.43 | GGB | 226338.05 | 2810.89 | 2810.89 |  |  |  | 1 | 1 |  |  |  |  | 131177.49 | 2810.89 | 131177.49 | 2810.89 | 9.5748 | [5 empty] | 102.4237 |  |  | #VALUE!
10.05.2008 19:00 | 3600 | 2 | 766.41 | GGB | 763.004 | 774.75 | 769.597 | 256.56 | GGB | 10581.3 | GGB | 9.78 | GGB | 1013.15 | GGB | 64.51 | GGB | 163008.44 | GGB | 131870.12 | GGB | 0 | 0 | 2857 | 3600 | 2841.83 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 226373.93 | GGB | 226376.55 | 2841.83 | 2841.83 |  |  |  | 0 | 1 | [14 empty] | 104.0979 |  |  | #VALUE!
10.05.2008 20:00 | 3600 | 2 | 766.01 | GGB | 764.102 | 775.5 | 770.696 | 257.97 | GGB | 10618.3 | GGB | 9.78 | GGB | 1013.38 | GGB | 64.05 | GGB | 163997.64 | GGB | 132881.34 | GGB | 0 | 0 | 2885 | 3600 | 2869.41 | GGB | 100 | GGB | 38.57 | GGB | 38.57 | GGB | 226412.5 | GGB | 226415.12 | 2869.41 | 2844.1014 |  |  |  | 1 | 1 |  |  |  |  | 132881.34 | 2844.1014 | 132881.34 | 2844.1014 | 9.7985 | [5 empty] | 105.9142 | 2844.1014 |  | 104.98
10.05.2008 21:00 | 3600 | 2 | 765 | GGB | 763.004 | 774.281 | 768.498 | 258.98 | GGB | 10688.2 | GGB | 9.77 | GGB | 1014.16 | GGB | 63.86 | GGB | 164857 | GGB | 133756.73 | GGB | 0 | 0 | 2962 | 3600 | 2946.18 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 226451.29 | GGB | 226453.91 | 2946.18 | 2825.4877 |  |  |  | 0 | 1 | [14 empty] | 109.4643 | 2825.4877 |  | 104.98
10.05.2008 22:00 | 3600 | 2 | 763.8 | GGB | 762.637 | 774.281 | 768.132 | 262.08 | GGB | 10770.6 | GGB | 9.77 | GGB | 1015.45 | GGB | 63.43 | GGB | 167495.61 | GGB | 136242.97 | GGB | 0 | 0 | 3081 | 3600 | 3065.37 | GGB | 100 | GGB | 38.91 | GGB | 38.91 | GGB | 226490.2 | GGB | 226492.82 | 3065.37 | 2773.9266 |  |  |  | 0 | 1 | [14 empty] | 116.0098 | 2773.9266 |  | 104.98
10.05.2008 23:00 | 3600 | 2 | 763.32 | GGB | 761.538 | 773.297 | 767.033 | 263.69 | GGB | 10852.1 | GGB | 9.77 | GGB | 1016.55 | GGB | 62.9 | GGB | 169442.11 | GGB | 138196.26 | GGB | 0 | 0 | 3139 | 3600 | 3123.22 | GGB | 100 | GGB | 39.29 | GGB | 39.29 | GGB | 226529.49 | GGB | 226532.11 | 3123.22 | 2734.7194 |  |  |  | 0 | 1 | [14 empty] | 119.8937 | 2734.7194 |  | 104.98
10.05.2008 24:00 | 3600 | 2 | 763.69 | GGB | 763.004 | 774.375 | 768.132 | 264.95 | GGB | 10910.4 | GGB | 9.79 | GGB | 1017.28 | GGB | 62.54 | GGB | 170480.83 | GGB | 139290.95 | GGB | 0 | 0 | 3164 | 3600 | 3147.85 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 226569.01 | GGB | 226571.63 | 3147.85 | 2713.2272 |  |  |  | 0 | 1 | [14 empty] | 121.7964 | 2713.2272 |  | 104.98
11.05.2008 01:00 | 3600 | 2 | 763.67 | GGB | 763.004 | 774.352 | 767.033 | 264.87 | GGB | 10904.6 | GGB | 9.78 | GGB | 1017.34 | GGB | 62.52 | GGB | 170433.51 | GGB | 139267.95 | GGB | 0 | 0 | 3159 | 3600 | 3142.9 | GGB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 226608.82 | GGB | 226611.44 | 3142.9 | 2713.6753 |  |  |  | 0 | 1 | [14 empty] | 121.5848 | 2713.6753 |  | 104.98
11.05.2008 02:00 | 3600 | 2 | 763.05 | GGB | 762.637 | 774.352 | 768.132 | 265.93 | GGB | 10938.5 | GGB | 9.78 | GGB | 1017.77 | GGB | 62.24 | GGB | 171564.66 | GGB | 140368.91 | GGB | 0 | 0 | 3210 | 3600 | 3194.59 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 226648.74 | GGB | 226651.37 | 3194.59 | 2692.3911 |  |  |  | 0 | 1 | [14 empty] | 124.5614 | 2692.3911 |  | 104.98
11.05.2008 03:00 | 3600 | 2 | 762.94 | GGB | 763.004 | 774.328 | 768.132 | 267.28 | GGB | 10983.3 | GGB | 9.78 | GGB | 1018.19 | GGB | 61.96 | GGB | 172974.19 | GGB | 141699.01 | GGB | 0 | 0 | 3238 | 3600 | 3222.14 | GGB | 100 | GGB | 39.79 | GGB | 39.79 | GGB | 226688.53 | GGB | 226691.16 | 3222.14 | 2667.1181 |  |  |  | 0 | 1 | [14 empty] | 126.8261 | 2667.1181 |  | 104.98
11.05.2008 04:00 | 3600 | 2 | 762.36 | GGB | 761.538 | 772.172 | 767.033 | 267.86 | GGB | 11005.3 | GGB | 9.78 | GGB | 1018.59 | GGB | 61.61 | GGB | 173565.08 | GGB | 142387.39 | GGB | 0 | 0 | 3269 | 3600 | 3253.13 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 226727.91 | GGB | 226730.55 | 3253.13 | 2654.2238 |  |  |  | 0 | 1 | [14 empty] | 128.668 | 2654.2238 |  | 104.98
11.05.2008 05:00 | 3600 | 2 | 761.74 | GGB | 761.538 | 772.172 | 765.934 | 269.37 | GGB | 11049.8 | GGB | 9.77 | GGB | 1018.72 | GGB | 61.16 | GGB | 175279.4 | GGB | 144005.86 | GGB | 0 | 0 | 3317 | 3600 | 3301 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 226767.25 | GGB | 226769.89 | 3301 | 2624.3932 |  |  |  | 0 | 1 | [14 empty] | 132.0454 | 2624.3932 |  | 104.98
11.05.2008 06:00 | 3600 | 2 | 761.75 | GGB | 760.44 | 771.188 | 764.835 | 269.71 | GGB | 11090.4 | GGB | 9.78 | GGB | 1019.13 | GGB | 60.72 | GGB | 176200.39 | GGB | 145013.22 | GGB | 0 | 0 | 3332 | 3600 | 3315.9 | GNB | 100 | GGB | 40.62 | GGB | 40.62 | GGB | 226807.87 | GGB | 226810.51 | 3315.9 | 2606.1624 |  |  |  | 0 | 1 | [14 empty] | 133.5693 | 2606.1624 |  | 104.98
11.05.2008 07:00 | 3600 | 2 | 761.98 | GGB | 761.538 | 772.242 | 767.033 | 270.21 | GGB | 11118 | GGB | 9.79 | GGB | 1019.2 | GGB | 60.6 | GGB | 176715.34 | GGB | 145499.55 | GGB | 0 | 0 | 3339 | 3600 | 3322.69 | GNB | 100 | GGB | 40.91 | GGB | 40.91 | GGB | 226848.78 | GGB | 226851.42 | 3322.69 | 2597.4513 |  |  |  | 0 | 1 | [14 empty] | 134.2916 | 2597.4513 |  | 104.98
11.05.2008 08:00 | 3600 | 2 | 763.68 | GGB | 764.102 | 774.516 | 768.498 | 268.12 | GGB | 11090.8 | GGB | 9.82 | GGB | 1019.27 | GGB | 61.07 | GGB | 174366.12 | GGB | 143374.39 | GGB | 0 | 0 | 3247 | 3600 | 3230.68 | GGB | 100 | GGB | 40.82 | GGB | 40.82 | GGB | 226889.6 | GGB | 226892.24 | 3230.68 | 2635.9519 |  |  |  | 1 | 1 |  |  |  |  | 143374.39 | 2635.9519 | 143374.39 | 2635.9519 | 9.2584 | [5 empty] | 128.6658 | 2635.9519 |  | 104.98
11.05.2008 09:00 | 3600 | 2 | 764.45 | GGB | 764.102 | 775.359 | 769.597 | 265.1 | GGB | 10971.4 | GGB | 9.81 | GGB | 1018.91 | GGB | 61.9 | GGB | 170784.52 | GGB | 140030.41 | GGB | 0 | 0 | 3175 | 3600 | 3159.37 | GGB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 226930.32 | GGB | 226932.96 | 3159.37 | 2698.8995 |  |  |  | 1 | 1 |  |  |  |  | 140030.41 | 2698.8995 | 140030.41 | 2698.8995 | 9.2811 | [5 empty] | 122.8911 | 2698.8995 |  | 104.98
11.05.2008 10:00 | 3600 | 2 | 765.09 | GGB | 765.201 | 775.336 | 770.696 | 262.79 | GGB | 10862.4 | GGB | 9.8 | GGB | 1018.73 | GGB | 63.03 | GGB | 168051.28 | GGB | 137300.95 | GGB | 0 | 0 | 3086 | 3600 | 3070.09 | GGB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 226970.8 | GGB | 226973.44 | 3070.09 | 2752.552 |  |  |  | 1 | 1 |  |  |  |  | 137300.95 | 2752.552 | 137300.95 | 2752.552 | 9.3362 | [5 empty] | 117.0906 | 2752.552 |  | 104.98
11.05.2008 11:00 | 3600 | 2 | 765.38 | GGB | 765.201 | 775.57 | 769.597 | 261.38 | GGB | 10777.7 | GGB | 9.79 | GGB | 1016.87 | GGB | 63.76 | GGB | 166577.93 | GGB | 135557.18 | GGB | 0 | 0 | 3028 | 3600 | 3012.62 | GGB | 100 | GGB | 40.1 | GGB | 40.1 | GGB | 227010.9 | GGB | 227013.54 | 3012.62 | 2787.96 |  |  |  | 1 | 1 |  |  |  |  | 135557.18 | 2787.96 | 135557.18 | 2787.96 | 9.4246 | [5 empty] | 113.4395 | 2787.96 |  | 104.98
11.05.2008 12:00 | 3600 | 2 | 765.64 | GGB | 764.102 | 775.313 | 769.597 | 259.96 | GGB | 10711.1 | GGB | 9.79 | GGB | 1016.13 | GGB | 64.33 | GGB | 165019.85 | GGB | 133963.52 | GGB | 0 | 0 | 2982 | 3600 | 2966.33 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 227050.63 | GGB | 227053.28 | 2966.33 | 2821.1262 |  |  |  | 1 | 1 |  |  |  |  | 133963.52 | 2821.1262 | 133963.52 | 2821.1262 | 9.51 | [5 empty] | 110.3833 | 2821.1262 |  | 104.98
11.05.2008 13:00 | 3600 | 2 | 766.16 | GGB | 765.201 | 776.602 | 770.696 | 258.79 | GGB | 10663.5 | GGB | 9.79 | GGB | 1014.95 | GGB | 64.54 | GGB | 164261.72 | GGB | 133111.76 | GGB | 0 | 0 | 2938 | 3600 | 2922.22 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 227090.14 | GGB | 227092.79 | 2922.22 | 2839.1781 |  |  |  | 1 | 1 |  |  |  |  | 133111.76 | 2839.1781 | 133111.76 | 2839.1781 | 9.5654 | [5 empty] | 108.0505 | 2839.1781 |  | 104.98
11.05.2008 14:00 | 3600 | 2 | 766.22 | GGB | 765.201 | 776.484 | 770.696 | 258.29 | GGB | 10629.1 | GGB | 9.78 | GGB | 1014.24 | GGB | 64.47 | GGB | 163872.2 | GGB | 132727.4 | GGB | 0 | 0 | 2904 | 3600 | 2888.56 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 227129.51 | GGB | 227132.15 | 2888.56 | 2847.4 |  |  |  | 1 | 1 |  |  |  |  | 132727.4 | 2847.4 | 132727.4 | 2847.4 | 9.6018 | [5 empty] | 106.4975 | 2847.4 |  | 104.98
11.05.2008 15:00 | 3600 | 2 | 766.62 | GGB | 766.3 | 777.445 | 771.795 | 257.26 | GGB | 10603.3 | GGB | 9.79 | GGB | 1013.53 | GGB | 64.62 | GGB | 163183.39 | GGB | 132019.28 | GGB | 0 | 0 | 2867 | 3600 | 2851 | GGB | 100 | GGB | 39.26 | GGB | 39.26 | GGB | 227168.76 | GGB | 227171.41 | 2851 | 2851 |  |  |  | 1 | 1 |  |  |  |  | 132019.28 | 2851 | 132019.28 | 2851 | 9.587 | [5 empty] | 104.5519 |  |  | #VALUE!
11.05.2008 16:00 | 3600 | 2 | 767.33 | GGB | 765.201 | 777.422 | 771.795 | 256.23 | GGB | 10569.1 | GGB | 9.79 | GGB | 1012.56 | GGB | 64.57 | GGB | 162845.59 | GGB | 131638.09 | GGB | 0 | 0 | 2803 | 3600 | 2787.47 | GGB | 100 | GGB | 39.18 | GGB | 39.18 | GGB | 227207.95 | GGB | 227210.59 | 2787.47 | 2787.47 |  |  |  | 1 | 1 |  |  |  |  | 131638.09 | 2787.47 | 131638.09 | 2787.47 | 9.3654 | [5 empty] | 101.927 |  |  | #VALUE!
11.05.2008 17:00 | 3600 | 2 | 767.06 | GGB | 766.3 | 777.328 | 772.161 | 255.4 | GGB | 10545 | GGB | 9.78 | GGB | 1011.49 | GGB | 64.65 | GGB | 162285.51 | GGB | 131014.81 | GGB | 0 | 0 | 2802 | 3600 | 2786.63 | GGB | 100 | GGB | 38.72 | GGB | 38.72 | GGB | 227246.66 | GGB | 227249.31 | 2786.63 | 2786.63 |  |  |  | 1 | 1 |  |  |  |  | 131014.81 | 2786.63 | 131014.81 | 2786.63 | 9.429 | [5 empty] | 101.4138 |  |  | #VALUE!
11.05.2008 18:00 | 3600 | 2 | 766.97 | GGB | 765.201 | 777.352 | 770.696 | 255.04 | GGB | 10530.4 | GGB | 9.78 | GGB | 1010.94 | GGB | 64.64 | GGB | 161975.22 | GGB | 130701.34 | GGB | 0 | 0 | 2791 | 3600 | 2775.6 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 227285.14 | GGB | 227287.79 | 2775.6 | 2775.6 |  |  |  | 1 | 1 |  |  |  |  | 130701.34 | 2775.6 | 130701.34 | 2775.6 | 9.4276 | [5 empty] | 100.7707 |  |  | #VALUE!
11.05.2008 19:00 | 3600 | 2 | 767.23 | GGB | 765.201 | 777.281 | 771.795 | 254.68 | GGB | 10521.8 | GGB | 9.78 | GGB | 1010.27 | GGB | 64.71 | GGB | 161679.23 | GGB | 130346.85 | GGB | 0 | 0 | 2785 | 3600 | 2769.16 | GGB | 100 | GGB | 36.99 | GGB | 36.99 | GGB | 227322.13 | GGB | 227324.78 | 2769.16 | 2769.16 |  |  |  | 1 | 1 |  |  |  |  | 130346.85 | 2769.16 | 130346.85 | 2769.16 | 9.7581 | [5 empty] | 100.2642 |  |  | #VALUE!
11.05.2008 20:00 | 3600 | 2 | 766.7 | GGB | 765.201 | 777.305 | 770.696 | 254.98 | GGB | 10529.5 | GGB | 9.78 | GGB | 1010.19 | GGB | 64.64 | GGB | 161788.16 | GGB | 130452.66 | GGB | 0 | 0 | 2808 | 3600 | 2792.01 | GGB | 100 | GGB | 37.02 | GGB | 37.02 | GGB | 227359.15 | GGB | 227361.8 | 2792.01 | 2792.01 |  |  |  | 1 | 1 |  |  |  |  | 130452.66 | 2792.01 | 130452.66 | 2792.01 | 9.8386 | [5 empty] | 101.1736 |  |  | #VALUE!
11.05.2008 21:00 | 3600 | 2 | 765.62 | GGB | 763.004 | 775.242 | 769.597 | 256.63 | GGB | 10592.7 | GGB | 9.77 | GGB | 1010.31 | GGB | 64.1 | GGB | 163156.98 | GGB | 131781.86 | GGB | 0 | 0 | 2884 | 3600 | 2868.21 | GGB | 100 | GGB | 37.18 | GGB | 37.18 | GGB | 227396.33 | GGB | 227398.98 | 2868.21 | 2867.8302 |  |  |  | 0 | 1 | [14 empty] | 104.9939 | 2867.8302 |  | 104.98
11.05.2008 22:00 | 3600 | 2 | 764.1 | GGB | 761.538 | 774.047 | 767.033 | 260.4 | GGB | 10703.2 | GGB | 9.76 | GGB | 1011.54 | GGB | 63.48 | GGB | 166185.11 | GGB | 134638.95 | GGB | 0 | 0 | 3038 | 3600 | 3022.26 | GGB | 100 | GGB | 37.65 | GGB | 37.65 | GGB | 227433.99 | GGB | 227436.63 | 3022.26 | 2806.9738 |  |  |  | 0 | 1 | [14 empty] | 113.0316 | 2806.9738 |  | 104.98
11.05.2008 23:00 | 3600 | 2 | 763.78 | GGB | 762.637 | 773.133 | 768.132 | 262.48 | GGB | 10797.9 | GGB | 9.77 | GGB | 1012.36 | GGB | 63.05 | GGB | 168077.69 | GGB | 136455.41 | GGB | 0 | 0 | 3104 | 3600 | 3088.5 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 227474.86 | GGB | 227477.5 | 3088.5 | 2769.608 |  |  |  | 0 | 1 | [14 empty] | 117.0674 | 2769.608 |  | 104.98
11.05.2008 24:00 | 3600 | 2 | 763.96 | GGB | 764.102 | 775.148 | 769.597 | 262.94 | GGB | 10874.1 | GGB | 9.79 | GGB | 1012.75 | GGB | 62.49 | GGB | 169514.73 | GGB | 137904.73 | GGB | 0 | 0 | 3117 | 3600 | 3101 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 227513.67 | GGB | 227516.31 | 3101 | 2740.5006 |  |  |  | 1 | 1 |  |  |  |  | 137904.73 | 2740.5006 | 137904.73 | 2740.5006 | 9.7379 | [5 empty] | 118.7896 | 2740.5006 |  | 104.98
12.05.2008 01:00 | 3600 | 2 | 762.95 | GGB | 763.004 | 773.859 | 767.033 | 264.23 | GGB | 10857.3 | GGB | 9.77 | GGB | 1012.71 | GGB | 62.09 | GGB | 170305.88 | GGB | 138711.02 | GGB | 0 | 0 | 3177 | 3600 | 3160.75 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 227552.72 | GGB | 227555.36 | 3160.75 | 2724.5708 |  |  |  | 0 | 1 | [14 empty] | 121.7863 | 2724.5708 |  | 104.98
12.05.2008 02:00 | 3600 | 2 | 762.98 | GGB | 762.637 | 773.672 | 767.033 | 264.53 | GGB | 10889 | GGB | 9.78 | GGB | 1013.17 | GGB | 62.15 | GGB | 170144.13 | GGB | 138616.2 | GGB | 0 | 0 | 3194 | 3600 | 3178.14 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 227592.24 | GGB | 227594.88 | 3178.14 | 2726.4346 |  |  |  | 0 | 1 | [14 empty] | 122.3727 | 2726.4346 |  | 104.98
12.05.2008 03:00 | 3600 | 2 | 763.05 | GGB | 763.004 | 773.648 | 768.132 | 264.7 | GGB | 10913 | GGB | 9.79 | GGB | 1012.88 | GGB | 61.86 | GGB | 170654.68 | GGB | 139111.8 | GGB | 0 | 0 | 3190 | 3600 | 3174.67 | GGB | 100 | GGB | 40.2 | GGB | 40.2 | GGB | 227632.44 | GGB | 227635.08 | 3174.67 | 2716.7214 |  |  |  | 0 | 1 | [14 empty] | 122.6761 | 2716.7214 |  | 104.98
12.05.2008 04:00 | 3600 | 2 | 762.75 | GGB | 761.538 | 772.453 | 767.033 | 265 | GGB | 10920.2 | GGB | 9.78 | GGB | 1012.47 | GGB | 61.65 | GGB | 171233.46 | GGB | 139613.06 | GGB | 0 | 0 | 3218 | 3600 | 3202.57 | GGB | 100 | GGB | 40.4 | GGB | 40.4 | GGB | 227672.84 | GGB | 227675.48 | 3202.57 | 2706.9674 |  |  |  | 0 | 1 | [14 empty] | 124.2002 | 2706.9674 |  | 104.98
12.05.2008 05:00 | 3600 | 2 | 762.38 | GGB | 762.637 | 772.453 | 767.033 | 266.82 | GGB | 10948.4 | GGB | 9.78 | GGB | 1013.03 | GGB | 61.64 | GGB | 172539.56 | GGB | 140760.82 | GGB | 0 | 0 | 3241 | 3600 | 3224.68 | GGB | 100 | GGB | 39.23 | GGB | 39.23 | GGB | 227712.06 | GGB | 227714.71 | 3224.68 | 2684.8948 |  |  |  | 0 | 1 | [14 empty] | 126.0857 | 2684.8948 |  | 104.98
12.05.2008 06:00 | 3600 | 2 | 763.23 | GGB | 763.004 | 772.805 | 768.132 | 266.91 | GGB | 10977 | GGB | 9.79 | GGB | 1012.98 | GGB | 61.51 | GGB | 172644.09 | GGB | 140896.28 | GGB | 0 | 0 | 3218 | 3600 | 3201.81 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 227751.37 | GGB | 227754.02 | 3201.81 | 2682.3135 |  |  |  | 0 | 1 | [14 empty] | 125.312 | 2682.3135 |  | 104.98
12.05.2008 07:00 | 3600 | 2 | 763.17 | GGB | 762.637 | 772.805 | 767.033 | 267.01 | GGB | 10976.7 | GGB | 9.79 | GGB | 1012.91 | GGB | 61.37 | GGB | 172915.88 | GGB | 141167.64 | GGB | 0 | 0 | 3236 | 3600 | 3220.23 | GGB | 100 | GGB | 39.35 | GGB | 39.35 | GGB | 227790.72 | GGB | 227793.37 | 3220.23 | 2677.1575 |  |  |  | 0 | 1 | [14 empty] | 126.2756 | 2677.1575 |  | 104.98
12.05.2008 08:00 | 3600 | 2 | 763.77 | GGB | 763.004 | 773.789 | 767.033 | 265.86 | GGB | 10962 | GGB | 9.8 | GGB | 1013.25 | GGB | 61.7 | GGB | 171909.07 | GGB | 140251.95 | GGB | 0 | 0 | 3192 | 3600 | 3176.2 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 227830.22 | GGB | 227832.87 | 3176.2 | 2694.6363 |  |  |  | 0 | 1 | [14 empty] | 123.7412 | 2694.6363 |  | 104.98
12.05.2008 09:00 | 3600 | 2 | 764.17 | GGB | 765.201 | 776.344 | 770.696 | 264.59 | GGB | 10926 | GGB | 9.8 | GGB | 1012.4 | GGB | 61.93 | GGB | 170740.51 | GGB | 139087.2 | GGB | 0 | 0 | 3149 | 3600 | 3132.96 | GGB | 100 | GGB | 39.51 | GGB | 39.51 | GGB | 227869.73 | GGB | 227872.38 | 3132.96 | 2717.2019 |  |  |  | 1 | 1 |  |  |  |  | 139087.2 | 2717.2019 | 139087.2 | 2717.2019 | 9.5654 | [5 empty] | 121.043 | 2717.2019 |  | 104.98
12.05.2008 10:00 | 3600 | 2 | 764.48 | GGB | 764.102 | 775.219 | 769.597 | 263.4 | GGB | 10814.8 | GGB | 9.79 | GGB | 1012.02 | GGB | 62.2 | GGB | 169826.13 | GGB | 138180.13 | GGB | 0 | 0 | 3070 | 3600 | 3054.35 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 227909.32 | GGB | 227911.97 | 3054.35 | 2735.0387 |  |  |  | 1 | 1 |  |  |  |  | 138180.13 | 2735.0387 | 138180.13 | 2735.0387 | 9.546 | [5 empty] | 117.2362 | 2735.0387 |  | 104.98
12.05.2008 11:00 | 3600 | 2 | 765.73 | GGB | 764.102 | 775.219 | 769.597 | 261.98 | GGB | 10734.5 | GGB | 9.8 | GGB | 1011.43 | GGB | 62.35 | GGB | 168802.81 | GGB | 137206.42 | GGB | 0 | 0 | 2946 | 3600 | 2930.79 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 227948.74 | GGB | 227951.39 | 2930.79 | 2754.4484 |  |  |  | 1 | 1 |  |  |  |  | 137206.42 | 2754.4484 | 137206.42 | 2754.4484 | 9.5872 | [5 empty] | 111.7009 | 2754.4484 |  | 104.98
12.05.2008 12:00 | 3600 | 2 | 765.82 | GGB | 764.102 | 775.266 | 769.597 | 258.53 | GGB | 10693.7 | GGB | 9.8 | GGB | 1010.37 | GGB | 63.24 | GGB | 164934.03 | GGB | 133566.15 | GGB | 0 | 0 | 2922 | 3600 | 2906.3 | GGB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 227987.84 | GGB | 227990.48 | 2906.3 | 2829.5193 |  |  |  | 1 | 1 |  |  |  |  | 133566.15 | 2829.5193 | 133566.15 | 2829.5193 | 9.6682 | [5 empty] | 107.8287 | 2829.5193 |  | 104.98
12.05.2008 13:00 | 3600 | 2 | 765.08 | GGB | 764.102 | 775.266 | 769.597 | 258.57 | GGB | 10682 | GGB | 9.79 | GGB | 1010.32 | GGB | 63.37 | GGB | 165009.95 | GGB | 133568.12 | GGB | 0 | 0 | 2961 | 3600 | 2944.96 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 228027 | GGB | 228029.65 | 2944.96 | 2829.4776 |  |  |  | 1 | 1 |  |  |  |  | 133568.12 | 2829.4776 | 133568.12 | 2829.4776 | 9.6484 | [5 empty] | 109.2647 | 2829.4776 |  | 104.98
12.05.2008 14:00 | 3600 | 2 | 764.45 | GGB | 764.102 | 775.078 | 768.498 | 259.87 | GGB | 10717.3 | GGB | 9.78 | GGB | 1010.34 | GGB | 63.19 | GGB | 165861.61 | GGB | 134333.46 | GGB | 0 | 0 | 3021 | 3600 | 3005.15 | GGB | 100 | GGB | 39.05 | GGB | 39.05 | GGB | 228066.05 | GGB | 228068.7 | 3005.15 | 2813.3571 |  |  |  | 1 | 1 |  |  |  |  | 134333.46 | 2813.3571 | 134333.46 | 2813.3571 | 9.6781 | [5 empty] | 112.1367 | 2813.3571 |  | 104.98
12.05.2008 15:00 | 3600 | 2 | 764.51 | GGB | 763.004 | 773.859 | 768.498 | 261.24 | GGB | 10744.7 | GGB | 9.78 | GGB | 1010.53 | GGB | 63.06 | GGB | 167025.77 | GGB | 135352.95 | GGB | 0 | 0 | 3031 | 3600 | 3015.03 | GGB | 100 | GGB | 38.97 | GGB | 38.97 | GGB | 228105.02 | GGB | 228107.67 | 3015.03 | 2792.1667 |  |  |  | 0 | 1 | [14 empty] | 113.3592 | 2792.1667 |  | 104.98
12.05.2008 16:00 | 3600 | 2 | 765.47 | GGB | 765.201 | 775.945 | 769.597 | 260.37 | GGB | 10719.9 | GGB | 9.8 | GGB | 1010.04 | GGB | 63.57 | GGB | 165744.98 | GGB | 134044.98 | GGB | 0 | 0 | 2982 | 3600 | 2966.81 | GGB | 100 | GGB | 39.01 | GGB | 39.01 | GGB | 228144.03 | GGB | 228146.68 | 2966.81 | 2819.4118 |  |  |  | 1 | 1 |  |  |  |  | 134044.98 | 2819.4118 | 134044.98 | 2819.4118 | 9.688 | [5 empty] | 110.4683 | 2819.4118 |  | 104.98
12.05.2008 17:00 | 3600 | 2 | 765.7 | GGB | 764.102 | 775.945 | 770.696 | 259.1 | GGB | 10626.2 | GGB | 9.79 | GGB | 1008.71 | GGB | 64.27 | GGB | 164829.49 | GGB | 132854.39 | GGB | 0 | 0 | 2916 | 3600 | 2900.31 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 228182.92 | GGB | 228185.57 | 2900.31 | 2844.6783 |  |  |  | 1 | 1 |  |  |  |  | 132854.39 | 2844.6783 | 132854.39 | 2844.6783 | 9.7179 | [5 empty] | 107.033 | 2844.6783 |  | 104.98
12.05.2008 18:00 | 3600 | 2 | 765.58 | GGB | 764.102 | 774.938 | 769.597 | 258.12 | GGB | 10627.1 | GGB | 9.79 | GGB | 1007.88 | GGB | 64.04 | GGB | 164309.04 | GGB | 132415.95 | GGB | 0 | 0 | 2910 | 3600 | 2894.88 | GGB | 100 | GGB | 38.94 | GGB | 38.94 | GGB | 228221.86 | GGB | 228224.51 | 2894.88 | 2854.0973 |  |  |  | 1 | 1 |  |  |  |  | 132415.95 | 2854.0973 | 132415.95 | 2854.0973 | 9.7054 | [5 empty] | 106.4801 | 2854.0973 |  | 104.98
12.05.2008 19:00 | 3600 | 2 | 763.84 | GGB | 761.538 | 771.961 | 765.934 | 260.43 | GGB | 10690 | GGB | 9.76 | GGB | 1008.53 | GGB | 61.91 | GGB | 167056.58 | GGB | 135574.57 | GGB | 0 | 0 | 3017 | 3600 | 3001.48 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 228261.29 | GGB | 228263.94 | 3001.48 | 2787.6024 |  |  |  | 0 | 1 | [14 empty] | 113.0345 | 2787.6024 |  | 104.98
12.05.2008 20:00 | 3600 | 2 | 763.13 | GGB | 760.44 | 772.195 | 765.934 | 262.8 | GGB | 10804.6 | GGB | 9.77 | GGB | 1009.74 | GGB | 62.68 | GGB | 168079.89 | GGB | 136256.5 | GGB | 0 | 0 | 3146 | 3600 | 3130.12 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 228300.59 | GGB | 228303.24 | 3130.12 | 2773.6512 |  |  |  | 0 | 1 | [14 empty] | 118.472 | 2773.6512 |  | 104.98
12.05.2008 21:00 | 3600 | 2 | 763.36 | GGB | 762.637 | 773.484 | 768.132 | 263.86 | GGB | 10853.5 | GGB | 9.78 | GGB | 1010.03 | GGB | 62.62 | GGB | 168997.57 | GGB | 137062.92 | GGB | 0 | 0 | 3160 | 3600 | 3144.3 | GGB | 100 | GGB | 39.33 | GGB | 39.33 | GGB | 228339.92 | GGB | 228342.57 | 3144.3 | 2757.3322 |  |  |  | 0 | 1 | [14 empty] | 119.713 | 2757.3322 |  | 104.98
12.05.2008 22:00 | 3600 | 2 | 762.33 | GGB | 764.102 | 774.563 | 768.132 | 266.43 | GGB | 10879.8 | GGB | 9.76 | GGB | 1010.66 | GGB | 61.46 | GGB | 172005.9 | GGB | 140076.14 | GGB | 0 | 0 | 3225 | 3600 | 3209.07 | GGB | 100 | GGB | 39.82 | GGB | 39.82 | GGB | 228379.74 | GGB | 228382.39 | 3209.07 | 2698.0184 |  |  |  | 1 | 1 |  |  |  |  | 140076.14 | 2698.0184 | 140076.14 | 2698.0184 | 9.4909 | [5 empty] | 124.865 | 2698.0184 |  | 104.98
12.05.2008 23:00 | 3600 | 2 | 763.7 | GGB | 763.004 | 773.414 | 767.033 | 266.2 | GGB | 10955.2 | GGB | 9.79 | GGB | 1011.34 | GGB | 61.34 | GGB | 172068.62 | GGB | 140269.41 | GGB | 0 | 0 | 3188 | 3600 | 3171.87 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 228419.37 | GGB | 228422.02 | 3171.87 | 2694.3009 |  |  |  | 0 | 1 | [14 empty] | 123.5879 | 2694.3009 |  | 104.98
12.05.2008 24:00 | 3600 | 2 | 762.71 | GGB | 763.004 | 773.438 | 768.132 | 267.35 | GGB | 10989.6 | GGB | 9.78 | GGB | 1011.91 | GGB | 60.78 | GGB | 173855.57 | GGB | 142044.27 | GGB | 0 | 0 | 3235 | 3600 | 3219.29 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 228459.29 | GGB | 228461.93 | 3219.29 | 2660.6353 |  |  |  | 0 | 1 | [14 empty] | 127.0227 | 2660.6353 |  | 104.98
13.05.2008 01:00 | 3600 | 2 | 762.58 | GGB | 762.637 | 773.133 | 767.033 | 267.67 | GGB | 11039.3 | GGB | 9.78 | GGB | 1012.78 | GGB | 60.27 | GGB | 174890.98 | GGB | 143233.08 | GGB | 0 | 0 | 3243 | 3600 | 3227.06 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 228499.21 | GGB | 228501.85 | 3227.06 | 2638.5525 |  |  |  | 0 | 1 | [14 empty] | 128.3949 | 2638.5525 |  | 104.98
13.05.2008 02:00 | 3600 | 2 | 762.01 | GGB | 762.637 | 773.344 | 768.132 | 269.59 | GGB | 11045.4 | GGB | 9.78 | GGB | 1013.4 | GGB | 59.16 | GGB | 177693.54 | GGB | 146101.13 | GGB | 0 | 0 | 3266 | 3600 | 3249.8 | GGB | 100 | GGB | 40.45 | GGB | 40.45 | GGB | 228539.66 | GGB | 228542.3 | 3249.8 | 2586.7562 |  |  |  | 0 | 1 | [14 empty] | 131.8887 | 2586.7562 |  | 104.98
13.05.2008 03:00 | 3600 | 2 | 761.96 | GGB | 763.37 | 773.227 | 768.132 | 270.12 | GGB | 11065.6 | GGB | 9.78 | GGB | 1013.58 | GGB | 58.71 | GGB | 178442.87 | GGB | 146945.56 | GGB | 0 | 0 | 3268 | 3600 | 3251.97 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 228579.87 | GGB | 228582.51 | 3251.97 | 2571.8913 |  |  |  | 0 | 1 | [14 empty] | 132.7396 | 2571.8913 |  | 104.98
13.05.2008 04:00 | 3600 | 2 | 762.26 | GGB | 762.271 | 772.172 | 767.033 | 269.3 | GGB | 11129.2 | GGB | 9.79 | GGB | 1013.67 | GGB | 59.06 | GGB | 176936.51 | GGB | 145562.36 | GGB | 0 | 0 | 3296 | 3600 | 3279.98 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 228619.93 | GGB | 228622.57 | 3279.98 | 2596.3305 |  |  |  | 0 | 1 | [14 empty] | 132.6227 | 2596.3305 |  | 104.98
13.05.2008 05:00 | 3600 | 2 | 761.41 | GGB | 759.707 | 771.117 | 764.835 | 269.74 | GGB | 11113.4 | GGB | 9.78 | GGB | 1014.12 | GGB | 58.93 | GGB | 177246.81 | GGB | 145939.3 | GGB | 0 | 0 | 3330 | 3600 | 3314.47 | GNB | 100 | GGB | 40.22 | GGB | 40.22 | GGB | 228660.15 | GGB | 228662.79 | 3314.47 | 2589.6246 |  |  |  | 0 | 1 | [14 empty] | 134.3643 | 2589.6246 |  | 104.98
13.05.2008 06:00 | 3600 | 2 | 761.05 | GGB | 761.172 | 771.961 | 765.934 | 272.05 | GGB | 11115 | GGB | 9.77 | GGB | 1014.43 | GGB | 57.87 | GGB | 180409.18 | GGB | 149065.4 | GGB | 0 | 0 | 3344 | 3600 | 3328.01 | GNB | 100 | GGB | 40.24 | GGB | 40.24 | GGB | 228700.39 | GGB | 228703.03 | 3328.01 | 2535.3167 |  |  |  | 0 | 1 | [14 empty] | 137.8031 | 2535.3167 |  | 104.98
13.05.2008 07:00 | 3600 | 2 | 761.38 | GGB | 761.172 | 771.984 | 765.934 | 273.02 | GGB | 11150.4 | GGB | 9.78 | GGB | 1015.43 | GGB | 57.77 | GGB | 181192.62 | GGB | 149906.46 | GGB | 0 | 0 | 3348 | 3600 | 3331.84 | GNB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 228740.55 | GGB | 228743.19 | 3331.84 | 2521.0922 |  |  |  | 0 | 1 | [14 empty] | 138.7401 | 2521.0922 |  | 104.98
13.05.2008 08:00 | 3600 | 2 | 762.49 | GGB | 762.271 | 773.039 | 768.132 | 272.99 | GGB | 11183.4 | GGB | 9.8 | GGB | 1016.33 | GGB | 58.02 | GGB | 180813 | GGB | 149609.31 | GGB | 0 | 0 | 3311 | 3600 | 3295.22 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 228780.63 | GGB | 228783.28 | 3295.22 | 2526.0995 |  |  |  | 0 | 1 | [14 empty] | 136.9432 | 2526.0995 |  | 104.98
13.05.2008 09:00 | 3600 | 2 | 762.83 | GGB | 762.271 | 771.961 | 767.033 | 270.9 | GGB | 11156.8 | GGB | 9.8 | GGB | 1016.49 | GGB | 59.07 | GGB | 177631.92 | GGB | 146536.11 | GGB | 0 | 0 | 3283 | 3600 | 3267.46 | GGB | 100 | GGB | 39.9 | GGB | 39.9 | GGB | 228820.53 | GGB | 228823.18 | 3267.46 | 2579.0776 |  |  |  | 0 | 1 | [14 empty] | 133.0002 | 2579.0776 |  | 104.98
13.05.2008 10:00 | 3600 | 2 | 762.96 | GGB | 763.37 | 774.117 | 768.132 | 270.48 | GGB | 11120.3 | GGB | 9.79 | GGB | 1016.6 | GGB | 59.29 | GGB | 177196.19 | GGB | 146098.15 | GGB | 0 | 0 | 3259 | 3600 | 3243.34 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 228860.43 | GGB | 228863.07 | 3243.34 | 2586.8089 |  |  |  | 0 | 1 | [14 empty] | 131.6239 | 2586.8089 |  | 104.98
13.05.2008 11:00 | 3600 | 2 | 763.12 | GGB | 761.172 | 772.242 | 765.934 | 270.57 | GGB | 11059.9 | GGB | 9.78 | GGB | 1016.89 | GGB | 59.41 | GGB | 177638.53 | GGB | 146449.68 | GGB | 0 | 0 | 3212 | 3600 | 3195.68 | GGB | 100 | GGB | 39.97 | GGB | 39.97 | GGB | 228900.39 | GGB | 228903.04 | 3195.68 | 2580.5997 |  |  |  | 0 | 1 | [14 empty] | 130.0018 | 2580.5997 |  | 104.98
13.05.2008 12:00 | 3600 | 2 | 764.25 | GGB | 764.835 | 775.617 | 770.696 | 271.15 | GGB | 11058 | GGB | 9.8 | GGB | 1016.63 | GGB | 58.97 | GGB | 178840.1 | GGB | 147598.14 | GGB | 0 | 0 | 3142 | 3600 | 3126.48 | GGB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 228940.33 | GGB | 228942.98 | 3126.48 | 2560.5201 |  |  |  | 1 | 1 |  |  |  |  | 147598.14 | 2560.5201 | 147598.14 | 2560.5201 | 9.4624 | [5 empty] | 128.1841 | 2560.5201 |  | 104.98
13.05.2008 13:00 | 3600 | 2 | 764.53 | GGB | 765.934 | 776.813 | 770.696 | 269.49 | GGB | 11029.6 | GGB | 9.8 | GGB | 1016.14 | GGB | 59.41 | GGB | 177184.09 | GGB | 145969.58 | GGB | 0 | 0 | 3108 | 3600 | 3092.42 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 228980.13 | GGB | 228982.78 | 3092.42 | 2589.0874 |  |  |  | 1 | 1 |  |  |  |  | 145969.58 | 2589.0874 | 145969.58 | 2589.0874 | 9.4957 | [5 empty] | 125.3887 | 2589.0874 |  | 104.98
13.05.2008 14:00 | 3600 | 2 | 764.46 | GGB | 764.469 | 774.797 | 769.597 | 267.66 | GGB | 11014.1 | GGB | 9.79 | GGB | 1015.74 | GGB | 60.28 | GGB | 174875.58 | GGB | 143633.2 | GGB | 0 | 0 | 3119 | 3600 | 3103.01 | GGB | 100 | GGB | 39.84 | GGB | 39.84 | GGB | 229019.97 | GGB | 229022.62 | 3103.01 | 2631.2023 |  |  |  | 1 | 1 |  |  |  |  | 143633.2 | 2631.2023 | 143633.2 | 2631.2023 | 9.4861 | [5 empty] | 123.8042 | 2631.2023 |  | 104.98
13.05.2008 15:00 | 3600 | 2 | 764.39 | GGB | 762.271 | 773.719 | 768.132 | 267.26 | GGB | 10968.4 | GGB | 9.78 | GGB | 1015.3 | GGB | 60.36 | GGB | 174857.97 | GGB | 143523.3 | GGB | 0 | 0 | 3096 | 3600 | 3080.34 | GGB | 100 | GGB | 39.91 | GGB | 39.91 | GGB | 229059.88 | GGB | 229062.53 | 3080.34 | 2633.217 |  |  |  | 0 | 1 | [14 empty] | 122.8057 | 2633.217 |  | 104.98
13.05.2008 16:00 | 3600 | 2 | 764.88 | GGB | 763.37 | 774.773 | 768.498 | 268.05 | GGB | 10951.9 | GGB | 9.79 | GGB | 1014.89 | GGB | 59.85 | GGB | 176310.42 | GGB | 144879.51 | GGB | 0 | 0 | 3047 | 3600 | 3031.72 | GGB | 100 | GGB | 39.92 | GGB | 39.92 | GGB | 229099.8 | GGB | 229102.45 | 3031.72 | 2608.5676 |  |  |  | 0 | 1 | [14 empty] | 122.0095 | 2608.5676 |  | 104.98
13.05.2008 17:00 | 3600 | 2 | 764.74 | GGB | 767.033 | 777.141 | 771.795 | 267.34 | GGB | 10943.7 | GGB | 9.79 | GGB | 1014.44 | GGB | 59.78 | GGB | 176021.03 | GGB | 144604.89 | GGB | 0 | 0 | 3047 | 3600 | 3031.5 | GGB | 100 | GGB | 39.87 | GGB | 39.87 | GGB | 229139.67 | GGB | 229142.32 | 3031.5 | 2613.5216 |  |  |  | 1 | 1 |  |  |  |  | 144604.89 | 2613.5216 | 144604.89 | 2613.5216 | 9.479 | [5 empty] | 121.7694 | 2613.5216 |  | 104.98
13.05.2008 18:00 | 3600 | 2 | 764.84 | GGB | 765.934 | 776.297 | 770.696 | 265.99 | GGB | 10930.4 | GGB | 9.8 | GGB | 1014.17 | GGB | 60.1 | GGB | 174954.8 | GGB | 143555.82 | GGB | 0 | 0 | 3031 | 3600 | 3015.64 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 229179.52 | GGB | 229182.17 | 3015.64 | 2632.6205 |  |  |  | 1 | 1 |  |  |  |  | 143555.82 | 2632.6205 | 143555.82 | 2632.6205 | 9.4838 | [5 empty] | 120.2535 | 2632.6205 |  | 104.98
13.05.2008 19:00 | 3600 | 2 | 764.69 | GGB | 763.37 | 774.352 | 768.498 | 264.87 | GGB | 10951 | GGB | 9.79 | GGB | 1013.78 | GGB | 60.51 | GGB | 173301 | GGB | 141968.31 | GGB | 0 | 0 | 3060 | 3600 | 3044.73 | GGB | 100 | GGB | 39.88 | GGB | 39.88 | GGB | 229219.4 | GGB | 229222.05 | 3044.73 | 2662.0589 |  |  |  | 0 | 1 | [14 empty] | 120.0709 | 2662.0589 |  | 104.98
13.05.2008 20:00 | 3600 | 2 | 763.88 | GGB | 762.271 | 773.039 | 767.033 | 265.35 | GGB | 10934.6 | GGB | 9.77 | GGB | 1013.88 | GGB | 60.21 | GGB | 174120.75 | GGB | 142780.46 | GGB | 0 | 0 | 3091 | 3600 | 3074.81 | GGB | 100 | GGB | 40.26 | GGB | 40.26 | GGB | 229259.66 | GGB | 229262.31 | 3074.81 | 2646.9168 |  |  |  | 0 | 1 | [14 empty] | 121.9508 | 2646.9168 |  | 104.98
13.05.2008 21:00 | 3600 | 2 | 763.26 | GGB | 762.271 | 774.117 | 768.132 | 268.76 | GGB | 10975.2 | GGB | 9.77 | GGB | 1014.53 | GGB | 58.86 | GGB | 177960.93 | GGB | 146616.93 | GGB | 0 | 0 | 3132 | 3600 | 3116.34 | GGB | 100 | GGB | 40.39 | GGB | 40.39 | GGB | 229300.05 | GGB | 229302.7 | 3116.34 | 2577.6559 |  |  |  | 0 | 1 | [14 empty] | 126.9189 | 2577.6559 |  | 104.98
13.05.2008 22:00 | 3600 | 2 | 762.64 | GGB | 762.271 | 771.797 | 767.033 | 270.93 | GGB | 11035.7 | GGB | 9.77 | GGB | 1015.03 | GGB | 58.43 | GGB | 179418.87 | GGB | 148083.92 | GGB | 0 | 0 | 3175 | 3600 | 3158.92 | GGB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 229340.55 | GGB | 229343.2 | 3158.92 | 2552.1204 |  |  |  | 0 | 1 | [14 empty] | 129.9403 | 2552.1204 |  | 104.98
13.05.2008 23:00 | 3600 | 2 | 762.93 | GGB | 761.172 | 771.773 | 767.033 | 271.77 | GGB | 11072.6 | GGB | 9.78 | GGB | 1015.57 | GGB | 58.33 | GGB | 180019.66 | GGB | 148703.52 | GGB | 0 | 0 | 3183 | 3600 | 3166.91 | GGB | 100 | GGB | 40.44 | GGB | 40.44 | GGB | 229380.98 | GGB | 229383.64 | 3166.91 | 2541.4866 |  |  |  | 0 | 1 | [14 empty] | 130.8141 | 2541.4866 |  | 104.98
13.05.2008 24:00 | 3600 | 2 | 762.27 | GGB | 760.806 | 771.75 | 767.033 | 271.77 | GGB | 11119.2 | GGB | 9.78 | GGB | 1016.09 | GGB | 59.03 | GGB | 178840.1 | GGB | 147494.04 | GGB | 0 | 0 | 3260 | 3600 | 3244.09 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 229421.13 | GGB | 229423.79 | 3244.09 | 2562.3273 |  |  |  | 0 | 1 | [14 empty] | 132.9122 | 2562.3273 |  | 104.98
14.05.2008 01:00 | 3600 | 2 | 762.42 | GGB | 761.172 | 771.68 | 765.934 | 272.42 | GGB | 11151.1 | GGB | 9.78 | GGB | 1016.53 | GGB | 59.24 | GGB | 178879.71 | GGB | 147497.83 | GGB | 0 | 0 | 3290 | 3600 | 3273.75 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 229461.25 | GGB | 229463.91 | 3273.75 | 2562.2614 |  |  |  | 0 | 1 | [14 empty] | 134.1308 | 2562.2614 |  | 104.98
14.05.2008 02:00 | 3600 | 2 | 762.33 | GGB | 762.271 | 772.594 | 767.033 | 273.31 | GGB | 11188.7 | GGB | 9.78 | GGB | 1016.67 | GGB | 59.2 | GGB | 179801.79 | GGB | 148294.36 | GGB | 0 | 0 | 3321 | 3600 | 3304.73 | GGB | 100 | GGB | 40.11 | GGB | 40.11 | GGB | 229501.37 | GGB | 229504.02 | 3304.73 | 2548.4988 |  |  |  | 0 | 1 | [14 empty] | 136.1313 | 2548.4988 |  | 104.98
14.05.2008 03:00 | 3600 | 2 | 761.38 | GGB | 758.608 | 768.375 | 763.37 | 275.47 | GGB | 11156.9 | GGB | 9.76 | GGB | 1017.39 | GGB | 58.24 | GGB | 182635.16 | GGB | 151175.86 | GGB | 0 | 0 | 3343 | 3600 | 3327.45 | GNB | 100 | GGB | 40.33 | GGB | 40.33 | GGB | 229541.69 | GGB | 229544.35 | 3327.45 | 2499.9229 |  |  |  | 0 | 1 | [14 empty] | 139.7306 | 2499.9229 |  | 104.98
14.05.2008 04:00 | 3600 | 2 | 761.08 | GGB | 762.271 | 772.617 | 768.132 | 277.63 | GGB | 11262.8 | GGB | 9.78 | GGB | 1017.49 | GGB | 57.57 | GGB | 184819.33 | GGB | 153309.16 | GNB | 0 | 0 | 3418 | 3600 | 3401.85 | GNB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 229581.99 | GGB | 229584.65 | 3401.85 | 2465.1365 |  |  |  | 0 | 1 | [14 empty] | 144.8708 | 2465.1365 |  | 104.98
14.05.2008 05:00 | 3600 | 2 | 761.14 | GGB | 762.271 | 772.406 | 767.033 | 277.96 | GGB | 11359.2 | GGB | 9.78 | GGB | 1017.84 | GGB | 58.03 | GGB | 184689.49 | GGB | 153041.51 | GNB | 0 | 0 | 3485 | 3600 | 3468.49 | GNB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 229622.35 | GGB | 229625.01 | 3468.49 | 2469.4477 |  |  |  | 0 | 1 | [14 empty] | 147.4508 | 2469.4477 |  | 104.98
14.05.2008 06:00 | 3600 | 2 | 761.43 | GGB | 762.271 | 772.148 | 767.033 | 277.99 | GGB | 11341.5 | GGB | 9.79 | GGB | 1017.73 | GGB | 57.69 | GGB | 185633.58 | GGB | 153966.06 | GNB | 0 | 0 | 3456 | 3600 | 3439.91 | GNB | 100 | GGB | 40.75 | GGB | 40.75 | GGB | 229663.1 | GGB | 229665.76 | 3439.91 | 2454.6189 |  |  |  | 0 | 1 | [14 empty] | 147.1193 | 2454.6189 |  | 104.98
14.05.2008 07:00 | 3600 | 2 | 762.69 | GGB | 761.172 | 770.883 | 765.934 | 277.01 | GGB | 11340.6 | GGB | 9.81 | GGB | 1017.64 | GGB | 57.72 | GGB | 184553.05 | GGB | 153040.62 | GNB | 0 | 0 | 3373 | 3600 | 3356.98 | GNB | 100 | GGB | 41.65 | GGB | 41.65 | GGB | 229704.75 | GGB | 229707.41 | 3356.98 | 2469.462 |  |  |  | 0 | 1 | [14 empty] | 142.7095 | 2469.462 |  | 104.98
14.05.2008 08:00 | 3600 | 2 | 762 | GGB | 762.271 | 773.109 | 767.033 | 275.58 | GGB | 11303.9 | GGB | 9.79 | GGB | 1017.81 | GGB | 58.27 | GGB | 182719.89 | GGB | 151293.84 | GGB | 0 | 0 | 3405 | 3600 | 3389.1 | GNB | 100 | GGB | 41.89 | GGB | 41.89 | GGB | 229746.64 | GGB | 229749.3 | 3389.1 | 2497.9735 |  |  |  | 0 | 1 | [14 empty] | 142.4305 | 2497.9735 |  | 104.98
14.05.2008 09:00 | 3600 | 2 | 762.34 | GGB | 761.172 | 771.914 | 765.934 | 274.61 | GGB | 11234 | GGB | 9.79 | GGB | 1018.11 | GGB | 58.23 | GGB | 181671.26 | GGB | 150490.54 | GGB | 0 | 0 | 3347 | 3600 | 3331.49 | GNB | 100 | GGB | 40.95 | GGB | 40.95 | GGB | 229787.59 | GGB | 229790.25 | 3331.49 | 2511.3074 |  |  |  | 0 | 1 | [14 empty] | 139.266 | 2511.3074 |  | 104.98
14.05.2008 10:00 | 3600 | 2 | 762.72 | GGB | 758.608 | 768.516 | 763.37 | 274.55 | GGB | 11146.1 | GGB | 9.78 | GGB | 1018.27 | GGB | 58.35 | GGB | 181773.6 | GGB | 150541.97 | GGB | 0 | 0 | 3281 | 3600 | 3265.17 | GGB | 100 | GGB | 40.9 | GGB | 40.9 | GGB | 229828.48 | GGB | 229831.15 | 3265.17 | 2510.4494 |  |  |  | 0 | 1 | [14 empty] | 136.5403 | 2510.4494 |  | 104.98
14.05.2008 11:00 | 3600 | 2 | 764.83 | GGB | 762.271 | 773.555 | 767.033 | 272.51 | GGB | 11150.1 | GGB | 9.82 | GGB | 1017.37 | GGB | 58.82 | GGB | 180071.37 | GGB | 148792.41 | GGB | 0 | 0 | 3170 | 3600 | 3154.04 | GGB | 100 | GGB | 40.71 | GGB | 40.71 | GGB | 229869.2 | GGB | 229871.86 | 3154.04 | 2539.9683 |  |  |  | 0 | 1 | [14 empty] | 130.3603 | 2539.9683 |  | 104.98
14.05.2008 12:00 | 3600 | 2 | 764.26 | GGB | 763.37 | 774.352 | 768.498 | 271.33 | GGB | 11080.6 | GGB | 9.8 | GGB | 1016.77 | GGB | 58.94 | GGB | 179251.62 | GGB | 147970.99 | GGB | 0 | 0 | 3161 | 3600 | 3144.85 | GGB | 100 | GGB | 40.73 | GGB | 40.73 | GGB | 229909.93 | GGB | 229912.59 | 3144.85 | 2554.0682 |  |  |  | 0 | 1 | [14 empty] | 129.2629 | 2554.0682 |  | 104.98
14.05.2008 13:00 | 3600 | 2 | 764.31 | GGB | 763.37 | 774.211 | 768.498 | 270.26 | GGB | 11046.2 | GGB | 9.79 | GGB | 1015.92 | GGB | 59.03 | GGB | 178547.41 | GGB | 147228.38 | GGB | 0 | 0 | 3138 | 3600 | 3122.35 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 229950.58 | GGB | 229953.24 | 3122.35 | 2566.9507 |  |  |  | 0 | 1 | [14 empty] | 127.694 | 2566.9507 |  | 104.98
14.05.2008 14:00 | 3600 | 2 | 764.4 | GGB | 764.469 | 775.102 | 769.597 | 269.7 | GGB | 11016.7 | GGB | 9.79 | GGB | 1015.39 | GGB | 59.31 | GGB | 177660.53 | GGB | 146298.38 | GGB | 0 | 0 | 3115 | 3600 | 3099.09 | GGB | 100 | GGB | 40.61 | GGB | 40.61 | GGB | 229991.19 | GGB | 229993.85 | 3099.09 | 2583.2685 |  |  |  | 1 | 1 |  |  |  |  | 146298.38 | 2583.2685 | 146298.38 | 2583.2685 | 9.3063 | [5 empty] | 125.9422 | 2583.2685 |  | 104.98
14.05.2008 15:00 | 3600 | 2 | 764.81 | GGB | 764.469 | 775.148 | 770.696 | 268.78 | GGB | 10983 | GGB | 9.8 | GGB | 1014.38 | GGB | 59.65 | GGB | 176801.17 | GGB | 145294.87 | GGB | 0 | 0 | 3079 | 3600 | 3062.97 | GGB | 100 | GGB | 40.3 | GGB | 40.3 | GGB | 230031.49 | GGB | 230034.15 | 3062.97 | 2601.1104 |  |  |  | 1 | 1 |  |  |  |  | 145294.87 | 2601.1104 | 145294.87 | 2601.1104 | 9.3779 | [5 empty] | 123.6205 | 2601.1104 |  | 104.98
14.05.2008 16:00 | 3600 | 2 | 764.12 | GGB | 764.469 | 775.359 | 769.597 | 268.62 | GGB | 10963.2 | GGB | 9.78 | GGB | 1013.9 | GGB | 59.48 | GGB | 176909 | GGB | 145391.25 | GGB | 0 | 0 | 3102 | 3600 | 3086.16 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 230071.62 | GGB | 230074.28 | 3086.16 | 2599.3861 |  |  |  | 1 | 1 |  |  |  |  | 145391.25 | 2599.3861 | 145391.25 | 2599.3861 | 9.4176 | [5 empty] | 124.6391 | 2599.3861 |  | 104.98
14.05.2008 17:00 | 3600 | 2 | 764.82 | GGB | 764.835 | 775.383 | 769.597 | 267.76 | GGB | 10963.2 | GGB | 9.79 | GGB | 1013.44 | GGB | 59.51 | GGB | 176191.58 | GGB | 144721.14 | GGB | 0 | 0 | 3062 | 3600 | 3046.76 | GGB | 100 | GGB | 39.68 | GGB | 39.68 | GGB | 230111.3 | GGB | 230113.96 | 3046.76 | 2611.4222 |  |  |  | 1 | 1 |  |  |  |  | 144721.14 | 2611.4222 | 144721.14 | 2611.4222 | 9.5244 | [5 empty] | 122.4807 | 2611.4222 |  | 104.98
14.05.2008 18:00 | 3600 | 2 | 764.34 | GGB | 763.37 | 774.516 | 768.498 | 267.74 | GGB | 10962.6 | GGB | 9.79 | GGB | 1013.1 | GGB | 59.34 | GGB | 176394.04 | GGB | 144912.51 | GGB | 0 | 0 | 3085 | 3600 | 3069.28 | GGB | 100 | GGB | 39.58 | GGB | 39.58 | GGB | 230150.88 | GGB | 230153.54 | 3069.28 | 2607.9736 |  |  |  | 0 | 1 | [14 empty] | 123.5492 | 2607.9736 |  | 104.98
14.05.2008 19:00 | 3600 | 2 | 764.1 | GGB | 762.271 | 773.508 | 768.132 | 267.56 | GGB | 10953.3 | GGB | 9.78 | GGB | 1013.06 | GGB | 59.28 | GGB | 175904.39 | GGB | 144532.75 | GGB | 0 | 0 | 3099 | 3600 | 3083.27 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 230190.44 | GGB | 230193.09 | 3083.27 | 2614.8261 |  |  |  | 0 | 1 | [14 empty] | 123.7871 | 2614.8261 |  | 104.98
14.05.2008 20:00 | 3600 | 2 | 764.26 | GGB | 763.37 | 773.508 | 768.498 | 267.74 | GGB | 10959.8 | GGB | 9.79 | GGB | 1013.12 | GGB | 59.21 | GGB | 175873.58 | GGB | 144543.82 | GGB | 0 | 0 | 3097 | 3600 | 3081.47 | GGB | 100 | GGB | 39.5 | GGB | 39.5 | GGB | 230229.94 | GGB | 230232.59 | 3081.47 | 2614.6258 |  |  |  | 0 | 1 | [14 empty] | 123.7243 | 2614.6258 |  | 104.98
14.05.2008 21:00 | 3600 | 2 | 764.11 | GGB | 762.271 | 772.547 | 767.033 | 266.34 | GGB | 10993.4 | GGB | 9.79 | GGB | 1012.67 | GGB | 59.92 | GGB | 173552.97 | GGB | 142269.41 | GGB | 0 | 0 | 3120 | 3600 | 3104.18 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 230269.25 | GGB | 230271.9 | 3104.18 | 2656.4249 |  |  |  | 0 | 1 | [14 empty] | 122.675 | 2656.4249 |  | 104.98
14.05.2008 22:00 | 3600 | 2 | 762.61 | GGB | 761.172 | 771.563 | 765.934 | 267.47 | GGB | 11001.1 | GGB | 9.77 | GGB | 1012.65 | GGB | 59.85 | GGB | 174497.06 | GGB | 143070.17 | GGB | 0 | 0 | 3200 | 3600 | 3184.15 | GGB | 100 | GGB | 39.96 | GGB | 39.96 | GGB | 230309.2 | GGB | 230311.86 | 3184.15 | 2641.5569 |  |  |  | 0 | 1 | [14 empty] | 126.5436 | 2641.5569 |  | 104.98
14.05.2008 23:00 | 3600 | 2 | 762.75 | GGB | 759.707 | 771.188 | 764.835 | 267.95 | GGB | 11049.5 | GGB | 9.78 | GGB | 1012.19 | GGB | 59.64 | GGB | 175394.94 | GGB | 143834.85 | GGB | 0 | 0 | 3209 | 3600 | 3192.73 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 230349.79 | GGB | 230352.44 | 3192.73 | 2627.5134 |  |  |  | 0 | 1 | [14 empty] | 127.5627 | 2627.5134 |  | 104.98
14.05.2008 24:00 | 3600 | 2 | 762.62 | GGB | 761.172 | 771.633 | 765.934 | 268.81 | GGB | 11059.2 | GGB | 9.79 | GGB | 1011.73 | GGB | 59.61 | GGB | 175682.13 | GGB | 144018.2 | GGB | 0 | 0 | 3239 | 3600 | 3223.6 | GGB | 100 | GGB | 40.51 | GGB | 40.51 | GGB | 230390.29 | GGB | 230392.95 | 3223.6 | 2624.1683 |  |  |  | 0 | 1 | [14 empty] | 128.9603 | 2624.1683 |  | 104.98
15.05.2008 01:00 | 3600 | 2 | 762.79 | GGB | 761.172 | 771.445 | 765.934 | 268.89 | GGB | 11060.2 | GGB | 9.79 | GGB | 1011.33 | GGB | 59.53 | GGB | 176060.64 | GGB | 144302.94 | GGB | 0 | 0 | 3241 | 3600 | 3224.86 | GGB | 100 | GGB | 40.58 | GGB | 40.58 | GGB | 230430.87 | GGB | 230433.53 | 3224.86 | 2618.9903 |  |  |  | 0 | 1 | [14 empty] | 129.2658 | 2618.9903 |  | 104.98
15.05.2008 02:00 | 3600 | 2 | 762.24 | GGB | 758.608 | 768.82 | 763.37 | 268.65 | GGB | 11060.8 | GGB | 9.78 | GGB | 1010.83 | GGB | 59.47 | GGB | 175784.46 | GGB | 144030.68 | GGB | 0 | 0 | 3266 | 3600 | 3250.17 | GGB | 100 | GGB | 40.56 | GGB | 40.56 | GGB | 230471.43 | GGB | 230474.09 | 3250.17 | 2623.941 |  |  |  | 0 | 1 | [14 empty] | 130.0345 | 2623.941 |  | 104.98
15.05.2008 03:00 | 3600 | 2 | 762.76 | GGB | 762.271 | 773.133 | 768.132 | 268.65 | GGB | 11080.1 | GGB | 9.79 | GGB | 1011.13 | GGB | 59.46 | GGB | 175888.99 | GGB | 144165.67 | GGB | 0 | 0 | 3242 | 3600 | 3226.29 | GGB | 100 | GGB | 40.55 | GGB | 40.55 | GGB | 230511.98 | GGB | 230514.64 | 3226.29 | 2621.484 |  |  |  | 0 | 1 | [14 empty] | 129.2001 | 2621.484 |  | 104.98
15.05.2008 04:00 | 3600 | 2 | 762.83 | GGB | 762.271 | 773.133 | 768.132 | 268.69 | GGB | 11075 | GGB | 9.79 | GGB | 1011.05 | GGB | 59.33 | GGB | 176024.33 | GGB | 144319.84 | GGB | 0 | 0 | 3237 | 3600 | 3220.92 | GGB | 100 | GGB | 40.59 | GGB | 40.59 | GGB | 230552.57 | GGB | 230555.23 | 3220.92 | 2618.6836 |  |  |  | 0 | 1 | [14 empty] | 129.123 | 2618.6836 |  | 104.98
15.05.2008 05:00 | 3600 | 2 | 762.41 | GGB | 759.707 | 771 | 764.835 | 268.74 | GGB | 11072.1 | GGB | 9.78 | GGB | 1010.56 | GGB | 59.3 | GGB | 176165.17 | GGB | 144380.38 | GGB | 0 | 0 | 3251 | 3600 | 3234.9 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 230593 | GGB | 230595.66 | 3234.9 | 2617.5856 |  |  |  | 0 | 1 | [14 empty] | 129.7378 | 2617.5856 |  | 104.98
15.05.2008 06:00 | 3600 | 2 | 761.93 | GGB | 763.37 | 774.164 | 768.498 | 269.88 | GGB | 11120.6 | GGB | 9.79 | GGB | 1010.3 | GGB | 59.05 | GGB | 177510.89 | GGB | 145552.23 | GGB | 0 | 0 | 3296 | 3600 | 3280.53 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 230633.09 | GGB | 230635.75 | 3280.53 | 2596.5112 |  |  |  | 0 | 1 | [14 empty] | 132.6357 | 2596.5112 |  | 104.98
15.05.2008 07:00 | 3600 | 2 | 762.33 | GGB | 763.37 | 773.203 | 768.132 | 269.79 | GGB | 11114.5 | GGB | 9.79 | GGB | 1009.78 | GGB | 59.11 | GGB | 177587.91 | GGB | 145514.94 | GGB | 0 | 0 | 3276 | 3600 | 3260.42 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 230672.95 | GGB | 230675.61 | 3260.42 | 2597.1766 |  |  |  | 0 | 1 | [14 empty] | 131.7888 | 2597.1766 |  | 104.98
15.05.2008 08:00 | 3600 | 2 | 762.72 | GGB | 762.271 | 771.938 | 765.934 | 269.03 | GGB | 11090.8 | GGB | 9.79 | GGB | 1009.42 | GGB | 59.36 | GGB | 176642.72 | GGB | 144583.11 | GGB | 0 | 0 | 3249 | 3600 | 3233.03 | GGB | 100 | GGB | 39.89 | GGB | 39.89 | GGB | 230712.84 | GGB | 230715.5 | 3233.03 | 2613.9153 |  |  |  | 0 | 1 | [14 empty] | 129.8449 | 2613.9153 |  | 104.98
15.05.2008 09:00 | 3600 | 2 | 763.64 | GGB | 762.271 | 773.086 | 767.033 | 267.59 | GGB | 11059.1 | GGB | 9.8 | GGB | 1009.21 | GGB | 59.75 | GGB | 175256.3 | GGB | 143249.25 | GGB | 0 | 0 | 3186 | 3600 | 3170.34 | GGB | 100 | GGB | 40.21 | GGB | 40.21 | GGB | 230753.05 | GGB | 230755.71 | 3170.34 | 2638.2547 |  |  |  | 0 | 1 | [14 empty] | 126.1525 | 2638.2547 |  | 104.98
15.05.2008 10:00 | 3600 | 2 | 763.74 | GGB | 763.37 | 774.047 | 768.498 | 266.07 | GGB | 10992.7 | GGB | 9.8 | GGB | 1008.62 | GGB | 60.1 | GGB | 173600.29 | GGB | 141662.25 | GGB | 0 | 0 | 3150 | 3600 | 3134.41 | GGB | 100 | GGB | 40.15 | GGB | 40.15 | GGB | 230793.2 | GGB | 230795.86 | 3134.41 | 2667.8102 |  |  |  | 0 | 1 | [14 empty] | 123.341 | 2667.8102 |  | 104.98
15.05.2008 11:00 | 3600 | 2 | 764.55 | GGB | 764.469 | 776.391 | 769.597 | 264.5 | GGB | 10938.2 | GGB | 9.8 | GGB | 1007.89 | GGB | 60.64 | GGB | 172209.46 | GGB | 140197.11 | GGB | 0 | 0 | 3073 | 3600 | 3057.6 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 230833.27 | GGB | 230835.93 | 3057.6 | 2695.6904 |  |  |  | 1 | 1 |  |  |  |  | 140197.11 | 2695.6904 | 140197.11 | 2695.6904 | 9.4317 | [5 empty] | 119.0741 | 2695.6904 |  | 104.98
15.05.2008 12:00 | 3600 | 2 | 764.97 | GGB | 763.37 | 775.43 | 768.498 | 262.91 | GGB | 10868.1 | GGB | 9.79 | GGB | 1006.87 | GGB | 61.07 | GGB | 170764.72 | GGB | 138705.15 | GGB | 0 | 0 | 3012 | 3600 | 2996.75 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 230873.2 | GGB | 230875.86 | 2996.75 | 2724.6861 |  |  |  | 0 | 1 | [14 empty] | 115.4624 | 2724.6861 |  | 104.98
15.05.2008 13:00 | 3600 | 2 | 765.09 | GGB | 763.37 | 775.289 | 769.597 | 261.79 | GGB | 10826.8 | GGB | 9.79 | GGB | 1005.84 | GGB | 61.42 | GGB | 169965.87 | GGB | 137768.75 | GGB | 0 | 0 | 2988 | 3600 | 2972.8 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 230912.83 | GGB | 230915.49 | 2972.8 | 2743.2056 |  |  |  | 0 | 1 | [14 empty] | 113.7664 | 2743.2056 |  | 104.98
15.05.2008 14:00 | 3600 | 2 | 765.14 | GGB | 763.37 | 773.977 | 768.498 | 260.79 | GGB | 10781.3 | GGB | 9.79 | GGB | 1004.93 | GGB | 61.63 | GGB | 169060.29 | GGB | 136823.3 | GGB | 0 | 0 | 2949 | 3600 | 2933.62 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 230952.11 | GGB | 230954.77 | 2933.62 | 2762.1611 |  |  |  | 0 | 1 | [14 empty] | 111.4965 | 2762.1611 |  | 104.98
15.05.2008 15:00 | 3600 | 2 | 763.72 | GGB | 763.37 | 774.023 | 768.132 | 262.76 | GGB | 10815.1 | GGB | 9.77 | GGB | 1005.15 | GGB | 61.31 | GGB | 170227.75 | GGB | 137931.18 | GGB | 0 | 0 | 3058 | 3600 | 3042.72 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 230991.42 | GGB | 230994.08 | 3042.72 | 2739.9751 |  |  |  | 0 | 1 | [14 empty] | 116.5794 | 2739.9751 |  | 104.98
15.05.2008 16:00 | 3600 | 2 | 763.76 | GGB | 762.271 | 774 | 768.498 | 264.51 | GGB | 10864.9 | GGB | 9.78 | GGB | 1005.58 | GGB | 61.16 | GGB | 171352.3 | GGB | 138964.04 | GGB | 0 | 0 | 3087 | 3600 | 3071.25 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 231031.02 | GGB | 231033.68 | 3071.25 | 2719.6101 |  |  |  | 0 | 1 | [14 empty] | 118.5537 | 2719.6101 |  | 104.98
15.05.2008 17:00 | 3600 | 2 | 763.83 | GGB | 763.37 | 773.93 | 768.498 | 265.07 | GGB | 10895.3 | GGB | 9.79 | GGB | 1005.76 | GGB | 61.24 | GGB | 171878.26 | GGB | 139383.27 | GGB | 0 | 0 | 3095 | 3600 | 3079.26 | GGB | 100 | GGB | 40 | GGB | 40 | GGB | 231071.02 | GGB | 231073.68 | 3079.26 | 2711.4301 |  |  |  | 0 | 1 | [14 empty] | 119.2215 | 2711.4301 |  | 104.98
15.05.2008 18:00 | 3600 | 2 | 763.56 | GGB | 761.172 | 771.703 | 765.934 | 265.14 | GGB | 10900.7 | GGB | 9.78 | GGB | 1005.72 | GGB | 61.21 | GGB | 172033.41 | GGB | 139517.78 | GGB | 0 | 0 | 3107 | 3600 | 3091.34 | GGB | 100 | GGB | 39.93 | GGB | 39.93 | GGB | 231110.95 | GGB | 231113.61 | 3091.34 | 2708.816 |  |  |  | 0 | 1 | [14 empty] | 119.8047 | 2708.816 |  | 104.98
15.05.2008 19:00 | 3600 | 2 | 763.47 | GGB | 763.37 | 774.234 | 768.132 | 265.42 | GGB | 10924.9 | GGB | 9.79 | GGB | 1005.91 | GGB | 61.2 | GGB | 172570.37 | GGB | 139982.67 | GGB | 0 | 0 | 3127 | 3600 | 3111.55 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 231150.89 | GGB | 231153.56 | 3111.55 | 2699.8199 |  |  |  | 0 | 1 | [14 empty] | 120.9897 | 2699.8199 |  | 104.98
15.05.2008 20:00 | 3600 | 2 | 763.2 | GGB | 762.271 | 773.227 | 767.033 | 265.53 | GGB | 10931 | GGB | 9.79 | GGB | 1005.71 | GGB | 61.13 | GGB | 172655.1 | GGB | 140054.21 | GGB | 0 | 0 | 3149 | 3600 | 3133.41 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 231190.85 | GGB | 231193.51 | 3133.41 | 2698.4408 |  |  |  | 0 | 1 | [14 empty] | 121.902 | 2698.4408 |  | 104.98
15.05.2008 21:00 | 3600 | 2 | 763.08 | GGB | 762.271 | 773.063 | 768.132 | 265.35 | GGB | 10932.1 | GGB | 9.79 | GGB | 1005.93 | GGB | 61 | GGB | 172548.36 | GGB | 140050.75 | GGB | 0 | 0 | 3150 | 3600 | 3133.94 | GGB | 100 | GGB | 39.59 | GGB | 39.59 | GGB | 231230.43 | GGB | 231233.1 | 3133.94 | 2698.5075 |  |  |  | 0 | 1 | [14 empty] | 121.9196 | 2698.5075 |  | 104.98
15.05.2008 22:00 | 3600 | 2 | 761.67 | GGB | 761.172 | 772.289 | 765.934 | 267.01 | GGB | 10955.4 | GGB | 9.77 | GGB | 1006.18 | GGB | 60.71 | GGB | 173803.85 | GGB | 141227.04 | GGB | 0 | 0 | 3222 | 3600 | 3205.79 | GGB | 100 | GGB | 39.49 | GGB | 39.49 | GGB | 231269.92 | GGB | 231272.59 | 3205.79 | 2676.0314 |  |  |  | 0 | 1 | [14 empty] | 125.7623 | 2676.0314 |  | 104.98
15.05.2008 23:00 | 3600 | 2 | 762.7 | GGB | 763.37 | 773.555 | 768.498 | 267.03 | GGB | 11016.2 | GGB | 9.79 | GGB | 1006.2 | GGB | 60.49 | GGB | 174543.28 | GGB | 141924.75 | GGB | 0 | 0 | 3209 | 3600 | 3193.07 | GGB | 100 | GGB | 39.52 | GGB | 39.52 | GGB | 231309.44 | GGB | 231312.11 | 3193.07 | 2662.8759 |  |  |  | 0 | 1 | [14 empty] | 125.8821 | 2662.8759 |  | 104.98
15.05.2008 24:00 | 3600 | 2 | 761.28 | GGB | 762.271 | 772.734 | 767.033 | 268.1 | GGB | 11004.5 | GGB | 9.78 | GGB | 1006.36 | GGB | 60.22 | GGB | 174944.9 | GGB | 142388.1 | GGB | 0 | 0 | 3278 | 3600 | 3261.98 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 231348.92 | GGB | 231351.59 | 3261.98 | 2654.2106 |  |  |  | 0 | 1 | [14 empty] | 129.0186 | 2654.2106 |  | 104.98
16.05.2008 01:00 | 3600 | 2 | 761.44 | GGB | 761.172 | 771.68 | 765.934 | 268.32 | GGB | 11031.7 | GGB | 9.78 | GGB | 1006.1 | GGB | 59.94 | GGB | 175290.41 | GGB | 142754.82 | GGB | 0 | 0 | 3280 | 3600 | 3264.5 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 231388.77 | GGB | 231391.44 | 3264.5 | 2647.3922 |  |  |  | 0 | 1 | [14 empty] | 129.4509 | 2647.3922 |  | 104.98
16.05.2008 02:00 | 3600 | 2 | 761.06 | GGB | 759.707 | 770.391 | 764.469 | 269.1 | GGB | 11048.2 | GGB | 9.77 | GGB | 1006.32 | GGB | 59.67 | GGB | 176236.7 | GGB | 143672.21 | GGB | 0 | 0 | 3324 | 3600 | 3308.2 | GNB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 231428.71 | GGB | 231431.38 | 3308.2 | 2630.4878 |  |  |  | 0 | 1 | [14 empty] | 132.0268 | 2630.4878 |  | 104.98
16.05.2008 03:00 | 3600 | 2 | 760.66 | GGB | 757.509 | 767.203 | 762.271 | 271.14 | GGB | 11086.9 | GGB | 9.77 | GGB | 1006.12 | GGB | 59.07 | GGB | 178940.23 | GGB | 146111.99 | GGB | 0 | 0 | 3365 | 3600 | 3348.69 | GNB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 231468.87 | GGB | 231471.54 | 3348.69 | 2586.5639 |  |  |  | 0 | 1 | [14 empty] | 135.9122 | 2586.5639 |  | 104.98
16.05.2008 04:00 | 3600 | 2 | 761.79 | GGB | 761.172 | 771.82 | 765.934 | 271.83 | GGB | 11187.6 | GGB | 9.8 | GGB | 1006.32 | GGB | 58.78 | GGB | 179770.98 | GGB | 146947.92 | GGB | 0 | 0 | 3366 | 3600 | 3350.08 | GNB | 100 | GGB | 40.16 | GGB | 40.16 | GGB | 231509.04 | GGB | 231511.7 | 3350.08 | 2571.8499 |  |  |  | 0 | 1 | [14 empty] | 136.7465 | 2571.8499 |  | 104.98
16.05.2008 05:00 | 3600 | 2 | 760.82 | GGB | 762.271 | 771.633 | 767.033 | 271.43 | GGB | 11182.3 | GGB | 9.78 | GGB | 1006.32 | GGB | 58.8 | GGB | 179702.76 | GGB | 146884.32 | GGB | 0 | 0 | 3400 | 3600 | 3383.73 | GNB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 231549.38 | GGB | 231552.05 | 3383.73 | 2572.9635 |  |  |  | 0 | 1 | [14 empty] | 138.0602 | 2572.9635 |  | 104.98
16.05.2008 06:00 | 3600 | 2 | 760.13 | GGB | 760.806 | 770.719 | 764.835 | 271.79 | GGB | 11188.6 | GGB | 9.77 | GGB | 1005.82 | GGB | 58.41 | GGB | 180689.76 | GGB | 147790.26 | GGB | 0 | 0 | 3438 | 3600 | 3422 | GNB | 100 | GGB | 40.48 | GGB | 40.48 | GGB | 231589.86 | GGB | 231592.53 | 3422 | 2557.1915 |  |  |  | 0 | 1 | [14 empty] | 140.4829 | 2557.1915 |  | 104.98
16.05.2008 07:00 | 3600 | 2 | 761.68 | GGB | 762.271 | 772.711 | 767.033 | 271.77 | GGB | 11244.6 | GGB | 9.81 | GGB | 1006.07 | GGB | 58.25 | GGB | 180855.91 | GGB | 148032.67 | GGB | 0 | 0 | 3378 | 3600 | 3361.98 | GNB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 231630.36 | GGB | 231633.03 | 3361.98 | 2553.004 |  |  |  | 0 | 1 | [14 empty] | 138.2452 | 2553.004 |  | 104.98
16.05.2008 08:00 | 3600 | 2 | 762.53 | GGB | 764.835 | 775.805 | 769.597 | 269.58 | GGB | 11201.1 | GGB | 9.81 | GGB | 1005.53 | GGB | 58.62 | GGB | 178756.47 | GGB | 146071.66 | GGB | 0 | 0 | 3314 | 3600 | 3298.52 | GGB | 100 | GGB | 40.69 | GGB | 40.69 | GGB | 231671.05 | GGB | 231673.72 | 3298.52 | 2587.2781 |  |  |  | 1 | 1 |  |  |  |  | 146071.66 | 2587.2781 | 146071.66 | 2587.2781 | 9.288 | [5 empty] | 133.839 | 2587.2781 |  | 104.98
16.05.2008 09:00 | 3600 | 2 | 762.85 | GGB | 762.271 | 772.453 | 767.033 | 267.03 | GGB | 11062.4 | GGB | 9.81 | GGB | 1004.93 | GGB | 59.71 | GGB | 174663.21 | GGB | 142175.95 | GGB | 0 | 0 | 3245 | 3209 | 3229.37 | GGB | 100 | GGB | 40.6 | GGB | 40.6 | GGB | 231711.64 | GGB | 231714.32 | 3229.37 | 2658.1711 |  |  |  | 0 | 1 | [14 empty] | 127.5385 | 2658.1711 |  | 104.98
16.05.2008 10:00 | 3600 | 2 | 763.71 | GGB | 763.37 | 774.586 | 768.498 | 264.6 | GGB | 10911.2 | GGB | 9.8 | GGB | 1004.31 | GGB | 61.21 | GGB | 171187.25 | GGB | 138636.14 | GGB | 0 | 0 | 3154 | 3600 | 3138.17 | GGB | 100 | GGB | 40.09 | GGB | 40.09 | GGB | 231751.73 | GGB | 231754.41 | 3138.17 | 2726.0424 |  |  |  | 0 | 1 | [14 empty] | 120.851 | 2726.0424 |  | 104.98
16.05.2008 11:00 | 3600 | 2 | 764.89 | GGB | 765.934 | 776.859 | 770.696 | 263.47 | GGB | 10793.2 | GGB | 9.8 | GGB | 1003.62 | GGB | 61.68 | GGB | 170726.2 | GGB | 137971.34 | GGB | 0 | 0 | 3028 | 3600 | 3012.13 | GGB | 100 | GGB | 39.3 | GGB | 39.3 | GGB | 231791.03 | GGB | 231793.71 | 3012.13 | 2739.1776 |  |  |  | 1 | 1 |  |  |  |  | 137971.34 | 2739.1776 | 137971.34 | 2739.1776 | 9.6165 | [5 empty] | 115.441 | 2739.1776 |  | 104.98
16.05.2008 12:00 | 3600 | 2 | 765.35 | GGB | 763.37 | 775.641 | 769.597 | 259.9 | GGB | 10732.3 | GGB | 9.8 | GGB | 1001.99 | GGB | 62.56 | GGB | 167110.49 | GGB | 134478.01 | GGB | 0 | 0 | 2962 | 3600 | 2946.61 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 231829.96 | GGB | 231832.64 | 2946.61 | 2810.3331 |  |  |  | 0 | 1 | [14 empty] | 110.0706 | 2810.3331 |  | 104.98
16.05.2008 13:00 | 3600 | 2 | 764.19 | GGB | 761.172 | 772.336 | 767.033 | 260.91 | GGB | 10735.7 | GGB | 9.77 | GGB | 1002.2 | GGB | 62.35 | GGB | 167690.37 | GGB | 135058.99 | GGB | 0 | 0 | 3034 | 3600 | 3017.9 | GGB | 100 | GGB | 39.25 | GGB | 39.25 | GGB | 231869.21 | GGB | 231871.89 | 3017.9 | 2798.2439 |  |  |  | 0 | 1 | [14 empty] | 113.2207 | 2798.2439 |  | 104.98
16.05.2008 14:00 | 3600 | 2 | 765.25 | GGB | 764.835 | 776.93 | 770.696 | 261.22 | GGB | 10704.7 | GGB | 9.8 | GGB | 1001.93 | GGB | 62.37 | GGB | 168389.09 | GGB | 135575.6 | GGB | 0 | 0 | 2967 | 3600 | 2951.24 | GGB | 100 | GGB | 39.46 | GGB | 39.46 | GGB | 231908.66 | GGB | 231911.35 | 2951.24 | 2787.5812 |  |  |  | 1 | 1 |  |  |  |  | 135575.6 | 2787.5812 | 135575.6 | 2787.5812 | 9.5775 | [5 empty] | 111.1434 | 2787.5812 |  | 104.98
16.05.2008 15:00 | 3600 | 2 | 766.19 | GGB | 765.934 | 777.938 | 771.795 | 258.61 | GGB | 10614.2 | GGB | 9.8 | GGB | 1000.61 | GGB | 62.84 | GGB | 166228.02 | GGB | 133470.88 | GGB | 0 | 0 | 2865 | 3600 | 2849.23 | GGB | 100 | GGB | 39.34 | GGB | 39.34 | GGB | 231948.01 | GGB | 231950.69 | 2849.23 | 2831.539 |  |  |  | 1 | 1 |  |  |  |  | 133470.88 | 2831.539 | 133470.88 | 2831.539 | 9.6067 | [5 empty] | 105.6359 | 2831.539 |  | 104.98
16.05.2008 16:00 | 3600 | 2 | 765.54 | GGB | 763.37 | 775.734 | 769.597 | 256.17 | GGB | 10564.4 | GGB | 9.78 | GGB | 999.04 | GGB | 63.58 | GGB | 163564.11 | GGB | 130838.38 | GGB | 0 | 0 | 2871 | 3600 | 2855.42 | GGB | 100 | GGB | 38.59 | GGB | 38.59 | GGB | 231986.59 | GGB | 231989.28 | 2855.42 | 2855.42 |  |  |  | 0 | 1 | [14 empty] | 103.7774 |  |  | #VALUE!
16.05.2008 17:00 | 3600 | 2 | 764.96 | GGB | 762.271 | 774.891 | 768.132 | 257.61 | GGB | 10602.3 | GGB | 9.78 | GGB | 998.7 | GGB | 63.33 | GGB | 164335.44 | GGB | 131507.19 | GGB | 0 | 0 | 2931 | 3600 | 2915.78 | GGB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 232025.12 | GGB | 232027.81 | 2915.78 | 2873.8201 |  |  |  | 0 | 1 | [14 empty] | 106.5128 | 2873.8201 |  | 104.98
16.05.2008 18:00 | 3600 | 2 | 764.89 | GGB | 764.469 | 775.922 | 770.696 | 258.18 | GGB | 10633.2 | GGB | 9.79 | GGB | 998.72 | GGB | 63.61 | GGB | 164610.53 | GGB | 131621.58 | GGB | 0 | 0 | 2959 | 3600 | 2943.11 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 232063.88 | GGB | 232066.57 | 2943.11 | 2871.3225 |  |  |  | 1 | 1 |  |  |  |  | 131621.58 | 2871.3225 | 131621.58 | 2871.3225 | 9.7505 | [5 empty] | 107.6047 | 2871.3225 |  | 104.98
16.05.2008 19:00 | 3600 | 2 | 764.77 | GGB | 763.37 | 774.82 | 768.498 | 258.07 | GGB | 10612.3 | GGB | 9.78 | GGB | 998.65 | GGB | 63.81 | GGB | 164500.49 | GGB | 131445.26 | GGB | 0 | 0 | 2959 | 3600 | 2943.28 | GGB | 100 | GGB | 38.54 | GGB | 38.54 | GGB | 232102.42 | GGB | 232105.11 | 2943.28 | 2875.174 |  |  |  | 0 | 1 | [14 empty] | 107.4667 | 2875.174 |  | 104.98
16.05.2008 20:00 | 3600 | 2 | 764.48 | GGB | 763.37 | 774.867 | 768.498 | 258.55 | GGB | 10619.2 | GGB | 9.78 | GGB | 999.15 | GGB | 63.78 | GGB | 164468.58 | GGB | 131498.7 | GGB | 0 | 0 | 2982 | 3600 | 2966.4 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 232140.9 | GGB | 232143.59 | 2966.4 | 2874.0056 |  |  |  | 0 | 1 | [14 empty] | 108.3549 | 2874.0056 |  | 104.98
16.05.2008 21:00 | 3600 | 2 | 764.31 | GGB | 763.37 | 774.867 | 768.498 | 259.94 | GGB | 10669 | GGB | 9.78 | GGB | 999.53 | GGB | 63.4 | GGB | 165770.28 | GGB | 132737.31 | GGB | 0 | 0 | 3018 | 3600 | 3002.55 | GGB | 100 | GGB | 38.51 | GGB | 38.51 | GGB | 232179.41 | GGB | 232182.1 | 3002.55 | 2847.1874 |  |  |  | 0 | 1 | [14 empty] | 110.7084 | 2847.1874 |  | 104.98
16.05.2008 22:00 | 3600 | 2 | 763.9 | GGB | 763.37 | 774.867 | 768.132 | 261.15 | GGB | 10721.2 | GGB | 9.78 | GGB | 1000.49 | GGB | 63.09 | GGB | 166740.78 | GGB | 133766.76 | GGB | 0 | 0 | 3064 | 3600 | 3048.58 | GGB | 100 | GGB | 38.77 | GGB | 38.77 | GGB | 232218.18 | GGB | 232220.87 | 3048.58 | 2825.2759 |  |  |  | 0 | 1 | [14 empty] | 113.2774 | 2825.2759 |  | 104.98
16.05.2008 23:00 | 3600 | 2 | 762.97 | GGB | 761.172 | 772.594 | 765.934 | 262.97 | GGB | 10769.6 | GGB | 9.77 | GGB | 1001.25 | GGB | 62.75 | GGB | 168370.38 | GGB | 135313.89 | GGB | 0 | 0 | 3133 | 3600 | 3117.24 | GGB | 100 | GGB | 38.98 | GGB | 38.98 | GGB | 232257.16 | GGB | 232259.85 | 3117.24 | 2792.9727 |  |  |  | 0 | 1 | [14 empty] | 117.1683 | 2792.9727 |  | 104.98
16.05.2008 24:00 | 3600 | 2 | 762.83 | GGB | 762.271 | 772.453 | 767.033 | 264.15 | GGB | 10830.1 | GGB | 9.78 | GGB | 1001.89 | GGB | 62.28 | GGB | 169867.94 | GGB | 136795.87 | GGB | 0 | 0 | 3168 | 3600 | 3152.12 | GGB | 100 | GGB | 39.15 | GGB | 39.15 | GGB | 232296.31 | GGB | 232299 | 3152.12 | 2762.715 |  |  |  | 0 | 1 | [14 empty] | 119.7769 | 2762.715 |  | 104.98
17.05.2008 01:00 | 3600 | 2 | 762.16 | GGB | 759.707 | 771.188 | 764.469 | 265.54 | GGB | 10870.5 | GGB | 9.77 | GGB | 1002.25 | GGB | 61.72 | GGB | 171242.26 | GGB | 138184.26 | GGB | 0 | 0 | 3212 | 3600 | 3196.52 | GGB | 100 | GGB | 39.28 | GGB | 39.28 | GGB | 232335.59 | GGB | 232338.28 | 3196.52 | 2734.9569 |  |  |  | 0 | 1 | [14 empty] | 122.6969 | 2734.9569 |  | 104.98
17.05.2008 02:00 | 3600 | 2 | 761.93 | GGB | 760.806 | 771.094 | 764.835 | 267.14 | GGB | 10933.6 | GGB | 9.78 | GGB | 1002.65 | GGB | 61.12 | GGB | 173141.45 | GGB | 140022.36 | GGB | 0 | 0 | 3256 | 3600 | 3239.99 | GGB | 100 | GGB | 39.4 | GGB | 39.4 | GGB | 232374.98 | GGB | 232377.68 | 3239.99 | 2699.0546 |  |  |  | 0 | 1 | [14 empty] | 126.0197 | 2699.0546 |  | 104.98
17.05.2008 03:00 | 3600 | 2 | 762.13 | GGB | 762.271 | 773.297 | 767.033 | 267.68 | GGB | 10993.6 | GGB | 9.79 | GGB | 1002.84 | GGB | 60.76 | GGB | 174224.18 | GGB | 141075.85 | GGB | 0 | 0 | 3264 | 3600 | 3247.8 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 232414.51 | GGB | 232417.21 | 3247.8 | 2678.8993 |  |  |  | 0 | 1 | [14 empty] | 127.2739 | 2678.8993 |  | 104.98
17.05.2008 04:00 | 3600 | 2 | 761.46 | GGB | 762.271 | 772.266 | 767.033 | 267.73 | GGB | 11001.1 | GGB | 9.78 | GGB | 1003.05 | GGB | 60.58 | GGB | 174828.26 | GGB | 141674.65 | GGB | 0 | 0 | 3298 | 3600 | 3282.11 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 232454.26 | GGB | 232456.96 | 3282.11 | 2667.5767 |  |  |  | 0 | 1 | [14 empty] | 129.1644 | 2667.5767 |  | 104.98
17.05.2008 05:00 | 3600 | 2 | 761.65 | GGB | 761.172 | 771.234 | 765.934 | 267.51 | GGB | 11006.6 | GGB | 9.79 | GGB | 1003.15 | GGB | 60.44 | GGB | 174754.54 | GGB | 141689.44 | GGB | 0 | 0 | 3291 | 3600 | 3275.12 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 232494.11 | GGB | 232496.81 | 3275.12 | 2667.2983 |  |  |  | 0 | 1 | [14 empty] | 128.9028 | 2667.2983 |  | 104.98
17.05.2008 06:00 | 3600 | 2 | 761.17 | GGB | 761.172 | 771.281 | 765.934 | 268.15 | GGB | 11023 | GGB | 9.78 | GGB | 1003.29 | GGB | 60.17 | GGB | 175512.67 | GGB | 142437.67 | GGB | 0 | 0 | 3329 | 3600 | 3313.54 | GNB | 100 | GGB | 39.94 | GGB | 39.94 | GGB | 232534.05 | GGB | 232536.75 | 3313.54 | 2653.2869 |  |  |  | 0 | 1 | [14 empty] | 131.1036 | 2653.2869 |  | 104.98
17.05.2008 07:00 | 3600 | 2 | 761.25 | GGB | 761.172 | 772.383 | 767.033 | 268.21 | GGB | 11036.8 | GGB | 9.79 | GGB | 1003.63 | GGB | 59.9 | GGB | 175577.59 | GGB | 142654.66 | GGB | 0 | 0 | 3327 | 3600 | 3310.64 | GNB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 232574.41 | GGB | 232577.11 | 3310.64 | 2649.251 |  |  |  | 0 | 1 | [14 empty] | 131.1884 | 2649.251 |  | 104.98
17.05.2008 08:00 | 3600 | 2 | 761.82 | GGB | 762.271 | 773.297 | 767.033 | 267.43 | GGB | 11030.9 | GGB | 9.8 | GGB | 1003.98 | GGB | 59.97 | GGB | 174672.02 | GGB | 141935.92 | GGB | 0 | 0 | 3296 | 3600 | 3280.1 | GGB | 100 | GGB | 40.43 | GGB | 40.43 | GGB | 232614.84 | GGB | 232617.54 | 3280.1 | 2662.6664 |  |  |  | 0 | 1 | [14 empty] | 129.3233 | 2662.6664 |  | 104.98
17.05.2008 09:00 | 3600 | 2 | 762.98 | GGB | 763.37 | 774.281 | 767.033 | 264.45 | GGB | 10951.9 | GGB | 9.81 | GGB | 1003.7 | GGB | 60.84 | GGB | 171725.31 | GGB | 139141.4 | GGB | 0 | 0 | 3220 | 3600 | 3204.37 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 232654.88 | GGB | 232657.58 | 3204.37 | 2716.1434 |  |  |  | 0 | 1 | [14 empty] | 123.8501 | 2716.1434 |  | 104.98
17.05.2008 10:00 | 3600 | 2 | 763.63 | GGB | 763.37 | 774.305 | 769.597 | 262.54 | GGB | 10854.9 | GGB | 9.8 | GGB | 1003.41 | GGB | 61.9 | GGB | 169175.83 | GGB | 136600.73 | GGB | 0 | 0 | 3155 | 3600 | 3138.77 | GGB | 100 | GGB | 39.67 | GGB | 39.67 | GGB | 232694.55 | GGB | 232697.25 | 3138.77 | 2766.6616 |  |  |  | 0 | 1 | [14 empty] | 119.0995 | 2766.6616 |  | 104.98
17.05.2008 11:00 | 3600 | 2 | 764.31 | GGB | 763.37 | 774.094 | 768.132 | 261.17 | GGB | 10769.5 | GGB | 9.79 | GGB | 1003.44 | GGB | 62.36 | GGB | 167859.82 | GGB | 135356.23 | GGB | 0 | 0 | 3056 | 3600 | 3040.46 | GGB | 100 | GGB | 39.43 | GGB | 39.43 | GGB | 232733.98 | GGB | 232736.68 | 3040.46 | 2792.099 |  |  |  | 0 | 1 | [14 empty] | 114.3181 | 2792.099 |  | 104.98
17.05.2008 12:00 | 3600 | 2 | 764.59 | GGB | 763.37 | 775.219 | 768.498 | 260.96 | GGB | 10751.4 | GGB | 9.79 | GGB | 1003.67 | GGB | 62.55 | GGB | 167682.67 | GGB | 135167.19 | GGB | 0 | 0 | 3034 | 3600 | 3018.44 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 232772.68 | GGB | 232775.38 | 3018.44 | 2796.004 |  |  |  | 0 | 1 | [14 empty] | 113.3317 | 2796.004 |  | 104.98
17.05.2008 13:00 | 3600 | 2 | 764.37 | GGB | 763.37 | 774.727 | 768.498 | 261.02 | GGB | 10760 | GGB | 9.78 | GGB | 1003.66 | GGB | 62.28 | GGB | 167831.22 | GGB | 135395.92 | GGB | 0 | 0 | 3049 | 3600 | 3032.85 | GGB | 100 | GGB | 38.5 | GGB | 38.5 | GGB | 232811.18 | GGB | 232813.88 | 3032.85 | 2791.2806 |  |  |  | 0 | 1 | [14 empty] | 114.0654 | 2791.2806 |  | 104.98
17.05.2008 14:00 | 3600 | 2 | 763.77 | GGB | 763.37 | 774.492 | 768.132 | 261.73 | GGB | 10794 | GGB | 9.79 | GGB | 1003.66 | GGB | 62.45 | GGB | 168060.09 | GGB | 135513.59 | GGB | 0 | 0 | 3115 | 3600 | 3098.92 | GGB | 100 | GGB | 39.7 | GGB | 39.7 | GGB | 232850.88 | GGB | 232853.58 | 3098.92 | 2788.8568 |  |  |  | 0 | 1 | [14 empty] | 116.6516 | 2788.8568 |  | 104.98
17.05.2008 15:00 | 3600 | 2 | 764.3 | GGB | 763.37 | 774.563 | 768.498 | 260.5 | GGB | 10747.7 | GGB | 9.79 | GGB | 1003.23 | GGB | 63.19 | GGB | 166446.99 | GGB | 133858.29 | GGB | 0 | 0 | 3071 | 3600 | 3055.47 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 232891.07 | GGB | 232893.77 | 3055.47 | 2823.344 |  |  |  | 0 | 1 | [14 empty] | 113.6111 | 2823.344 |  | 104.98
17.05.2008 16:00 | 3600 | 2 | 764.85 | GGB | 763.37 | 774.563 | 768.498 | 259.02 | GGB | 10678.1 | GGB | 9.79 | GGB | 1002.17 | GGB | 63.45 | GGB | 165378.56 | GGB | 132754.66 | GGB | 0 | 0 | 3004 | 3600 | 2987.85 | GGB | 100 | GGB | 39.39 | GGB | 39.39 | GGB | 232930.46 | GGB | 232933.16 | 2987.85 | 2846.8153 |  |  |  | 0 | 1 | [14 empty] | 110.1808 | 2846.8153 |  | 104.98
17.05.2008 17:00 | 3600 | 2 | 765.18 | GGB | 763.37 | 775.453 | 769.597 | 258.1 | GGB | 10635.7 | GGB | 9.79 | GGB | 1001.62 | GGB | 63.54 | GGB | 164875.71 | GGB | 132244.85 | GGB | 0 | 0 | 2953 | 3600 | 2937.52 | GGB | 100 | GGB | 38.39 | GGB | 38.39 | GGB | 232968.85 | GGB | 232971.55 | 2937.52 | 2857.7899 |  |  |  | 0 | 1 | [14 empty] | 107.9089 | 2857.7899 |  | 104.98
17.05.2008 18:00 | 3600 | 2 | 765.79 | GGB | 764.469 | 776.625 | 770.696 | 256.48 | GGB | 10576.1 | GGB | 9.8 | GGB | 1000.64 | GGB | 64.13 | GGB | 163498.09 | GGB | 130782.71 | GGB | 0 | 0 | 2891 | 3600 | 2875.12 | GGB | 100 | GGB | 37.9 | GGB | 37.9 | GGB | 233006.75 | GGB | 233009.45 | 2875.12 | 2875.12 |  |  |  | 1 | 1 |  |  |  |  | 130782.71 | 2875.12 | 130782.71 | 2875.12 | 9.9213 | [5 empty] | 104.4489 |  |  | #VALUE!
17.05.2008 19:00 | 3600 | 2 | 765.51 | GGB | 764.469 | 775.406 | 769.597 | 256 | GGB | 10546.1 | GGB | 9.79 | GGB | 1000.1 | GGB | 64.3 | GGB | 162890.7 | GGB | 130160.99 | GGB | 0 | 0 | 2889 | 3600 | 2873.85 | GGB | 100 | GGB | 37.9 | GGB | 37.9 | GGB | 233044.64 | GGB | 233047.35 | 2873.85 | 2873.85 |  |  |  | 1 | 1 |  |  |  |  | 130160.99 | 2873.85 | 130160.99 | 2873.85 | 9.8697 | [5 empty] | 103.9064 |  |  | #VALUE!
17.05.2008 20:00 | 3600 | 2 | 765.24 | GGB | 763.37 | 776.555 | 769.597 | 256.37 | GGB | 10541.9 | GGB | 9.78 | GGB | 1000.27 | GGB | 64.49 | GGB | 162724.55 | GGB | 129974.11 | GGB | 0 | 0 | 2908 | 3600 | 2891.92 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 233082.81 | GGB | 233085.51 | 2891.92 | 2891.92 |  |  |  | 0 | 1 | [14 empty] | 104.4096 |  |  | #VALUE!
17.05.2008 21:00 | 3600 | 2 | 765.05 | GGB | 763.37 | 775.383 | 768.498 | 257.05 | GGB | 10558.7 | GGB | 9.78 | GGB | 1000.17 | GGB | 64.42 | GGB | 163068.95 | GGB | 130267.07 | GGB | 0 | 0 | 2930 | 3600 | 2914.84 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 233121.55 | GGB | 233124.25 | 2914.84 | 2901.1783 |  |  |  | 0 | 1 | [14 empty] | 105.4744 | 2901.1783 |  | 104.98
17.05.2008 22:00 | 3600 | 2 | 764.47 | GGB | 761.172 | 773.156 | 767.033 | 259.02 | GGB | 10620.1 | GGB | 9.78 | GGB | 1000.56 | GGB | 64.01 | GGB | 164645.74 | GGB | 131734.28 | GGB | 0 | 0 | 3000 | 3600 | 2984.06 | GGB | 100 | GGB | 38.9 | GGB | 38.9 | GGB | 233160.45 | GGB | 233163.15 | 2984.06 | 2868.866 |  |  |  | 0 | 1 | [14 empty] | 109.1953 | 2868.866 |  | 104.98
17.05.2008 23:00 | 3600 | 2 | 763.84 | GGB | 762.271 | 774.234 | 767.033 | 260.89 | GGB | 10695.3 | GGB | 9.78 | GGB | 1001.07 | GGB | 63.54 | GGB | 166290.74 | GGB | 133305.19 | GGB | 0 | 0 | 3073 | 3600 | 3057.6 | GGB | 100 | GGB | 38.75 | GGB | 38.75 | GGB | 233199.2 | GGB | 233201.9 | 3057.6 | 2835.0584 |  |  |  | 0 | 1 | [14 empty] | 113.2205 | 2835.0584 |  | 104.98
17.05.2008 24:00 | 3600 | 2 | 763.54 | GGB | 761.172 | 771.961 | 765.934 | 261.11 | GGB | 10711.8 | GGB | 9.78 | GGB | 1000.71 | GGB | 63.36 | GGB | 166618.64 | GGB | 133591.1 | GGB | 0 | 0 | 3093 | 3600 | 3077.23 | GGB | 100 | GGB | 38.81 | GGB | 38.81 | GGB | 233238.01 | GGB | 233240.71 | 3077.23 | 2828.9909 |  |  |  | 0 | 1 | [14 empty] | 114.1918 | 2828.9909 |  | 104.98
18.05.2008 01:00 | 3600 | 2 | 763.59 | GGB | 761.172 | 772.43 | 765.934 | 262.08 | GGB | 10749 | GGB | 9.78 | GGB | 1000.76 | GGB | 63.19 | GGB | 167446.1 | GGB | 134329.53 | GGB | 0 | 0 | 3117 | 3600 | 3101.2 | GGB | 100 | GGB | 38.89 | GGB | 38.89 | GGB | 233276.91 | GGB | 233279.6 | 3101.2 | 2813.4395 |  |  |  | 0 | 1 | [14 empty] | 115.7174 | 2813.4395 |  | 104.98
18.05.2008 02:00 | 3600 | 2 | 763.88 | GGB | 763.37 | 775.43 | 768.498 | 261.72 | GGB | 10796.5 | GGB | 9.8 | GGB | 1000.54 | GGB | 62.97 | GGB | 168301.06 | GGB | 135075.83 | GGB | 0 | 0 | 3115 | 3600 | 3099.69 | GGB | 100 | GGB | 38.95 | GGB | 38.95 | GGB | 233315.85 | GGB | 233318.55 | 3099.69 | 2797.8951 |  |  |  | 0 | 1 | [14 empty] | 116.3037 | 2797.8951 |  | 104.98
18.05.2008 03:00 | 3600 | 2 | 762.85 | GGB | 763.37 | 775.172 | 768.498 | 261.91 | GGB | 10759.5 | GGB | 9.78 | GGB | 999.69 | GGB | 62.88 | GGB | 167864.23 | GGB | 134646.95 | GGB | 0 | 0 | 3161 | 3600 | 3144.89 | GGB | 100 | GGB | 39.03 | GGB | 39.03 | GGB | 233354.88 | GGB | 233357.58 | 3144.89 | 2806.807 |  |  |  | 0 | 1 | [14 empty] | 117.625 | 2806.807 |  | 104.98
18.05.2008 04:00 | 3600 | 2 | 763.12 | GGB | 762.271 | 774.117 | 767.033 | 261.65 | GGB | 10756.9 | GGB | 9.78 | GGB | 999.06 | GGB | 62.91 | GGB | 167700.28 | GGB | 134419.4 | GGB | 0 | 0 | 3148 | 3600 | 3132.02 | GGB | 100 | GGB | 39.31 | GGB | 39.31 | GGB | 233394.2 | GGB | 233396.89 | 3132.02 | 2811.5585 |  |  |  | 0 | 1 | [14 empty] | 116.9456 | 2811.5585 |  | 104.98
18.05.2008 05:00 | 3600 | 2 | 763.26 | GGB | 763.37 | 774.75 | 768.132 | 261.93 | GGB | 10765.4 | GGB | 9.79 | GGB | 998.87 | GGB | 62.97 | GGB | 167925.85 | GGB | 134549.6 | GGB | 0 | 0 | 3150 | 3600 | 3134.57 | GGB | 100 | GGB | 39.24 | GGB | 39.24 | GGB | 233433.44 | GGB | 233436.13 | 3134.57 | 2808.8378 |  |  |  | 0 | 1 | [14 empty] | 117.1542 | 2808.8378 |  | 104.98
18.05.2008 06:00 | 3600 | 2 | 763.25 | GGB | 762.271 | 773.859 | 768.132 | 261.88 | GGB | 10754.1 | GGB | 9.79 | GGB | 998.11 | GGB | 62.97 | GGB | 167666.17 | GGB | 134236.83 | GGB | 0 | 0 | 3141 | 3600 | 3125.49 | GGB | 100 | GGB | 39.22 | GGB | 39.22 | GGB | 233472.66 | GGB | 233475.35 | 3125.49 | 2815.3823 |  |  |  | 0 | 1 | [14 empty] | 116.5433 | 2815.3823 |  | 104.98
18.05.2008 07:00 | 3600 | 2 | 763.77 | GGB | 762.271 | 774.773 | 767.033 | 260.88 | GGB | 10731 | GGB | 9.79 | GGB | 997.38 | GGB | 63.16 | GGB | 166736.38 | GGB | 133320.92 | GGB | 0 | 0 | 3118 | 3600 | 3102.52 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 233511.59 | GGB | 233514.28 | 3102.52 | 2834.7239 |  |  |  | 0 | 1 | [14 empty] | 114.8975 | 2834.7239 |  | 104.98
18.05.2008 08:00 | 3600 | 2 | 764.21 | GGB | 763.37 | 774.703 | 768.498 | 259.25 | GGB | 10673.3 | GGB | 9.8 | GGB | 997.8 | GGB | 63.65 | GGB | 164840.5 | GGB | 131670.97 | GGB | 0 | 0 | 3082 | 3600 | 3065.77 | GGB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 233550.24 | GGB | 233552.93 | 3065.77 | 2870.2454 |  |  |  | 0 | 1 | [14 empty] | 112.1314 | 2870.2454 |  | 104.98
18.05.2008 09:00 | 3600 | 2 | 764.18 | GGB | 763.37 | 774.703 | 768.498 | 257.99 | GGB | 10602.5 | GGB | 9.79 | GGB | 997.23 | GGB | 64.39 | GGB | 163140.48 | GGB | 129951.01 | GGB | 0 | 0 | 3056 | 3600 | 3039.79 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 233588.9 | GGB | 233591.59 | 3039.79 | 2908.2344 |  |  |  | 0 | 1 | [14 empty] | 109.7288 | 2908.2344 |  | 104.98
18.05.2008 10:00 | 3600 | 2 | 764.36 | GGB | 763.37 | 774.773 | 768.132 | 256.24 | GGB | 10532 | GGB | 9.79 | GGB | 996.72 | GGB | 65.28 | GGB | 161315.02 | GGB | 128094.91 | GGB | 0 | 0 | 3013 | 3600 | 2997.16 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 233627.36 | GGB | 233630.05 | 2997.16 | 2950.3748 |  |  |  | 0 | 1 | [14 empty] | 106.6447 | 2950.3748 |  | 104.98
18.05.2008 11:00 | 3600 | 2 | 764.4 | GGB | 763.37 | 775.688 | 768.498 | 255.14 | GGB | 10485.6 | GGB | 9.79 | GGB | 996.69 | GGB | 65.57 | GGB | 160435.85 | GGB | 127284.1 | GGB | 0 | 0 | 2959 | 3600 | 2943.57 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 233665.53 | GGB | 233668.22 | 2943.57 | 2943.57 |  |  |  | 0 | 1 | [14 empty] | 104.0749 |  |  | #VALUE!
18.05.2008 12:00 | 3600 | 2 | 765.04 | GGB | 764.835 | 775.781 | 770.696 | 254.56 | GGB | 10427.2 | GGB | 9.79 | GGB | 996.56 | GGB | 65.67 | GGB | 159883.48 | GGB | 126787.94 | GGB | 0 | 0 | 2889 | 3600 | 2873.35 | GGB | 100 | GGB | 37.53 | GGB | 37.53 | GGB | 233703.06 | GGB | 233705.75 | 2873.35 | 2873.35 |  |  |  | 1 | 1 |  |  |  |  | 126787.94 | 2873.35 | 126787.94 | 2873.35 | 9.7071 | [5 empty] | 101.1961 |  |  | #VALUE!
18.05.2008 13:00 | 3600 | 2 | 764.52 | GGB | 763.37 | 774.656 | 768.498 | 253.98 | GGB | 10422.2 | GGB | 9.78 | GGB | 996.61 | GGB | 66.11 | GGB | 159305.8 | GGB | 126175.85 | GGB | 0 | 0 | 2921 | 3600 | 2905.3 | GGB | 100 | GGB | 37.57 | GGB | 37.57 | GGB | 233740.63 | GGB | 233743.32 | 2905.3 | 2905.3 |  |  |  | 0 | 1 | [14 empty] | 101.8274 |  |  | #VALUE!
18.05.2008 14:00 | 3600 | 2 | 765.19 | GGB | 763.37 | 774.633 | 769.597 | 253.85 | GGB | 10427.5 | GGB | 9.78 | GGB | 996.89 | GGB | 66.15 | GGB | 159213.37 | GGB | 126120.62 | GGB | 0 | 0 | 2894 | 3600 | 2877.96 | GGB | 100 | GGB | 37.6 | GGB | 37.6 | GGB | 233778.23 | GGB | 233780.92 | 2877.96 | 2877.96 |  |  |  | 0 | 1 | [14 empty] | 100.825 |  |  | #VALUE!
18.05.2008 15:00 | 3600 | 2 | 765.25 | GGB | 763.37 | 775.57 | 769.597 | 253.51 | GGB | 10413.3 | GGB | 9.78 | GGB | 996.59 | GGB | 66.25 | GGB | 159087.93 | GGB | 125947.09 | GGB | 0 | 0 | 2885 | 3600 | 2869.16 | GGB | 100 | GGB | 38.09 | GGB | 38.09 | GGB | 233816.32 | GGB | 233819.01 | 2869.16 | 2869.16 |  |  |  | 0 | 1 | [14 empty] | 100.3784 |  |  | #VALUE!
18.05.2008 16:00 | 3600 | 2 | 764.81 | GGB | 764.469 | 775.711 | 768.864 | 253.52 | GGB | 10415.3 | GGB | 9.78 | GGB | 996.52 | GGB | 65.95 | GGB | 159255.18 | GGB | 126182.36 | GGB | 0 | 0 | 2874 | 2344 | 1363.35 | GNB | 100 | GGB | 38.23 | GGB | 38.23 | GGB | 233854.55 | GGB | 233857.24 | 1363.3839 | 1363.3839 |  |  |  | 1 | 1 |  |  |  |  | 126182.36 | 1363.3839 | 126182.36 |  | 4.5 | 1363.3839 |  |  |  |  | 47.7875 |  |  | #VALUE!
18.05.2008 17:00 | 3600 | 2 | 764.45 | GGB | 762.271 | 773.672 | 767.766 | 254.14 | GGB | 10446.7 | GGB | 9.77 | GGB | 996.73 | GGB | 65.82 | GGB | 159863.67 | GGB | 126741.43 | GGB | 0 | 0 | 0 | 0 | 1353.44 | GNB | 100 | GGB | 38.12 | GGB | 38.12 | GGB | 233892.67 | GGB | 233895.36 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
18.05.2008 18:00 | 3600 | 2 | 764.46 | GGB | 763.37 | 775.852 | 768.864 | 255.32 | GGB | 10496 | GGB | 9.78 | GGB | 997.33 | GGB | 65.49 | GGB | 161045.43 | GGB | 127878.04 | GGB | 0 | 0 | 0 | 0 | 1342.8 | GNB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 233930.83 | GGB | 233933.52 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
18.05.2008 19:00 | 3600 | 2 | 764.17 | GGB | 764.469 | 775.805 | 768.864 | 256.44 | GGB | 10534.6 | GGB | 9.77 | GGB | 998.39 | GGB | 64.9 | GGB | 162332.83 | GGB | 129260.86 | GGB | 0 | 0 | 0 | 0 | 1329.16 | GNB | 100 | GGB | 38.18 | GGB | 38.18 | GGB | 233969.01 | GGB | 233971.7 | 1329.1727 | 1329.1727 |  |  |  | 1 | 1 |  |  |  |  | 129260.86 | 1329.1727 | 129260.86 |  | 4.5 | 1329.1727 |  |  |  |  | 47.725 |  |  | #VALUE!
18.05.2008 20:00 | 3600 | 2 | 764.57 | GGB | 763.37 | 774.492 | 768.864 | 256.44 | GGB | 10554.2 | GGB | 9.78 | GGB | 998.36 | GGB | 64.77 | GGB | 162741.05 | GGB | 129634.18 | GGB | 0 | 0 | 0 | 0 | 1331.03 | GNB | 100 | GGB | 38.34 | GGB | 38.34 | GGB | 234007.36 | GGB | 234010.04 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
18.05.2008 21:00 | 3600 | 2 | 763.81 | GGB | 763.37 | 774.539 | 767.766 | 259.47 | GGB | 10572.8 | GGB | 9.76 | GGB | 999.67 | GGB | 63.5 | GGB | 166211.52 | GGB | 133071.24 | GGB | 0 | 0 | 0 | 0 | 1307.1 | GNB | 100 | GGB | 38.65 | GGB | 38.65 | GGB | 234046.01 | GGB | 234048.69 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
18.05.2008 22:00 | 3600 | 2 | 763.69 | GGB | 762.271 | 773.578 | 767.033 | 259.24 | GGB | 10672.4 | GGB | 9.78 | GGB | 1000.55 | GGB | 63.47 | GGB | 165669.05 | GGB | 132767.81 | GGB | 0 | 0 | 0 | 0 | 1290.36 | GNB | 100 | GGB | 38.07 | GGB | 38.07 | GGB | 234084.08 | GGB | 234086.76 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
18.05.2008 23:00 | 3600 | 2 | 763.21 | GGB | 761.172 | 772.43 | 766.667 | 259.23 | GGB | 10718.6 | GGB | 9.78 | GGB | 1001.16 | GGB | 63.09 | GGB | 166795.8 | GGB | 133902.01 | GGB | 0 | 0 | 0 | 0 | 1286.4 | GNB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 234122.36 | GGB | 234125.04 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
18.05.2008 24:00 | 3600 | 2 | 763.43 | GGB | 763.37 | 774.328 | 767.766 | 260.34 | GGB | 10736.6 | GGB | 9.78 | GGB | 1001.05 | GGB | 63.11 | GGB | 167104.99 | GGB | 134128.44 | GGB | 0 | 0 | 0 | 0 | 1282.88 | GNB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 234160.59 | GGB | 234163.28 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 01:00 | 3600 | 2 | 762.4 | GGB | 762.271 | 773.32 | 766.667 | 262.11 | GGB | 10790.8 | GGB | 9.77 | GGB | 1002.04 | GGB | 62.35 | GGB | 169303.47 | GGB | 136334.15 | GGB | 0 | 0 | 0 | 0 | 1271.73 | GNB | 100 | GGB | 38.53 | GGB | 38.53 | GGB | 234199.12 | GGB | 234201.81 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 02:00 | 3600 | 2 | 762.21 | GGB | 761.172 | 771.961 | 765.201 | 263.35 | GGB | 10861.4 | GGB | 9.78 | GGB | 1003.14 | GGB | 61.65 | GGB | 170743.81 | GGB | 137935.41 | GGB | 0 | 0 | 0 | 0 | 1287.69 | GNB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 234238.59 | GGB | 234241.28 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 03:00 | 3600 | 2 | 761.65 | GGB | 761.172 | 771.797 | 766.3 | 264.48 | GGB | 10905.3 | GGB | 9.78 | GGB | 1003.68 | GGB | 61.41 | GGB | 171906.87 | GGB | 139046.1 | GGB | 0 | 0 | 0 | 0 | 1283.01 | GNB | 100 | GGB | 39.64 | GGB | 39.64 | GGB | 234278.24 | GGB | 234280.92 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 04:00 | 3600 | 2 | 761.31 | GGB | 762.271 | 772.664 | 766.667 | 264.88 | GGB | 10943.4 | GGB | 9.78 | GGB | 1004.42 | GGB | 60.73 | GGB | 172820.15 | GGB | 140173.1 | GGB | 0 | 0 | 0 | 0 | 1278.14 | GNB | 100 | GGB | 39.81 | GGB | 39.81 | GGB | 234318.05 | GGB | 234320.73 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 05:00 | 3600 | 2 | 761.28 | GGB | 761.172 | 771.633 | 766.3 | 265.81 | GGB | 10971.2 | GGB | 9.78 | GGB | 1004.51 | GGB | 60.73 | GGB | 173692.72 | GGB | 140896.03 | GGB | 0 | 0 | 0 | 0 | 1282.08 | GNB | 100 | GGB | 40.14 | GGB | 40.14 | GGB | 234358.19 | GGB | 234360.87 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 06:00 | 3600 | 2 | 760.86 | GGB | 759.707 | 770.625 | 765.201 | 266.43 | GGB | 10991.5 | GGB | 9.78 | GGB | 1004.78 | GGB | 60.2 | GGB | 174416.74 | GGB | 141744.36 | GGB | 0 | 0 | 0 | 0 | 1292.75 | GNB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 234398.91 | GGB | 234401.59 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 07:00 | 3600 | 2 | 760.74 | GGB | 761.172 | 771.703 | 766.3 | 267.86 | GGB | 11036.2 | GGB | 9.78 | GGB | 1005.52 | GGB | 59.64 | GGB | 175791.06 | GGB | 143207.97 | GGB | 0 | 0 | 0 | 0 | 1280.04 | GNB | 100 | GGB | 40.74 | GGB | 40.74 | GGB | 234439.65 | GGB | 234442.33 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 08:00 | 3600 | 2 | 761.1 | GGB | 762.271 | 772.641 | 766.667 | 268.19 | GGB | 11056.8 | GGB | 9.79 | GGB | 1006.04 | GGB | 59.46 | GGB | 176336.83 | GGB | 143802.92 | GGB | 0 | 0 | 0 | 0 | 1274.3 | GNB | 100 | GGB | 40.72 | GGB | 40.72 | GGB | 234480.37 | GGB | 234483.05 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 09:00 | 3600 | 2 | 761.19 | GGB | 761.172 | 771.633 | 766.3 | 268.4 | GGB | 11032.7 | GGB | 9.78 | GGB | 1006.49 | GGB | 59.25 | GGB | 177197.29 | GGB | 144662.84 | GGB | 0 | 0 | 0 | 0 | 1259.75 | GNB | 100 | GGB | 40.5 | GGB | 40.5 | GGB | 234520.87 | GGB | 234523.55 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 10:00 | 3600 | 2 | 761.84 | GGB | 761.172 | 771.563 | 766.3 | 269 | GGB | 11018.3 | GGB | 9.79 | GGB | 1007.06 | GGB | 58.63 | GGB | 178335.04 | GGB | 145946.66 | GGB | 0 | 0 | 0 | 0 | 1226.38 | GNB | 100 | GGB | 39.78 | GGB | 39.78 | GGB | 234560.64 | GGB | 234563.33 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
19.05.2008 11:00 | 3600 | 2 | 762.19 | GGB | 762.271 | 772.43 | 766.667 | 267.1 | GGB | 11046.4 | GGB | 9.8 | GGB | 1007.89 | GGB | 59.51 | GGB | 175712.94 | GGB | 143538.84 | GGB | 0 | 0 | 3240 | 2711 | 3224.6 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 234600.39 | GGB | 234603.07 | 3224.6 | 2632.932 |  |  |  | 0 | 1 | [14 empty] | 128.5709 | 2632.932 |  | 104.98
19.05.2008 12:00 | 3600 | 2 | 761.45 | GGB | 762.271 | 772.711 | 767.033 | 267.02 | GGB | 11028.8 | GGB | 9.79 | GGB | 1008.62 | GGB | 59.69 | GGB | 175408.14 | GGB | 143314.9 | GGB | 0 | 0 | 3244 | 3600 | 3227.84 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 234640.41 | GGB | 234643.09 | 3227.84 | 2637.0461 |  |  |  | 0 | 1 | [14 empty] | 128.4993 | 2637.0461 |  | 104.98
19.05.2008 13:00 | 3600 | 2 | 762.14 | GGB | 762.271 | 772.945 | 767.033 | 266.67 | GGB | 10978.4 | GGB | 9.79 | GGB | 1008.75 | GGB | 59.66 | GGB | 175412.54 | GGB | 143349.83 | GGB | 0 | 0 | 3195 | 3600 | 3178.78 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 234680.42 | GGB | 234683.1 | 3178.78 | 2636.4035 |  |  |  | 0 | 1 | [14 empty] | 126.5771 | 2636.4035 |  | 104.98
19.05.2008 14:00 | 3600 | 2 | 763.15 | GGB | 763.37 | 774.234 | 768.498 | 266.74 | GGB | 10935.7 | GGB | 9.79 | GGB | 1008.39 | GGB | 59.5 | GGB | 175621.61 | GGB | 143537.9 | GGB | 0 | 0 | 3133 | 3600 | 3117.68 | GGB | 100 | GGB | 40.04 | GGB | 40.04 | GGB | 234720.46 | GGB | 234723.14 | 3117.68 | 2632.9492 |  |  |  | 0 | 1 | [14 empty] | 124.307 | 2632.9492 |  | 104.98
19.05.2008 15:00 | 3600 | 2 | 763.7 | GGB | 763.37 | 775.617 | 768.498 | 265.84 | GGB | 10899 | GGB | 9.79 | GGB | 1008.06 | GGB | 60 | GGB | 174755.64 | GGB | 142568.85 | GGB | 0 | 0 | 3094 | 3600 | 3078.32 | GGB | 100 | GGB | 39.95 | GGB | 39.95 | GGB | 234760.41 | GGB | 234763.09 | 3078.32 | 2650.8455 |  |  |  | 0 | 1 | [14 empty] | 121.909 | 2650.8455 |  | 104.98
19.05.2008 16:00 | 3600 | 2 | 763.92 | GGB | 762.271 | 773.109 | 768.498 | 264.97 | GGB | 10857.9 | GGB | 9.79 | GGB | 1007.67 | GGB | 60.52 | GGB | 173804.95 | GGB | 141517.85 | GGB | 0 | 0 | 3057 | 3600 | 3041.75 | GGB | 100 | GGB | 39.85 | GGB | 39.85 | GGB | 234800.26 | GGB | 234802.94 | 3041.75 | 2670.5324 |  |  |  | 0 | 1 | [14 empty] | 119.5728 | 2670.5324 |  | 104.98
19.05.2008 17:00 | 3600 | 2 | 763.67 | GGB | 763.37 | 775.172 | 769.597 | 263.66 | GGB | 10890 | GGB | 9.79 | GGB | 1007.25 | GGB | 60.79 | GGB | 171801.23 | GGB | 139715.58 | GGB | 0 | 0 | 3087 | 3600 | 3070.95 | GGB | 100 | GGB | 40.02 | GGB | 40.02 | GGB | 234840.28 | GGB | 234842.96 | 3070.95 | 2704.9811 |  |  |  | 0 | 1 | [14 empty] | 119.1832 | 2704.9811 |  | 104.98
19.05.2008 18:00 | 3600 | 2 | 763.3 | GGB | 762.271 | 773.016 | 767.033 | 263.74 | GGB | 10876.9 | GGB | 9.78 | GGB | 1007.77 | GGB | 60.98 | GGB | 171593.27 | GGB | 139538.87 | GGB | 0 | 0 | 3109 | 3600 | 3093.51 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 234880.32 | GGB | 234882.99 | 3093.51 | 2708.4066 |  |  |  | 0 | 1 | [14 empty] | 119.9069 | 2708.4066 |  | 104.98
19.05.2008 19:00 | 3600 | 2 | 763.93 | GGB | 763.37 | 775.148 | 768.498 | 263.85 | GGB | 10894.9 | GGB | 9.79 | GGB | 1007.82 | GGB | 60.97 | GGB | 171620.78 | GGB | 139570.76 | GGB | 0 | 0 | 3091 | 3600 | 3075.46 | GGB | 100 | GGB | 41.1 | GGB | 41.1 | GGB | 234921.42 | GGB | 234924.09 | 3075.46 | 2707.7878 |  |  |  | 0 | 1 | [14 empty] | 119.2345 | 2707.7878 |  | 104.98
19.05.2008 20:00 | 3600 | 2 | 763.38 | GGB | 763.37 | 774.164 | 768.498 | 263.62 | GGB | 10886.9 | GGB | 9.78 | GGB | 1008.15 | GGB | 60.89 | GGB | 171618.58 | GGB | 139648.85 | GGB | 0 | 0 | 3110 | 3600 | 3094.17 | GGB | 100 | GGB | 34.84 | GGB | 34.84 | GGB | 234956.25 | GGB | 234958.93 | 3094.17 | 2706.2736 |  |  |  | 0 | 1 | [14 empty] | 120.027 | 2706.2736 |  | 104.98
19.05.2008 21:00 | 3600 | 2 | 763.16 | GGB | 762.271 | 773.977 | 767.033 | 264.13 | GGB | 10916.6 | GGB | 9.78 | GGB | 1008.82 | GGB | 60.73 | GGB | 172013.6 | GGB | 140129.45 | GGB | 0 | 0 | 3139 | 3600 | 3123.23 | GGB | 100 | GGB | 40.35 | GGB | 40.35 | GGB | 234996.6 | GGB | 234999.28 | 3123.23 | 2696.992 |  |  |  | 0 | 1 | [14 empty] | 121.5713 | 2696.992 |  | 104.98
19.05.2008 22:00 | 3600 | 2 | 762.48 | GGB | 762.271 | 772.945 | 767.033 | 265.23 | GGB | 10939.7 | GGB | 9.78 | GGB | 1009.71 | GGB | 60.48 | GGB | 172894.97 | GGB | 141079.66 | GGB | 0 | 0 | 3176 | 3600 | 3160.62 | GGB | 100 | GGB | 40.06 | GGB | 40.06 | GGB | 235036.67 | GGB | 235039.34 | 3160.62 | 2678.827 |  |  |  | 0 | 1 | [14 empty] | 123.8609 | 2678.827 |  | 104.98
19.05.2008 23:00 | 3600 | 2 | 762.42 | GGB | 761.172 | 772.008 | 767.033 | 266.29 | GGB | 10954.2 | GGB | 9.78 | GGB | 1009.95 | GGB | 60.22 | GGB | 173936.99 | GGB | 142072.22 | GGB | 0 | 0 | 3184 | 3600 | 3168.47 | GGB | 100 | GGB | 40.13 | GGB | 40.13 | GGB | 235076.8 | GGB | 235079.47 | 3168.47 | 2660.1119 |  |  |  | 0 | 1 | [14 empty] | 125.0421 | 2660.1119 |  | 104.98
19.05.2008 24:00 | 3600 | 2 | 762.73 | GGB | 762.271 | 773.086 | 768.132 | 267.51 | GGB | 10969.7 | GGB | 9.79 | GGB | 1010.14 | GGB | 59.75 | GGB | 176367.64 | GGB | 144291.71 | GGB | 0 | 0 | 3177 | 3600 | 3161.48 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 235116.86 | GGB | 235119.54 | 3161.48 | 2619.1941 |  |  |  | 0 | 1 | [14 empty] | 126.7154 | 2619.1941 |  | 104.98
20.05.2008 01:00 | 3600 | 2 | 762.14 | GGB | 762.271 | 772.852 | 767.033 | 266.12 | GGB | 10993.6 | GGB | 9.79 | GGB | 1010.08 | GGB | 60.47 | GGB | 173755.43 | GGB | 141839.2 | GGB | 0 | 0 | 3215 | 3600 | 3198.84 | GGB | 100 | GGB | 39.8 | GGB | 39.8 | GGB | 235156.66 | GGB | 235159.34 | 3198.84 | 2664.482 |  |  |  | 0 | 1 | [14 empty] | 126.0336 | 2664.482 |  | 104.98
20.05.2008 02:00 | 3600 | 2 | 761.66 | GGB | 761.172 | 772.852 | 765.934 | 267.06 | GGB | 10986.6 | GGB | 9.78 | GGB | 1010.24 | GGB | 60.52 | GGB | 174329.81 | GGB | 142305.15 | GGB | 0 | 0 | 3252 | 3600 | 3236.36 | GGB | 100 | GGB | 40.65 | GGB | 40.65 | GGB | 235197.31 | GGB | 235199.99 | 3236.36 | 2655.7577 |  |  |  | 0 | 1 | [14 empty] | 127.9307 | 2655.7577 |  | 104.98
20.05.2008 03:00 | 3600 | 2 | 762.08 | GGB | 763.37 | 774.117 | 768.132 | 268.69 | GGB | 10989.6 | GGB | 9.78 | GGB | 1010.5 | GGB | 59.69 | GGB | 176368.74 | GGB | 144370.82 | GGB | 0 | 0 | 3227 | 3600 | 3211.02 | GGB | 100 | GGB | 40.42 | GGB | 40.42 | GGB | 235237.73 | GGB | 235240.41 | 3211.02 | 2617.7589 |  |  |  | 0 | 1 | [14 empty] | 128.7716 | 2617.7589 |  | 104.98
20.05.2008 04:00 | 3600 | 2 | 762.17 | GGB | 762.271 | 772.734 | 768.132 | 269.35 | GGB | 11004.8 | GGB | 9.78 | GGB | 1010.86 | GGB | 59.29 | GGB | 177280.92 | GGB | 145342.41 | GGB | 0 | 0 | 3228 | 3600 | 3211.87 | GGB | 100 | GGB | 39.71 | GGB | 39.71 | GGB | 235277.44 | GGB | 235280.12 | 3211.87 | 2600.2596 |  |  |  | 0 | 1 | [14 empty] | 129.6725 | 2600.2596 |  | 104.98
20.05.2008 05:00 | 3600 | 2 | 762.53 | GGB | 763.37 | 773.484 | 768.132 | 268.2 | GGB | 11069.5 | GGB | 9.8 | GGB | 1010.59 | GGB | 59.87 | GGB | 175548.99 | GGB | 143630.76 | GGB | 0 | 0 | 3250 | 3600 | 3233.82 | GGB | 100 | GGB | 40.01 | GGB | 40.01 | GGB | 235317.45 | GGB | 235320.13 | 3233.82 | 2631.247 |  |  |  | 0 | 1 | [14 empty] | 129.0211 | 2631.247 |  | 104.98
20.05.2008 06:00 | 3600 | 2 | 761.87 | GGB | 762.271 | 771.727 | 767.033 | 268.56 | GGB | 11064.3 | GGB | 9.78 | GGB | 1010.96 | GGB | 59.72 | GGB | 176079.35 | GGB | 144185.83 | GGB | 0 | 0 | 3271 | 3600 | 3255.33 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 235357.52 | GGB | 235360.2 | 3255.33 | 2621.1175 |  |  |  | 0 | 1 | [14 empty] | 130.3812 | 2621.1175 |  | 104.98
20.05.2008 07:00 | 3600 | 2 | 761.71 | GGB | 762.271 | 773.016 | 767.033 | 268.72 | GGB | 11074.4 | GGB | 9.78 | GGB | 1011.6 | GGB | 59.7 | GGB | 176267.51 | GGB | 144440.89 | GGB | 0 | 0 | 3288 | 3600 | 3272.32 | GGB | 100 | GGB | 40.07 | GGB | 40.07 | GGB | 235397.6 | GGB | 235400.27 | 3272.32 | 2616.489 |  |  |  | 0 | 1 | [14 empty] | 131.2936 | 2616.489 |  | 104.98
20.05.2008 08:00 | 3600 | 2 | 761.66 | GGB | 763.37 | 774.164 | 768.132 | 270.34 | GGB | 11044.6 | GGB | 9.78 | GGB | 1011.89 | GGB | 59.15 | GGB | 178402.16 | GGB | 146471.69 | GGB | 0 | 0 | 3270 | 3600 | 3253.7 | GGB | 100 | GGB | 40.36 | GGB | 40.36 | GGB | 235437.95 | GGB | 235440.63 | 3253.7 | 2580.2119 |  |  |  | 0 | 1 | [14 empty] | 132.3819 | 2580.2119 |  | 104.98
20.05.2008 09:00 | 3600 | 2 | 763.38 | GGB | 763.37 | 774.07 | 768.498 | 269.58 | GGB | 11024.7 | GGB | 9.8 | GGB | 1012.54 | GGB | 59.38 | GGB | 177558.2 | GGB | 145771.97 | GGB | 0 | 0 | 3172 | 3600 | 3155.84 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 235478.07 | GGB | 235480.75 | 3155.84 | 2592.5972 |  |  |  | 0 | 1 | [14 empty] | 127.7869 | 2592.5972 |  | 104.98
20.05.2008 10:00 | 3600 | 2 | 764.12 | GGB | 763.37 | 775.148 | 769.597 | 267.24 | GGB | 10996 | GGB | 9.8 | GGB | 1012.59 | GGB | 60.28 | GGB | 174873.38 | GGB | 143186.7 | GGB | 0 | 0 | 3131 | 3600 | 3115.07 | GGB | 100 | GGB | 39.6 | GGB | 39.6 | GGB | 235517.67 | GGB | 235520.35 | 3115.07 | 2639.4072 |  |  |  | 0 | 1 | [14 empty] | 123.8991 | 2639.4072 |  | 104.98
20.05.2008 11:00 | 3600 | 2 | 764.16 | GGB | 762.271 | 773.648 | 767.033 | 266.83 | GGB | 10957 | GGB | 9.79 | GGB | 1012.66 | GGB | 60.32 | GGB | 174895.38 | GGB | 143197.62 | GGB | 0 | 0 | 3106 | 3600 | 3090.08 | GGB | 100 | GGB | 39.47 | GGB | 39.47 | GGB | 235557.13 | GGB | 235559.82 | 3090.08 | 2639.2059 |  |  |  | 0 | 1 | [14 empty] | 122.9145 | 2639.2059 |  | 104.98
20.05.2008 12:00 | 3600 | 2 | 763.82 | GGB | 763.37 | 774.352 | 768.498 | 264.81 | GGB | 10949.1 | GGB | 9.8 | GGB | 1012.72 | GGB | 61.1 | GGB | 172727.72 | GGB | 141101.93 | GGB | 0 | 0 | 3080 | 3600 | 3064.52 | GGB | 100 | GGB | 39.36 | GGB | 39.36 | GGB | 235596.49 | GGB | 235599.18 | 3064.52 | 2678.4042 |  |  |  | 0 | 1 | [14 empty] | 120.1138 | 2678.4042 |  | 104.98
20.05.2008 13:00 | 3600 | 2 | 763.55 | GGB | 762.271 | 774.398 | 767.033 | 263.92 | GGB | 10905.3 | GGB | 9.79 | GGB | 1012.9 | GGB | 61.3 | GGB | 171954.18 | GGB | 140408.46 | GGB | 0 | 0 | 3069 | 3600 | 3053.32 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 235636.35 | GGB | 235639.04 | 3053.32 | 2691.6327 |  |  |  | 0 | 1 | [14 empty] | 119.0867 | 2691.6327 |  | 104.98
20.05.2008 14:00 | 3600 | 2 | 763.84 | GGB | 761.172 | 772.688 | 765.934 | 263.64 | GGB | 10871.4 | GGB | 9.79 | GGB | 1011.94 | GGB | 61.37 | GGB | 171888.16 | GGB | 140192.67 | GGB | 0 | 0 | 3039 | 3600 | 3023.36 | GGB | 100 | GGB | 39.75 | GGB | 39.75 | GGB | 235676.1 | GGB | 235678.79 | 3023.36 | 2695.7757 |  |  |  | 0 | 1 | [14 empty] | 117.7369 | 2695.7757 |  | 104.98
20.05.2008 15:00 | 3600 | 2 | 764.35 | GGB | 763.37 | 774.844 | 768.498 | 264.15 | GGB | 10821.8 | GGB | 9.79 | GGB | 1011.89 | GGB | 60.96 | GGB | 173069.92 | GGB | 141323.07 | GGB | 0 | 0 | 2992 | 3600 | 2976.1 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 235716.14 | GGB | 235718.82 | 2976.1 | 2674.2131 |  |  |  | 0 | 1 | [14 empty] | 116.831 | 2674.2131 |  | 104.98
20.05.2008 16:00 | 3600 | 2 | 764.81 | GGB | 763.37 | 774.867 | 768.864 | 263.52 | GGB | 10823.2 | GGB | 9.8 | GGB | 1011.59 | GGB | 61.37 | GGB | 171944.28 | GGB | 140190.6 | GGB | 0 | 0 | 2971 | 3600 | 2955.04 | GGB | 100 | GGB | 40.05 | GGB | 40.05 | GGB | 235756.19 | GGB | 235758.87 | 2955.04 | 2695.8156 |  |  |  | 0 | 1 | [14 empty] | 115.0747 | 2695.8156 |  | 104.98
20.05.2008 17:00 | 3600 | 2 | 764.55 | GGB | 763.37 | 775.078 | 768.864 | 261.7 | GGB | 10799.9 | GGB | 9.78 | GGB | 1011.51 | GGB | 62.27 | GGB | 169719.4 | GGB | 137993.15 | GGB | 0 | 0 | 2977 | 3600 | 2961 | GGB | 100 | GGB | 40.03 | GGB | 40.03 | GGB | 235796.22 | GGB | 235798.9 | 2961 | 2738.7446 |  |  |  | 0 | 1 | [14 empty] | 113.4994 | 2738.7446 |  | 104.98
20.05.2008 18:00 | 3600 | 2 | 764.77 | GGB | 764.469 | 775.289 | 769.597 | 262.12 | GGB | 10793.6 | GGB | 9.79 | GGB | 1011.44 | GGB | 62.31 | GGB | 170135.32 | GGB | 138304.38 | GGB | 0 | 0 | 2971 | 3600 | 2955.51 | GGB | 100 | GGB | 40.19 | GGB | 40.19 | GGB | 235836.41 | GGB | 235839.09 | 2955.51 | 2732.5816 |  |  |  | 1 | 1 |  |  |  |  | 138304.38 | 2732.5816 | 138304.38 | 2732.5816 | 9.4035 | [5 empty] | 113.5444 | 2732.5816 |  | 104.98
20.05.2008 19:00 | 3600 | 2 | 764.87 | GGB | 763.37 | 775.336 | 769.597 | 263.83 | GGB | 10776.3 | GGB | 9.78 | GGB | 1011.61 | GGB | 61.52 | GGB | 172178.65 | GGB | 140320.46 | GGB | 0 | 0 | 2950 | 3600 | 2934.33 | GGB | 100 | GGB | 39.74 | GGB | 39.74 | GGB | 235876.15 | GGB | 235878.83 | 2934.33 | 2693.3207 |  |  |  | 0 | 1 | [14 empty] | 114.374 | 2693.3207 |  | 104.98
20.05.2008 20:00 | 3600 | 2 | 764.4 | GGB | 763.37 | 775.102 | 768.498 | 264.42 | GGB | 10790.7 | GGB | 9.78 | GGB | 1011.49 | GGB | 61.2 | GGB | 172616.59 | GGB | 140796.89 | GGB | 0 | 0 | 2973 | 3600 | 2957.72 | GGB | 100 | GGB | 39.63 | GGB | 39.63 | GGB | 235915.78 | GGB | 235918.46 | 2957.72 | 2684.207 |  |  |  | 0 | 1 | [14 empty] | 115.6772 | 2684.207 |  | 104.98
20.05.2008 21:00 | 3600 | 2 | 764.25 | GGB | 763.37 | 774.117 | 768.498 | 263.29 | GGB | 10862.4 | GGB | 9.79 | GGB | 1011.7 | GGB | 61.51 | GGB | 170964.98 | GGB | 139349.66 | GGB | 0 | 0 | 3009 | 3600 | 2993.57 | GGB | 100 | GGB | 39.54 | GGB | 39.54 | GGB | 235955.32 | GGB | 235958 | 2993.57 | 2712.0841 |  |  |  | 0 | 1 | [14 empty] | 115.8758 | 2712.0841 |  | 104.98
20.05.2008 22:00 | 3600 | 2 | 763.17 | GGB | 762.271 | 773.953 | 767.033 | 264.6 | GGB | 10894.8 | GGB | 9.77 | GGB | 1012.45 | GGB | 61.21 | GGB | 172117.03 | GGB | 140516.6 | GGB | 0 | 0 | 3083 | 3600 | 3066.83 | GGB | 100 | GGB | 39.44 | GGB | 39.44 | GGB | 235994.76 | GGB | 235997.44 | 3066.83 | 2689.5612 |  |  |  | 0 | 1 | [14 empty] | 119.7057 | 2689.5612 |  | 104.98
20.05.2008 23:00 | 3600 | 2 | 762.55 | GGB | 762.271 | 772.805 | 767.033 | 266.41 | GGB | 10945.6 | GGB | 9.77 | GGB | 1013.55 | GGB | 60.94 | GGB | 173578.28 | GGB | 141980.16 | GGB | 0 | 0 | 3147 | 3600 | 3131.53 | GGB | 100 | GGB | 40.12 | GGB | 40.12 | GGB | 236034.88 | GGB | 236037.56 | 3131.53 | 2661.8367 |  |  |  | 0 | 1 | [14 empty] | 123.5042 | 2661.8367 |  | 104.98
20.05.2008 24:00 | 3600 | 2 | 761.9 | GGB | 762.271 | 772.945 | 767.033 | 269.22 | GGB | 10953.3 | GGB | 9.77 | GGB | 1014.38 | GGB | 60.18 | GGB | 176673.53 | GGB | 144960.96 | GGB | 0 | 0 | 3185 | 3600 | 3169.63 | GGB | 100 | GGB | 40.94 | GGB | 40.94 | GGB | 236075.82 | GGB | 236078.5 | 3169.63 | 2607.1019 |  |  |  | 0 | 1 | [14 empty] | 127.6313 | 2607.1019 |  | 104.98
21.05.2008 01:00 | 3600 | 2 | 762.99 | GGB | 762.271 | 773.203 | 767.033 | 268.19 | GGB | 11032.9 | GGB | 9.79 | GGB | 1014.59 | GGB | 60.49 | GGB | 175119.85 | GGB | 143581.32 | GGB | 0 | 0 | 3182 | 3600 | 3166.66 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236114.94 | GGB | 236117.62 | 3166.66 | 2632.153 |  |  |  | 0 | 1 | [14 empty] | 126.2981 | 2632.153 |  | 104.98
21.05.2008 02:00 | 3600 | 2 | 761.66 | GGB | 762.271 | 773.133 | 767.033 | 268.94 | GGB | 11050.7 | GGB | 9.78 | GGB | 1014.86 | GGB | 60.33 | GGB | 175962.71 | GGB | 144379.41 | GGB | 0 | 0 | 3254 | 3600 | 3237.83 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236154.06 | GGB | 236156.74 | 3237.83 | 2617.6032 |  |  |  | 0 | 1 | [14 empty] | 129.8544 | 2617.6032 |  | 104.98
21.05.2008 03:00 | 3600 | 2 | 761.45 | GGB | 762.271 | 772.031 | 765.934 | 271.23 | GGB | 11037.3 | GGB | 9.77 | GGB | 1015.03 | GGB | 59.27 | GGB | 179120.68 | GGB | 147466.52 | GGB | 0 | 0 | 3266 | 3600 | 3249.68 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236193.18 | GGB | 236195.86 | 3249.68 | 2562.8054 |  |  |  | 0 | 1 | [14 empty] | 133.1164 | 2562.8054 |  | 104.98
21.05.2008 04:00 | 3600 | 2 | 762.11 | GGB | 762.271 | 773.109 | 767.033 | 270.96 | GGB | 11067 | GGB | 9.79 | GGB | 1015.16 | GGB | 59.07 | GGB | 178962.23 | GGB | 147440.19 | GGB | 0 | 0 | 3227 | 3600 | 3211.44 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236232.3 | GGB | 236234.98 | 3211.44 | 2563.2631 |  |  |  | 0 | 1 | [14 empty] | 131.5265 | 2563.2631 |  | 104.98
21.05.2008 05:00 | 3600 | 2 | 761.31 | GGB | 761.172 | 771.797 | 765.934 | 270.38 | GGB | 11101.7 | GGB | 9.78 | GGB | 1015.52 | GGB | 59.44 | GGB | 178066.56 | GGB | 146593.23 | GGB | 0 | 0 | 3292 | 3600 | 3275.62 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236271.42 | GGB | 236274.1 | 3275.62 | 2578.0727 |  |  |  | 0 | 1 | [14 empty] | 133.3844 | 2578.0727 |  | 104.98
21.05.2008 06:00 | 3600 | 2 | 761.59 | GGB | 763.37 | 773.836 | 767.033 | 270.14 | GGB | 11123.8 | GGB | 9.79 | GGB | 1015.57 | GGB | 59.43 | GGB | 177349.14 | GGB | 146011.78 | GGB | 0 | 0 | 3306 | 3600 | 3290.21 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236310.54 | GGB | 236313.22 | 3290.21 | 2588.3391 |  |  |  | 0 | 1 | [14 empty] | 133.4471 | 2588.3391 |  | 104.98
21.05.2008 07:00 | 3600 | 2 | 761.21 | GGB | 761.172 | 771.539 | 765.934 | 270.74 | GGB | 11119.4 | GGB | 9.78 | GGB | 1015.33 | GGB | 59.43 | GGB | 177964.23 | GGB | 146483.25 | GGB | 0 | 0 | 3336 | 3600 | 3320.54 | GNB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236349.66 | GGB | 236352.34 | 3320.54 | 2580.0083 |  |  |  | 0 | 1 | [14 empty] | 135.1121 | 2580.0083 |  | 104.98
21.05.2008 08:00 | 3600 | 2 | 762.05 | GGB | 762.271 | 772.477 | 767.033 | 271.85 | GGB | 11094.2 | GGB | 9.79 | GGB | 1015.71 | GGB | 59.03 | GGB | 179693.96 | GGB | 148142.57 | GGB | 0 | 0 | 3277 | 3600 | 3261.2 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236388.78 | GGB | 236391.46 | 3261.2 | 2551.1101 |  |  |  | 0 | 1 | [14 empty] | 134.2007 | 2551.1101 |  | 104.98
21.05.2008 09:00 | 3600 | 2 | 762.95 | GGB | 763.37 | 773.555 | 767.033 | 270.67 | GGB | 11065.8 | GGB | 9.8 | GGB | 1016.08 | GGB | 59.47 | GGB | 178120.47 | GGB | 146704.65 | GGB | 0 | 0 | 3222 | 3600 | 3205.7 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236427.9 | GGB | 236430.58 | 3205.7 | 2576.1147 |  |  |  | 0 | 1 | [14 empty] | 130.6364 | 2576.1147 |  | 104.98
21.05.2008 10:00 | 3600 | 2 | 764.18 | GGB | 763.37 | 773.273 | 768.132 | 268.23 | GGB | 10984.5 | GGB | 9.81 | GGB | 1015.61 | GGB | 60.27 | GGB | 175221.08 | GGB | 143903.97 | GGB | 0 | 0 | 3124 | 3600 | 3108.57 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236467.02 | GGB | 236469.7 | 3108.57 | 2626.2514 |  |  |  | 0 | 1 | [14 empty] | 124.2599 | 2626.2514 |  | 104.98
21.05.2008 11:00 | 3600 | 2 | 764.31 | GGB | 764.469 | 775.617 | 769.597 | 266.37 | GGB | 10886.4 | GGB | 9.79 | GGB | 1014.34 | GGB | 60.82 | GGB | 173200.86 | GGB | 141831.38 | GGB | 0 | 0 | 3074 | 3600 | 3058.77 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236506.14 | GGB | 236508.82 | 3058.77 | 2664.6289 |  |  |  | 1 | 1 |  |  |  |  | 141831.38 | 2664.6289 | 141831.38 | 2664.6289 | 9.6607 | [5 empty] | 120.5082 | 2664.6289 |  | 104.98
21.05.2008 12:00 | 3600 | 2 | 765.81 | GGB | 764.835 | 776.344 | 770.696 | 264.28 | GGB | 10821.8 | GGB | 9.81 | GGB | 1013.43 | GGB | 61.64 | GGB | 171507.44 | GGB | 139975.1 | GGB | 0 | 0 | 2955 | 3600 | 2939.39 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236545.26 | GGB | 236547.94 | 2939.39 | 2699.9659 |  |  |  | 1 | 1 |  |  |  |  | 139975.1 | 2699.9659 | 139975.1 | 2699.9659 | 9.6607 | [5 empty] | 114.2893 | 2699.9659 |  | 104.98
21.05.2008 13:00 | 3600 | 2 | 765.31 | GGB | 762.271 | 774.047 | 768.498 | 262.9 | GGB | 10716.6 | GGB | 9.78 | GGB | 1012.78 | GGB | 62.2 | GGB | 170028.59 | GGB | 138448.9 | GGB | 0 | 0 | 2935 | 3600 | 2918.91 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236584.39 | GGB | 236587.06 | 2918.91 | 2729.7292 |  |  |  | 0 | 1 | [14 empty] | 112.2555 | 2729.7292 |  | 104.98
21.05.2008 14:00 | 3600 | 2 | 766.12 | GGB | 765.934 | 777 | 770.696 | 262.87 | GGB | 10742.8 | GGB | 9.8 | GGB | 1012.49 | GGB | 62.95 | GGB | 168583.85 | GGB | 136924.6 | GGB | 0 | 0 | 2934 | 3600 | 2918.21 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236623.51 | GGB | 236626.18 | 2918.21 | 2760.1176 |  |  |  | 1 | 1 |  |  |  |  | 136924.6 | 2760.1176 | 136924.6 | 2760.1176 | 9.6607 | [5 empty] | 110.993 | 2760.1176 |  | 104.98
21.05.2008 15:00 | 3600 | 2 | 765.78 | GGB | 764.469 | 776.039 | 769.597 | 261.16 | GGB | 10689.3 | GGB | 9.79 | GGB | 1011.73 | GGB | 64.28 | GGB | 166424.98 | GGB | 134538.12 | GGB | 0 | 0 | 2951 | 3600 | 2935.2 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236662.63 | GGB | 236665.3 | 2935.2 | 2809.0775 |  |  |  | 1 | 1 |  |  |  |  | 134538.12 | 2809.0775 | 134538.12 | 2809.0775 | 9.6607 | [5 empty] | 109.6934 | 2809.0775 |  | 104.98
21.05.2008 16:00 | 3600 | 2 | 766.05 | GGB | 763.37 | 775.313 | 768.498 | 261.35 | GGB | 10657 | GGB | 9.78 | GGB | 1011.4 | GGB | 64.7 | GGB | 166347.96 | GGB | 134265.21 | GGB | 0 | 0 | 2934 | 3600 | 2917.92 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236701.75 | GGB | 236704.42 | 2917.92 | 2814.7872 |  |  |  | 0 | 1 | [14 empty] | 108.8264 | 2814.7872 |  | 104.98
21.05.2008 17:00 | 3600 | 2 | 766.01 | GGB | 763.37 | 774.516 | 768.864 | 261.9 | GGB | 10632.7 | GGB | 9.78 | GGB | 1010.87 | GGB | 64.49 | GGB | 166925.64 | GGB | 134746.29 | GGB | 0 | 0 | 2929 | 3600 | 2913.89 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236740.87 | GGB | 236743.54 | 2913.89 | 2804.7377 |  |  |  | 0 | 1 | [14 empty] | 109.0655 | 2804.7377 |  | 104.98
21.05.2008 18:00 | 3600 | 2 | 767.32 | GGB | 765.934 | 777.609 | 771.429 | 262.41 | GGB | 10620.3 | GGB | 9.8 | GGB | 1010.72 | GGB | 64.27 | GGB | 167626.55 | GGB | 135376.84 | GGB | 0 | 0 | 2863 | 3600 | 2847.82 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236779.99 | GGB | 236782.66 | 2847.82 | 2791.674 |  |  |  | 1 | 1 |  |  |  |  | 135376.84 | 2791.674 | 135376.84 | 2791.674 | 9.6607 | [5 empty] | 107.0914 | 2791.674 |  | 104.98
21.05.2008 19:00 | 3600 | 2 | 767.26 | GGB | 765.934 | 777.445 | 771.429 | 261.43 | GGB | 10609.6 | GGB | 9.78 | GGB | 1010.22 | GGB | 64.34 | GGB | 166877.22 | GGB | 134679.58 | GGB | 0 | 0 | 2868 | 3600 | 2852.52 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236819.11 | GGB | 236821.78 | 2852.52 | 2806.127 |  |  |  | 1 | 1 |  |  |  |  | 134679.58 | 2806.127 | 134679.58 | 2806.127 | 9.6607 | [5 empty] | 106.7156 | 2806.127 |  | 104.98
21.05.2008 20:00 | 3600 | 2 | 766.48 | GGB | 764.469 | 775.313 | 768.864 | 260.94 | GGB | 10643.1 | GGB | 9.77 | GGB | 1010.25 | GGB | 64.35 | GGB | 165895.72 | GGB | 133887.17 | GGB | 0 | 0 | 2920 | 3600 | 2904.38 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236858.23 | GGB | 236860.9 | 2904.38 | 2822.735 |  |  |  | 1 | 1 |  |  |  |  | 133887.17 | 2822.735 | 133887.17 | 2822.735 | 9.6607 | [5 empty] | 108.0164 | 2822.735 |  | 104.98
21.05.2008 21:00 | 3600 | 2 | 765.83 | GGB | 762.271 | 774.422 | 767.766 | 262.43 | GGB | 10689.2 | GGB | 9.77 | GGB | 1011.18 | GGB | 64.04 | GGB | 166822.21 | GGB | 134880.31 | GGB | 0 | 0 | 2971 | 3600 | 2955.39 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236897.35 | GGB | 236900.02 | 2955.39 | 2801.9509 |  |  |  | 0 | 1 | [14 empty] | 110.7289 | 2801.9509 |  | 104.98
21.05.2008 22:00 | 3600 | 2 | 765.91 | GGB | 763.37 | 775.734 | 768.864 | 263.81 | GGB | 10726.7 | GGB | 9.77 | GGB | 1011.93 | GGB | 63.79 | GGB | 168099.7 | GGB | 136115.71 | GGB | 0 | 0 | 2985 | 3600 | 2969.22 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236936.47 | GGB | 236939.14 | 2969.22 | 2776.5201 |  |  |  | 0 | 1 | [14 empty] | 112.266 | 2776.5201 |  | 104.98
21.05.2008 23:00 | 3600 | 2 | 765.5 | GGB | 765.934 | 778.289 | 771.429 | 265.86 | GGB | 10780.6 | GGB | 9.78 | GGB | 1012.66 | GGB | 62.86 | GGB | 171061.81 | GGB | 138997.76 | GGB | 0 | 0 | 3031 | 3600 | 3015.25 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 236975.59 | GGB | 236978.26 | 3015.25 | 2718.9503 |  |  |  | 1 | 1 |  |  |  |  | 138997.76 | 2718.9503 | 138997.76 | 2718.9503 | 9.6607 | [5 empty] | 116.4203 | 2718.9503 |  | 104.98
21.05.2008 24:00 | 3600 | 2 | 765.3 | GGB | 763.37 | 775.219 | 768.864 | 265.46 | GGB | 10811.2 | GGB | 9.78 | GGB | 1012.94 | GGB | 63.29 | GGB | 169322.17 | GGB | 137449.75 | GGB | 0 | 0 | 3070 | 3600 | 3054.16 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 237014.71 | GGB | 237017.38 | 3054.16 | 2749.5721 |  |  |  | 0 | 1 | [14 empty] | 116.6093 | 2749.5721 |  | 104.98
22.05.2008 01:00 | 3600 | 2 | 764.06 | GGB | 762.271 | 773.133 | 766.667 | 269.04 | GGB | 10830.9 | GGB | 9.76 | GGB | 1013.43 | GGB | 62.21 | GGB | 172969.79 | GGB | 140926.66 | GGB | 0 | 0 | 3158 | 3600 | 3142.64 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237053.85 | GGB | 237056.52 | 3142.64 | 2681.7353 |  |  |  | 0 | 1 | [14 empty] | 123.0227 | 2681.7353 |  | 104.98
22.05.2008 02:00 | 3600 | 2 | 764.51 | GGB | 764.835 | 776.227 | 769.963 | 269.17 | GGB | 10901.5 | GGB | 9.79 | GGB | 1013.27 | GGB | 62 | GGB | 172958.79 | GGB | 140984.57 | GGB | 0 | 0 | 3157 | 3600 | 3141.12 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237092.99 | GGB | 237095.66 | 3141.12 | 2680.6338 |  |  |  | 1 | 1 |  |  |  |  | 140984.57 | 2680.6338 | 140984.57 | 2680.6338 | 9.6558 | [5 empty] | 123.0137 | 2680.6338 |  | 104.98
22.05.2008 03:00 | 3600 | 2 | 763.96 | GGB | 763.37 | 775.008 | 768.864 | 268.68 | GGB | 10919.9 | GGB | 9.78 | GGB | 1013.38 | GGB | 62.56 | GGB | 171998.2 | GGB | 139985.58 | GGB | 0 | 0 | 3202 | 3600 | 3186.37 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237132.13 | GGB | 237134.8 | 3186.37 | 2699.7638 |  |  |  | 0 | 1 | [14 empty] | 123.9016 | 2699.7638 |  | 104.98
22.05.2008 04:00 | 3600 | 2 | 763.43 | GGB | 763.37 | 774.023 | 767.766 | 270.29 | GGB | 10901.7 | GGB | 9.77 | GGB | 1013.34 | GGB | 61.99 | GGB | 173853.36 | GGB | 141728.26 | GGB | 0 | 0 | 3220 | 3600 | 3204.13 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237171.27 | GGB | 237173.94 | 3204.13 | 2666.5677 |  |  |  | 0 | 1 | [14 empty] | 126.1433 | 2666.5677 |  | 104.98
22.05.2008 05:00 | 3600 | 2 | 764.79 | GGB | 763.37 | 773.883 | 767.766 | 270.08 | GGB | 10948.7 | GGB | 9.8 | GGB | 1012.84 | GGB | 61.92 | GGB | 173340.61 | GGB | 141269.89 | GGB | 0 | 0 | 3179 | 3600 | 3162.9 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237210.41 | GGB | 237213.08 | 3162.9 | 2675.2198 |  |  |  | 0 | 1 | [14 empty] | 124.1174 | 2675.2198 |  | 104.98
22.05.2008 06:00 | 3600 | 2 | 764.58 | GGB | 763.37 | 774.07 | 767.766 | 269.26 | GGB | 10935.2 | GGB | 9.79 | GGB | 1012.56 | GGB | 62.31 | GGB | 172421.83 | GGB | 140317.89 | GGB | 0 | 0 | 3193 | 3600 | 3177.45 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237249.55 | GGB | 237252.22 | 3177.45 | 2693.37 |  |  |  | 0 | 1 | [14 empty] | 123.8481 | 2693.37 |  | 104.98
22.05.2008 07:00 | 3600 | 2 | 764.77 | GGB | 764.469 | 776.016 | 769.963 | 270.19 | GGB | 10921.4 | GGB | 9.79 | GGB | 1012.36 | GGB | 61.93 | GGB | 174069.03 | GGB | 141794.82 | GGB | 0 | 0 | 3187 | 3600 | 3170.83 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237288.69 | GGB | 237291.36 | 3170.83 | 2665.316 |  |  |  | 1 | 1 |  |  |  |  | 141794.82 | 2665.316 | 141794.82 | 2665.316 | 9.6558 | [5 empty] | 124.8909 | 2665.316 |  | 104.98
22.05.2008 08:00 | 3600 | 2 | 764.93 | GGB | 762.271 | 773.813 | 767.766 | 269.02 | GGB | 10916.9 | GGB | 9.79 | GGB | 1012.81 | GGB | 62.38 | GGB | 172662.8 | GGB | 140519.99 | GGB | 0 | 0 | 3164 | 3600 | 3147.9 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237327.83 | GGB | 237330.5 | 3147.9 | 2689.4963 |  |  |  | 0 | 1 | [14 empty] | 122.873 | 2689.4963 |  | 104.98
22.05.2008 09:00 | 3600 | 2 | 765.41 | GGB | 764.469 | 774.961 | 769.963 | 268.99 | GGB | 10883.4 | GGB | 9.79 | GGB | 1013.38 | GGB | 61.91 | GGB | 173609.09 | GGB | 141568.09 | GGB | 0 | 0 | 3127 | 3600 | 3111.04 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237366.97 | GGB | 237369.64 | 3111.04 | 2669.5847 |  |  |  | 1 | 1 |  |  |  |  | 141568.09 | 2669.5847 | 141568.09 | 2669.5847 | 9.6558 | [5 empty] | 122.34 | 2669.5847 |  | 104.98
22.05.2008 10:00 | 3600 | 2 | 765.48 | GGB | 764.469 | 775.805 | 769.597 | 267.61 | GGB | 10869.4 | GGB | 9.8 | GGB | 1013.04 | GGB | 61.83 | GGB | 172929.08 | GGB | 140999.55 | GGB | 0 | 0 | 3094 | 3600 | 3078.5 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237406.1 | GGB | 237408.78 | 3078.5 | 2680.349 |  |  |  | 1 | 1 |  |  |  |  | 140999.55 | 2680.349 | 140999.55 | 2680.349 | 9.6558 | [5 empty] | 120.5742 | 2680.349 |  | 104.98
22.05.2008 11:00 | 3600 | 2 | 765.63 | GGB | 764.469 | 774.961 | 769.597 | 266.84 | GGB | 10847.3 | GGB | 9.79 | GGB | 1012.63 | GGB | 61.66 | GGB | 172261.18 | GGB | 140472.32 | GGB | 0 | 0 | 3067 | 3600 | 3051.49 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237445.24 | GGB | 237447.92 | 3051.49 | 2690.409 |  |  |  | 1 | 1 |  |  |  |  | 140472.32 | 2690.409 | 140472.32 | 2690.409 | 9.6558 | [5 empty] | 119.0694 | 2690.409 |  | 104.98
22.05.2008 12:00 | 3600 | 2 | 765.76 | GGB | 764.835 | 777.164 | 770.696 | 266.44 | GGB | 10840 | GGB | 9.79 | GGB | 1011.97 | GGB | 61.7 | GGB | 172102.73 | GGB | 140232.17 | GGB | 0 | 0 | 3063 | 3600 | 3047.32 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237484.38 | GGB | 237487.06 | 3047.32 | 2695.0164 |  |  |  | 1 | 1 |  |  |  |  | 140232.17 | 2695.0164 | 140232.17 | 2695.0164 | 9.6558 | [5 empty] | 118.7034 | 2695.0164 |  | 104.98
22.05.2008 13:00 | 3600 | 2 | 764.85 | GGB | 764.469 | 774.984 | 769.597 | 266.61 | GGB | 10817.6 | GGB | 9.77 | GGB | 1012.18 | GGB | 61.67 | GGB | 172195.16 | GGB | 140352.02 | GGB | 0 | 0 | 3103 | 3600 | 3087.65 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237523.52 | GGB | 237526.2 | 3087.65 | 2692.7151 |  |  |  | 1 | 1 |  |  |  |  | 140352.02 | 2692.7151 | 140352.02 | 2692.7151 | 9.6558 | [5 empty] | 120.3772 | 2692.7151 |  | 104.98
22.05.2008 14:00 | 3600 | 2 | 765.3 | GGB | 763.37 | 774.891 | 768.498 | 267.03 | GGB | 10852.4 | GGB | 9.79 | GGB | 1012.49 | GGB | 61.75 | GGB | 172206.16 | GGB | 140369 | GGB | 0 | 0 | 3094 | 3600 | 3078.7 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237562.66 | GGB | 237565.34 | 3078.7 | 2692.3893 |  |  |  | 0 | 1 | [14 empty] | 120.0428 | 2692.3893 |  | 104.98
22.05.2008 15:00 | 3600 | 2 | 765 | GGB | 762.271 | 773.859 | 767.033 | 266.17 | GGB | 10857.7 | GGB | 9.79 | GGB | 1012.66 | GGB | 61.87 | GGB | 171066.21 | GGB | 139413.85 | GGB | 0 | 0 | 3130 | 3600 | 3113.91 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237601.8 | GGB | 237604.48 | 3113.91 | 2710.8354 |  |  |  | 0 | 1 | [14 empty] | 120.5895 | 2710.8354 |  | 104.98
22.05.2008 16:00 | 3600 | 2 | 764.35 | GGB | 762.271 | 772.617 | 767.033 | 265.68 | GGB | 10880.3 | GGB | 9.78 | GGB | 1012.37 | GGB | 62.46 | GGB | 170104.51 | GGB | 138344.92 | GGB | 0 | 0 | 3191 | 3600 | 3175.26 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237640.94 | GGB | 237643.62 | 3175.26 | 2731.7808 |  |  |  | 0 | 1 | [14 empty] | 122.0225 | 2731.7808 |  | 104.98
22.05.2008 17:00 | 3600 | 2 | 764.48 | GGB | 761.172 | 771.938 | 765.934 | 266.7 | GGB | 10910.6 | GGB | 9.78 | GGB | 1012.02 | GGB | 62.37 | GGB | 171050.8 | GGB | 139105.9 | GGB | 0 | 0 | 3202 | 3600 | 3186.07 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237680.08 | GGB | 237682.76 | 3186.07 | 2716.8366 |  |  |  | 0 | 1 | [14 empty] | 123.1114 | 2716.8366 |  | 104.98
22.05.2008 18:00 | 3600 | 2 | 764.27 | GGB | 761.172 | 772.641 | 765.934 | 267.86 | GGB | 10912.4 | GGB | 9.78 | GGB | 1011.79 | GGB | 61.69 | GGB | 172777.23 | GGB | 140762.07 | GGB | 0 | 0 | 3216 | 3600 | 3200.62 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237719.22 | GGB | 237721.9 | 3200.62 | 2684.871 |  |  |  | 0 | 1 | [14 empty] | 125.1461 | 2684.871 |  | 104.98
22.05.2008 19:00 | 3600 | 2 | 765.62 | GGB | 762.271 | 773.813 | 768.132 | 266.84 | GGB | 10938.3 | GGB | 9.8 | GGB | 1011.59 | GGB | 61.73 | GGB | 171735.21 | GGB | 139871.99 | GGB | 0 | 0 | 3155 | 3600 | 3139.54 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237758.36 | GGB | 237761.04 | 3139.54 | 2701.9563 |  |  |  | 0 | 1 | [14 empty] | 121.9816 | 2701.9563 |  | 104.98
22.05.2008 20:00 | 3600 | 2 | 765.09 | GGB | 763.37 | 773.953 | 768.498 | 267.66 | GGB | 10884 | GGB | 9.78 | GGB | 1011.93 | GGB | 61.29 | GGB | 173336.21 | GGB | 141405.94 | GGB | 0 | 0 | 3153 | 3600 | 3137.18 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237797.5 | GGB | 237800.18 | 3137.18 | 2672.6459 |  |  |  | 0 | 1 | [14 empty] | 123.2266 | 2672.6459 |  | 104.98
22.05.2008 21:00 | 3600 | 2 | 765.89 | GGB | 762.271 | 773.883 | 767.033 | 267.59 | GGB | 10887.2 | GGB | 9.79 | GGB | 1011.57 | GGB | 60.91 | GGB | 173705.92 | GGB | 141820.35 | GGB | 0 | 0 | 3109 | 3600 | 3092.88 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237836.64 | GGB | 237839.32 | 3092.88 | 2664.8362 |  |  |  | 0 | 1 | [14 empty] | 121.8426 | 2664.8362 |  | 104.98
22.05.2008 22:00 | 3600 | 2 | 766.04 | GGB | 762.271 | 774.094 | 767.033 | 266.02 | GGB | 10918.3 | GGB | 9.79 | GGB | 1011.08 | GGB | 61.25 | GGB | 171954.18 | GGB | 140179.74 | GGB | 0 | 0 | 3126 | 3600 | 3110.56 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237875.78 | GGB | 237878.46 | 3110.56 | 2696.0244 |  |  |  | 0 | 1 | [14 empty] | 121.1215 | 2696.0244 |  | 104.98
22.05.2008 23:00 | 3600 | 2 | 765.72 | GGB | 764.469 | 775.148 | 769.597 | 265.76 | GGB | 10939.3 | GGB | 9.79 | GGB | 1010.89 | GGB | 61.35 | GGB | 172202.86 | GGB | 140314.28 | GGB | 0 | 0 | 3147 | 3600 | 3131.59 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237914.92 | GGB | 237917.6 | 3131.59 | 2693.4393 |  |  |  | 1 | 1 |  |  |  |  | 140314.28 | 2693.4393 | 140314.28 | 2693.4393 | 9.6558 | [5 empty] | 122.0574 | 2693.4393 |  | 104.98
22.05.2008 24:00 | 3600 | 2 | 765.22 | GGB | 762.271 | 774.164 | 768.132 | 266 | GGB | 10909.8 | GGB | 9.78 | GGB | 1010.81 | GGB | 61.53 | GGB | 172030.11 | GGB | 140084.67 | GGB | 0 | 0 | 3163 | 3600 | 3147.28 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 237954.06 | GGB | 237956.74 | 3147.28 | 2697.8541 |  |  |  | 0 | 1 | [14 empty] | 122.4682 | 2697.8541 |  | 104.98
23.05.2008 01:00 | 3600 | 2 | 765.49 | GGB | 763.37 | 774.234 | 767.033 | 265.79 | GGB | 10914.5 | GGB | 9.78 | GGB | 1010.89 | GGB | 61.44 | GGB | 172059.81 | GGB | 140158.76 | GGB | 0 | 0 | 3150 | 3600 | 3133.74 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 237993.17 | GGB | 237995.86 | 3133.74 | 2696.428 |  |  |  | 0 | 1 | [14 empty] | 122.0059 | 2696.428 |  | 104.98
23.05.2008 02:00 | 3600 | 2 | 765.53 | GGB | 762.271 | 774.211 | 767.033 | 265.92 | GGB | 10923.4 | GGB | 9.79 | GGB | 1010.71 | GGB | 61.37 | GGB | 172155.54 | GGB | 140239.19 | GGB | 0 | 0 | 3150 | 3600 | 3134.33 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238032.29 | GGB | 238034.98 | 3134.33 | 2694.8815 |  |  |  | 0 | 1 | [14 empty] | 122.0989 | 2694.8815 |  | 104.98
23.05.2008 03:00 | 3600 | 2 | 765.54 | GGB | 763.37 | 773.93 | 768.132 | 265.99 | GGB | 10926.1 | GGB | 9.79 | GGB | 1010.25 | GGB | 61.29 | GGB | 172488.95 | GGB | 140482.18 | GGB | 0 | 0 | 3155 | 3600 | 3139.64 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238071.41 | GGB | 238074.1 | 3139.64 | 2690.2202 |  |  |  | 0 | 1 | [14 empty] | 122.5176 | 2690.2202 |  | 104.98
23.05.2008 04:00 | 3600 | 2 | 765.75 | GGB | 763.37 | 773.789 | 768.132 | 265.94 | GGB | 10927.6 | GGB | 9.79 | GGB | 1009.8 | GGB | 61.4 | GGB | 172352.5 | GGB | 140263.18 | GGB | 0 | 0 | 3149 | 3600 | 3133.55 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238110.52 | GGB | 238113.22 | 3133.55 | 2694.4206 |  |  |  | 0 | 1 | [14 empty] | 122.0894 | 2694.4206 |  | 104.98
23.05.2008 05:00 | 3600 | 2 | 765.22 | GGB | 762.271 | 773.789 | 767.033 | 265.9 | GGB | 10923.9 | GGB | 9.78 | GGB | 1009.55 | GGB | 61.14 | GGB | 172342.6 | GGB | 140328.34 | GGB | 0 | 0 | 3176 | 3600 | 3159.74 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238149.64 | GGB | 238152.34 | 3159.74 | 2693.1695 |  |  |  | 0 | 1 | [14 empty] | 123.167 | 2693.1695 |  | 104.98
23.05.2008 06:00 | 3600 | 2 | 765.99 | GGB | 763.37 | 774.938 | 768.498 | 265.6 | GGB | 10939.8 | GGB | 9.79 | GGB | 1009.37 | GGB | 61.11 | GGB | 172355.81 | GGB | 140327.49 | GGB | 0 | 0 | 3150 | 3600 | 3134.41 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238188.76 | GGB | 238191.46 | 3134.41 | 2693.1858 |  |  |  | 0 | 1 | [14 empty] | 122.1789 | 2693.1858 |  | 104.98
23.05.2008 07:00 | 3600 | 2 | 765.7 | GGB | 763.37 | 775.102 | 768.132 | 265.32 | GGB | 10924.6 | GGB | 9.79 | GGB | 1009.51 | GGB | 61.13 | GGB | 172060.91 | GGB | 140099.75 | GGB | 0 | 0 | 3164 | 3600 | 3148.25 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238227.87 | GGB | 238230.58 | 3148.25 | 2697.5637 |  |  |  | 0 | 1 | [14 empty] | 122.5192 | 2697.5637 |  | 104.98
23.05.2008 08:00 | 3600 | 2 | 765.92 | GGB | 762.271 | 773.883 | 768.132 | 264.97 | GGB | 10920.8 | GGB | 9.79 | GGB | 1009 | GGB | 61.31 | GGB | 171704.41 | GGB | 139662.6 | GGB | 0 | 0 | 3152 | 3600 | 3136.24 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238266.99 | GGB | 238269.7 | 3136.24 | 2706.0072 |  |  |  | 0 | 1 | [14 empty] | 121.671 | 2706.0072 |  | 104.98
23.05.2008 09:00 | 3600 | 2 | 766.18 | GGB | 763.37 | 775.031 | 768.498 | 266.37 | GGB | 10872.4 | GGB | 9.79 | GGB | 1009.38 | GGB | 60.94 | GGB | 173426.43 | GGB | 141273.59 | GGB | 0 | 0 | 3127 | 3206 | 3111.26 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238306.11 | GGB | 238308.82 | 3111.26 | 2675.1497 |  |  |  | 0 | 1 | [14 empty] | 122.0941 | 2675.1497 |  | 104.98
23.05.2008 10:00 | 3600 | 2 | 766.86 | GGB | 764.469 | 775.008 | 768.498 | 265.51 | GGB | 10852.7 | GGB | 9.79 | GGB | 1009.27 | GGB | 61.15 | GGB | 172682.61 | GGB | 140562.87 | GGB | 0 | 0 | 3090 | 3600 | 3074.51 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238345.22 | GGB | 238347.94 | 3074.51 | 2688.6759 |  |  |  | 1 | 1 |  |  |  |  | 140562.87 | 2688.6759 | 140562.87 | 2688.6759 | 9.6607 | [5 empty] | 120.045 | 2688.6759 |  | 104.98
23.05.2008 11:00 | 3600 | 2 | 766.57 | GGB | 763.37 | 773.953 | 768.132 | 263.59 | GGB | 10866.1 | GGB | 9.79 | GGB | 1008.77 | GGB | 61.81 | GGB | 170115.52 | GGB | 138129.52 | GGB | 0 | 0 | 3119 | 3600 | 3103.27 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238384.34 | GGB | 238387.06 | 3103.27 | 2736.0408 |  |  |  | 0 | 1 | [14 empty] | 119.0703 | 2736.0408 |  | 104.98
23.05.2008 12:00 | 3600 | 2 | 766.65 | GGB | 762.271 | 774.047 | 767.033 | 263.74 | GGB | 10858.1 | GGB | 9.79 | GGB | 1009.27 | GGB | 61.98 | GGB | 169850.34 | GGB | 137912.59 | GGB | 0 | 0 | 3128 | 3600 | 3112.27 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238423.46 | GGB | 238426.18 | 3112.27 | 2740.3444 |  |  |  | 0 | 1 | [14 empty] | 119.2281 | 2740.3444 |  | 104.98
23.05.2008 13:00 | 3600 | 2 | 766.67 | GGB | 764.469 | 775.172 | 768.864 | 264.28 | GGB | 10868.6 | GGB | 9.79 | GGB | 1009.26 | GGB | 61.93 | GGB | 170397.2 | GGB | 138375.82 | GGB | 0 | 0 | 3145 | 3600 | 3129.03 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238462.57 | GGB | 238465.3 | 3129.03 | 2731.1708 |  |  |  | 1 | 1 |  |  |  |  | 138375.82 | 2731.1708 | 138375.82 | 2731.1708 | 9.6607 | [5 empty] | 120.2728 | 2731.1708 |  | 104.98
23.05.2008 14:00 | 3600 | 2 | 766.78 | GGB | 762.271 | 774.352 | 767.766 | 264.54 | GGB | 10873.1 | GGB | 9.78 | GGB | 1009.17 | GGB | 61.83 | GGB | 170737.21 | GGB | 138682.54 | GGB | 0 | 0 | 3151 | 3600 | 3134.79 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238501.69 | GGB | 238504.42 | 3134.79 | 2725.1304 |  |  |  | 0 | 1 | [14 empty] | 120.7613 | 2725.1304 |  | 104.98
23.05.2008 15:00 | 3600 | 2 | 766.66 | GGB | 762.271 | 774.023 | 767.766 | 264.7 | GGB | 10881.5 | GGB | 9.78 | GGB | 1009.21 | GGB | 61.73 | GGB | 171068.41 | GGB | 138996.07 | GGB | 0 | 0 | 3163 | 3600 | 3147.08 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238540.81 | GGB | 238543.54 | 3147.08 | 2718.9833 |  |  |  | 0 | 1 | [14 empty] | 121.5088 | 2718.9833 |  | 104.98
23.05.2008 16:00 | 3600 | 2 | 766.72 | GGB | 762.271 | 774.07 | 767.766 | 265.02 | GGB | 10890.6 | GGB | 9.78 | GGB | 1009.6 | GGB | 61.7 | GGB | 171121.23 | GGB | 139108.33 | GGB | 0 | 0 | 3166 | 3600 | 3149.98 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238579.92 | GGB | 238582.66 | 3149.98 | 2716.7891 |  |  |  | 0 | 1 | [14 empty] | 121.719 | 2716.7891 |  | 104.98
23.05.2008 17:00 | 3600 | 2 | 766.79 | GGB | 762.271 | 774.07 | 767.766 | 265.32 | GGB | 10910.6 | GGB | 9.79 | GGB | 1009.66 | GGB | 61.54 | GGB | 171606.48 | GGB | 139577.33 | GGB | 0 | 0 | 3182 | 3600 | 3165.76 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238619.04 | GGB | 238621.78 | 3165.76 | 2707.6603 |  |  |  | 0 | 1 | [14 empty] | 122.7412 | 2707.6603 |  | 104.98
23.05.2008 18:00 | 3600 | 2 | 766.51 | GGB | 762.271 | 772.945 | 766.667 | 265.55 | GGB | 10914.6 | GGB | 9.78 | GGB | 1009.58 | GGB | 61.44 | GGB | 171684.6 | GGB | 139672.44 | GGB | 0 | 0 | 3197 | 3600 | 3180.96 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238658.16 | GGB | 238660.9 | 3180.96 | 2705.8166 |  |  |  | 0 | 1 | [14 empty] | 123.4146 | 2705.8166 |  | 104.98
23.05.2008 19:00 | 3600 | 2 | 765.82 | GGB | 762.271 | 772.734 | 766.667 | 265.94 | GGB | 10925.7 | GGB | 9.78 | GGB | 1009.65 | GGB | 61.49 | GGB | 171870.56 | GGB | 139813.2 | GGB | 0 | 0 | 3218 | 3600 | 3201.68 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238697.27 | GGB | 238700.02 | 3201.68 | 2703.0924 |  |  |  | 0 | 1 | [14 empty] | 124.3436 | 2703.0924 |  | 104.98
23.05.2008 20:00 | 3600 | 2 | 765.82 | GGB | 762.271 | 772.852 | 767.766 | 266.51 | GGB | 10943 | GGB | 9.78 | GGB | 1009.66 | GGB | 61.2 | GGB | 172557.17 | GGB | 140492.73 | GGB | 0 | 0 | 3224 | 3600 | 3208.14 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238736.39 | GGB | 238739.14 | 3208.14 | 2690.0182 |  |  |  | 0 | 1 | [14 empty] | 125.2001 | 2690.0182 |  | 104.98
23.05.2008 21:00 | 3600 | 2 | 765.81 | GGB | 761.172 | 772.828 | 766.3 | 266.93 | GGB | 10956.6 | GGB | 9.78 | GGB | 1009.85 | GGB | 61.11 | GGB | 172864.16 | GGB | 140806.77 | GGB | 0 | 0 | 3237 | 3600 | 3221.35 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238775.5 | GGB | 238778.26 | 3221.35 | 2684.0187 |  |  |  | 0 | 1 | [14 empty] | 125.9966 | 2684.0187 |  | 104.98
23.05.2008 22:00 | 3600 | 2 | 766.1 | GGB | 763.37 | 774.281 | 767.766 | 267.17 | GGB | 10976.8 | GGB | 9.79 | GGB | 1009.72 | GGB | 60.86 | GGB | 173572.78 | GGB | 141473.76 | GGB | 0 | 0 | 3235 | 3600 | 3219.36 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238814.62 | GGB | 238817.38 | 3219.36 | 2671.3646 |  |  |  | 0 | 1 | [14 empty] | 126.5153 | 2671.3646 |  | 104.98
23.05.2008 23:00 | 3600 | 2 | 765.97 | GGB | 762.271 | 774.094 | 767.766 | 267.32 | GGB | 10983.4 | GGB | 9.78 | GGB | 1009.88 | GGB | 60.72 | GGB | 173779.64 | GGB | 141723.6 | GGB | 0 | 0 | 3247 | 3600 | 3231.25 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238853.74 | GGB | 238856.5 | 3231.25 | 2666.6554 |  |  |  | 0 | 1 | [14 empty] | 127.2068 | 2666.6554 |  | 104.98
23.05.2008 24:00 | 3600 | 2 | 765.94 | GGB | 762.271 | 774.07 | 767.766 | 267.37 | GGB | 10993.1 | GGB | 9.79 | GGB | 1009.72 | GGB | 60.53 | GGB | 173873.17 | GGB | 141856.57 | GGB | 0 | 0 | 3247 | 3600 | 3230.71 | GGB | 100 | GGB | 39.12 | GGB | 39.12 | GGB | 238892.85 | GGB | 238895.62 | 3230.71 | 2664.1558 |  |  |  | 0 | 1 | [14 empty] | 127.3048 | 2664.1558 |  | 104.98
24.05.2008 01:00 | 3600 | 2 | 765.84 | GGB | 761.172 | 773.203 | 766.667 | 267.23 | GGB | 10987.7 | GGB | 9.79 | GGB | 1009.19 | GGB | 60.45 | GGB | 173954.6 | GGB | 141881.98 | GGB | 0 | 0 | 3244 | 3600 | 3228.39 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 238932.58 | GGB | 238935.34 | 3228.39 | 2663.6786 |  |  |  | 0 | 1 | [14 empty] | 127.2362 | 2663.6786 |  | 104.98
24.05.2008 02:00 | 3600 | 2 | 765.96 | GGB | 762.271 | 773.344 | 766.667 | 267.06 | GGB | 10988.9 | GGB | 9.79 | GGB | 1008.62 | GGB | 60.29 | GGB | 173895.18 | GGB | 141824.28 | GGB | 0 | 0 | 3242 | 3600 | 3226.13 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 238972.3 | GGB | 238975.06 | 3226.13 | 2664.7623 |  |  |  | 0 | 1 | [14 empty] | 127.0954 | 2664.7623 |  | 104.98
24.05.2008 03:00 | 3600 | 2 | 765.52 | GGB | 761.172 | 771.961 | 765.201 | 267.53 | GGB | 10975.5 | GGB | 9.78 | GGB | 1009.09 | GGB | 60.23 | GGB | 174598.29 | GGB | 142488.59 | GGB | 0 | 0 | 3244 | 3600 | 3227.94 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239012.02 | GGB | 239014.78 | 3227.94 | 2652.3387 |  |  |  | 0 | 1 | [14 empty] | 127.7624 | 2652.3387 |  | 104.98
24.05.2008 04:00 | 3600 | 2 | 764.91 | GGB | 762.271 | 773.297 | 765.201 | 269.28 | GGB | 10980.7 | GGB | 9.78 | GGB | 1008.97 | GGB | 59.05 | GGB | 177032.24 | GGB | 144972.07 | GGB | 0 | 0 | 3256 | 3600 | 3239.91 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239051.74 | GGB | 239054.5 | 3239.91 | 2606.9021 |  |  |  | 0 | 1 | [14 empty] | 130.4712 | 2606.9021 |  | 104.98
24.05.2008 05:00 | 3600 | 2 | 764.93 | GGB | 761.172 | 771.563 | 766.3 | 268.14 | GGB | 11044.9 | GGB | 9.79 | GGB | 1008.54 | GGB | 59.53 | GGB | 175306.91 | GGB | 143292.22 | GGB | 0 | 0 | 3293 | 3600 | 3277.04 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239091.46 | GGB | 239094.22 | 3277.04 | 2637.4635 |  |  |  | 0 | 1 | [14 empty] | 130.4373 | 2637.4635 |  | 104.98
24.05.2008 06:00 | 3600 | 2 | 764.38 | GGB | 762.271 | 772.195 | 766.3 | 268.24 | GGB | 11052.4 | GGB | 9.79 | GGB | 1008.84 | GGB | 59.44 | GGB | 175323.42 | GGB | 143383.32 | GGB | 0 | 0 | 3320 | 3600 | 3303.96 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239131.19 | GGB | 239133.94 | 3303.96 | 2635.7878 |  |  |  | 0 | 1 | [14 empty] | 131.5924 | 2635.7878 |  | 104.98
24.05.2008 07:00 | 3600 | 2 | 764.1 | GGB | 759.707 | 770.695 | 764.102 | 268.9 | GGB | 11037 | GGB | 9.78 | GGB | 1009.27 | GGB | 59.36 | GGB | 176204.79 | GGB | 144202.4 | GGB | 0 | 0 | 3332 | 3600 | 3315.89 | GNB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239170.91 | GGB | 239173.66 | 3315.89 | 2620.8163 |  |  |  | 0 | 1 | [14 empty] | 132.822 | 2620.8163 |  | 104.98
24.05.2008 08:00 | 3600 | 2 | 764.83 | GGB | 761.172 | 771.961 | 766.667 | 269.72 | GGB | 11048.8 | GGB | 9.79 | GGB | 1009.75 | GGB | 59.25 | GGB | 177036.64 | GGB | 145001.01 | GGB | 0 | 0 | 3294 | 3600 | 3277.87 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239210.63 | GGB | 239213.38 | 3277.87 | 2606.3818 |  |  |  | 0 | 1 | [14 empty] | 132.0262 | 2606.3818 |  | 104.98
24.05.2008 09:00 | 3600 | 2 | 764.39 | GGB | 762.271 | 773.086 | 766.667 | 270.31 | GGB | 11025.3 | GGB | 9.78 | GGB | 1009.89 | GGB | 59.04 | GGB | 178069.86 | GGB | 145958.27 | GGB | 0 | 0 | 3299 | 3600 | 3282.62 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239250.35 | GGB | 239253.1 | 3282.62 | 2589.288 |  |  |  | 0 | 1 | [14 empty] | 133.0904 | 2589.288 |  | 104.98
24.05.2008 10:00 | 3600 | 2 | 766.69 | GGB | 763.37 | 774.469 | 768.864 | 268.79 | GGB | 11071.9 | GGB | 9.8 | GGB | 1009.09 | GGB | 59.9 | GGB | 175595.2 | GGB | 143442.2 | GGB | 0 | 0 | 3214 | 3600 | 3198.55 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239290.07 | GGB | 239292.82 | 3198.55 | 2634.7058 |  |  |  | 0 | 1 | [14 empty] | 127.4464 | 2634.7058 |  | 104.98
24.05.2008 11:00 | 3600 | 2 | 767.2 | GGB | 768.132 | 778.641 | 772.527 | 269.4 | GGB | 11024.3 | GGB | 9.79 | GGB | 1009.27 | GGB | 59.98 | GGB | 176411.65 | GGB | 144101.21 | GGB | 0 | 0 | 3172 | 3600 | 3155.95 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239329.8 | GGB | 239332.54 | 3155.95 | 2622.6567 |  |  |  | 1 | 1 |  |  |  |  | 144101.21 | 2622.6567 | 144101.21 | 2622.6567 | 9.5148 | [5 empty] | 126.3267 | 2622.6567 |  | 104.98
24.05.2008 12:00 | 3600 | 2 | 768.74 | GGB | 763.37 | 775.313 | 768.864 | 269.04 | GGB | 11024.2 | GGB | 9.8 | GGB | 1009.36 | GGB | 60.11 | GGB | 176150.87 | GGB | 143846.5 | GGB | 0 | 0 | 3084 | 3600 | 3068.41 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239369.52 | GGB | 239372.26 | 3068.41 | 2627.3006 |  |  |  | 0 | 1 | [14 empty] | 122.6056 | 2627.3006 |  | 104.98
24.05.2008 13:00 | 3600 | 2 | 765.13 | GGB | 762.271 | 773.18 | 766.667 | 268.04 | GGB | 11007.5 | GGB | 9.78 | GGB | 1009.11 | GGB | 60.11 | GGB | 175294.81 | GGB | 143110.21 | GGB | 0 | 0 | 3234 | 3600 | 3218.15 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239409.24 | GGB | 239411.98 | 3218.15 | 2640.8179 |  |  |  | 0 | 1 | [14 empty] | 127.9306 | 2640.8179 |  | 104.98
24.05.2008 14:00 | 3600 | 2 | 765.67 | GGB | 762.271 | 774.445 | 767.766 | 268.8 | GGB | 10974 | GGB | 9.79 | GGB | 1009.39 | GGB | 59.7 | GGB | 176583.3 | GGB | 144382.34 | GGB | 0 | 0 | 3184 | 3600 | 3168.04 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239448.96 | GGB | 239451.7 | 3168.04 | 2617.55 |  |  |  | 0 | 1 | [14 empty] | 127.0581 | 2617.55 |  | 104.98
24.05.2008 15:00 | 3600 | 2 | 765.97 | GGB | 762.271 | 773.203 | 766.667 | 267.04 | GGB | 10992.6 | GGB | 9.8 | GGB | 1009.25 | GGB | 60.44 | GGB | 174311.11 | GGB | 142188.51 | GGB | 0 | 0 | 3180 | 3600 | 3164.05 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239488.68 | GGB | 239491.42 | 3164.05 | 2657.9363 |  |  |  | 0 | 1 | [14 empty] | 124.9699 | 2657.9363 |  | 104.98
24.05.2008 16:00 | 3600 | 2 | 766.61 | GGB | 762.271 | 772.008 | 766.667 | 267.18 | GGB | 10944.8 | GGB | 9.78 | GGB | 1009.31 | GGB | 60.47 | GGB | 174717.13 | GGB | 142514.01 | GGB | 0 | 0 | 3119 | 3600 | 3103.66 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239528.41 | GGB | 239531.14 | 3103.66 | 2651.8656 |  |  |  | 0 | 1 | [14 empty] | 122.8653 | 2651.8656 |  | 104.98
24.05.2008 17:00 | 3600 | 2 | 765.96 | GGB | 765.934 | 776.672 | 769.963 | 266.92 | GGB | 10948.6 | GGB | 9.8 | GGB | 1009.46 | GGB | 60.32 | GGB | 174666.51 | GGB | 142558.54 | GGB | 0 | 0 | 3135 | 3600 | 3119.46 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239568.13 | GGB | 239570.86 | 3119.46 | 2651.0373 |  |  |  | 1 | 1 |  |  |  |  | 142558.54 | 2651.0373 | 142558.54 | 2651.0373 | 9.5148 | [5 empty] | 123.5294 | 2651.0373 |  | 104.98
24.05.2008 18:00 | 3600 | 2 | 765.66 | GGB | 763.37 | 774.539 | 767.766 | 265.62 | GGB | 10937.7 | GGB | 9.79 | GGB | 1009.52 | GGB | 60.88 | GGB | 172769.53 | GGB | 140780.29 | GGB | 0 | 0 | 3149 | 3600 | 3133.69 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239607.85 | GGB | 239610.58 | 3133.69 | 2684.5235 |  |  |  | 0 | 1 | [14 empty] | 122.5449 | 2684.5235 |  | 104.98
24.05.2008 19:00 | 3600 | 2 | 766.28 | GGB | 764.835 | 775.664 | 769.963 | 267.24 | GGB | 10905.6 | GGB | 9.78 | GGB | 1009.96 | GGB | 60.34 | GGB | 174670.92 | GGB | 142622.17 | GGB | 0 | 0 | 3130 | 3600 | 3114.54 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239647.57 | GGB | 239650.3 | 3114.54 | 2649.8545 |  |  |  | 1 | 1 |  |  |  |  | 142622.17 | 2649.8545 | 142622.17 | 2649.8545 | 9.5148 | [5 empty] | 123.3896 | 2649.8545 |  | 104.98
24.05.2008 20:00 | 3600 | 2 | 766.71 | GGB | 762.271 | 773.32 | 766.667 | 265.76 | GGB | 10933.2 | GGB | 9.79 | GGB | 1010.09 | GGB | 60.93 | GGB | 172728.82 | GGB | 140807.58 | GGB | 0 | 0 | 3136 | 3600 | 3120.37 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239687.29 | GGB | 239690.02 | 3120.37 | 2684.0032 |  |  |  | 0 | 1 | [14 empty] | 122.0477 | 2684.0032 |  | 104.98
24.05.2008 21:00 | 3600 | 2 | 765.88 | GGB | 763.37 | 773.648 | 767.766 | 266.85 | GGB | 10921.6 | GGB | 9.78 | GGB | 1010.38 | GGB | 60.62 | GGB | 173678.41 | GGB | 141751.64 | GGB | 0 | 0 | 3175 | 3600 | 3159.48 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239727.02 | GGB | 239729.74 | 3159.48 | 2666.1279 |  |  |  | 0 | 1 | [14 empty] | 124.406 | 2666.1279 |  | 104.98
24.05.2008 22:00 | 3600 | 2 | 766.61 | GGB | 764.469 | 775.922 | 769.963 | 267.24 | GGB | 10948.8 | GGB | 9.79 | GGB | 1010.44 | GGB | 60.37 | GGB | 174163.66 | GGB | 142262.9 | GGB | 0 | 0 | 3139 | 3600 | 3122.82 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239766.74 | GGB | 239769.46 | 3122.82 | 2656.5464 |  |  |  | 1 | 1 |  |  |  |  | 142262.9 | 2656.5464 | 142262.9 | 2656.5464 | 9.5148 | [5 empty] | 123.406 | 2656.5464 |  | 104.98
24.05.2008 23:00 | 3600 | 2 | 766.39 | GGB | 764.469 | 774.797 | 768.864 | 266.19 | GGB | 10963.8 | GGB | 9.79 | GGB | 1010.37 | GGB | 60.75 | GGB | 172912.58 | GGB | 141069.68 | GGB | 0 | 0 | 3178 | 3600 | 3161.74 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239806.46 | GGB | 239809.18 | 3161.74 | 2679.0165 |  |  |  | 1 | 1 |  |  |  |  | 141069.68 | 2679.0165 | 141069.68 | 2679.0165 | 9.5148 | [5 empty] | 123.896 | 2679.0165 |  | 104.98
24.05.2008 24:00 | 3600 | 2 | 766.72 | GGB | 764.835 | 776.297 | 769.963 | 266.66 | GGB | 10948.6 | GGB | 9.79 | GGB | 1010.36 | GGB | 60.41 | GGB | 173927.09 | GGB | 142040.63 | GGB | 0 | 0 | 3155 | 3600 | 3139.62 | GGB | 100 | GGB | 39.72 | GGB | 39.72 | GGB | 239846.18 | GGB | 239848.9 | 3139.62 | 2660.7035 |  |  |  | 1 | 1 |  |  |  |  | 142040.63 | 2660.7035 | 142040.63 | 2660.7035 | 9.5148 | [5 empty] | 123.876 | 2660.7035 |  | 104.98
25.05.2008 01:00 | 3600 | 2 | 767.54 | GGB | 764.469 | 776.086 | 769.963 | 264.81 | GGB | 10926.8 | GGB | 9.79 | GGB | 1009.99 | GGB | 61.15 | GGB | 171314.89 | GGB | 139549.9 | GGB | 0 | 0 | 3127 | 3600 | 3111.5 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 239884.77 | GGB | 239887.48 | 3111.5 | 2708.1926 |  |  |  | 1 | 1 |  |  |  |  | 139549.9 | 2708.1926 | 139549.9 | 2708.1926 | 9.796 | [5 empty] | 120.6138 | 2708.1926 |  | 104.98
25.05.2008 02:00 | 3600 | 2 | 768.39 | GGB | 765.934 | 777.117 | 771.429 | 264.62 | GGB | 10923.4 | GGB | 9.79 | GGB | 1009.61 | GGB | 61.04 | GGB | 171412.82 | GGB | 139620.7 | GGB | 0 | 0 | 3099 | 3600 | 3083.67 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 239923.35 | GGB | 239926.06 | 3083.67 | 2706.8193 |  |  |  | 1 | 1 |  |  |  |  | 139620.7 | 2706.8193 | 139620.7 | 2706.8193 | 9.796 | [5 empty] | 119.5956 | 2706.8193 |  | 104.98
25.05.2008 03:00 | 3600 | 2 | 769.12 | GGB | 768.132 | 779.367 | 772.527 | 265.02 | GGB | 10922.2 | GGB | 9.79 | GGB | 1009.79 | GGB | 61.03 | GGB | 171767.12 | GGB | 139940.7 | GGB | 0 | 0 | 3076 | 3600 | 3059.81 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 239961.94 | GGB | 239964.64 | 3059.81 | 2700.6296 |  |  |  | 0 | 1 | [14 empty] | 118.9422 | 2700.6296 |  | 104.98
25.05.2008 04:00 | 3600 | 2 | 768.01 | GGB | 764.469 | 776.086 | 769.963 | 266.93 | GGB | 10889.5 | GGB | 9.77 | GGB | 1010.03 | GGB | 60.45 | GGB | 174177.96 | GGB | 142182.7 | GGB | 0 | 0 | 3098 | 3600 | 3082.33 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240000.52 | GGB | 240003.22 | 3082.33 | 2658.0449 |  |  |  | 1 | 1 |  |  |  |  | 142182.7 | 2658.0449 | 142182.7 | 2658.0449 | 9.796 | [5 empty] | 121.7372 | 2658.0449 |  | 104.98
25.05.2008 05:00 | 3600 | 2 | 768.62 | GGB | 765.934 | 777.188 | 770.33 | 266.9 | GGB | 10937.4 | GGB | 9.79 | GGB | 1009.78 | GGB | 60.13 | GGB | 174458.55 | GGB | 142512.5 | GGB | 0 | 0 | 3085 | 3600 | 3069.41 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240039.1 | GGB | 240041.8 | 3069.41 | 2651.8937 |  |  |  | 1 | 1 |  |  |  |  | 142512.5 | 2651.8937 | 142512.5 | 2651.8937 | 9.796 | [5 empty] | 121.5081 | 2651.8937 |  | 104.98
25.05.2008 06:00 | 3600 | 2 | 767.55 | GGB | 764.469 | 776.086 | 769.963 | 266.73 | GGB | 10924 | GGB | 9.73 | GGB | 1009.74 | GGB | 60.29 | GGB | 173968.9 | GGB | 142041.59 | GGB | 0 | 0 | 3155 | 3600 | 3139.4 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240077.69 | GGB | 240080.38 | 3139.4 | 2660.6855 |  |  |  | 1 | 1 |  |  |  |  | 142041.59 | 2660.6855 | 142041.59 | 2660.6855 | 9.796 | [5 empty] | 123.8682 | 2660.6855 |  | 104.98
25.05.2008 07:00 | 3600 | 2 | 773.66 | GGB | 760.806 | 771.727 | 766.3 | 267.25 | GGB | 11007.7 | GGB | 9.79 | GGB | 1010.15 | GGB | 60.99 | GGB | 173667.41 | GGB | 141556.22 | GGB | 0 | 0 | 2941 | 3600 | 2925.85 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240116.27 | GGB | 240118.96 | 2925.85 | 2669.8085 |  |  |  | 0 | 1 | [14 empty] | 115.0479 | 2669.8085 |  | 104.98
25.05.2008 08:00 | 3600 | 2 | 767.78 | GGB | 764.469 | 774.984 | 768.864 | 267.26 | GGB | 11022 | GGB | 9.79 | GGB | 1010.6 | GGB | 60.21 | GGB | 174597.19 | GGB | 142711.21 | GGB | 0 | 0 | 3153 | 3600 | 3136.87 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240154.86 | GGB | 240157.54 | 3136.87 | 2648.2012 |  |  |  | 1 | 1 |  |  |  |  | 142711.21 | 2648.2012 | 142711.21 | 2648.2012 | 9.796 | [5 empty] | 124.3518 | 2648.2012 |  | 104.98
25.05.2008 09:00 | 3600 | 2 | 770.47 | GGB | 763.37 | 774.773 | 767.766 | 266.5 | GGB | 11014.3 | GGB | 9.8 | GGB | 1011.07 | GGB | 60.68 | GGB | 173490.25 | GGB | 141669.1 | GGB | 0 | 0 | 3035 | 3600 | 3019.73 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240193.44 | GGB | 240196.12 | 3019.73 | 2667.6812 |  |  |  | 0 | 1 | [14 empty] | 118.834 | 2667.6812 |  | 104.98
25.05.2008 10:00 | 3600 | 2 | 770.13 | GGB | 765.934 | 776.93 | 771.429 | 264.99 | GGB | 10952.6 | GGB | 9.8 | GGB | 1011.62 | GGB | 60.92 | GGB | 172435.03 | GGB | 140784.9 | GGB | 0 | 0 | 3043 | 3600 | 3027.01 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240232.03 | GGB | 240234.7 | 3027.01 | 2684.4356 |  |  |  | 0 | 1 | [14 empty] | 118.377 | 2684.4356 |  | 104.98
25.05.2008 11:00 | 3600 | 2 | 771.89 | GGB | 765.934 | 777 | 770.33 | 263.57 | GGB | 10894.7 | GGB | 9.8 | GGB | 1011.18 | GGB | 61.57 | GGB | 170806.53 | GGB | 139122.13 | GGB | 0 | 0 | 2965 | 3600 | 2949.68 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240270.61 | GGB | 240273.28 | 2949.68 | 2716.5197 |  |  |  | 0 | 1 | [14 empty] | 113.9905 | 2716.5197 |  | 104.98
25.05.2008 12:00 | 3600 | 2 | 773.57 | GGB | 764.835 | 777.328 | 770.33 | 262.42 | GGB | 10837.2 | GGB | 9.79 | GGB | 1010.83 | GGB | 61.99 | GGB | 169737 | GGB | 138031.35 | GGB | 0 | 0 | 2903 | 3600 | 2887.03 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240309.19 | GGB | 240311.86 | 2887.03 | 2737.9867 |  |  |  | 0 | 1 | [14 empty] | 110.6946 | 2737.9867 |  | 104.98
25.05.2008 13:00 | 3600 | 2 | 773.37 | GGB | 765.934 | 778.242 | 771.429 | 261.76 | GGB | 10814.8 | GGB | 9.79 | GGB | 1011.2 | GGB | 62.19 | GGB | 169242.95 | GGB | 137597.72 | GGB | 0 | 0 | 2902 | 3600 | 2886.36 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240347.78 | GGB | 240350.44 | 2886.36 | 2746.6153 |  |  |  | 0 | 1 | [14 empty] | 110.3213 | 2746.6153 |  | 104.98
25.05.2008 14:00 | 3600 | 2 | 773.5 | GGB | 767.033 | 779.18 | 771.429 | 260.85 | GGB | 10783.6 | GGB | 9.79 | GGB | 1011.38 | GGB | 62.58 | GGB | 168400.09 | GGB | 136778.01 | GGB | 0 | 0 | 2883 | 3600 | 2867.79 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240386.36 | GGB | 240389.02 | 2867.79 | 2763.0757 |  |  |  | 0 | 1 | [14 empty] | 108.9585 | 2763.0757 |  | 104.98
25.05.2008 15:00 | 3600 | 2 | 774.08 | GGB | 765.934 | 778.148 | 771.429 | 260.85 | GGB | 10775.5 | GGB | 9.78 | GGB | 1010.64 | GGB | 62.35 | GGB | 168448.51 | GGB | 136809.8 | GGB | 0 | 0 | 2877 | 3600 | 2861.13 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240424.95 | GGB | 240427.6 | 2861.13 | 2762.4337 |  |  |  | 0 | 1 | [14 empty] | 108.7307 | 2762.4337 |  | 104.98
25.05.2008 16:00 | 3600 | 2 | 774.44 | GGB | 767.033 | 778.078 | 771.429 | 260.48 | GGB | 10760.6 | GGB | 9.78 | GGB | 1010.88 | GGB | 62.66 | GGB | 167936.85 | GGB | 136302.57 | GGB | 0 | 0 | 2873 | 3600 | 2857.52 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240463.53 | GGB | 240466.18 | 2857.52 | 2772.7137 |  |  |  | 0 | 1 | [14 empty] | 108.1909 | 2772.7137 |  | 104.98
25.05.2008 17:00 | 3600 | 2 | 775.31 | GGB | 767.033 | 778.875 | 772.527 | 260.14 | GGB | 10733 | GGB | 9.77 | GGB | 1010.96 | GGB | 62.71 | GGB | 167911.54 | GGB | 136272.96 | GGB | 0 | 0 | 2835 | 3600 | 2819.93 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240502.12 | GGB | 240504.76 | 2819.93 | 2773.3161 |  |  |  | 0 | 1 | [14 empty] | 106.7445 | 2773.3161 |  | 104.98
25.05.2008 18:00 | 3600 | 2 | 779.69 | GNB | 769.597 | 782.016 | 776.19 | 259.93 | GGB | 10739.1 | GGB | 9.78 | GGB | 1010.67 | GGB | 63.07 | GGB | 167337.16 | GGB | 135620.44 | GGB | 0 | 0 | 2675 | 3600 | 2659.58 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240540.7 | GGB | 240543.34 | 2659.58 | 2659.58 |  |  |  | 0 | 1 | [14 empty] | 100.1926 |  |  | #VALUE!
25.05.2008 19:00 | 3600 | 2 | 777.75 | GGB | 767.033 | 779.883 | 772.527 | 259.81 | GGB | 10728.8 | GGB | 9.77 | GGB | 1010.9 | GGB | 63.09 | GGB | 167384.48 | GGB | 135682.43 | GGB | 0 | 0 | 2719 | 3600 | 2703.47 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240579.28 | GGB | 240581.92 | 2703.47 | 2703.47 |  |  |  | 0 | 1 | [14 empty] | 101.8926 |  |  | #VALUE!
25.05.2008 20:00 | 3600 | 2 | 775.73 | GGB | 765.934 | 777.516 | 771.429 | 260.14 | GGB | 10722.8 | GGB | 9.75 | GGB | 1011.06 | GGB | 62.84 | GGB | 167770.7 | GGB | 136118.76 | GGB | 0 | 0 | 2763 | 3600 | 2748.03 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240617.87 | GGB | 240620.5 | 2748.03 | 2748.03 |  |  |  | 0 | 1 | [14 empty] | 103.9051 |  |  | #VALUE!
25.05.2008 21:00 | 3600 | 2 | 775.46 | GGB | 768.132 | 779.602 | 773.626 | 261.11 | GGB | 10770.7 | GGB | 9.76 | GGB | 1011.65 | GGB | 62.54 | GGB | 168775.31 | GGB | 137135.45 | GGB | 0 | 0 | 2730 | 3600 | 2714.1 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240656.45 | GGB | 240659.08 | 2714.1 | 2714.1 |  |  |  | 0 | 1 | [14 empty] | 103.3887 |  |  | #VALUE!
25.05.2008 22:00 | 3600 | 2 | 773.04 | GGB | 763.37 | 776.133 | 768.498 | 262.62 | GGB | 10821.5 | GGB | 9.75 | GGB | 1012.28 | GGB | 61.95 | GGB | 170227.75 | GGB | 138643 | GGB | 0 | 0 | 2766 | 3600 | 2750.5 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240695.04 | GGB | 240697.66 | 2750.5 | 2725.9075 |  |  |  | 0 | 1 | [14 empty] | 105.9271 | 2725.9075 |  | 104.98
25.05.2008 23:00 | 3600 | 2 | 771.21 | GGB | 761.172 | 773.859 | 765.934 | 263.99 | GGB | 10865.5 | GGB | 9.75 | GGB | 1013.59 | GGB | 61.32 | GGB | 171762.72 | GGB | 140339.39 | GGB | 0 | 0 | 2806 | 3600 | 2790.83 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240733.62 | GGB | 240736.24 | 2790.83 | 2692.9574 |  |  |  | 0 | 1 | [14 empty] | 108.7954 | 2692.9574 |  | 104.98
25.05.2008 24:00 | 3600 | 2 | 769.77 | GGB | 763.37 | 776.18 | 768.498 | 267.35 | GGB | 10926 | GGB | 9.75 | GGB | 1014.59 | GGB | 59.79 | GGB | 175759.15 | GGB | 144405.94 | GGB | 0 | 0 | 2873 | 3600 | 2857.04 | GGB | 100 | GGB | 38.58 | GGB | 38.58 | GGB | 240772.21 | GGB | 240774.82 | 2857.04 | 2617.1223 |  |  |  | 0 | 1 | [14 empty] | 114.6038 | 2617.1223 |  | 104.98
26.05.2008 01:00 | 3600 | 2 | 770.54 | GGB | 763.37 | 774.984 | 768.498 | 266.34 | GGB | 11022.4 | GGB | 9.78 | GGB | 1014.88 | GGB | 60.08 | GGB | 174129.55 | GGB | 142986.16 | GGB | 0 | 0 | 2864 | 3600 | 2848.4 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 240811.27 | GGB | 240813.89 | 2848.4 | 2643.109 |  |  |  | 0 | 1 | [14 empty] | 113.1338 | 2643.109 |  | 104.98
26.05.2008 02:00 | 3600 | 2 | 766.59 | GGB | 760.806 | 771.773 | 765.934 | 268.42 | GGB | 11015.3 | GGB | 9.74 | GGB | 1015.82 | GGB | 59.88 | GGB | 176552.49 | GGB | 145199.1 | GGB | 0 | 0 | 3017 | 3600 | 3001.22 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 240850.34 | GGB | 240852.96 | 3001.22 | 2602.8261 |  |  |  | 0 | 1 | [14 empty] | 121.0485 | 2602.8261 |  | 104.98
26.05.2008 03:00 | 3600 | 2 | 766.75 | GGB | 763.37 | 774.797 | 767.033 | 269.99 | GGB | 11062 | GGB | 9.77 | GGB | 1016.56 | GGB | 59.01 | GGB | 178702.55 | GGB | 147457.09 | GGB | 0 | 0 | 3021 | 3600 | 3004.9 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 240889.41 | GGB | 240892.03 | 3004.9 | 2562.9693 |  |  |  | 0 | 1 | [14 empty] | 123.0816 | 2562.9693 |  | 104.98
26.05.2008 04:00 | 3600 | 2 | 765.87 | GGB | 762.271 | 771.867 | 765.934 | 269.51 | GGB | 11129.4 | GGB | 9.77 | GGB | 1016.9 | GGB | 59.53 | GGB | 177579.11 | GGB | 146350.01 | GGB | 0 | 0 | 3101 | 3600 | 3085.53 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 240928.47 | GGB | 240931.1 | 3085.53 | 2582.3572 |  |  |  | 0 | 1 | [14 empty] | 125.4354 | 2582.3572 |  | 104.98
26.05.2008 05:00 | 3600 | 2 | 764.21 | GGB | 762.271 | 771.844 | 766.3 | 271.99 | GGB | 11131.5 | GGB | 9.75 | GGB | 1017.31 | GGB | 58.62 | GGB | 180825.1 | GGB | 149493.81 | GGB | 0 | 0 | 3195 | 3600 | 3179.47 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 240967.54 | GGB | 240970.17 | 3179.47 | 2528.0512 |  |  |  | 0 | 1 | [14 empty] | 132.0309 | 2528.0512 |  | 104.98
26.05.2008 06:00 | 3600 | 2 | 763.3 | GGB | 762.271 | 773.039 | 766.667 | 275.24 | GGB | 11225.6 | GGB | 9.76 | GGB | 1017.93 | GGB | 57.96 | GGB | 184523.34 | GGB | 152948.07 | GNB | 0 | 0 | 3265 | 3600 | 3249.36 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241006.61 | GGB | 241009.24 | 3249.36 | 2470.9563 |  |  |  | 0 | 1 | [14 empty] | 138.0509 | 2470.9563 |  | 104.98
26.05.2008 07:00 | 3600 | 2 | 764.33 | GGB | 763.37 | 773.063 | 767.766 | 273.51 | GGB | 11300.9 | GGB | 9.8 | GGB | 1018.15 | GGB | 58.81 | GGB | 182127.9 | GGB | 150609.14 | GGB | 0 | 0 | 3251 | 3600 | 3235.55 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241045.67 | GGB | 241048.31 | 3235.55 | 2509.3298 |  |  |  | 0 | 1 | [14 empty] | 135.3621 | 2509.3298 |  | 104.98
26.05.2008 08:00 | 3600 | 2 | 765.47 | GGB | 764.835 | 775.219 | 768.864 | 270.58 | GGB | 11224.9 | GGB | 9.82 | GGB | 1018.08 | GGB | 59.52 | GGB | 178782.88 | GGB | 147519.54 | GGB | 0 | 0 | 3177 | 3600 | 3161.28 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241084.74 | GGB | 241087.38 | 3161.28 | 2561.8843 |  |  |  | 1 | 1 |  |  |  |  | 147519.54 | 2561.8843 | 147519.54 | 2561.8843 | 9.6731 | [5 empty] | 129.5418 | 2561.8843 |  | 104.98
26.05.2008 09:00 | 3600 | 2 | 769.42 | GGB | 768.498 | 780.352 | 773.993 | 267.18 | GGB | 11064.5 | GGB | 9.82 | GGB | 1017.56 | GGB | 60.63 | GGB | 174672.02 | GGB | 143571.3 | GGB | 0 | 0 | 2974 | 3600 | 2958.54 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241123.81 | GGB | 241126.45 | 2958.54 | 2632.3367 |  |  |  | 0 | 1 | [14 empty] | 117.9893 | 2632.3367 |  | 104.98
26.05.2008 10:00 | 3600 | 2 | 768.81 | GGB | 767.033 | 778.148 | 771.429 | 264.67 | GGB | 10920.8 | GGB | 9.8 | GGB | 1017.23 | GGB | 61.57 | GGB | 172063.12 | GGB | 140986.15 | GGB | 0 | 0 | 2959 | 3600 | 2942.88 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241162.87 | GGB | 241165.52 | 2942.88 | 2680.6037 |  |  |  | 1 | 1 |  |  |  |  | 140986.15 | 2680.6037 | 140986.15 | 2680.6037 | 9.6731 | [5 empty] | 115.2515 | 2680.6037 |  | 104.98
26.05.2008 11:00 | 3600 | 2 | 771 | GGB | 768.132 | 780.141 | 773.626 | 262.31 | GGB | 10849.9 | GGB | 9.8 | GGB | 1016.12 | GGB | 62.28 | GGB | 170062.7 | GGB | 138898.33 | GGB | 0 | 0 | 2874 | 3600 | 2858.17 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241201.94 | GGB | 241204.59 | 2858.17 | 2720.8966 |  |  |  | 0 | 1 | [14 empty] | 110.2764 | 2720.8966 |  | 104.98
26.05.2008 12:00 | 3600 | 2 | 774.14 | GGB | 768.498 | 780 | 772.527 | 262.46 | GGB | 10768.8 | GGB | 9.78 | GGB | 1015.3 | GGB | 62.36 | GGB | 170695.4 | GGB | 139269.02 | GGB | 0 | 0 | 2741 | 3600 | 2725.36 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241241 | GGB | 241243.66 | 2725.36 | 2713.6545 |  |  |  | 0 | 1 | [14 empty] | 105.4328 | 2713.6545 |  | 104.98
26.05.2008 13:00 | 3600 | 2 | 773.76 | GGB | 767.033 | 777.938 | 772.527 | 260.58 | GGB | 10777.8 | GGB | 9.78 | GGB | 1014.33 | GGB | 63.06 | GGB | 168707.09 | GGB | 137228.78 | GGB | 0 | 0 | 2761 | 3600 | 2745.55 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241280.07 | GGB | 241282.73 | 2745.55 | 2745.55 |  |  |  | 0 | 1 | [14 empty] | 104.6579 |  |  | #VALUE!
26.05.2008 14:00 | 3600 | 2 | 774.63 | GGB | 769.597 | 781.336 | 773.993 | 260.47 | GGB | 10755.3 | GGB | 9.78 | GGB | 1013.99 | GGB | 62.8 | GGB | 168677.38 | GGB | 137268.18 | GGB | 0 | 0 | 2726 | 3600 | 2711.07 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241319.14 | GGB | 241321.8 | 2711.07 | 2711.07 |  |  |  | 0 | 1 | [14 empty] | 103.3732 |  |  | #VALUE!
26.05.2008 15:00 | 3600 | 2 | 772.83 | GGB | 765.934 | 776.813 | 771.429 | 260.37 | GGB | 10720.3 | GGB | 9.76 | GGB | 1013.52 | GGB | 62.85 | GGB | 168537.63 | GGB | 137067.92 | GGB | 0 | 0 | 2763 | 3600 | 2747.84 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241358.2 | GGB | 241360.87 | 2747.84 | 2747.84 |  |  |  | 0 | 1 | [14 empty] | 104.6224 |  |  | #VALUE!
26.05.2008 16:00 | 3600 | 2 | 774.43 | GGB | 764.469 | 776.648 | 770.33 | 259.92 | GGB | 10725.3 | GGB | 9.77 | GGB | 1012.45 | GGB | 62.8 | GGB | 167984.16 | GGB | 136492.98 | GGB | 0 | 0 | 2684 | 3600 | 2668.37 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241397.27 | GGB | 241399.94 | 2668.37 | 2668.37 |  |  |  | 0 | 1 | [14 empty] | 101.1705 |  |  | #VALUE!
26.05.2008 17:00 | 3600 | 2 | 774.36 | GGB | 767.033 | 778.805 | 772.527 | 259.9 | GGB | 10692.8 | GGB | 9.76 | GGB | 1011.88 | GGB | 62.91 | GGB | 168211.93 | GGB | 136557.35 | GGB | 0 | 0 | 2630 | 3600 | 2614.55 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241436.34 | GGB | 241439.01 | 2614.55 | 2614.55 |  |  |  | 0 | 1 | [14 empty] | 99.1767 |  |  | #VALUE!
26.05.2008 18:00 | 3600 | 2 | 775.09 | GGB | 768.498 | 780.469 | 773.993 | 259.73 | GGB | 10694.6 | GGB | 9.77 | GGB | 1011.35 | GGB | 62.86 | GGB | 167833.42 | GGB | 136197.26 | GGB | 0 | 0 | 2582 | 635 | 1290.77 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241475.4 | GGB | 241478.08 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
26.05.2008 19:00 | 3600 | 2 | 774.07 | GGB | 764.835 | 776.273 | 769.963 | 259.16 | GGB | 10666 | GGB | 9.75 | GGB | 1011.04 | GGB | 63.31 | GGB | 167053.28 | GGB | 135343.07 | GGB | 0 | 0 | 0 | 0 | 1298.92 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241514.47 | GGB | 241517.15 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
26.05.2008 20:00 | 3600 | 2 | 774.93 | GGB | 768.132 | 779.273 | 773.626 | 259.89 | GGB | 10660.5 | GGB | 9.76 | GGB | 1011.2 | GGB | 62.68 | GGB | 168242.74 | GGB | 136585.31 | GGB | 0 | 0 | 0 | 0 | 1287.11 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241553.54 | GGB | 241556.22 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
26.05.2008 21:00 | 3600 | 2 | 773.37 | GGB | 764.835 | 777.141 | 770.33 | 259.11 | GGB | 10710.2 | GGB | 9.76 | GGB | 1010.61 | GGB | 62.94 | GGB | 166845.31 | GGB | 135268.42 | GGB | 0 | 0 | 0 | 0 | 1299.64 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241592.6 | GGB | 241595.29 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
26.05.2008 22:00 | 3600 | 2 | 771.77 | GGB | 763.37 | 775.383 | 768.864 | 261.99 | GGB | 10723.9 | GGB | 9.74 | GGB | 1010.87 | GGB | 62.14 | GGB | 169834.93 | GGB | 138055.04 | GGB | 0 | 0 | 0 | 0 | 1273.4 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241631.67 | GGB | 241634.36 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
26.05.2008 23:00 | 3600 | 2 | 771.05 | GGB | 763.37 | 774.867 | 767.766 | 262.88 | GGB | 10862.5 | GGB | 9.76 | GGB | 1011.3 | GGB | 61.75 | GGB | 171073.91 | GGB | 139280.96 | GGB | 0 | 0 | 0 | 0 | 1262.2 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241670.74 | GGB | 241673.43 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
26.05.2008 24:00 | 3600 | 2 | 768.47 | GGB | 763.37 | 773.93 | 767.766 | 264.77 | GGB | 10875 | GGB | 9.74 | GGB | 1011.6 | GGB | 61.82 | GGB | 171891.46 | GGB | 139959.47 | GGB | 0 | 0 | 0 | 0 | 1256.08 | GNB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 241709.8 | GGB | 241712.5 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
27.05.2008 01:00 | 3600 | 2 | 768.5 | GGB | 764.835 | 776.203 | 769.963 | 266.73 | GGB | 10907.9 | GGB | 9.76 | GGB | 1011.73 | GGB | 61.03 | GGB | 174148.26 | GGB | 142150.32 | GGB | 0 | 0 | 0 | 0 | 1233.2 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241748.76 | GGB | 241751.46 | 1233.3423 | 1233.3423 |  |  |  | 1 | 1 |  |  |  |  | 142150.32 | 1233.3423 | 142150.32 |  | 4.5 | 1233.3423 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 02:00 | 3600 | 2 | 768.91 | GGB | 764.469 | 775.195 | 768.864 | 264.95 | GGB | 10947.6 | GGB | 9.77 | GGB | 1011.24 | GGB | 61.55 | GGB | 172053.21 | GGB | 140153.55 | GGB | 0 | 0 | 0 | 0 | 1250.77 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241787.71 | GGB | 241790.42 | 1250.9137 | 1250.9137 |  |  |  | 1 | 1 |  |  |  |  | 140153.55 | 1250.9137 | 140153.55 |  | 4.5 | 1250.9137 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 03:00 | 3600 | 2 | 768.08 | GGB | 765.934 | 776.461 | 770.33 | 266.4 | GGB | 10917.6 | GGB | 9.77 | GGB | 1011.26 | GGB | 61.09 | GGB | 173859.97 | GGB | 141825.32 | GGB | 0 | 0 | 0 | 0 | 1236.02 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241826.67 | GGB | 241829.38 | 1236.1685 | 1236.1685 |  |  |  | 1 | 1 |  |  |  |  | 141825.32 | 1236.1685 | 141825.32 |  | 4.5 | 1236.1685 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 04:00 | 3600 | 2 | 771.01 | GGB | 768.498 | 779.625 | 773.626 | 265.4 | GGB | 10868.3 | GGB | 9.73 | GGB | 1011.5 | GGB | 61.55 | GGB | 172319.49 | GGB | 140408.34 | GGB | 0 | 0 | 0 | 0 | 1248.5 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241865.63 | GGB | 241868.34 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
27.05.2008 05:00 | 3600 | 2 | 769.04 | GGB | 763.37 | 774.281 | 767.766 | 265.07 | GGB | 10936.9 | GGB | 9.77 | GGB | 1012.34 | GGB | 61.54 | GGB | 171700 | GGB | 140024.07 | GGB | 0 | 0 | 0 | 0 | 1251.92 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241904.58 | GGB | 241907.3 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
27.05.2008 06:00 | 3600 | 2 | 767.07 | GGB | 762.271 | 774.422 | 767.766 | 267.52 | GGB | 10916.3 | GGB | 9.75 | GGB | 1012.57 | GGB | 60.88 | GGB | 174521.27 | GGB | 142637.29 | GGB | 0 | 0 | 0 | 0 | 1228.99 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241943.54 | GGB | 241946.26 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
27.05.2008 07:00 | 3600 | 2 | 767.75 | GGB | 764.469 | 775.406 | 768.864 | 266 | GGB | 10985.8 | GGB | 9.78 | GGB | 1012.04 | GGB | 61.53 | GGB | 172507.65 | GGB | 140644.05 | GGB | 0 | 0 | 0 | 0 | 1246.4 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 241982.49 | GGB | 241985.22 | 1246.5511 | 1246.5511 |  |  |  | 1 | 1 |  |  |  |  | 140644.05 | 1246.5511 | 140644.05 |  | 4.5 | 1246.5511 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 08:00 | 3600 | 2 | 766.89 | GGB | 764.469 | 775.898 | 768.864 | 267.14 | GGB | 10949.9 | GGB | 9.76 | GGB | 1011.97 | GGB | 61.29 | GGB | 173734.53 | GGB | 141738.63 | GGB | 0 | 0 | 0 | 0 | 1236.78 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242021.45 | GGB | 242024.18 | 1236.9246 | 1236.9246 |  |  |  | 1 | 1 |  |  |  |  | 141738.63 | 1236.9246 | 141738.63 |  | 4.5 | 1236.9246 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 09:00 | 3600 | 2 | 768.66 | GGB | 764.835 | 776.883 | 769.963 | 266.56 | GGB | 10913.4 | GGB | 9.79 | GGB | 1011.97 | GGB | 61.33 | GGB | 173382.42 | GGB | 141431.12 | GGB | 0 | 0 | 0 | 0 | 1239.47 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242060.4 | GGB | 242063.14 | 1239.614 | 1239.614 |  |  |  | 1 | 1 |  |  |  |  | 141431.12 | 1239.614 | 141431.12 |  | 4.5 | 1239.614 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 10:00 | 3600 | 2 | 769.1 | GGB | 765.934 | 777.82 | 770.33 | 265.69 | GGB | 10871.6 | GGB | 9.78 | GGB | 1011.54 | GGB | 61.51 | GGB | 172738.72 | GGB | 140774.83 | GGB | 0 | 0 | 0 | 0 | 1245.25 | GNB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242099.36 | GGB | 242102.1 | 1245.3931 | 1245.3931 |  |  |  | 1 | 1 |  |  |  |  | 140774.83 | 1245.3931 | 140774.83 |  | 4.5 | 1245.3931 |  |  |  |  | 48.7 |  |  | #VALUE!
27.05.2008 11:00 | 3600 | 2 | 769.71 | GGB | 764.469 | 775.734 | 769.963 | 264.23 | GGB | 10868.3 | GGB | 9.78 | GGB | 1011.27 | GGB | 62.03 | GGB | 170933.07 | GGB | 139048.16 | GGB | 0 | 0 | 2952 | 3187 | 2936.28 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242138.31 | GGB | 242141.06 | 2936.28 | 2717.9648 |  |  |  | 0 | 1 | [14 empty] | 113.4123 | 2717.9648 |  | 104.98
27.05.2008 12:00 | 3600 | 2 | 770.99 | GGB | 769.597 | 780.141 | 775.091 | 265.23 | GGB | 10814.5 | GGB | 9.74 | GGB | 1011.48 | GGB | 61.78 | GGB | 171912.37 | GGB | 139977.99 | GGB | 0 | 0 | 2953 | 3600 | 2936.97 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242177.27 | GGB | 242180.02 | 2936.97 | 2699.9102 |  |  |  | 0 | 1 | [14 empty] | 114.1975 | 2699.9102 |  | 104.98
27.05.2008 13:00 | 3600 | 2 | 768.21 | GGB | 763.37 | 774.68 | 768.864 | 267.47 | GGB | 10816 | GGB | 9.71 | GGB | 1012.3 | GGB | 60.66 | GGB | 174498.16 | GGB | 142675.09 | GGB | 0 | 0 | 3115 | 3600 | 3098.99 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242216.22 | GGB | 242218.98 | 3098.99 | 2648.8716 |  |  |  | 0 | 1 | [14 empty] | 122.8191 | 2648.8716 |  | 104.98
27.05.2008 14:00 | 3600 | 2 | 769.9 | GGB | 764.835 | 776.648 | 769.963 | 265.66 | GGB | 10871.4 | GGB | 9.75 | GGB | 1012.43 | GGB | 61.82 | GGB | 172014.7 | GGB | 140174.72 | GGB | 0 | 0 | 3072 | 3600 | 3056.78 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242255.18 | GGB | 242257.94 | 3056.78 | 2696.121 |  |  |  | 0 | 1 | [14 empty] | 119.0231 | 2696.121 |  | 104.98
27.05.2008 15:00 | 3600 | 2 | 769.32 | GGB | 764.469 | 775.617 | 768.864 | 264.74 | GGB | 10780.8 | GGB | 9.73 | GGB | 1012.1 | GGB | 62.09 | GGB | 171511.85 | GGB | 139605.92 | GGB | 0 | 0 | 3059 | 3600 | 3043.25 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242294.13 | GGB | 242296.9 | 3043.25 | 2707.1058 |  |  |  | 1 | 1 |  |  |  |  | 139605.92 | 2707.1058 | 139605.92 | 2707.1058 | 9.7004 | [5 empty] | 118.0155 | 2707.1058 |  | 104.98
27.05.2008 16:00 | 3600 | 2 | 770.45 | GGB | 762.271 | 773.555 | 767.766 | 262.69 | GGB | 10753 | GGB | 9.75 | GGB | 1011.47 | GGB | 62.57 | GGB | 169801.92 | GGB | 137930.43 | GGB | 0 | 0 | 2974 | 3600 | 2958.01 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242333.09 | GGB | 242335.86 | 2958.01 | 2739.99 |  |  |  | 0 | 1 | [14 empty] | 113.3332 | 2739.99 |  | 104.98
27.05.2008 17:00 | 3600 | 2 | 768.32 | GGB | 762.271 | 773.883 | 767.766 | 262.57 | GGB | 10659.9 | GGB | 9.73 | GGB | 1010.8 | GGB | 62.01 | GGB | 170709.7 | GGB | 138809.64 | GGB | 0 | 0 | 3092 | 3600 | 3076.03 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242372.05 | GGB | 242374.82 | 3076.03 | 2722.6351 |  |  |  | 0 | 1 | [14 empty] | 118.6063 | 2722.6351 |  | 104.98
27.05.2008 18:00 | 3600 | 2 | 770.13 | GGB | 759.707 | 771.938 | 765.201 | 260.43 | GGB | 10650 | GGB | 9.74 | GGB | 1010.38 | GGB | 62.37 | GGB | 168609.16 | GGB | 136898.58 | GGB | 0 | 0 | 3027 | 3600 | 3011.68 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242411 | GGB | 242413.78 | 3011.68 | 2760.6422 |  |  |  | 0 | 1 | [14 empty] | 114.5263 | 2760.6422 |  | 104.98
27.05.2008 19:00 | 3600 | 2 | 768.99 | GGB | 763.37 | 775.031 | 768.132 | 259.53 | GGB | 10640.9 | GGB | 9.73 | GGB | 1010 | GGB | 62.46 | GGB | 167840.02 | GGB | 136183.88 | GGB | 0 | 0 | 3076 | 3600 | 3060 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242449.96 | GGB | 242452.74 | 3060 | 2775.1302 |  |  |  | 0 | 1 | [14 empty] | 115.7563 | 2775.1302 |  | 104.98
27.05.2008 20:00 | 3600 | 2 | 767.39 | GGB | 761.172 | 772.078 | 766.667 | 260.29 | GGB | 10636.3 | GGB | 9.7 | GGB | 1010.62 | GGB | 61.88 | GGB | 168874.34 | GGB | 137348.43 | GGB | 0 | 0 | 3135 | 3600 | 3119.54 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242488.91 | GGB | 242491.7 | 3119.54 | 2751.6004 |  |  |  | 0 | 1 | [14 empty] | 119.0178 | 2751.6004 |  | 104.98
27.05.2008 21:00 | 3600 | 2 | 766.31 | GGB | 760.806 | 772.688 | 766.3 | 264.07 | GGB | 10705.7 | GGB | 9.7 | GGB | 1012.15 | GGB | 60.58 | GGB | 172977.5 | GGB | 141445.12 | GGB | 0 | 0 | 3177 | 3600 | 3161.09 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242527.87 | GGB | 242530.66 | 3161.09 | 2671.9055 |  |  |  | 0 | 1 | [14 empty] | 124.2002 | 2671.9055 |  | 104.98
27.05.2008 22:00 | 3600 | 2 | 765.35 | GGB | 764.102 | 776.25 | 768.864 | 265 | GGB | 10814.9 | GGB | 9.71 | GGB | 1013.36 | GGB | 60.07 | GGB | 174058.03 | GGB | 142716.47 | GGB | 0 | 0 | 3194 | 3600 | 3178.14 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242566.82 | GGB | 242569.62 | 3178.14 | 2648.1036 |  |  |  | 1 | 1 |  |  |  |  | 142716.47 | 2648.1036 | 142716.47 | 2648.1036 | 9.7004 | [5 empty] | 125.9925 | 2648.1036 |  | 104.98
27.05.2008 23:00 | 3600 | 2 | 764.13 | GGB | 757.875 | 769.172 | 762.637 | 265.44 | GGB | 10869.4 | GGB | 9.71 | GGB | 1014.22 | GGB | 59.68 | GGB | 174937.2 | GGB | 143728.27 | GGB | 0 | 0 | 3259 | 3600 | 3242.86 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242605.78 | GGB | 242608.58 | 3242.86 | 2629.4618 |  |  |  | 0 | 1 | [14 empty] | 129.4696 | 2629.4618 |  | 104.98
27.05.2008 24:00 | 3600 | 2 | 765.21 | GGB | 765.201 | 776.344 | 771.429 | 266.27 | GGB | 10961.3 | GGB | 9.74 | GGB | 1015.22 | GGB | 59.21 | GGB | 175622.71 | GGB | 144636.59 | GGB | 0 | 0 | 3232 | 3600 | 3215.68 | GGB | 100 | GGB | 38.96 | GGB | 38.96 | GGB | 242644.73 | GGB | 242647.54 | 3215.68 | 2612.9488 |  |  |  | 1 | 1 |  |  |  |  | 144636.59 | 2612.9488 | 144636.59 | 2612.9488 | 9.7004 | [5 empty] | 129.1958 | 2612.9488 |  | 104.98
28.05.2008 01:00 | 3600 | 2 | 763.14 | GGB | 759.341 | 770.391 | 764.835 | 266.58 | GGB | 10944.1 | GGB | 9.71 | GGB | 1015.99 | GGB | 58.98 | GGB | 175985.82 | GGB | 145149.82 | GGB | 0 | 0 | 3305 | 3600 | 3289.46 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242684.15 | GGB | 242686.96 | 3289.46 | 2603.7097 |  |  |  | 0 | 1 | [14 empty] | 132.629 | 2603.7097 |  | 104.98
28.05.2008 02:00 | 3600 | 2 | 762.74 | GGB | 759.341 | 769.477 | 763.37 | 267.55 | GGB | 10986.7 | GGB | 9.72 | GGB | 1015.87 | GGB | 58.89 | GGB | 176816.57 | GGB | 145855.37 | GGB | 0 | 0 | 3316 | 3600 | 3300.22 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242723.57 | GGB | 242726.38 | 3300.22 | 2591.1147 |  |  |  | 0 | 1 | [14 empty] | 133.7097 | 2591.1147 |  | 104.98
28.05.2008 03:00 | 3600 | 2 | 762 | GGB | 758.974 | 769.5 | 763.37 | 268.62 | GGB | 11037.6 | GGB | 9.72 | GGB | 1015.72 | GGB | 58.52 | GGB | 178001.64 | GGB | 146972.5 | GGB | 0 | 0 | 3350 | 3600 | 3333.99 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242762.99 | GGB | 242765.8 | 3333.99 | 2571.4198 |  |  |  | 0 | 1 | [14 empty] | 136.1125 | 2571.4198 |  | 104.98
28.05.2008 04:00 | 3600 | 2 | 761.35 | GGB | 759.341 | 770.719 | 764.469 | 269.56 | GGB | 11082.8 | GGB | 9.72 | GGB | 1015.39 | GGB | 58.2 | GGB | 179538.81 | GGB | 148340.38 | GGB | 0 | 0 | 3383 | 3600 | 3367.43 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242802.41 | GGB | 242805.22 | 3367.43 | 2547.7082 |  |  |  | 0 | 1 | [14 empty] | 138.7572 | 2547.7082 |  | 104.98
28.05.2008 05:00 | 3600 | 2 | 760.58 | GGB | 757.875 | 768.516 | 763.37 | 270.58 | GGB | 11117.5 | GGB | 9.71 | GGB | 1015.81 | GGB | 57.58 | GGB | 180980.25 | GGB | 149874.88 | GGB | 0 | 0 | 3436 | 3600 | 3419.81 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242841.82 | GGB | 242844.64 | 3419.81 | 2521.6234 |  |  |  | 0 | 1 | [14 empty] | 142.3732 | 2521.6234 |  | 104.98
28.05.2008 06:00 | 3600 | 2 | 760.82 | GGB | 757.875 | 768.633 | 763.37 | 271.51 | GGB | 11177.4 | GGB | 9.72 | GGB | 1016.47 | GGB | 57.13 | GGB | 181980.46 | GGB | 151001.33 | GGB | 0 | 0 | 3445 | 3600 | 3428.54 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242881.24 | GGB | 242884.06 | 3428.54 | 2502.8124 |  |  |  | 0 | 1 | [14 empty] | 143.8095 | 2502.8124 |  | 104.98
28.05.2008 07:00 | 3600 | 2 | 761.75 | GGB | 756.776 | 768.188 | 762.271 | 271.58 | GGB | 11220.9 | GGB | 9.75 | GGB | 1017.4 | GGB | 57.02 | GGB | 182004.67 | GGB | 151214.17 | GGB | 0 | 0 | 3424 | 3600 | 3407.53 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242920.66 | GGB | 242923.48 | 3407.53 | 2499.2896 |  |  |  | 0 | 1 | [14 empty] | 143.1297 | 2499.2896 |  | 104.98
28.05.2008 08:00 | 3600 | 2 | 762.08 | GGB | 760.44 | 771.188 | 765.934 | 269.98 | GGB | 11130.3 | GGB | 9.74 | GGB | 1017.79 | GGB | 57.61 | GGB | 179976.74 | GGB | 149319.31 | GGB | 0 | 0 | 3405 | 3600 | 3388.92 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242960.08 | GGB | 242962.9 | 3388.92 | 2531.0055 |  |  |  | 0 | 1 | [14 empty] | 140.5642 | 2531.0055 |  | 104.98
28.05.2008 09:00 | 3600 | 2 | 762.71 | GGB | 761.538 | 772.125 | 765.934 | 268.7 | GGB | 11062.1 | GGB | 9.74 | GGB | 1017.9 | GGB | 58.36 | GGB | 177810.18 | GGB | 147203.34 | GGB | 0 | 0 | 3338 | 3600 | 3321.82 | GNB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 242999.5 | GGB | 243002.32 | 3321.82 | 2567.3874 |  |  |  | 0 | 1 | [14 empty] | 135.8286 | 2567.3874 |  | 104.98
28.05.2008 10:00 | 3600 | 2 | 763.36 | GGB | 760.44 | 772.219 | 765.934 | 267.57 | GGB | 11003.4 | GGB | 9.74 | GGB | 1017.73 | GGB | 58.98 | GGB | 176223.49 | GGB | 145591.35 | GGB | 0 | 0 | 3239 | 3600 | 3223.22 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243038.91 | GGB | 243041.74 | 3223.22 | 2595.8136 |  |  |  | 0 | 1 | [14 empty] | 130.3536 | 2595.8136 |  | 104.98
28.05.2008 11:00 | 3600 | 2 | 763.31 | GGB | 762.637 | 774.398 | 768.132 | 266.56 | GGB | 10955.5 | GGB | 9.74 | GGB | 1018.14 | GGB | 59.36 | GGB | 175308.01 | GGB | 144729.67 | GGB | 0 | 0 | 3204 | 3600 | 3188.34 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243078.33 | GGB | 243081.16 | 3188.34 | 2611.2683 |  |  |  | 0 | 1 | [14 empty] | 128.1798 | 2611.2683 |  | 104.98
28.05.2008 12:00 | 3600 | 2 | 763.32 | GGB | 762.637 | 774.398 | 767.033 | 266.06 | GGB | 10917.4 | GGB | 9.74 | GGB | 1018.13 | GGB | 59.54 | GGB | 174968.01 | GGB | 144370.58 | GGB | 0 | 0 | 3144 | 3600 | 3128.42 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243117.75 | GGB | 243120.58 | 3128.42 | 2617.7633 |  |  |  | 0 | 1 | [14 empty] | 125.4588 | 2617.7633 |  | 104.98
28.05.2008 13:00 | 3600 | 2 | 762.51 | GGB | 762.637 | 774.703 | 767.033 | 267.03 | GGB | 10866.6 | GGB | 9.73 | GGB | 1018.59 | GGB | 59.22 | GGB | 176277.41 | GGB | 145653.73 | GGB | 0 | 0 | 3140 | 3600 | 3123.82 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243157.17 | GGB | 243160 | 3123.82 | 2594.7018 |  |  |  | 0 | 1 | [14 empty] | 126.3878 | 2594.7018 |  | 104.98
28.05.2008 14:00 | 3600 | 2 | 765.97 | GGB | 764.102 | 775.734 | 768.498 | 265.24 | GGB | 10946.4 | GGB | 9.81 | GGB | 1018.65 | GGB | 60.21 | GGB | 173672.91 | GGB | 143083.53 | GGB | 0 | 0 | 2990 | 3600 | 2973.89 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243196.59 | GGB | 243199.42 | 2973.89 | 2641.3103 |  |  |  | 1 | 1 |  |  |  |  | 143083.53 | 2641.3103 | 143083.53 | 2641.3103 | 9.5872 | [5 empty] | 118.1985 | 2641.3103 |  | 104.98
28.05.2008 15:00 | 3600 | 2 | 765.65 | GGB | 764.102 | 775.805 | 769.597 | 263.65 | GGB | 10899.5 | GGB | 9.79 | GGB | 1018.07 | GGB | 61.22 | GGB | 172111.53 | GGB | 141288.37 | GGB | 0 | 0 | 2987 | 3600 | 2971.31 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243236 | GGB | 243238.84 | 2971.31 | 2674.8698 |  |  |  | 1 | 1 |  |  |  |  | 141288.37 | 2674.8698 | 141288.37 | 2674.8698 | 9.5872 | [5 empty] | 116.6143 | 2674.8698 |  | 104.98
28.05.2008 16:00 | 3600 | 2 | 766.2 | GGB | 765.201 | 777.961 | 770.696 | 264.65 | GGB | 10839.1 | GGB | 9.79 | GGB | 1017.56 | GGB | 60.92 | GGB | 173802.75 | GGB | 142734.33 | GGB | 0 | 0 | 2931 | 3600 | 2915.87 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243275.42 | GGB | 243278.26 | 2915.87 | 2647.7723 |  |  |  | 1 | 1 |  |  |  |  | 142734.33 | 2647.7723 | 142734.33 | 2647.7723 | 9.5872 | [5 empty] | 115.6097 | 2647.7723 |  | 104.98
28.05.2008 17:00 | 3600 | 2 | 766.46 | GGB | 767.766 | 779.203 | 773.26 | 263.74 | GGB | 10824.8 | GGB | 9.79 | GGB | 1017.13 | GGB | 61.17 | GGB | 172821.25 | GGB | 141762.57 | GGB | 0 | 0 | 2904 | 3600 | 2888.09 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243314.84 | GGB | 243317.68 | 2888.09 | 2665.9223 |  |  |  | 0 | 1 | [14 empty] | 113.7286 | 2665.9223 |  | 104.98
28.05.2008 18:00 | 3600 | 2 | 766.74 | GGB | 766.3 | 778.172 | 771.795 | 261.99 | GGB | 10827.6 | GGB | 9.8 | GGB | 1016.92 | GGB | 62.22 | GGB | 170538.05 | GGB | 139424.79 | GGB | 0 | 0 | 2894 | 3600 | 2877.97 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243354.26 | GGB | 243357.1 | 2877.97 | 2710.6227 |  |  |  | 1 | 1 |  |  |  |  | 139424.79 | 2710.6227 | 139424.79 | 2710.6227 | 9.5872 | [5 empty] | 111.4612 | 2710.6227 |  | 104.98
28.05.2008 19:00 | 3600 | 2 | 766.48 | GGB | 765.201 | 777.07 | 770.696 | 261.67 | GGB | 10803.7 | GGB | 9.79 | GGB | 1017.25 | GGB | 62.22 | GGB | 170468.73 | GGB | 139411.2 | GGB | 0 | 0 | 2901 | 3600 | 2885.57 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243393.68 | GGB | 243396.52 | 2885.57 | 2710.8869 |  |  |  | 1 | 1 |  |  |  |  | 139411.2 | 2710.8869 | 139411.2 | 2710.8869 | 9.5872 | [5 empty] | 111.7447 | 2710.8869 |  | 104.98
28.05.2008 20:00 | 3600 | 2 | 766.3 | GGB | 764.102 | 775.992 | 769.597 | 261.35 | GGB | 10807.4 | GGB | 9.79 | GGB | 1017.35 | GGB | 62.37 | GGB | 169689.69 | GGB | 138726.02 | GGB | 0 | 0 | 2915 | 3600 | 2898.99 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243433.09 | GGB | 243435.94 | 2898.99 | 2724.2762 |  |  |  | 1 | 1 |  |  |  |  | 138726.02 | 2724.2762 | 138726.02 | 2724.2762 | 9.5872 | [5 empty] | 111.7126 | 2724.2762 |  | 104.98
28.05.2008 21:00 | 3600 | 2 | 765.77 | GGB | 764.102 | 775.969 | 769.597 | 262.18 | GGB | 10814.5 | GGB | 9.78 | GGB | 1017.97 | GGB | 62.17 | GGB | 170428.01 | GGB | 139498.46 | GGB | 0 | 0 | 2939 | 3600 | 2923.15 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243472.51 | GGB | 243475.36 | 2923.15 | 2709.1912 |  |  |  | 1 | 1 |  |  |  |  | 139498.46 | 2709.1912 | 139498.46 | 2709.1912 | 9.5872 | [5 empty] | 113.2708 | 2709.1912 |  | 104.98
28.05.2008 22:00 | 3600 | 2 | 765.03 | GGB | 764.102 | 775.945 | 768.498 | 262.94 | GGB | 10853.3 | GGB | 9.78 | GGB | 1018.4 | GGB | 61.99 | GGB | 170885.75 | GGB | 140004.09 | GGB | 0 | 0 | 2983 | 3600 | 2967.74 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243511.93 | GGB | 243514.78 | 2967.74 | 2699.4069 |  |  |  | 1 | 1 |  |  |  |  | 140004.09 | 2699.4069 | 140004.09 | 2699.4069 | 9.5872 | [5 empty] | 115.4155 | 2699.4069 |  | 104.98
28.05.2008 23:00 | 3600 | 2 | 764.53 | GGB | 764.102 | 775.805 | 768.498 | 264.23 | GGB | 10891.3 | GGB | 9.78 | GGB | 1019.52 | GGB | 61.39 | GGB | 171969.59 | GGB | 141300.01 | GGB | 0 | 0 | 3041 | 3600 | 3025.49 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243551.35 | GGB | 243554.2 | 3025.49 | 2674.6495 |  |  |  | 1 | 1 |  |  |  |  | 141300.01 | 2674.6495 | 141300.01 | 2674.6495 | 9.5872 | [5 empty] | 118.7505 | 2674.6495 |  | 104.98
28.05.2008 24:00 | 3600 | 2 | 763.85 | GGB | 763.37 | 774.75 | 768.132 | 265.36 | GGB | 10916.6 | GGB | 9.77 | GGB | 1020.24 | GGB | 60.75 | GGB | 174026.12 | GGB | 143368.69 | GGB | 0 | 0 | 3078 | 3600 | 3061.84 | GGB | 100 | GGB | 39.42 | GGB | 39.42 | GGB | 243590.77 | GGB | 243593.62 | 3061.84 | 2636.0567 |  |  |  | 0 | 1 | [14 empty] | 121.9367 | 2636.0567 |  | 104.98
29.05.2008 01:00 | 3600 | 2 | 763.9 | GGB | 762.271 | 773.555 | 767.033 | 267.32 | GGB | 10992.4 | GGB | 9.78 | GGB | 1020.65 | GGB | 60.52 | GGB | 174631.3 | GGB | 144023.29 | GGB | 0 | 0 | 3125 | 3600 | 3109.36 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243628.81 | GGB | 243631.67 | 3109.36 | 2624.0756 |  |  |  | 0 | 1 | [14 empty] | 124.3945 | 2624.0756 |  | 104.98
29.05.2008 02:00 | 3600 | 2 | 762.75 | GGB | 762.271 | 773.602 | 767.033 | 270.06 | GGB | 11026.6 | GGB | 9.77 | GGB | 1021.49 | GGB | 60.04 | GGB | 177476.78 | GGB | 146699.88 | GGB | 0 | 0 | 3193 | 3600 | 3177.04 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243666.86 | GGB | 243669.72 | 3177.04 | 2576.1984 |  |  |  | 0 | 1 | [14 empty] | 129.4643 | 2576.1984 |  | 104.98
29.05.2008 03:00 | 3600 | 2 | 762.35 | GGB | 762.271 | 773.555 | 767.033 | 271.77 | GGB | 11140.2 | GGB | 9.77 | GGB | 1021.79 | GGB | 60.02 | GGB | 178591.42 | GGB | 147674.9 | GGB | 0 | 0 | 3288 | 3600 | 3271.8 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243704.91 | GGB | 243707.77 | 3271.8 | 2559.1891 |  |  |  | 0 | 1 | [14 empty] | 134.2119 | 2559.1891 |  | 104.98
29.05.2008 04:00 | 3600 | 2 | 762.11 | GGB | 761.172 | 772.57 | 765.934 | 274.81 | GGB | 11160.4 | GGB | 9.77 | GGB | 1022.33 | GGB | 58.9 | GGB | 182620.86 | GGB | 151596.72 | GGB | 0 | 0 | 3309 | 3600 | 3292.95 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243742.96 | GGB | 243745.82 | 3292.95 | 2492.9827 |  |  |  | 0 | 1 | [14 empty] | 138.6668 | 2492.9827 |  | 104.98
29.05.2008 05:00 | 3600 | 2 | 762.42 | GGB | 761.172 | 772.406 | 765.934 | 274.43 | GGB | 11253.6 | GGB | 9.79 | GGB | 1022.5 | GGB | 59.02 | GGB | 181918.84 | GGB | 150982.98 | GGB | 0 | 0 | 3338 | 3600 | 3322.2 | GNB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243781 | GGB | 243783.87 | 3322.2 | 2503.1166 |  |  |  | 0 | 1 | [14 empty] | 139.3321 | 2503.1166 |  | 104.98
29.05.2008 06:00 | 3600 | 2 | 761.49 | GGB | 762.271 | 773.508 | 765.934 | 275.25 | GGB | 11284.4 | GGB | 9.78 | GGB | 1022.7 | GGB | 58.8 | GGB | 183160.02 | GGB | 152143.65 | GGB | 0 | 0 | 3399 | 3600 | 3383.44 | GNB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243819.05 | GGB | 243821.92 | 3383.44 | 2484.0209 |  |  |  | 0 | 1 | [14 empty] | 142.9914 | 2484.0209 |  | 104.98
29.05.2008 07:00 | 3600 | 2 | 763.49 | GGB | 764.469 | 775.547 | 768.498 | 274.33 | GGB | 11265.2 | GGB | 9.81 | GGB | 1022.79 | GGB | 58.68 | GGB | 182539.43 | GGB | 151699.09 | GGB | 0 | 0 | 3296 | 3600 | 3280.1 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243857.1 | GGB | 243859.97 | 3280.1 | 2491.3004 |  |  |  | 1 | 1 |  |  |  |  | 151699.09 | 2491.3004 | 151699.09 | 2491.3004 | 9.9324 | [5 empty] | 138.2189 | 2491.3004 |  | 104.98
29.05.2008 08:00 | 3600 | 2 | 763.77 | GGB | 762.271 | 773.32 | 767.033 | 271.24 | GGB | 11177.1 | GGB | 9.81 | GGB | 1022.57 | GGB | 59.84 | GGB | 178596.92 | GGB | 147870.77 | GGB | 0 | 0 | 3257 | 3600 | 3240.91 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243895.15 | GGB | 243898.02 | 3240.91 | 2555.7992 |  |  |  | 0 | 1 | [14 empty] | 133.1211 | 2555.7992 |  | 104.98
29.05.2008 09:00 | 3600 | 2 | 764.97 | GGB | 764.469 | 776.719 | 769.597 | 269.42 | GGB | 11043.6 | GGB | 9.82 | GGB | 1022.26 | GGB | 60.15 | GGB | 176749.45 | GGB | 146162.46 | GGB | 0 | 0 | 3116 | 3600 | 3099.89 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243933.19 | GGB | 243936.07 | 3099.89 | 2585.6708 |  |  |  | 1 | 1 |  |  |  |  | 146162.46 | 2585.6708 | 146162.46 | 2585.6708 | 9.9324 | [5 empty] | 125.8577 | 2585.6708 |  | 104.98
29.05.2008 10:00 | 3600 | 2 | 765.15 | GGB | 764.469 | 774.563 | 769.597 | 265.43 | GGB | 10987.3 | GGB | 9.81 | GGB | 1021.69 | GGB | 61.55 | GGB | 172669.4 | GGB | 142108.97 | GGB | 0 | 0 | 3062 | 3600 | 3046.27 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 243971.24 | GGB | 243974.12 | 3046.27 | 2659.424 |  |  |  | 1 | 1 |  |  |  |  | 142108.97 | 2659.424 | 142108.97 | 2659.424 | 9.9324 | [5 empty] | 120.2506 | 2659.424 |  | 104.98
29.05.2008 11:00 | 3600 | 2 | 764.29 | GGB | 763.37 | 774.82 | 768.132 | 264.81 | GGB | 10911.3 | GGB | 9.79 | GGB | 1021.19 | GGB | 61.76 | GGB | 172512.05 | GGB | 141825.38 | GGB | 0 | 0 | 3058 | 3600 | 3042.02 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244009.29 | GGB | 244012.17 | 3042.02 | 2664.7417 |  |  |  | 0 | 1 | [14 empty] | 119.8432 | 2664.7417 |  | 104.98
29.05.2008 12:00 | 3600 | 2 | 765.32 | GGB | 764.469 | 775.758 | 769.597 | 263.75 | GGB | 10893.1 | GGB | 9.8 | GGB | 1020.46 | GGB | 61.98 | GGB | 171464.53 | GGB | 140769.24 | GGB | 0 | 0 | 2993 | 3600 | 2977.77 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244047.34 | GGB | 244050.22 | 2977.77 | 2684.7343 |  |  |  | 1 | 1 |  |  |  |  | 140769.24 | 2684.7343 | 140769.24 | 2684.7343 | 9.9324 | [5 empty] | 116.4384 | 2684.7343 |  | 104.98
29.05.2008 13:00 | 3600 | 2 | 765.14 | GGB | 765.934 | 778.148 | 771.795 | 263.39 | GGB | 10814.9 | GGB | 9.79 | GGB | 1019.7 | GGB | 62.19 | GGB | 171560.26 | GGB | 140652.15 | GGB | 0 | 0 | 2960 | 3600 | 2944.05 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244085.39 | GGB | 244088.27 | 2944.05 | 2686.9692 |  |  |  | 1 | 1 |  |  |  |  | 140652.15 | 2686.9692 | 140652.15 | 2686.9692 | 9.9324 | [5 empty] | 115.0242 | 2686.9692 |  | 104.98
29.05.2008 14:00 | 3600 | 2 | 766.31 | GGB | 767.033 | 777.961 | 771.795 | 262.25 | GGB | 10793.5 | GGB | 9.8 | GGB | 1018.91 | GGB | 62.38 | GGB | 170710.8 | GGB | 139771.06 | GGB | 0 | 0 | 2876 | 3600 | 2860.54 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244123.43 | GGB | 244126.32 | 2860.54 | 2703.9074 |  |  |  | 1 | 1 |  |  |  |  | 139771.06 | 2703.9074 | 139771.06 | 2703.9074 | 9.9324 | [5 empty] | 111.0613 | 2703.9074 |  | 104.98
29.05.2008 15:00 | 3600 | 2 | 765.97 | GGB | 765.934 | 777.961 | 770.696 | 260.52 | GGB | 10764.1 | GGB | 9.79 | GGB | 1017.58 | GGB | 63.08 | GGB | 168648.77 | GGB | 137613.9 | GGB | 0 | 0 | 2889 | 3600 | 2873.72 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244161.48 | GGB | 244164.37 | 2873.72 | 2746.2923 |  |  |  | 1 | 1 |  |  |  |  | 137613.9 | 2746.2923 | 137613.9 | 2746.2923 | 9.9324 | [5 empty] | 109.8511 | 2746.2923 |  | 104.98
29.05.2008 16:00 | 3600 | 2 | 766.06 | GGB | 765.934 | 778.008 | 771.795 | 260.72 | GGB | 10698.7 | GGB | 9.79 | GGB | 1017.01 | GGB | 62.93 | GGB | 169261.66 | GGB | 138098.67 | GGB | 0 | 0 | 2858 | 3600 | 2841.98 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244199.53 | GGB | 244202.42 | 2841.98 | 2736.652 |  |  |  | 1 | 1 |  |  |  |  | 138098.67 | 2736.652 | 138098.67 | 2736.652 | 9.9324 | [5 empty] | 109.0205 | 2736.652 |  | 104.98
29.05.2008 17:00 | 3600 | 2 | 766.59 | GGB | 765.934 | 778.055 | 771.795 | 260.06 | GGB | 10671.9 | GGB | 9.79 | GGB | 1016.13 | GGB | 62.92 | GGB | 168769.8 | GGB | 137582.6 | GGB | 0 | 0 | 2823 | 3600 | 2807.5 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244237.58 | GGB | 244240.47 | 2807.5 | 2746.9171 |  |  |  | 1 | 1 |  |  |  |  | 137582.6 | 2746.9171 | 137582.6 | 2746.9171 | 9.9324 | [5 empty] | 107.2953 | 2746.9171 |  | 104.98
29.05.2008 18:00 | 3600 | 2 | 766.69 | GGB | 765.934 | 777.211 | 771.795 | 258.29 | GGB | 10670.9 | GGB | 9.79 | GGB | 1015.38 | GGB | 63.72 | GGB | 166317.15 | GGB | 135161.89 | GGB | 0 | 0 | 2820 | 3600 | 2804.82 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244275.62 | GGB | 244278.52 | 2804.82 | 2796.1136 |  |  |  | 1 | 1 |  |  |  |  | 135161.89 | 2796.1136 | 135161.89 | 2796.1136 | 9.9324 | [5 empty] | 105.3069 | 2796.1136 |  | 104.98
29.05.2008 19:00 | 3600 | 2 | 766.3 | GGB | 765.934 | 777.164 | 770.696 | 258.98 | GGB | 10630.5 | GGB | 9.78 | GGB | 1014.97 | GGB | 63.62 | GGB | 167163.31 | GGB | 135832.98 | GGB | 0 | 0 | 2823 | 3600 | 2807.8 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244313.67 | GGB | 244316.57 | 2807.8 | 2782.2993 |  |  |  | 1 | 1 |  |  |  |  | 135832.98 | 2782.2993 | 135832.98 | 2782.2993 | 9.9324 | [5 empty] | 105.9422 | 2782.2993 |  | 104.98
29.05.2008 20:00 | 3600 | 2 | 766.38 | GGB | 765.934 | 777.164 | 770.696 | 260.4 | GGB | 10625.1 | GGB | 9.78 | GGB | 1014.62 | GGB | 62.89 | GGB | 168583.85 | GGB | 137236.08 | GGB | 0 | 0 | 2812 | 3600 | 2796.45 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244351.72 | GGB | 244354.62 | 2796.45 | 2753.8531 |  |  |  | 1 | 1 |  |  |  |  | 137236.08 | 2753.8531 | 137236.08 | 2753.8531 | 9.9324 | [5 empty] | 106.6038 | 2753.8531 |  | 104.98
29.05.2008 21:00 | 3600 | 2 | 766.04 | GGB | 765.934 | 777.445 | 770.696 | 259.09 | GGB | 10681.8 | GGB | 9.79 | GGB | 1014.47 | GGB | 63.31 | GGB | 166882.73 | GGB | 135665.09 | GGB | 0 | 0 | 2835 | 3600 | 2819.96 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244389.77 | GGB | 244392.67 | 2819.96 | 2785.7424 |  |  |  | 1 | 1 |  |  |  |  | 135665.09 | 2785.7424 | 135665.09 | 2785.7424 | 9.9324 | [5 empty] | 106.2695 | 2785.7424 |  | 104.98
29.05.2008 22:00 | 3600 | 2 | 764.23 | GGB | 763.37 | 775.266 | 768.132 | 261.27 | GGB | 10720.2 | GGB | 9.76 | GGB | 1014.83 | GGB | 62.98 | GGB | 168767.6 | GGB | 137381.01 | GGB | 0 | 0 | 2954 | 3600 | 2938.01 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244427.81 | GGB | 244430.72 | 2938.01 | 2750.9479 |  |  |  | 0 | 1 | [14 empty] | 112.1186 | 2750.9479 |  | 104.98
29.05.2008 23:00 | 3600 | 2 | 763.16 | GGB | 762.271 | 773.789 | 768.132 | 265.6 | GGB | 10806.6 | GGB | 9.76 | GGB | 1016.02 | GGB | 61.71 | GGB | 173493.55 | GGB | 141930.79 | GGB | 0 | 0 | 3057 | 3600 | 3041.7 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244465.86 | GGB | 244468.77 | 3041.7 | 2662.7626 |  |  |  | 0 | 1 | [14 empty] | 119.9197 | 2662.7626 |  | 104.98
29.05.2008 24:00 | 3600 | 2 | 763.39 | GGB | 762.271 | 773.93 | 767.033 | 266.91 | GGB | 10935.3 | GGB | 9.78 | GGB | 1016.59 | GGB | 61.5 | GGB | 173541.97 | GGB | 142135.39 | GGB | 0 | 0 | 3126 | 3600 | 3110.18 | GGB | 100 | GGB | 38.05 | GGB | 38.05 | GGB | 244503.91 | GGB | 244506.82 | 3110.18 | 2658.9296 |  |  |  | 0 | 1 | [14 empty] | 122.7963 | 2658.9296 |  | 104.98
30.05.2008 01:00 | 3600 | 2 | 761.49 | GGB | 760.806 | 772.289 | 764.469 | 269.54 | GGB | 10966.8 | GGB | 9.76 | GGB | 1017.45 | GGB | 61.09 | GGB | 176204.79 | GGB | 144616.14 | GGB | 0 | 0 | 3236 | 3600 | 3219.94 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244542.47 | GGB | 244545.38 | 3219.94 | 2613.3183 |  |  |  | 0 | 1 | [14 empty] | 129.3487 | 2613.3183 |  | 104.98
30.05.2008 02:00 | 3600 | 2 | 762.5 | GGB | 762.271 | 773.32 | 767.033 | 271.74 | GGB | 11037.6 | GGB | 9.79 | GGB | 1017.99 | GGB | 60.22 | GGB | 178841.2 | GGB | 147244.44 | GGB | 0 | 0 | 3216 | 3600 | 3200.58 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244581.03 | GGB | 244583.94 | 3200.58 | 2566.6708 |  |  |  | 0 | 1 | [14 empty] | 130.9077 | 2566.6708 |  | 104.98
30.05.2008 03:00 | 3600 | 2 | 761.51 | GGB | 762.271 | 773.203 | 765.934 | 271.4 | GGB | 11110.7 | GGB | 9.78 | GGB | 1017.97 | GGB | 60.34 | GGB | 178123.78 | GGB | 146597.64 | GGB | 0 | 0 | 3307 | 3600 | 3291.32 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244619.58 | GGB | 244622.5 | 3291.32 | 2577.9951 |  |  |  | 0 | 1 | [14 empty] | 134.0277 | 2577.9951 |  | 104.98
30.05.2008 04:00 | 3600 | 2 | 760.98 | GGB | 759.707 | 770.484 | 764.469 | 272.55 | GGB | 11126.2 | GGB | 9.77 | GGB | 1018.32 | GGB | 59.75 | GGB | 179876.61 | GGB | 148351.97 | GGB | 0 | 0 | 3353 | 3600 | 3336.78 | GNB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244658.14 | GGB | 244661.06 | 3336.78 | 2547.5091 |  |  |  | 0 | 1 | [14 empty] | 137.505 | 2547.5091 |  | 104.98
30.05.2008 05:00 | 3600 | 2 | 761.1 | GGB | 759.707 | 770.32 | 764.469 | 273.6 | GGB | 11182.6 | GGB | 9.78 | GGB | 1018.47 | GGB | 59.18 | GGB | 181330.16 | GGB | 149831.37 | GGB | 0 | 0 | 3372 | 3600 | 3356.08 | GNB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244696.7 | GGB | 244699.62 | 3356.08 | 2522.3556 |  |  |  | 0 | 1 | [14 empty] | 139.6795 | 2522.3556 |  | 104.98
30.05.2008 06:00 | 3600 | 2 | 761.19 | GGB | 761.172 | 771.492 | 765.934 | 275.27 | GGB | 11222.6 | GGB | 9.79 | GGB | 1018.97 | GGB | 58.39 | GGB | 183999.58 | GGB | 152472.56 | GGB | 0 | 0 | 3370 | 3600 | 3353.62 | GNB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244735.25 | GGB | 244738.18 | 3353.62 | 2478.6624 |  |  |  | 0 | 1 | [14 empty] | 142.0375 | 2478.6624 |  | 104.98
30.05.2008 07:00 | 3600 | 2 | 762.1 | GGB | 763.37 | 773.695 | 767.033 | 272.7 | GGB | 11259.6 | GGB | 9.81 | GGB | 1018.99 | GGB | 59.15 | GGB | 180915.33 | GGB | 149576.06 | GGB | 0 | 0 | 3355 | 3600 | 3339.37 | GNB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244773.81 | GGB | 244776.74 | 3339.37 | 2526.661 |  |  |  | 0 | 1 | [14 empty] | 138.7472 | 2526.661 |  | 104.98
30.05.2008 08:00 | 3600 | 2 | 763.87 | GGB | 764.835 | 777.164 | 770.696 | 268.89 | GGB | 11160 | GGB | 9.84 | GGB | 1018.59 | GGB | 60.22 | GGB | 176406.15 | GGB | 145322.87 | GGB | 0 | 0 | 3219 | 3600 | 3202.71 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244812.37 | GGB | 244815.3 | 3202.71 | 2600.6093 |  |  |  | 1 | 1 |  |  |  |  | 145322.87 | 2600.6093 | 145322.87 | 2600.6093 | 9.801 | [5 empty] | 129.2853 | 2600.6093 |  | 104.98
30.05.2008 09:00 | 3600 | 2 | 764.63 | GGB | 763.37 | 774.938 | 768.864 | 263.86 | GGB | 10950.7 | GGB | 9.82 | GGB | 1018.15 | GGB | 61.52 | GGB | 171687.9 | GGB | 140825.2 | GGB | 0 | 0 | 3090 | 3208 | 3073.88 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244850.93 | GGB | 244853.86 | 2813.5906 | 2683.6674 |  |  |  | 0 | 1 | [10 empty] | 3090 | -261 | 2829 | 2813.5906 | 110.0624 | 2683.6674 |  | 104.98
30.05.2008 10:00 | 3600 | 2 | 765.16 | GGB | 764.835 | 777.164 | 770.33 | 261.87 | GGB | 10838 | GGB | 9.8 | GGB | 1017.2 | GGB | 62.28 | GGB | 169667.68 | GGB | 138723.51 | GGB | 0 | 0 | 3012 | 3600 | 2996.73 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244889.48 | GGB | 244892.42 | 2735.6543 | 2724.3255 |  |  |  | 1 | 1 |  |  |  |  | 138723.51 | 2724.3255 | 138723.51 | 2724.3255 | 9.801 |  | 3012 | -261 | 2751 | 2735.6543 | 105.4165 | 2724.3255 |  | 104.98
30.05.2008 11:00 | 3600 | 2 | 765.56 | GGB | 765.934 | 777.047 | 769.963 | 260.09 | GGB | 10772.4 | GGB | 9.8 | GGB | 1016.41 | GGB | 62.99 | GGB | 168308.76 | GGB | 137213.55 | GGB | 0 | 0 | 2940 | 3600 | 2923.96 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244928.04 | GGB | 244930.98 | 2663.7131 | 2663.7131 |  |  |  | 1 | 1 |  |  |  |  | 137213.55 | 2663.7131 | 137213.55 | 2663.7131 | 9.4787 |  | 2940 | -261 | 2679 | 2663.7131 | 101.5271 |  |  | #VALUE!
30.05.2008 12:00 | 3600 | 2 | 765.88 | GGB | 765.934 | 777.469 | 770.33 | 258.51 | GGB | 10697.4 | GGB | 9.8 | GGB | 1014.96 | GGB | 63.54 | GGB | 166480 | GGB | 135311.43 | GGB | 0 | 0 | 2888 | 3600 | 2872.79 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 244966.6 | GGB | 244969.54 | 2611.7555 | 2611.7555 |  |  |  | 1 | 1 |  |  |  |  | 135311.43 | 2611.7555 | 135311.43 | 2611.7555 | 9.1649 |  | 2888 | -261 | 2627 | 2611.7555 | 98.1668 |  |  | #VALUE!
30.05.2008 13:00 | 3600 | 2 | 766.44 | GGB | 764.835 | 777.609 | 770.33 | 258.78 | GGB | 10617 | GGB | 9.79 | GGB | 1014.3 | GGB | 63.41 | GGB | 167271.14 | GGB | 135916.29 | GGB | 0 | 0 | 2842 | 3600 | 2826.09 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245005.16 | GGB | 245008.1 | 2565.7931 | 2565.7931 |  |  |  | 1 | 1 |  |  |  |  | 135916.29 | 2565.7931 | 135916.29 | 2565.7931 | 9.0439 |  | 2842 | -261 | 2581 | 2565.7931 | 96.8703 |  |  | #VALUE!
30.05.2008 14:00 | 3600 | 2 | 767.06 | GGB | 765.934 | 777.445 | 771.429 | 257.23 | GGB | 10606.9 | GGB | 9.79 | GGB | 1013.37 | GGB | 63.83 | GGB | 165672.35 | GGB | 134327.26 | GGB | 0 | 0 | 2811 | 3600 | 2795.26 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245043.71 | GGB | 245046.66 | 2534.8184 | 2534.8184 |  |  |  | 1 | 1 |  |  |  |  | 134327.26 | 2534.8184 | 134327.26 | 2534.8184 | 8.8303 |  | 2811 | -261 | 2550 | 2534.8184 | 94.582 |  |  | #VALUE!
30.05.2008 15:00 | 3600 | 2 | 766.88 | GGB | 765.934 | 777.422 | 771.429 | 257.46 | GGB | 10557.4 | GGB | 9.79 | GGB | 1012.53 | GGB | 63.76 | GGB | 166025.56 | GGB | 134527.63 | GGB | 0 | 0 | 2793 | 3600 | 2777.11 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245082.27 | GGB | 245085.22 | 2516.8331 | 2516.8331 |  |  |  | 1 | 1 |  |  |  |  | 134527.63 | 2516.8331 | 134527.63 | 2516.8331 | 8.7807 |  | 2793 | -261 | 2532 | 2516.8331 | 94.051 |  |  | #VALUE!
30.05.2008 16:00 | 3600 | 2 | 767.17 | GGB | 765.934 | 777.703 | 771.795 | 255.23 | GGB | 10547.7 | GGB | 9.79 | GGB | 1011.82 | GGB | 64.7 | GGB | 163267.02 | GGB | 131834.29 | GGB | 0 | 0 | 2785 | 3600 | 2769.14 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245120.83 | GGB | 245123.78 | 2508.8396 | 2508.8396 |  |  |  | 1 | 1 |  |  |  |  | 131834.29 | 2508.8396 | 131834.29 | 2508.8396 | 8.5776 |  | 2785 | -261 | 2524 | 2508.8396 | 91.8753 |  |  | #VALUE!
30.05.2008 17:00 | 3600 | 2 | 767.07 | GGB | 765.934 | 777.961 | 771.795 | 254.81 | GGB | 10516.5 | GGB | 9.78 | GGB | 1011.14 | GGB | 64.91 | GGB | 162865.39 | GGB | 131337.77 | GGB | 0 | 0 | 2773 | 3600 | 2758.02 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245159.39 | GGB | 245162.34 | 2496.8494 | 2496.8494 |  |  |  | 1 | 1 |  |  |  |  | 131337.77 | 2496.8494 | 131337.77 | 2496.8494 | 8.5044 |  | 2773 | -261 | 2512 | 2496.8494 | 91.0918 |  |  | #VALUE!
30.05.2008 18:00 | 3600 | 2 | 767.34 | GGB | 767.033 | 779.391 | 772.161 | 254.6 | GGB | 10504 | GGB | 9.79 | GGB | 1010.44 | GGB | 65.13 | GGB | 162443.96 | GGB | 130825.36 | GGB | 0 | 0 | 2761 | 3600 | 2745.44 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245197.94 | GGB | 245200.9 | 2484.8592 | 2484.8592 |  |  |  | 0 | 1 | [10 empty] | 2761 | -261 | 2500 | 2484.8592 | 90.3007 |  |  | #VALUE!
30.05.2008 19:00 | 3600 | 2 | 767.15 | GGB | 765.934 | 778.523 | 771.795 | 254.47 | GGB | 10487.4 | GGB | 9.78 | GGB | 1009.66 | GGB | 65.09 | GGB | 162124.86 | GGB | 130479.77 | GGB | 0 | 0 | 2764 | 3600 | 2748.21 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245236.5 | GGB | 245239.46 | 2487.8567 | 2487.8567 |  |  |  | 1 | 1 |  |  |  |  | 130479.77 | 2487.8567 | 130479.77 | 2487.8567 | 8.4184 |  | 2764 | -261 | 2503 | 2487.8567 | 90.1708 |  |  | #VALUE!
30.05.2008 20:00 | 3600 | 2 | 766.89 | GGB | 764.469 | 776.367 | 769.597 | 254.33 | GGB | 10484.4 | GGB | 9.78 | GGB | 1009.27 | GGB | 65.09 | GGB | 162004.93 | GGB | 130334.37 | GGB | 0 | 0 | 2766 | 3600 | 2750.28 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245275.06 | GGB | 245278.02 | 2489.8551 | 2489.8551 |  |  |  | 1 | 1 |  |  |  |  | 130334.37 | 2489.8551 | 130334.37 | 2489.8551 | 8.4158 |  | 2766 | -261 | 2505 | 2489.8551 | 90.1427 |  |  | #VALUE!
30.05.2008 21:00 | 3600 | 2 | 766.4 | GGB | 764.835 | 776.344 | 769.597 | 255.83 | GGB | 10521.6 | GGB | 9.78 | GGB | 1009.36 | GGB | 64.37 | GGB | 163247.21 | GGB | 131624.99 | GGB | 0 | 0 | 2796 | 3600 | 2780.5 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245313.62 | GGB | 245316.58 | 2519.8306 | 2519.8306 |  |  |  | 1 | 1 |  |  |  |  | 131624.99 | 2519.8306 | 131624.99 | 2519.8306 | 8.6015 |  | 2796 | -261 | 2535 | 2519.8306 | 92.1313 |  |  | #VALUE!
30.05.2008 22:00 | 3600 | 2 | 764.96 | GGB | 762.271 | 775.313 | 767.033 | 258.33 | GGB | 10604.1 | GGB | 9.76 | GGB | 1009.95 | GGB | 64.04 | GGB | 165264.13 | GGB | 133461.47 | GGB | 0 | 0 | 2905 | 3600 | 2889.3 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245352.17 | GGB | 245355.14 | 2628.7416 | 2628.7416 |  |  |  | 0 | 1 | [10 empty] | 2905 | -261 | 2644 | 2628.7416 | 97.4544 |  |  | #VALUE!
30.05.2008 23:00 | 3600 | 2 | 764.34 | GGB | 763.37 | 776.156 | 768.498 | 261.01 | GGB | 10703.2 | GGB | 9.77 | GGB | 1010.73 | GGB | 63.46 | GGB | 167635.36 | GGB | 135713.19 | GGB | 0 | 0 | 2993 | 3600 | 2977.48 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245390.73 | GGB | 245393.7 | 2716.6698 | 2716.6698 |  |  |  | 0 | 1 | [10 empty] | 2993 | -261 | 2732 | 2716.6698 | 102.4133 |  |  | #VALUE!
30.05.2008 24:00 | 3600 | 2 | 763.18 | GGB | 760.806 | 772.219 | 765.934 | 262.72 | GGB | 10780.9 | GGB | 9.76 | GGB | 1011.64 | GGB | 62.75 | GGB | 169757.91 | GGB | 137844.81 | GGB | 0 | 0 | 3092 | 3600 | 3076.02 | GGB | 100 | GGB | 38.56 | GGB | 38.56 | GGB | 245429.29 | GGB | 245432.26 | 2815.589 | 2741.6919 |  |  |  | 0 | 1 | [10 empty] | 3092 | -261 | 2831 | 2815.589 | 107.8095 | 2741.6919 |  | 104.98
31.05.2008 01:00 | 3600 | 2 | 764.23 | GGB | 764.469 | 775.242 | 769.597 | 265.3 | GGB | 10799.8 | GGB | 9.78 | GGB | 1012.73 | GGB | 62.03 | GGB | 172296.39 | GGB | 140357.84 | GGB | 0 | 0 | 3061 | 3600 | 3045.21 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245468.37 | GGB | 245471.34 | 2784.6143 | 2692.6034 |  |  |  | 1 | 1 |  |  |  |  | 140357.84 | 2692.6034 | 140357.84 | 2692.6034 | 9.6706 |  | 3061 | -261 | 2800 | 2784.6143 | 108.5673 | 2692.6034 |  | 104.98
31.05.2008 02:00 | 3600 | 2 | 764.63 | GGB | 763.37 | 774.422 | 768.498 | 264.56 | GGB | 10831.5 | GGB | 9.79 | GGB | 1012.91 | GGB | 61.59 | GGB | 171896.96 | GGB | 140241.7 | GGB | 0 | 0 | 3032 | 3600 | 3016.76 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245507.45 | GGB | 245510.42 | 2755.638 | 2694.8333 |  |  |  | 0 | 1 | [10 empty] | 3032 | -261 | 2771 | 2755.638 | 107.3487 | 2694.8333 |  | 104.98
31.05.2008 03:00 | 3600 | 2 | 763.22 | GGB | 761.172 | 772.031 | 765.934 | 264.82 | GGB | 10874.4 | GGB | 9.77 | GGB | 1012.92 | GGB | 61.52 | GGB | 172353.6 | GGB | 140645.56 | GGB | 0 | 0 | 3110 | 3600 | 3093.97 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245546.53 | GGB | 245549.5 | 2833.5743 | 2687.0951 |  |  |  | 0 | 1 | [10 empty] | 3110 | -261 | 2849 | 2833.5743 | 110.7027 | 2687.0951 |  | 104.98
31.05.2008 04:00 | 3600 | 2 | 762.65 | GGB | 761.172 | 773.18 | 765.934 | 267.68 | GGB | 10932.2 | GGB | 9.77 | GGB | 1013.32 | GGB | 60.9 | GGB | 175228.79 | GGB | 143313.48 | GGB | 0 | 0 | 3179 | 3600 | 3163.53 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245585.62 | GGB | 245588.58 | 2902.518 | 2637.0722 |  |  |  | 0 | 1 | [10 empty] | 3179 | -261 | 2918 | 2902.518 | 115.5472 | 2637.0722 |  | 104.98
31.05.2008 05:00 | 3600 | 2 | 761.92 | GGB | 762.271 | 773.25 | 767.033 | 268.98 | GGB | 10980.7 | GGB | 9.77 | GGB | 1013.68 | GGB | 60.51 | GGB | 176585.5 | GGB | 144643.18 | GGB | 0 | 0 | 3246 | 3600 | 3230.3 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245624.7 | GGB | 245627.66 | 2969.4633 | 2612.8297 |  |  |  | 0 | 1 | [10 empty] | 3246 | -261 | 2985 | 2969.4633 | 119.3091 | 2612.8297 |  | 104.98
31.05.2008 06:00 | 3600 | 2 | 762.57 | GGB | 763.37 | 774.164 | 767.033 | 269.18 | GGB | 11050.3 | GGB | 9.79 | GGB | 1013.77 | GGB | 60.53 | GGB | 176322.52 | GGB | 144431.36 | GGB | 0 | 0 | 3253 | 3600 | 3237.57 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245663.78 | GGB | 245666.74 | 2976.4576 | 2616.6616 |  |  |  | 0 | 1 | [10 empty] | 3253 | -261 | 2992 | 2976.4576 | 119.4149 | 2616.6616 |  | 104.98
31.05.2008 07:00 | 3600 | 2 | 763.49 | GGB | 763.37 | 774.422 | 768.132 | 268.97 | GGB | 10981.4 | GGB | 9.8 | GGB | 1014.24 | GGB | 60.31 | GGB | 176791.27 | GGB | 144981.17 | GGB | 0 | 0 | 3171 | 3600 | 3155.45 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245702.86 | GGB | 245705.82 | 2894.5245 | 2606.7385 |  |  |  | 0 | 1 | [10 empty] | 3171 | -261 | 2910 | 2894.5245 | 116.5699 | 2606.7385 |  | 104.98
31.05.2008 08:00 | 3600 | 2 | 763.22 | GGB | 764.835 | 775.711 | 769.597 | 267.87 | GGB | 10981.1 | GGB | 9.8 | GGB | 1014.52 | GGB | 60.4 | GGB | 175532.48 | GGB | 143948.79 | GGB | 0 | 0 | 3169 | 3600 | 3153.45 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245741.94 | GGB | 245744.9 | 2892.5261 | 2625.4337 |  |  |  | 1 | 1 |  |  |  |  | 143948.79 | 2625.4337 | 143948.79 | 2625.4337 | 9.6706 |  | 3169 | -261 | 2908 | 2892.5261 | 115.6599 | 2625.4337 |  | 104.98
31.05.2008 09:00 | 3600 | 2 | 763.63 | GGB | 763.37 | 774.492 | 768.132 | 265.97 | GGB | 10961.7 | GGB | 9.8 | GGB | 1014.29 | GGB | 61.3 | GGB | 173058.92 | GGB | 141507.07 | GGB | 0 | 0 | 3164 | 3600 | 3147.92 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245781.03 | GGB | 245783.98 | 2887.5302 | 2670.7358 |  |  |  | 0 | 1 | [10 empty] | 3164 | -261 | 2903 | 2887.5302 | 113.5016 | 2670.7358 |  | 104.98
31.05.2008 10:00 | 3600 | 2 | 764.18 | GGB | 763.37 | 775.336 | 768.498 | 265.29 | GGB | 10882.8 | GGB | 9.8 | GGB | 1014 | GGB | 61.68 | GGB | 172435.03 | GGB | 140795.85 | GGB | 0 | 0 | 3102 | 3600 | 3086.64 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245820.11 | GGB | 245823.06 | 2825.5808 | 2684.2268 |  |  |  | 0 | 1 | [10 empty] | 3102 | -261 | 2841 | 2825.5808 | 110.5083 | 2684.2268 |  | 104.98
31.05.2008 11:00 | 3600 | 2 | 766.19 | GGB | 767.033 | 778.734 | 771.795 | 262.7 | GGB | 10784.1 | GGB | 9.82 | GGB | 1013.19 | GGB | 62.72 | GGB | 169678.68 | GGB | 138005.06 | GGB | 0 | 0 | 2963 | 3600 | 2947.53 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245859.19 | GGB | 245862.14 | 2686.6943 | 2686.6943 |  |  |  | 0 | 1 | [10 empty] | 2963 | -261 | 2702 | 2686.6943 | 102.9937 |  |  | #VALUE!
31.05.2008 12:00 | 3600 | 2 | 766.23 | GGB | 767.033 | 778.313 | 771.795 | 258.79 | GGB | 10657.7 | GGB | 9.8 | GGB | 1011.56 | GGB | 64.2 | GGB | 165479.79 | GGB | 133785.34 | GGB | 0 | 0 | 2887 | 3600 | 2871.46 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245898.27 | GGB | 245901.22 | 2610.7563 | 2610.7563 |  |  |  | 1 | 1 |  |  |  |  | 133785.34 | 2610.7563 | 133785.34 | 2610.7563 | 8.9376 |  | 2887 | -261 | 2626 | 2610.7563 | 97.0225 |  |  | #VALUE!
31.05.2008 13:00 | 3600 | 2 | 766.08 | GGB | 765.934 | 778.406 | 771.795 | 258.78 | GGB | 10557.2 | GGB | 9.79 | GGB | 1011.15 | GGB | 64.08 | GGB | 165688.86 | GGB | 133945.79 | GGB | 0 | 0 | 2862 | 3600 | 2846.32 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245937.35 | GGB | 245940.3 | 2585.7767 | 2585.7767 |  |  |  | 1 | 1 |  |  |  |  | 133945.79 | 2585.7767 | 133945.79 | 2585.7767 | 8.8627 |  | 2862 | -261 | 2601 | 2585.7767 | 96.2094 |  |  | #VALUE!
31.05.2008 14:00 | 3600 | 2 | 767.16 | GGB | 764.835 | 777.422 | 770.696 | 257.15 | GGB | 10518.5 | GGB | 9.8 | GGB | 1010.85 | GGB | 64.57 | GGB | 164015.24 | GGB | 132363.09 | GGB | 0 | 0 | 2782 | 3600 | 2766.25 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 245976.44 | GGB | 245979.38 | 2505.842 | 2505.842 |  |  |  | 1 | 1 |  |  |  |  | 132363.09 | 2505.842 | 132363.09 | 2505.842 | 8.4872 |  | 2782 | -261 | 2521 | 2505.842 | 92.1336 |  |  | #VALUE!
31.05.2008 15:00 | 3600 | 2 | 766.73 | GGB | 765.934 | 777.961 | 770.696 | 255.84 | GGB | 10491.6 | GGB | 9.78 | GGB | 1009.83 | GGB | 65.01 | GGB | 162756.46 | GGB | 131042.01 | GGB | 0 | 0 | 2797 | 3600 | 2781.72 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246015.52 | GGB | 246018.46 | 2520.8298 | 2520.8298 |  |  |  | 1 | 1 |  |  |  |  | 131042.01 | 2520.8298 | 131042.01 | 2520.8298 | 8.4528 |  | 2797 | -261 | 2536 | 2520.8298 | 91.7596 |  |  | #VALUE!
31.05.2008 16:00 | 3600 | 2 | 767.41 | GGB | 765.934 | 778.805 | 772.527 | 257.02 | GGB | 10466.4 | GGB | 9.79 | GGB | 1009.84 | GGB | 64.76 | GGB | 164272.72 | GGB | 132362.2 | GGB | 0 | 0 | 2747 | 3600 | 2731.43 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246054.6 | GGB | 246057.54 | 2470.8706 | 2470.8706 |  |  |  | 0 | 1 | [10 empty] | 2747 | -261 | 2486 | 2470.8706 | 90.8472 |  |  | #VALUE!
31.05.2008 17:00 | 3600 | 2 | 767.79 | GGB | 765.934 | 777.609 | 771.429 | 255.07 | GGB | 10453.4 | GGB | 9.79 | GGB | 1009.09 | GGB | 65.2 | GGB | 162566.1 | GGB | 130717.24 | GGB | 0 | 0 | 2719 | 3600 | 2703.31 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246093.68 | GGB | 246096.62 | 2442.8935 | 2442.8935 |  |  |  | 1 | 1 |  |  |  |  | 130717.24 | 2442.8935 | 130717.24 | 2442.8935 | 8.1711 |  | 2719 | -261 | 2458 | 2442.8935 | 88.7023 |  |  | #VALUE!
31.05.2008 18:00 | 3600 | 2 | 767.24 | GGB | 765.934 | 778.852 | 772.527 | 254.98 | GGB | 10466.3 | GGB | 9.78 | GGB | 1008.69 | GGB | 65.38 | GGB | 162113.86 | GGB | 130236.23 | GGB | 0 | 0 | 2747 | 3600 | 2731.93 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246132.76 | GGB | 246135.7 | 2470.8706 | 2470.8706 |  |  |  | 0 | 1 | [10 empty] | 2747 | -261 | 2486 | 2470.8706 | 89.388 |  |  | #VALUE!
31.05.2008 19:00 | 3600 | 2 | 767.34 | GGB | 765.934 | 778.031 | 771.429 | 256.17 | GGB | 10434.6 | GGB | 9.78 | GGB | 1008.72 | GGB | 65.02 | GGB | 163493.68 | GGB | 131486.38 | GGB | 0 | 0 | 2725 | 3600 | 2709.17 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246171.85 | GGB | 246174.78 | 2448.8886 | 2448.8886 |  |  |  | 1 | 1 |  |  |  |  | 131486.38 | 2448.8886 | 131486.38 | 2448.8886 | 8.2394 |  | 2725 | -261 | 2464 | 2448.8886 | 89.4432 |  |  | #VALUE!
31.05.2008 20:00 | 3600 | 2 | 767.44 | GGB | 765.934 | 778.242 | 771.429 | 255.11 | GGB | 10450.1 | GGB | 9.78 | GGB | 1008.75 | GGB | 65.16 | GGB | 162286.61 | GGB | 130468.08 | GGB | 0 | 0 | 2731 | 3600 | 2715.71 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246210.93 | GGB | 246213.86 | 2454.8837 | 2454.8837 |  |  |  | 1 | 1 |  |  |  |  | 130468.08 | 2454.8837 | 130468.08 | 2454.8837 | 8.1956 |  | 2731 | -261 | 2470 | 2454.8837 | 88.9678 |  |  | #VALUE!
31.05.2008 21:00 | 3600 | 2 | 766.71 | GGB | 764.469 | 777.211 | 770.696 | 255.06 | GGB | 10482.5 | GGB | 9.78 | GGB | 1008.76 | GGB | 65.12 | GGB | 162078.65 | GGB | 130315.54 | GGB | 0 | 0 | 2786 | 3600 | 2770.52 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246250.01 | GGB | 246252.94 | 2509.8388 | 2509.8388 |  |  |  | 1 | 1 |  |  |  |  | 130315.54 | 2509.8388 | 130315.54 | 2509.8388 | 8.3693 |  | 2786 | -261 | 2525 | 2509.8388 | 90.8531 |  |  | #VALUE!
31.05.2008 22:00 | 3600 | 2 | 765.89 | GGB | 763.37 | 774.891 | 768.498 | 256.34 | GGB | 10505 | GGB | 9.77 | GGB | 1009.22 | GGB | 64.74 | GGB | 163044.75 | GGB | 131299.98 | GGB | 0 | 0 | 2851 | 3600 | 2835.36 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246289.09 | GGB | 246292.02 | 2574.7857 | 2574.7857 |  |  |  | 0 | 1 | [10 empty] | 2851 | -261 | 2590 | 2574.7857 | 93.9081 |  |  | #VALUE!
31.05.2008 23:00 | 3600 | 2 | 766.17 | GGB | 763.37 | 776.203 | 768.498 | 258.52 | GGB | 10563.9 | GGB | 9.78 | GGB | 1010.11 | GGB | 63.98 | GGB | 165071.57 | GGB | 133349.5 | GGB | 0 | 0 | 2872 | 3600 | 2856.48 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246328.17 | GGB | 246331.1 | 2595.7686 | 2595.7686 |  |  |  | 0 | 1 | [10 empty] | 2872 | -261 | 2611 | 2595.7686 | 96.1512 |  |  | #VALUE!
31.05.2008 24:00 | 3600 | 2 | 765.53 | GGB | 764.835 | 777.82 | 770.696 | 258.45 | GGB | 10620.8 | GGB | 9.78 | GGB | 1010.23 | GGB | 63.6 | GGB | 164664.44 | GGB | 133184.48 | GGB | 0 | 0 | 2904 | 3600 | 2888.52 | GGB | 100 | GGB | 39.08 | GGB | 39.08 | GGB | 246367.26 | GGB | 246370.18 | 2627.7424 | 2627.7424 |  |  |  | 1 | 1 |  |  |  |  | 133184.48 | 2627.7424 | 133184.48 | 2627.7424 | 8.9553 |  | 2904 | -261 | 2643 | 2627.7424 | 97.2151 |  |  | #VALUE!
01.06.2008 01:00 | 3600 | 2 | 765.04 | GGB | 765.934 | 779.086 | 771.795 | 260.99 | GGB | 10656.3 | GGB | 9.77 | GGB | 1010.88 | GGB | 62.76 | GGB | 167665.07 | GGB | 136041.47 | GGB | 0 | 0 | 2945 | 3600 | 2929.37 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246406.04 | GGB | 246408.97 | 2668.709 | 2668.709 |  |  |  | 0 | 1 | [10 empty] | 2945 | -261 | 2684 | 2668.709 | 100.8486 |  |  | #VALUE!
01.06.2008 02:00 | 3600 | 2 | 763.78 | GGB | 762.271 | 774.914 | 767.766 | 261.64 | GGB | 10727.2 | GGB | 9.76 | GGB | 1010.99 | GGB | 62.91 | GGB | 168193.23 | GGB | 136423.32 | GGB | 0 | 0 | 3045 | 3600 | 3029.31 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246444.83 | GGB | 246447.76 | 2768.6273 | 2768.6273 |  |  |  | 0 | 1 | [10 empty] | 3045 | -261 | 2784 | 2768.6273 | 104.9181 |  |  | #VALUE!
01.06.2008 03:00 | 3600 | 2 | 763.83 | GGB | 764.835 | 776.086 | 768.864 | 264.59 | GGB | 10776 | GGB | 9.77 | GGB | 1012.06 | GGB | 62.04 | GGB | 171636.18 | GGB | 139725.87 | GGB | 0 | 0 | 3074 | 3600 | 3058.03 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246483.62 | GGB | 246486.55 | 2797.6037 | 2704.7819 |  |  |  | 1 | 1 |  |  |  |  | 139725.87 | 2704.7819 | 139725.87 | 2704.7819 | 9.7429 |  | 3074 | -261 | 2813 | 2797.6037 | 108.5827 | 2704.7819 |  | 104.98
01.06.2008 04:00 | 3600 | 2 | 763.77 | GGB | 762.271 | 773.625 | 766.667 | 265.32 | GGB | 10843.7 | GGB | 9.77 | GGB | 1012.83 | GGB | 62.21 | GGB | 171964.08 | GGB | 140028.25 | GGB | 0 | 0 | 3126 | 3600 | 3110.06 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246522.41 | GGB | 246525.34 | 2849.5612 | 2698.9411 |  |  |  | 0 | 1 | [10 empty] | 3126 | -261 | 2865 | 2849.5612 | 110.8386 | 2698.9411 |  | 104.98
01.06.2008 05:00 | 3600 | 2 | 762.87 | GGB | 763.37 | 774.727 | 767.766 | 266.75 | GGB | 10920.8 | GGB | 9.77 | GGB | 1013.45 | GGB | 61.79 | GGB | 173029.21 | GGB | 141155.28 | GGB | 0 | 0 | 3202 | 3600 | 3186.54 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246561.2 | GGB | 246564.13 | 2925.4992 | 2677.3919 |  |  |  | 0 | 1 | [10 empty] | 3202 | -261 | 2941 | 2925.4992 | 114.7082 | 2677.3919 |  | 104.98
01.06.2008 06:00 | 3600 | 2 | 762.25 | GGB | 763.37 | 773.695 | 767.766 | 269.45 | GGB | 10932.7 | GGB | 9.77 | GGB | 1014.56 | GGB | 61.02 | GGB | 176258.7 | GGB | 144280.02 | GGB | 0 | 0 | 3247 | 3600 | 3230.88 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246599.99 | GGB | 246602.92 | 2970.4624 | 2619.4063 |  |  |  | 0 | 1 | [10 empty] | 3247 | -261 | 2986 | 2970.4624 | 119.0496 | 2619.4063 |  | 104.98
01.06.2008 07:00 | 3600 | 2 | 764.63 | GGB | 764.835 | 776.016 | 769.963 | 268.34 | GGB | 10985.1 | GGB | 9.81 | GGB | 1014.59 | GGB | 61.27 | GGB | 174942.7 | GGB | 143102.09 | GGB | 0 | 0 | 3147 | 3600 | 3130.78 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246638.78 | GGB | 246641.71 | 2870.5441 | 2640.9677 |  |  |  | 1 | 1 |  |  |  |  | 143102.09 | 2640.9677 | 143102.09 | 2640.9677 | 9.7429 |  | 3147 | -261 | 2886 | 2870.5441 | 114.1058 | 2640.9677 |  | 104.98
01.06.2008 08:00 | 3600 | 2 | 764.69 | GGB | 765.934 | 777.07 | 769.963 | 264.79 | GGB | 10920.3 | GGB | 9.81 | GGB | 1014.98 | GGB | 62.28 | GGB | 171159.74 | GGB | 139637.38 | GGB | 0 | 0 | 3114 | 3600 | 3098.58 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246677.57 | GGB | 246680.5 | 2837.571 | 2706.4959 |  |  |  | 1 | 1 |  |  |  |  | 139637.38 | 2706.4959 | 139637.38 | 2706.4959 | 9.7429 |  | 3114 | -261 | 2853 | 2837.571 | 110.0642 | 2706.4959 |  | 104.98
01.06.2008 09:00 | 3600 | 2 | 765.17 | GGB | 763.37 | 776.063 | 767.766 | 262.43 | GGB | 10804 | GGB | 9.8 | GGB | 1015.11 | GGB | 62.92 | GGB | 168885.34 | GGB | 137538.53 | GGB | 0 | 0 | 3035 | 3600 | 3018.85 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246716.35 | GGB | 246719.29 | 2758.6355 | 2747.7973 |  |  |  | 0 | 1 | [10 empty] | 3035 | -261 | 2774 | 2758.6355 | 105.3941 | 2747.7973 |  | 104.98
01.06.2008 10:00 | 3600 | 2 | 765.75 | GGB | 765.934 | 778.172 | 771.429 | 261.93 | GGB | 10696 | GGB | 9.8 | GGB | 1014.82 | GGB | 63.21 | GGB | 168648.77 | GGB | 137189.87 | GGB | 0 | 0 | 2956 | 3600 | 2940.13 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246755.14 | GGB | 246758.08 | 2679.7 | 2679.7 |  |  |  | 1 | 1 |  |  |  |  | 137189.87 | 2679.7 | 137189.87 | 2679.7 | 9.4774 |  | 2956 | -261 | 2695 | 2679.7 | 102.1188 |  |  | #VALUE!
01.06.2008 11:00 | 3600 | 2 | 766.16 | GGB | 765.934 | 779.156 | 771.429 | 259.62 | GGB | 10668.4 | GGB | 9.8 | GGB | 1014.21 | GGB | 64.11 | GGB | 165924.33 | GGB | 134528.73 | GGB | 0 | 0 | 2919 | 3600 | 2903.68 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246793.93 | GGB | 246796.87 | 2642.7302 | 2642.7302 |  |  |  | 0 | 1 | [10 empty] | 2919 | -261 | 2658 | 2642.7302 | 98.7564 |  |  | #VALUE!
01.06.2008 12:00 | 3600 | 2 | 766.74 | GGB | 764.835 | 777.117 | 770.33 | 258.71 | GGB | 10629 | GGB | 9.79 | GGB | 1013.48 | GGB | 64.54 | GGB | 165422.58 | GGB | 133856.54 | GGB | 0 | 0 | 2862 | 3600 | 2846.13 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246832.72 | GGB | 246835.66 | 2585.7767 | 2585.7767 |  |  |  | 1 | 1 |  |  |  |  | 133856.54 | 2585.7767 | 133856.54 | 2585.7767 | 8.923 |  | 2862 | -261 | 2601 | 2585.7767 | 96.1453 |  |  | #VALUE!
01.06.2008 13:00 | 3600 | 2 | 766.29 | GGB | 767.033 | 779.297 | 772.527 | 259.65 | GGB | 10582.9 | GGB | 9.78 | GGB | 1013.46 | GGB | 63.9 | GGB | 167215.03 | GGB | 135560.43 | GGB | 0 | 0 | 2850 | 3600 | 2834.09 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246871.51 | GGB | 246874.45 | 2573.7865 | 2573.7865 |  |  |  | 0 | 1 | [10 empty] | 2850 | -261 | 2589 | 2573.7865 | 96.9177 |  |  | #VALUE!
01.06.2008 14:00 | 3600 | 2 | 766.82 | GGB | 765.934 | 778.359 | 771.429 | 258.93 | GGB | 10601 | GGB | 9.79 | GGB | 1013.61 | GGB | 63.89 | GGB | 166586.73 | GGB | 135075.62 | GGB | 0 | 0 | 2828 | 3600 | 2812.39 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246910.3 | GGB | 246913.24 | 2551.8045 | 2551.8045 |  |  |  | 1 | 1 |  |  |  |  | 135075.62 | 2551.8045 | 135075.62 | 2551.8045 | 8.886 |  | 2828 | -261 | 2567 | 2551.8045 | 95.7463 |  |  | #VALUE!
01.06.2008 15:00 | 3600 | 2 | 766.99 | GGB | 767.033 | 779.602 | 772.527 | 257.69 | GGB | 10594.8 | GGB | 9.79 | GGB | 1013.45 | GGB | 64.41 | GGB | 165206.91 | GGB | 133727.37 | GGB | 0 | 0 | 2812 | 3600 | 2796.87 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246949.09 | GGB | 246952.03 | 2535.8176 | 2535.8176 |  |  |  | 0 | 1 | [10 empty] | 2812 | -261 | 2551 | 2535.8176 | 94.1967 |  |  | #VALUE!
01.06.2008 16:00 | 3600 | 2 | 767.61 | GGB | 767.033 | 779.32 | 772.527 | 257.1 | GGB | 10533.8 | GGB | 9.79 | GGB | 1012.88 | GGB | 64.4 | GGB | 165298.24 | GGB | 133732.39 | GGB | 0 | 0 | 2756 | 3600 | 2740.32 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 246987.87 | GGB | 246990.82 | 2479.8633 | 2479.8633 |  |  |  | 0 | 1 | [10 empty] | 2756 | -261 | 2495 | 2479.8633 | 92.1217 |  |  | #VALUE!
01.06.2008 17:00 | 3600 | 2 | 767.45 | GGB | 768.132 | 781.43 | 775.091 | 257.14 | GGB | 10534.9 | GGB | 9.79 | GGB | 1012.39 | GGB | 64.37 | GGB | 165071.57 | GGB | 133496.78 | GGB | 0 | 0 | 2769 | 3600 | 2753.78 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247026.66 | GGB | 247029.61 | 2492.8527 | 2492.8527 |  |  |  | 0 | 1 | [10 empty] | 2769 | -261 | 2508 | 2492.8527 | 92.4411 |  |  | #VALUE!
01.06.2008 18:00 | 3600 | 2 | 767.17 | GGB | 765.934 | 777.703 | 771.429 | 256.61 | GGB | 10543.5 | GGB | 9.78 | GGB | 1012.2 | GGB | 64.82 | GGB | 164210 | GGB | 132598.43 | GGB | 0 | 0 | 2789 | 3600 | 2773.4 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247065.45 | GGB | 247068.4 | 2512.8363 | 2512.8363 |  |  |  | 1 | 1 |  |  |  |  | 132598.43 | 2512.8363 | 132598.43 | 2512.8363 | 8.5898 |  | 2789 | -261 | 2528 | 2512.8363 | 92.555 |  |  | #VALUE!
01.06.2008 19:00 | 3600 | 2 | 767.31 | GGB | 764.835 | 778.969 | 771.795 | 256.78 | GGB | 10560.2 | GGB | 9.78 | GGB | 1012.24 | GGB | 64.76 | GGB | 164246.32 | GGB | 132655.99 | GGB | 0 | 0 | 2788 | 3600 | 2772.43 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247104.24 | GGB | 247107.19 | 2511.8371 | 2511.8371 |  |  |  | 0 | 1 | [10 empty] | 2788 | -261 | 2527 | 2511.8371 | 92.5584 |  |  | #VALUE!
01.06.2008 20:00 | 3600 | 2 | 766.96 | GGB | 765.934 | 777.82 | 771.795 | 257.16 | GGB | 10569.9 | GGB | 9.78 | GGB | 1012.35 | GGB | 64.65 | GGB | 164388.26 | GGB | 132828.25 | GGB | 0 | 0 | 2813 | 3600 | 2797.29 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247143.03 | GGB | 247145.98 | 2536.8167 | 2536.8167 |  |  |  | 1 | 1 |  |  |  |  | 132828.25 | 2536.8167 | 132828.25 | 2536.8167 | 8.6868 |  | 2813 | -261 | 2552 | 2536.8167 | 93.6003 |  |  | #VALUE!
01.06.2008 21:00 | 3600 | 2 | 766.45 | GGB | 765.934 | 777.727 | 771.795 | 257.8 | GGB | 10598.4 | GGB | 9.78 | GGB | 1012.82 | GGB | 64.47 | GGB | 165051.76 | GGB | 133495.77 | GGB | 0 | 0 | 2840 | 3600 | 2824.48 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247181.82 | GGB | 247184.77 | 2563.7947 | 2563.7947 |  |  |  | 1 | 1 |  |  |  |  | 133495.77 | 2563.7947 | 133495.77 | 2563.7947 | 8.8233 |  | 2840 | -261 | 2579 | 2563.7947 | 95.071 |  |  | #VALUE!
01.06.2008 22:00 | 3600 | 2 | 765.5 | GGB | 764.469 | 776.273 | 769.597 | 259.35 | GGB | 10657.4 | GGB | 9.77 | GGB | 1013.74 | GGB | 63.99 | GGB | 166499.81 | GGB | 134982.03 | GGB | 0 | 0 | 2922 | 3600 | 2906.45 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247220.61 | GGB | 247223.56 | 2645.7278 | 2645.7278 |  |  |  | 1 | 1 |  |  |  |  | 134982.03 | 2645.7278 | 134982.03 | 2645.7278 | 9.2066 |  | 2922 | -261 | 2661 | 2645.7278 | 99.2016 |  |  | #VALUE!
01.06.2008 23:00 | 3600 | 2 | 764.1 | GGB | 764.469 | 776.625 | 769.597 | 261.91 | GGB | 10776.8 | GGB | 9.76 | GGB | 1014.97 | GGB | 63.06 | GGB | 169409.1 | GGB | 137889.12 | GGB | 0 | 0 | 3046 | 3600 | 3030.76 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247259.4 | GGB | 247262.35 | 2769.6265 | 2740.8109 |  |  |  | 1 | 1 |  |  |  |  | 137889.12 | 2740.8109 | 137889.12 | 2740.8109 | 9.7429 |  | 3046 | -261 | 2785 | 2769.6265 | 106.0837 | 2740.8109 |  | 104.98
01.06.2008 24:00 | 3600 | 2 | 762.66 | GGB | 761.172 | 772.898 | 765.934 | 265.62 | GGB | 10867.2 | GGB | 9.75 | GGB | 1016.11 | GGB | 62.39 | GGB | 171862.85 | GGB | 140320.57 | GGB | 0 | 0 | 3188 | 3600 | 3171.76 | GGB | 100 | GGB | 38.79 | GGB | 38.79 | GGB | 247298.18 | GGB | 247301.14 | 2911.5106 | 2693.3186 |  |  |  | 0 | 1 | [10 empty] | 3188 | -261 | 2927 | 2911.5106 | 113.4847 | 2693.3186 |  | 104.98
02.06.2008 01:00 | 3600 | 2 | 763.13 | GGB | 762.271 | 773.977 | 767.033 | 267.54 | GGB | 10956 | GGB | 9.77 | GGB | 1016.93 | GGB | 62.15 | GGB | 173576.08 | GGB | 141939.54 | GGB | 0 | 0 | 3224 | 3600 | 3207.72 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247336.93 | GGB | 247339.88 | 2947.4812 | 2662.5985 |  |  |  | 0 | 1 | [10 empty] | 3224 | -261 | 2963 | 2947.4812 | 116.2123 | 2662.5985 |  | 104.98
02.06.2008 02:00 | 3600 | 2 | 762.59 | GGB | 761.172 | 773.063 | 765.934 | 268.89 | GGB | 11014.5 | GGB | 9.77 | GGB | 1017.57 | GGB | 61.51 | GGB | 175262.9 | GGB | 143679.11 | GGB | 0 | 0 | 3281 | 3600 | 3264.84 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247375.67 | GGB | 247378.62 | 3004.4347 | 2630.3615 |  |  |  | 0 | 1 | [10 empty] | 3281 | -261 | 3020 | 3004.4347 | 119.9096 | 2630.3615 |  | 104.98
02.06.2008 03:00 | 3600 | 2 | 762.45 | GGB | 763.37 | 774.188 | 768.132 | 269.73 | GGB | 11062.7 | GGB | 9.79 | GGB | 1018.24 | GGB | 61.14 | GGB | 176238.9 | GGB | 144738.4 | GGB | 0 | 0 | 3302 | 3600 | 3286.36 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247414.41 | GGB | 247417.36 | 3025.4176 | 2611.1108 |  |  |  | 0 | 1 | [10 empty] | 3302 | -261 | 3041 | 3025.4176 | 121.6372 | 2611.1108 |  | 104.98
02.06.2008 04:00 | 3600 | 2 | 761.8 | GGB | 760.806 | 772.219 | 765.934 | 270.62 | GGB | 11064.9 | GGB | 9.77 | GGB | 1018.49 | GGB | 60.69 | GGB | 177418.46 | GGB | 145937.02 | GGB | 0 | 0 | 3351 | 3600 | 3334.84 | GNB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247453.15 | GGB | 247456.1 | 3074.3776 | 2589.665 |  |  |  | 0 | 1 | [10 empty] | 3351 | -261 | 3090 | 3074.3776 | 124.6293 | 2589.665 |  | 104.98
02.06.2008 05:00 | 3600 | 2 | 762.24 | GGB | 762.271 | 773.367 | 767.033 | 271.87 | GGB | 11105.8 | GGB | 9.78 | GGB | 1018.95 | GGB | 60.07 | GGB | 179324.24 | GGB | 147846.15 | GGB | 0 | 0 | 3352 | 3600 | 3336 | GNB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247491.9 | GGB | 247494.84 | 3075.3767 | 2556.2248 |  |  |  | 0 | 1 | [10 empty] | 3352 | -261 | 3091 | 3075.3767 | 126.3007 | 2556.2248 |  | 104.98
02.06.2008 06:00 | 3600 | 2 | 762.16 | GGB | 764.469 | 775.781 | 768.498 | 272.23 | GGB | 11132.6 | GGB | 9.79 | GGB | 1018.96 | GGB | 59.52 | GGB | 180120.89 | GGB | 148750.53 | GGB | 0 | 0 | 3354 | 3600 | 3338.04 | GNB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247530.64 | GGB | 247533.58 | 3077.3751 | 2540.6834 |  |  |  | 1 | 1 |  |  |  |  | 148750.53 | 2540.6834 | 148750.53 | 2540.6834 | 9.7555 |  | 3354 | -261 | 3093 | 3077.3751 | 127.1559 | 2540.6834 |  | 104.98
02.06.2008 07:00 | 3600 | 2 | 762.96 | GGB | 763.37 | 774.656 | 767.766 | 270.45 | GGB | 11169.6 | GGB | 9.81 | GGB | 1018.77 | GGB | 60.05 | GGB | 177754.06 | GGB | 146533.47 | GGB | 0 | 0 | 3329 | 3600 | 3313.05 | GNB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247569.38 | GGB | 247572.32 | 3052.3955 | 2579.1241 |  |  |  | 0 | 1 | [10 empty] | 3329 | -261 | 3068 | 3052.3955 | 124.2439 | 2579.1241 |  | 104.98
02.06.2008 08:00 | 3600 | 2 | 764 | GGB | 764.469 | 776.742 | 769.963 | 267.8 | GGB | 11081.4 | GGB | 9.82 | GGB | 1018.51 | GGB | 60.83 | GGB | 174784.25 | GGB | 143712.47 | GGB | 0 | 0 | 3250 | 3600 | 3234.3 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247608.12 | GGB | 247611.06 | 2973.46 | 2629.7509 |  |  |  | 1 | 1 |  |  |  |  | 143712.47 | 2629.7509 | 143712.47 | 2629.7509 | 9.7555 |  | 3250 | -261 | 2989 | 2973.46 | 118.7009 | 2629.7509 |  | 104.98
02.06.2008 09:00 | 3600 | 2 | 764.99 | GGB | 764.469 | 775.969 | 769.963 | 264.42 | GGB | 10897.2 | GGB | 9.81 | GGB | 1018.26 | GGB | 61.87 | GGB | 171368.8 | GGB | 140431.74 | GGB | 0 | 0 | 3100 | 3600 | 3084.12 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247646.87 | GGB | 247649.8 | 2823.5824 | 2691.1865 |  |  |  | 1 | 1 |  |  |  |  | 140431.74 | 2691.1865 | 140431.74 | 2691.1865 | 9.7555 |  | 3100 | -261 | 2839 | 2823.5824 | 110.1446 | 2691.1865 |  | 104.98
02.06.2008 10:00 | 3600 | 2 | 766.49 | GGB | 764.835 | 776.977 | 769.963 | 261.05 | GGB | 10768.4 | GGB | 9.81 | GGB | 1017.11 | GGB | 62.88 | GGB | 168047.98 | GGB | 137140.6 | GGB | 0 | 0 | 2960 | 3600 | 2944.01 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247685.61 | GGB | 247688.54 | 2683.6967 | 2683.6967 |  |  |  | 1 | 1 |  |  |  |  | 137140.6 | 2683.6967 | 137140.6 | 2683.6967 | 9.5004 |  | 2960 | -261 | 2699 | 2683.6967 | 102.2344 |  |  | #VALUE!
02.06.2008 11:00 | 3600 | 2 | 766.95 | GGB | 764.835 | 777.141 | 770.33 | 259.33 | GGB | 10680.3 | GGB | 9.8 | GGB | 1016.23 | GGB | 63.68 | GGB | 166404.08 | GGB | 135360.56 | GGB | 0 | 0 | 2893 | 3600 | 2877.45 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247724.35 | GGB | 247727.28 | 2616.7514 | 2616.7514 |  |  |  | 1 | 1 |  |  |  |  | 135360.56 | 2616.7514 | 135360.56 | 2616.7514 | 9.1431 |  | 2893 | -261 | 2632 | 2616.7514 | 98.3903 |  |  | #VALUE!
02.06.2008 12:00 | 3600 | 2 | 766.96 | GGB | 764.835 | 777.234 | 770.33 | 257.83 | GGB | 10619.6 | GGB | 9.79 | GGB | 1015.27 | GGB | 64.53 | GGB | 164695.25 | GGB | 133505.96 | GGB | 0 | 0 | 2873 | 3600 | 2857.45 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247763.09 | GGB | 247766.02 | 2596.7678 | 2596.7678 |  |  |  | 1 | 1 |  |  |  |  | 133505.96 | 2596.7678 | 133505.96 | 2596.7678 | 8.949 |  | 2873 | -261 | 2612 | 2596.7678 | 96.3011 |  |  | #VALUE!
02.06.2008 13:00 | 3600 | 2 | 767.39 | GGB | 765.934 | 778.172 | 771.429 | 256.66 | GGB | 10584.2 | GGB | 9.79 | GGB | 1014.23 | GGB | 64.87 | GGB | 163620.22 | GGB | 132367.39 | GGB | 0 | 0 | 2835 | 3600 | 2819.4 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247801.83 | GGB | 247804.76 | 2558.7988 | 2558.7988 |  |  |  | 1 | 1 |  |  |  |  | 132367.39 | 2558.7988 | 132367.39 | 2558.7988 | 8.7429 |  | 2835 | -261 | 2574 | 2558.7988 | 94.0838 |  |  | #VALUE!
02.06.2008 14:00 | 3600 | 2 | 767.61 | GGB | 765.934 | 778.266 | 771.429 | 255.43 | GGB | 10533.1 | GGB | 9.79 | GGB | 1013.48 | GGB | 65.14 | GGB | 162372.44 | GGB | 131152.64 | GGB | 0 | 0 | 2788 | 3600 | 2772.85 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247840.58 | GGB | 247843.5 | 2511.8371 | 2511.8371 |  |  |  | 1 | 1 |  |  |  |  | 131152.64 | 2511.8371 | 131152.64 | 2511.8371 | 8.5037 |  | 2788 | -261 | 2527 | 2511.8371 | 91.5095 |  |  | #VALUE!
02.06.2008 15:00 | 3600 | 2 | 767.88 | GGB | 765.934 | 779.367 | 771.429 | 254.64 | GGB | 10487.7 | GGB | 9.79 | GGB | 1012.62 | GGB | 65.48 | GGB | 162032.44 | GGB | 130638.62 | GGB | 0 | 0 | 2761 | 3600 | 2745.08 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247879.32 | GGB | 247882.24 | 2484.8592 | 2484.8592 |  |  |  | 0 | 1 | [10 empty] | 2761 | -261 | 2500 | 2484.8592 | 90.1718 |  |  | #VALUE!
02.06.2008 16:00 | 3600 | 2 | 768.28 | GGB | 767.033 | 780.234 | 773.626 | 254.94 | GGB | 10436.1 | GGB | 9.79 | GGB | 1011.71 | GGB | 65.1 | GGB | 162668.43 | GGB | 131179.54 | GGB | 0 | 0 | 2709 | 3600 | 2693.93 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247918.06 | GGB | 247920.98 | 2432.9016 | 2432.9016 |  |  |  | 0 | 1 | [10 empty] | 2709 | -261 | 2448 | 2432.9016 | 88.6519 |  |  | #VALUE!
02.06.2008 17:00 | 3600 | 2 | 768.56 | GGB | 765.934 | 779.133 | 771.429 | 253.74 | GGB | 10428.1 | GGB | 9.78 | GGB | 1010.68 | GGB | 65.46 | GGB | 161349.13 | GGB | 129844.22 | GGB | 0 | 0 | 2697 | 3600 | 2681.66 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247956.8 | GGB | 247959.72 | 2420.9114 | 2420.9114 |  |  |  | 0 | 1 | [10 empty] | 2697 | -261 | 2436 | 2420.9114 | 87.317 |  |  | #VALUE!
02.06.2008 18:00 | 3600 | 2 | 767.96 | GGB | 765.934 | 778.969 | 772.527 | 253.25 | GGB | 10414.7 | GGB | 9.78 | GGB | 1009.91 | GGB | 66.01 | GGB | 160791.26 | GGB | 129088.32 | GGB | 0 | 0 | 2727 | 3600 | 2711.48 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 247995.55 | GGB | 247998.46 | 2450.8869 | 2450.8869 |  |  |  | 0 | 1 | [10 empty] | 2727 | -261 | 2466 | 2450.8869 | 87.8836 |  |  | #VALUE!
02.06.2008 19:00 | 3600 | 2 | 768.48 | GGB | 767.033 | 778.992 | 772.527 | 254.26 | GGB | 10402 | GGB | 9.78 | GGB | 1009.39 | GGB | 65.24 | GGB | 162191.99 | GGB | 130441.33 | GGB | 0 | 0 | 2691 | 3600 | 2675.68 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 248034.29 | GGB | 248037.2 | 2414.9163 | 2414.9163 |  |  |  | 0 | 1 | [10 empty] | 2691 | -261 | 2430 | 2414.9163 | 87.5014 |  |  | #VALUE!
02.06.2008 20:00 | 3600 | 2 | 767.85 | GGB | 764.835 | 777.094 | 770.33 | 253.07 | GGB | 10430.9 | GGB | 9.77 | GGB | 1008.78 | GGB | 65.55 | GGB | 160486.46 | GGB | 128875.58 | GGB | 0 | 0 | 2721 | 3600 | 2705.83 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 248073.03 | GGB | 248075.94 | 2444.8918 | 2444.8918 |  |  |  | 1 | 1 |  |  |  |  | 128875.58 | 2444.8918 | 128875.58 | 2444.8918 | 8.1334 |  | 2721 | -261 | 2460 | 2444.8918 | 87.5241 |  |  | #VALUE!
02.06.2008 21:00 | 3600 | 2 | 767.57 | GGB | 765.934 | 778.148 | 771.429 | 254.81 | GGB | 10437.3 | GGB | 9.77 | GGB | 1008.65 | GGB | 65.2 | GGB | 162105.06 | GGB | 130292.13 | GGB | 0 | 0 | 2746 | 3600 | 2730.27 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 248111.77 | GGB | 248114.68 | 2469.8714 | 2469.8714 |  |  |  | 1 | 1 |  |  |  |  | 130292.13 | 2469.8714 | 130292.13 | 2469.8714 | 8.3068 |  | 2746 | -261 | 2485 | 2469.8714 | 89.3902 |  |  | #VALUE!
02.06.2008 22:00 | 3600 | 2 | 766.94 | GGB | 764.835 | 778.031 | 770.33 | 256.42 | GGB | 10495.6 | GGB | 9.77 | GGB | 1008.81 | GGB | 64.79 | GGB | 163289.02 | GGB | 131422.79 | GGB | 0 | 0 | 2811 | 3600 | 2795.2 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 248150.51 | GGB | 248153.42 | 2534.8184 | 2534.8184 |  |  |  | 1 | 1 |  |  |  |  | 131422.79 | 2534.8184 | 131422.79 | 2534.8184 | 8.5992 |  | 2811 | -261 | 2550 | 2534.8184 | 92.5369 |  |  | #VALUE!
02.06.2008 23:00 | 3600 | 2 | 765.78 | GGB | 763.37 | 775.758 | 768.864 | 257.65 | GGB | 10565.2 | GGB | 9.76 | GGB | 1008.66 | GGB | 64.74 | GGB | 163908.51 | GGB | 131922.57 | GGB | 0 | 0 | 2897 | 3600 | 2881.14 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 248189.26 | GGB | 248192.16 | 2620.7482 | 2620.7482 |  |  |  | 0 | 1 | [10 empty] | 2897 | -261 | 2636 | 2620.7482 | 96.0377 |  |  | #VALUE!
02.06.2008 24:00 | 3600 | 2 | 765.6 | GGB | 764.469 | 776.555 | 768.864 | 259.46 | GGB | 10613.2 | GGB | 9.77 | GGB | 1009.17 | GGB | 63.63 | GGB | 166864.02 | GGB | 134812.98 | GGB | 0 | 0 | 2933 | 3600 | 2917.81 | GGB | 100 | GGB | 38.74 | GGB | 38.74 | GGB | 248228 | GGB | 248230.9 | 2656.7188 | 2656.7188 |  |  |  | 1 | 1 |  |  |  |  | 134812.98 | 2656.7188 | 134812.98 | 2656.7188 | 9.2452 |  | 2933 | -261 | 2672 | 2656.7188 | 99.4889 |  |  | #VALUE!
03.06.2008 01:00 | 3600 | 2 | 765.7 | GGB | 764.835 | 776.602 | 769.963 | 260.88 | GGB | 10672 | GGB | 9.78 | GGB | 1009.02 | GGB | 63.48 | GGB | 167498.91 | GGB | 135362.94 | GGB | 0 | 0 | 2959 | 3600 | 2943.5 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248267.17 | GGB | 248270.07 | 2682.6976 | 2682.6976 |  |  |  | 1 | 1 |  |  |  |  | 135362.94 | 2682.6976 | 135362.94 | 2682.6976 | 9.2708 |  | 2959 | -261 | 2698 | 2682.6976 | 100.8716 |  |  | #VALUE!
03.06.2008 02:00 | 3600 | 2 | 764.9 | GGB | 764.469 | 775.758 | 768.864 | 261.2 | GGB | 10727.1 | GGB | 9.77 | GGB | 1009.41 | GGB | 63.36 | GGB | 167503.32 | GGB | 135468.37 | GGB | 0 | 0 | 3026 | 3600 | 3009.84 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248306.33 | GGB | 248309.24 | 2749.6429 | 2749.6429 |  |  |  | 1 | 1 |  |  |  |  | 135468.37 | 2749.6429 | 135468.37 | 2749.6429 | 9.5096 |  | 3026 | -261 | 2765 | 2749.6429 | 103.4693 |  |  | #VALUE!
03.06.2008 03:00 | 3600 | 2 | 763.39 | GGB | 762.271 | 774.797 | 767.766 | 264.41 | GGB | 10743.7 | GGB | 9.75 | GGB | 1009.94 | GGB | 62.52 | GGB | 171058.51 | GGB | 138763.61 | GGB | 0 | 0 | 3103 | 3600 | 3086.81 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248345.5 | GGB | 248348.41 | 2826.58 | 2723.5383 |  |  |  | 0 | 1 | [10 empty] | 3103 | -261 | 2842 | 2826.58 | 108.9518 | 2723.5383 |  | 104.98
03.06.2008 04:00 | 3600 | 2 | 764.4 | GGB | 762.271 | 773.883 | 766.667 | 265.29 | GGB | 10844.5 | GGB | 9.79 | GGB | 1010.47 | GGB | 62.17 | GGB | 172057.61 | GGB | 139794.11 | GGB | 0 | 0 | 3097 | 3600 | 3081.59 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248384.67 | GGB | 248387.58 | 2820.5849 | 2703.4615 |  |  |  | 0 | 1 | [10 empty] | 3097 | -261 | 2836 | 2820.5849 | 109.5281 | 2703.4615 |  | 104.98
03.06.2008 05:00 | 3600 | 2 | 763.21 | GGB | 762.271 | 774.094 | 766.667 | 266.3 | GGB | 10903.9 | GGB | 9.77 | GGB | 1010.5 | GGB | 62.13 | GGB | 172751.93 | GGB | 140378.16 | GGB | 0 | 0 | 3210 | 3600 | 3194.3 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248423.84 | GGB | 248426.75 | 2933.4927 | 2692.2137 |  |  |  | 0 | 1 | [10 empty] | 3210 | -261 | 2949 | 2933.4927 | 114.3884 | 2692.2137 |  | 104.98
03.06.2008 06:00 | 3600 | 2 | 763.88 | GGB | 765.934 | 777.352 | 770.696 | 266.99 | GGB | 10920.3 | GGB | 9.79 | GGB | 1010.08 | GGB | 61.38 | GGB | 174459.65 | GGB | 142025.69 | GGB | 0 | 0 | 3173 | 3600 | 3157.38 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248463 | GGB | 248465.92 | 2896.5229 | 2660.9834 |  |  |  | 1 | 1 |  |  |  |  | 142025.69 | 2660.9834 | 142025.69 | 2660.9834 | 9.6484 |  | 3173 | -261 | 2912 | 2896.5229 | 114.2724 | 2660.9834 |  | 104.98
03.06.2008 07:00 | 3600 | 2 | 764.25 | GGB | 762.271 | 774.938 | 768.132 | 264.63 | GGB | 10920.2 | GGB | 9.8 | GGB | 1010.16 | GGB | 61.64 | GGB | 171907.97 | GGB | 139850.94 | GGB | 0 | 0 | 3140 | 3600 | 3124.5 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248502.17 | GGB | 248505.09 | 2863.5498 | 2702.363 |  |  |  | 0 | 1 | [10 empty] | 3140 | -261 | 2879 | 2863.5498 | 111.2417 | 2702.363 |  | 104.98
03.06.2008 08:00 | 3600 | 2 | 763.9 | GGB | 764.469 | 776.086 | 768.132 | 265.79 | GGB | 10883 | GGB | 9.79 | GGB | 1010.35 | GGB | 61.16 | GGB | 173310.9 | GGB | 141218.95 | GGB | 0 | 0 | 3140 | 3600 | 3124.38 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248541.34 | GGB | 248544.26 | 2863.5498 | 2676.1847 |  |  |  | 1 | 1 |  |  |  |  | 141218.95 | 2676.1847 | 141218.95 | 2676.1847 | 9.6484 |  | 3140 | -261 | 2879 | 2863.5498 | 112.3299 | 2676.1847 |  | 104.98
03.06.2008 09:00 | 3600 | 2 | 765 | GGB | 765.934 | 777.211 | 770.696 | 263.06 | GGB | 10864.2 | GGB | 9.81 | GGB | 1009.88 | GGB | 62.49 | GGB | 169818.43 | GGB | 137760.79 | GGB | 0 | 0 | 3084 | 3600 | 3068.48 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248580.51 | GGB | 248583.43 | 2807.5955 | 2743.3641 |  |  |  | 1 | 1 |  |  |  |  | 137760.79 | 2743.3641 | 137760.79 | 2743.3641 | 9.6484 |  | 3084 | -261 | 2823 | 2807.5955 | 107.4379 | 2743.3641 |  | 104.98
03.06.2008 10:00 | 3600 | 2 | 765.1 | GGB | 764.469 | 775.336 | 768.498 | 261.22 | GGB | 10775.9 | GGB | 9.8 | GGB | 1009.1 | GGB | 63.25 | GGB | 168020.47 | GGB | 135889.64 | GGB | 0 | 0 | 3039 | 3600 | 3022.98 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248619.67 | GGB | 248622.6 | 2762.6322 | 2762.6322 |  |  |  | 1 | 1 |  |  |  |  | 135889.64 | 2762.6322 | 135889.64 | 2762.6322 | 9.5842 |  | 3039 | -261 | 2778 | 2762.6322 | 104.2814 |  |  | #VALUE!
03.06.2008 11:00 | 3600 | 2 | 765.7 | GGB | 765.934 | 778.828 | 770.696 | 259.9 | GGB | 10725.6 | GGB | 9.8 | GGB | 1008.9 | GGB | 63.63 | GGB | 167025.77 | GGB | 134904.4 | GGB | 0 | 0 | 2987 | 3600 | 2971.12 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248658.84 | GGB | 248661.77 | 2710.6747 | 2710.6747 |  |  |  | 0 | 1 | [10 empty] | 2987 | -261 | 2726 | 2710.6747 | 101.5783 |  |  | #VALUE!
03.06.2008 12:00 | 3600 | 2 | 765.8 | GGB | 763.37 | 776.344 | 769.597 | 258.49 | GGB | 10662.5 | GGB | 9.79 | GGB | 1008.37 | GGB | 63.81 | GGB | 165796.69 | GGB | 133773.14 | GGB | 0 | 0 | 2944 | 3600 | 2928.25 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248698.01 | GGB | 248700.94 | 2667.7098 | 2667.7098 |  |  |  | 0 | 1 | [10 empty] | 2944 | -261 | 2683 | 2667.7098 | 99.13 |  |  | #VALUE!
03.06.2008 13:00 | 3600 | 2 | 766.21 | GGB | 764.835 | 777.164 | 770.696 | 257.5 | GGB | 10616.8 | GGB | 9.79 | GGB | 1007.75 | GGB | 64.3 | GGB | 164680.95 | GGB | 132597.19 | GGB | 0 | 0 | 2920 | 3600 | 2904.22 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248737.18 | GGB | 248740.11 | 2643.7294 | 2643.7294 |  |  |  | 1 | 1 |  |  |  |  | 132597.19 | 2643.7294 | 132597.19 | 2643.7294 | 8.9495 |  | 2920 | -261 | 2659 | 2643.7294 | 97.3753 |  |  | #VALUE!
03.06.2008 14:00 | 3600 | 2 | 766.38 | GGB | 765.934 | 778.055 | 770.696 | 257.02 | GGB | 10584.8 | GGB | 9.79 | GGB | 1007.25 | GGB | 64.46 | GGB | 164240.81 | GGB | 132112.23 | GGB | 0 | 0 | 2896 | 3600 | 2880.1 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248776.34 | GGB | 248779.28 | 2619.749 | 2619.749 |  |  |  | 1 | 1 |  |  |  |  | 132112.23 | 2619.749 | 132112.23 | 2619.749 | 8.8359 |  | 2896 | -261 | 2635 | 2619.749 | 96.1391 |  |  | #VALUE!
03.06.2008 15:00 | 3600 | 2 | 766.42 | GGB | 764.835 | 778.078 | 769.597 | 257.52 | GGB | 10543.2 | GGB | 9.78 | GGB | 1007.18 | GGB | 64.4 | GGB | 164640.24 | GGB | 132451.28 | GGB | 0 | 0 | 2877 | 3600 | 2861.85 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248815.51 | GGB | 248818.45 | 2600.7645 | 2600.7645 |  |  |  | 1 | 1 |  |  |  |  | 132451.28 | 2600.7645 | 132451.28 | 2600.7645 | 8.7943 |  | 2877 | -261 | 2616 | 2600.7645 | 95.6874 |  |  | #VALUE!
03.06.2008 16:00 | 3600 | 2 | 766.82 | GGB | 764.835 | 778.125 | 770.696 | 256.31 | GGB | 10560.8 | GGB | 9.79 | GGB | 1006.82 | GGB | 64.71 | GGB | 163257.11 | GGB | 131169.91 | GGB | 0 | 0 | 2869 | 3600 | 2853.46 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248854.68 | GGB | 248857.62 | 2592.771 | 2592.771 |  |  |  | 1 | 1 |  |  |  |  | 131169.91 | 2592.771 | 131169.91 | 2592.771 | 8.6825 |  | 2869 | -261 | 2608 | 2592.771 | 94.4704 |  |  | #VALUE!
03.06.2008 17:00 | 3600 | 2 | 766.15 | GGB | 765.934 | 778.125 | 771.795 | 256.91 | GGB | 10562.2 | GGB | 9.78 | GGB | 1006.8 | GGB | 64.6 | GGB | 163713.75 | GGB | 131577.53 | GGB | 0 | 0 | 2901 | 3600 | 2885.91 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248893.85 | GGB | 248896.79 | 2624.7449 | 2624.7449 |  |  |  | 1 | 1 |  |  |  |  | 131577.53 | 2624.7449 | 131577.53 | 2624.7449 | 8.8169 |  | 2901 | -261 | 2640 | 2624.7449 | 95.9326 |  |  | #VALUE!
03.06.2008 18:00 | 3600 | 2 | 766.6 | GGB | 764.835 | 777.938 | 770.696 | 257.2 | GGB | 10568.4 | GGB | 9.78 | GGB | 1006.73 | GGB | 64.74 | GGB | 163670.84 | GGB | 131477.56 | GGB | 0 | 0 | 2879 | 3600 | 2863.9 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248933.01 | GGB | 248935.96 | 2602.7629 | 2602.7629 |  |  |  | 1 | 1 |  |  |  |  | 131477.56 | 2602.7629 | 131477.56 | 2602.7629 | 8.7364 |  | 2879 | -261 | 2618 | 2602.7629 | 95.0569 |  |  | #VALUE!
03.06.2008 19:00 | 3600 | 2 | 766.06 | GGB | 764.835 | 777.023 | 770.696 | 258.04 | GGB | 10590.5 | GGB | 9.78 | GGB | 1006.9 | GGB | 64.41 | GGB | 164601.72 | GGB | 132376.01 | GGB | 0 | 0 | 2918 | 3600 | 2902.12 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 248972.18 | GGB | 248975.13 | 2641.731 | 2641.731 |  |  |  | 1 | 1 |  |  |  |  | 132376.01 | 2641.731 | 132376.01 | 2641.731 | 8.9278 |  | 2918 | -261 | 2657 | 2641.731 | 97.1394 |  |  | #VALUE!
03.06.2008 20:00 | 3600 | 2 | 765.91 | GGB | 764.469 | 778.008 | 769.597 | 258.51 | GGB | 10613.4 | GGB | 9.78 | GGB | 1007.69 | GGB | 64.24 | GGB | 164731.56 | GGB | 132655.1 | GGB | 0 | 0 | 2933 | 3600 | 2917.49 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 249011.35 | GGB | 249014.3 | 2656.7188 | 2656.7188 |  |  |  | 1 | 1 |  |  |  |  | 132655.1 | 2656.7188 | 132655.1 | 2656.7188 | 8.9974 |  | 2933 | -261 | 2672 | 2656.7188 | 97.8965 |  |  | #VALUE!
03.06.2008 21:00 | 3600 | 2 | 765.28 | GGB | 764.835 | 777.961 | 770.696 | 259.26 | GGB | 10636.1 | GGB | 9.77 | GGB | 1008.29 | GGB | 64.03 | GGB | 165359.86 | GGB | 133319.19 | GGB | 0 | 0 | 2970 | 3600 | 2954.47 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 249050.51 | GGB | 249053.47 | 2693.6886 | 2693.6886 |  |  |  | 1 | 1 |  |  |  |  | 133319.19 | 2693.6886 | 133319.19 | 2693.6886 | 9.1683 |  | 2970 | -261 | 2709 | 2693.6886 | 99.7557 |  |  | #VALUE!
03.06.2008 22:00 | 3600 | 2 | 764.86 | GGB | 762.271 | 773.883 | 767.766 | 262.17 | GGB | 10650.5 | GGB | 9.76 | GGB | 1008.94 | GGB | 63.38 | GGB | 168550.84 | GGB | 136246.42 | GGB | 0 | 0 | 3000 | 3600 | 2984.33 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 249089.68 | GGB | 249092.64 | 2723.6641 | 2723.6641 |  |  |  | 0 | 1 | [10 empty] | 3000 | -261 | 2739 | 2723.6641 | 103.0804 |  |  | #VALUE!
03.06.2008 23:00 | 3600 | 2 | 764.84 | GGB | 763.37 | 774.938 | 768.864 | 263.37 | GGB | 10743.8 | GGB | 9.78 | GGB | 1009.79 | GGB | 62.78 | GGB | 169840.43 | GGB | 137649.65 | GGB | 0 | 0 | 3029 | 3600 | 3013.46 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 249128.85 | GGB | 249131.81 | 2752.6404 | 2745.5791 |  |  |  | 0 | 1 | [10 empty] | 3029 | -261 | 2768 | 2752.6404 | 105.25 | 2745.5791 |  | 104.98
03.06.2008 24:00 | 3600 | 2 | 764.04 | GGB | 763.37 | 774.891 | 767.766 | 263.29 | GGB | 10831.7 | GGB | 9.78 | GGB | 1010.51 | GGB | 62.7 | GGB | 170325.68 | GGB | 138175.42 | GGB | 0 | 0 | 3102 | 3600 | 3086.21 | GGB | 100 | GGB | 39.17 | GGB | 39.17 | GGB | 249168.02 | GGB | 249170.98 | 2825.5808 | 2735.1319 |  |  |  | 0 | 1 | [10 empty] | 3102 | -261 | 2841 | 2825.5808 | 108.4516 | 2735.1319 |  | 104.98
04.06.2008 01:00 | 3600 | 2 | 764.24 | GGB | 763.37 | 775.078 | 766.667 | 264.47 | GGB | 10850.1 | GGB | 9.78 | GGB | 1011.13 | GGB | 62.76 | GGB | 170769.12 | GGB | 138593.43 | GGB | 0 | 0 | 3125 | 3600 | 3108.76 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249207.49 | GGB | 249210.46 | 2848.562 | 2726.8825 |  |  |  | 0 | 1 | [10 empty] | 3125 | -261 | 2864 | 2848.562 | 109.6644 | 2726.8825 |  | 104.98
04.06.2008 02:00 | 3600 | 2 | 764.39 | GGB | 763.37 | 775.406 | 767.766 | 264.33 | GGB | 10848.4 | GGB | 9.79 | GGB | 1011.42 | GGB | 62.79 | GGB | 170826.34 | GGB | 138665.1 | GGB | 0 | 0 | 3120 | 3600 | 3103.75 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249246.97 | GGB | 249249.94 | 2843.5661 | 2725.4731 |  |  |  | 0 | 1 | [10 empty] | 3120 | -261 | 2859 | 2843.5661 | 109.5287 | 2725.4731 |  | 104.98
04.06.2008 03:00 | 3600 | 2 | 764.24 | GGB | 763.37 | 775.172 | 767.766 | 265.85 | GGB | 10816.5 | GGB | 9.78 | GGB | 1011.63 | GGB | 61.99 | GGB | 172896.07 | GGB | 140712.54 | GGB | 0 | 0 | 3111 | 3600 | 3095.33 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249286.45 | GGB | 249289.42 | 2834.5735 | 2685.8161 |  |  |  | 0 | 1 | [10 empty] | 3111 | -261 | 2850 | 2834.5735 | 110.7945 | 2685.8161 |  | 104.98
04.06.2008 04:00 | 3600 | 2 | 764.75 | GGB | 763.37 | 776.344 | 768.864 | 266.41 | GGB | 10838.6 | GGB | 9.79 | GGB | 1012.04 | GGB | 61.79 | GGB | 173011.61 | GGB | 140946.62 | GGB | 0 | 0 | 3084 | 3600 | 3067.82 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249325.92 | GGB | 249328.9 | 2807.5955 | 2681.3555 |  |  |  | 0 | 1 | [10 empty] | 3084 | -261 | 2823 | 2807.5955 | 109.9225 | 2681.3555 |  | 104.98
04.06.2008 05:00 | 3600 | 2 | 764.87 | GGB | 764.835 | 776.273 | 769.963 | 265.49 | GGB | 10874.6 | GGB | 9.8 | GGB | 1011.93 | GGB | 62.05 | GGB | 171832.04 | GGB | 139860.93 | GGB | 0 | 0 | 3095 | 3600 | 3079 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249365.4 | GGB | 249368.38 | 2818.5865 | 2702.1699 |  |  |  | 1 | 1 |  |  |  |  | 139860.93 | 2702.1699 | 139860.93 | 2702.1699 | 9.5726 |  | 3095 | -261 | 2834 | 2818.5865 | 109.5028 | 2702.1699 |  | 104.98
04.06.2008 06:00 | 3600 | 2 | 763.62 | GGB | 763.37 | 775.078 | 768.864 | 265.27 | GGB | 10877.3 | GGB | 9.77 | GGB | 1012.22 | GGB | 62.27 | GGB | 171537.15 | GGB | 139570.54 | GGB | 0 | 0 | 3172 | 3600 | 3156.01 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249404.88 | GGB | 249407.86 | 2895.5237 | 2707.7921 |  |  |  | 0 | 1 | [10 empty] | 3172 | -261 | 2911 | 2895.5237 | 112.2583 | 2707.7921 |  | 104.98
04.06.2008 07:00 | 3600 | 2 | 764.13 | GGB | 764.469 | 777.141 | 769.963 | 265.95 | GGB | 10919.4 | GGB | 9.79 | GGB | 1012.44 | GGB | 61.93 | GGB | 172108.23 | GGB | 140207.49 | GGB | 0 | 0 | 3174 | 3600 | 3157.87 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249444.35 | GGB | 249447.34 | 2897.522 | 2695.4908 |  |  |  | 1 | 1 |  |  |  |  | 140207.49 | 2695.4908 | 140207.49 | 2695.4908 | 9.5726 |  | 3174 | -261 | 2913 | 2897.522 | 112.8484 | 2695.4908 |  | 104.98
04.06.2008 08:00 | 3600 | 2 | 764.43 | GGB | 762.271 | 774.773 | 767.766 | 267.22 | GGB | 10863.8 | GGB | 9.78 | GGB | 1013.33 | GGB | 61.25 | GGB | 173862.17 | GGB | 142049.94 | GGB | 0 | 0 | 3121 | 3600 | 3104.76 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249483.83 | GGB | 249486.82 | 2844.5653 | 2660.5291 |  |  |  | 0 | 1 | [10 empty] | 3121 | -261 | 2860 | 2844.5653 | 112.2418 | 2660.5291 |  | 104.98
04.06.2008 09:00 | 3600 | 2 | 765.08 | GGB | 764.469 | 776.133 | 768.864 | 266.98 | GGB | 10864.2 | GGB | 9.79 | GGB | 1013.37 | GGB | 61.08 | GGB | 173735.63 | GGB | 142024.96 | GGB | 0 | 0 | 3060 | 3600 | 3044.6 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249523.31 | GGB | 249526.3 | 2783.6151 | 2660.9971 |  |  |  | 1 | 1 |  |  |  |  | 142024.96 | 2660.9971 | 142024.96 | 2660.9971 | 9.5726 |  | 3060 | -261 | 2799 | 2783.6151 | 109.8175 | 2660.9971 |  | 104.98
04.06.2008 10:00 | 3600 | 2 | 765.18 | GGB | 764.469 | 776.016 | 768.864 | 266.15 | GGB | 10849.8 | GGB | 9.79 | GGB | 1013.24 | GGB | 61.45 | GGB | 173214.07 | GGB | 141421.98 | GGB | 0 | 0 | 3048 | 3600 | 3032.02 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249562.79 | GGB | 249565.78 | 2771.6249 | 2672.3427 |  |  |  | 1 | 1 |  |  |  |  | 141421.98 | 2672.3427 | 141421.98 | 2672.3427 | 9.5726 |  | 3048 | -261 | 2787 | 2771.6249 | 108.8802 | 2672.3427 |  | 104.98
04.06.2008 11:00 | 3600 | 2 | 765.67 | GGB | 763.37 | 777.047 | 768.864 | 263.58 | GGB | 10861.8 | GGB | 9.8 | GGB | 1012.87 | GGB | 62.25 | GGB | 170333.38 | GGB | 138686.9 | GGB | 0 | 0 | 3041 | 3600 | 3025.71 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249602.26 | GGB | 249605.26 | 2764.6306 | 2725.0447 |  |  |  | 0 | 1 | [10 empty] | 3041 | -261 | 2780 | 2764.6306 | 106.505 | 2725.0447 |  | 104.98
04.06.2008 12:00 | 3600 | 2 | 765.64 | GGB | 764.469 | 777.188 | 769.963 | 262.19 | GGB | 10806.4 | GGB | 9.8 | GGB | 1012.56 | GGB | 62.83 | GGB | 169021.78 | GGB | 137337.91 | GGB | 0 | 0 | 3011 | 3600 | 2995.24 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249641.74 | GGB | 249644.74 | 2734.6551 | 2734.6551 |  |  |  | 1 | 1 |  |  |  |  | 137337.91 | 2734.6551 | 137337.91 | 2734.6551 | 9.513 |  | 3011 | -261 | 2750 | 2734.6551 | 104.3255 |  |  | #VALUE!
04.06.2008 13:00 | 3600 | 2 | 765.61 | GGB | 764.835 | 777.516 | 770.33 | 262.58 | GGB | 10739.5 | GGB | 9.79 | GGB | 1012.45 | GGB | 62.73 | GGB | 169753.51 | GGB | 137961.59 | GGB | 0 | 0 | 2989 | 3600 | 2973.18 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249681.22 | GGB | 249684.22 | 2712.6731 | 2712.6731 |  |  |  | 1 | 1 |  |  |  |  | 137961.59 | 2712.6731 | 137961.59 | 2712.6731 | 9.4793 |  | 2989 | -261 | 2728 | 2712.6731 | 103.9569 |  |  | #VALUE!
04.06.2008 14:00 | 3600 | 2 | 766.53 | GGB | 764.835 | 777.516 | 768.864 | 261.98 | GGB | 10696.6 | GGB | 9.79 | GGB | 1012.19 | GGB | 62.89 | GGB | 169368.39 | GGB | 137545.24 | GGB | 0 | 0 | 2920 | 3600 | 2904.16 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249720.69 | GGB | 249723.7 | 2643.7294 | 2643.7294 |  |  |  | 1 | 1 |  |  |  |  | 137545.24 | 2643.7294 | 137545.24 | 2643.7294 | 9.2105 |  | 2920 | -261 | 2659 | 2643.7294 | 101.009 |  |  | #VALUE!
04.06.2008 15:00 | 3600 | 2 | 766.54 | GGB | 765.934 | 778.477 | 770.696 | 261.52 | GGB | 10680.8 | GGB | 9.79 | GGB | 1012.24 | GGB | 63 | GGB | 168803.91 | GGB | 137052.05 | GGB | 0 | 0 | 2913 | 3600 | 2897.12 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249760.17 | GGB | 249763.18 | 2636.7351 | 2636.7351 |  |  |  | 1 | 1 |  |  |  |  | 137052.05 | 2636.7351 | 137052.05 | 2636.7351 | 9.1532 |  | 2913 | -261 | 2652 | 2636.7351 | 100.3805 |  |  | #VALUE!
04.06.2008 16:00 | 3600 | 2 | 766.22 | GGB | 764.835 | 777.445 | 769.597 | 261.15 | GGB | 10652 | GGB | 9.78 | GGB | 1011.87 | GGB | 63.07 | GGB | 168361.58 | GGB | 136611.34 | GGB | 0 | 0 | 2911 | 3600 | 2895.34 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249799.65 | GGB | 249802.66 | 2634.7367 | 2634.7367 |  |  |  | 1 | 1 |  |  |  |  | 136611.34 | 2634.7367 | 136611.34 | 2634.7367 | 9.1169 |  | 2911 | -261 | 2650 | 2634.7367 | 99.9819 |  |  | #VALUE!
04.06.2008 17:00 | 3600 | 2 | 766.62 | GGB | 764.835 | 777.563 | 769.597 | 260.92 | GGB | 10642.9 | GGB | 9.79 | GGB | 1011.83 | GGB | 63.23 | GGB | 167952.25 | GGB | 136209.54 | GGB | 0 | 0 | 2891 | 3600 | 2875.78 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249839.12 | GGB | 249842.14 | 2614.7531 | 2614.7531 |  |  |  | 1 | 1 |  |  |  |  | 136209.54 | 2614.7531 | 136209.54 | 2614.7531 | 9.0211 |  | 2891 | -261 | 2630 | 2614.7531 | 98.9318 |  |  | #VALUE!
04.06.2008 18:00 | 3600 | 2 | 766.83 | GGB | 765.934 | 778.734 | 771.429 | 260.64 | GGB | 10633 | GGB | 9.79 | GGB | 1011.66 | GGB | 63.38 | GGB | 167793.8 | GGB | 135999.38 | GGB | 0 | 0 | 2879 | 3600 | 2863.33 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249878.6 | GGB | 249881.62 | 2602.7629 | 2602.7629 |  |  |  | 0 | 1 | [10 empty] | 2879 | -261 | 2618 | 2602.7629 | 98.3261 |  |  | #VALUE!
04.06.2008 19:00 | 3600 | 2 | 766.8 | GGB | 767.033 | 779.883 | 773.26 | 260.16 | GGB | 10618.9 | GGB | 9.79 | GGB | 1011.51 | GGB | 63.49 | GGB | 167347.07 | GGB | 135571.91 | GGB | 0 | 0 | 2872 | 3600 | 2856.2 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249918.08 | GGB | 249921.1 | 2595.7686 | 2595.7686 |  |  |  | 0 | 1 | [10 empty] | 2872 | -261 | 2611 | 2595.7686 | 97.7537 |  |  | #VALUE!
04.06.2008 20:00 | 3600 | 2 | 765.74 | GGB | 764.469 | 776.484 | 769.597 | 261.12 | GGB | 10625 | GGB | 9.76 | GGB | 1011.52 | GGB | 63.22 | GGB | 168372.58 | GGB | 136514.07 | GGB | 0 | 0 | 2932 | 3600 | 2916.32 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249957.55 | GGB | 249960.58 | 2655.7196 | 2655.7196 |  |  |  | 1 | 1 |  |  |  |  | 136514.07 | 2655.7196 | 136514.07 | 2655.7196 | 9.183 |  | 2932 | -261 | 2671 | 2655.7196 | 100.7064 |  |  | #VALUE!
04.06.2008 21:00 | 3600 | 2 | 766.31 | GGB | 764.469 | 777.82 | 769.597 | 260.72 | GGB | 10711.5 | GGB | 9.79 | GGB | 1011.51 | GGB | 63.47 | GGB | 167199.62 | GGB | 135462.32 | GGB | 0 | 0 | 2942 | 3600 | 2926.06 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 249997.03 | GGB | 250000.06 | 2665.7114 | 2665.7114 |  |  |  | 1 | 1 |  |  |  |  | 135462.32 | 2665.7114 | 135462.32 | 2665.7114 | 9.1465 |  | 2942 | -261 | 2681 | 2665.7114 | 100.3065 |  |  | #VALUE!
04.06.2008 22:00 | 3600 | 2 | 765.93 | GGB | 764.835 | 777.727 | 770.33 | 260.6 | GGB | 10719.7 | GGB | 9.78 | GGB | 1011.87 | GGB | 63.88 | GGB | 166707.77 | GGB | 134944.54 | GGB | 0 | 0 | 2969 | 3600 | 2953.31 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 250036.51 | GGB | 250039.54 | 2692.6894 | 2692.6894 |  |  |  | 1 | 1 |  |  |  |  | 134944.54 | 2692.6894 | 134944.54 | 2692.6894 | 9.2037 |  | 2969 | -261 | 2708 | 2692.6894 | 100.9344 |  |  | #VALUE!
04.06.2008 23:00 | 3600 | 2 | 764.64 | GGB | 762.271 | 775.523 | 767.766 | 261.91 | GGB | 10746.9 | GGB | 9.76 | GGB | 1012.7 | GGB | 63.57 | GGB | 167826.81 | GGB | 136087.96 | GGB | 0 | 0 | 3056 | 3600 | 3040.4 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 250075.98 | GGB | 250079.02 | 2779.6184 | 2777.0862 |  |  |  | 0 | 1 | [10 empty] | 3056 | -261 | 2795 | 2779.6184 | 105.0757 | 2777.0862 |  | 104.98
04.06.2008 24:00 | 3600 | 2 | 763.96 | GGB | 762.271 | 773.484 | 766.667 | 264.6 | GGB | 10832.6 | GGB | 9.76 | GGB | 1013.66 | GGB | 63 | GGB | 170148.53 | GGB | 138335.82 | GGB | 0 | 0 | 3148 | 3600 | 3132.21 | GGB | 100 | GGB | 39.48 | GGB | 39.48 | GGB | 250115.46 | GGB | 250118.5 | 2871.5433 | 2731.9605 |  |  |  | 0 | 1 | [10 empty] | 3148 | -261 | 2887 | 2871.5433 | 110.3437 | 2731.9605 |  | 104.98
05.06.2008 01:00 | 3600 | 2 | 763.96 | GGB | 764.469 | 776.836 | 768.864 | 266.81 | GGB | 10922.4 | GGB | 9.78 | GGB | 1014.75 | GGB | 62.59 | GGB | 172123.63 | GGB | 140263.41 | GGB | 0 | 0 | 3195 | 3600 | 3179.22 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250154.38 | GGB | 250157.42 | 2918.5049 | 2694.4162 |  |  |  | 1 | 1 |  |  |  |  | 140263.41 | 2694.4162 | 140263.41 | 2694.4162 | 9.7104 |  | 3195 | -261 | 2934 | 2918.5049 | 113.711 | 2694.4162 |  | 104.98
05.06.2008 02:00 | 3600 | 2 | 764.52 | GGB | 764.835 | 776.789 | 768.864 | 268.24 | GGB | 10900 | GGB | 9.78 | GGB | 1015.51 | GGB | 61.69 | GGB | 174477.26 | GGB | 142670.36 | GGB | 0 | 0 | 3147 | 3600 | 3131.61 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250193.31 | GGB | 250196.34 | 2870.5441 | 2648.9595 |  |  |  | 1 | 1 |  |  |  |  | 142670.36 | 2648.9595 | 142670.36 | 2648.9595 | 9.7104 |  | 3147 | -261 | 2886 | 2870.5441 | 113.7615 | 2648.9595 |  | 104.98
05.06.2008 03:00 | 3600 | 2 | 763.99 | GGB | 763.37 | 775.641 | 768.864 | 268.64 | GGB | 10919.4 | GGB | 9.78 | GGB | 1015.47 | GGB | 61.09 | GGB | 175256.3 | GGB | 143558.09 | GGB | 0 | 0 | 3168 | 3600 | 3152.43 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250232.23 | GGB | 250235.26 | 2891.5269 | 2632.5789 |  |  |  | 0 | 1 | [10 empty] | 3168 | -261 | 2907 | 2891.5269 | 115.3061 | 2632.5789 |  | 104.98
05.06.2008 04:00 | 3600 | 2 | 763.28 | GGB | 762.271 | 774.352 | 767.033 | 270.27 | GGB | 10965.9 | GGB | 9.77 | GGB | 1016.09 | GGB | 60.74 | GGB | 176868.29 | GGB | 145121.81 | GGB | 0 | 0 | 3238 | 3600 | 3221.69 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250271.16 | GGB | 250274.18 | 2961.4698 | 2604.2123 |  |  |  | 0 | 1 | [10 empty] | 3238 | -261 | 2977 | 2961.4698 | 119.3816 | 2604.2123 |  | 104.98
05.06.2008 05:00 | 3600 | 2 | 763.34 | GGB | 762.271 | 772.828 | 767.033 | 269.78 | GGB | 11057.6 | GGB | 9.79 | GGB | 1016.17 | GGB | 61.15 | GGB | 175741.54 | GGB | 144030.17 | GGB | 0 | 0 | 3279 | 3600 | 3263.01 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250310.08 | GGB | 250313.1 | 3002.4363 | 2623.9502 |  |  |  | 0 | 1 | [10 empty] | 3279 | -261 | 3018 | 3002.4363 | 120.1226 | 2623.9502 |  | 104.98
05.06.2008 06:00 | 3600 | 2 | 762.14 | GGB | 761.172 | 772.875 | 765.934 | 270.81 | GGB | 11081.8 | GGB | 9.78 | GGB | 1016.76 | GGB | 60.82 | GGB | 177100.46 | GGB | 145369.43 | GGB | 0 | 0 | 3346 | 3600 | 3329.69 | GNB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250349 | GGB | 250352.02 | 3069.3816 | 2599.7763 |  |  |  | 0 | 1 | [10 empty] | 3346 | -261 | 3085 | 3069.3816 | 123.9428 | 2599.7763 |  | 104.98
05.06.2008 07:00 | 3600 | 2 | 763.27 | GGB | 764.469 | 775.242 | 768.498 | 271.17 | GGB | 11064.9 | GGB | 9.8 | GGB | 1016.89 | GGB | 60.61 | GGB | 177563.7 | GGB | 145863.66 | GGB | 0 | 0 | 3293 | 3600 | 3277.44 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250387.93 | GGB | 250390.94 | 3016.4249 | 2590.9675 |  |  |  | 1 | 1 |  |  |  |  | 145863.66 | 2590.9675 | 145863.66 | 2590.9675 | 9.7104 |  | 3293 | -261 | 3032 | 3016.4249 | 122.2185 | 2590.9675 |  | 104.98
05.06.2008 08:00 | 3600 | 2 | 765.02 | GGB | 765.934 | 777.445 | 770.696 | 269.18 | GGB | 11009.9 | GGB | 9.82 | GGB | 1016.7 | GGB | 60.76 | GGB | 175937.4 | GGB | 144433.5 | GGB | 0 | 0 | 3170 | 3600 | 3154.67 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250426.85 | GGB | 250429.86 | 2893.5253 | 2616.6229 |  |  |  | 1 | 1 |  |  |  |  | 144433.5 | 2616.6229 | 144433.5 | 2616.6229 | 9.7104 |  | 3170 | -261 | 2909 | 2893.5253 | 116.0894 | 2616.6229 |  | 104.98
05.06.2008 09:00 | 3600 | 2 | 765.81 | GGB | 765.934 | 777.586 | 770.696 | 265.54 | GGB | 10884.4 | GGB | 9.82 | GGB | 1016.49 | GGB | 61.82 | GGB | 172257.87 | GGB | 140938.36 | GGB | 0 | 0 | 3061 | 3600 | 3045.3 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250465.78 | GGB | 250468.78 | 2784.6143 | 2681.5127 |  |  |  | 1 | 1 |  |  |  |  | 140938.36 | 2681.5127 | 140938.36 | 2681.5127 | 9.7104 |  | 3061 | -261 | 2800 | 2784.6143 | 109.0164 | 2681.5127 |  | 104.98
05.06.2008 10:00 | 3600 | 2 | 766.97 | GGB | 765.934 | 779.133 | 770.696 | 260.81 | GGB | 10769.9 | GGB | 9.81 | GGB | 1015.43 | GGB | 63.65 | GGB | 167003.76 | GGB | 135753.83 | GGB | 0 | 0 | 2961 | 3600 | 2945.67 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250504.7 | GGB | 250507.7 | 2684.6959 | 2684.6959 |  |  |  | 0 | 1 | [10 empty] | 2961 | -261 | 2700 | 2684.6959 | 101.2383 |  |  | #VALUE!
05.06.2008 11:00 | 3600 | 2 | 766.44 | GGB | 765.934 | 779.203 | 771.795 | 260.76 | GGB | 10652.4 | GGB | 9.78 | GGB | 1014.6 | GGB | 63.91 | GGB | 167315.16 | GGB | 135791.89 | GGB | 0 | 0 | 2938 | 3600 | 2922.74 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250543.62 | GGB | 250546.62 | 2661.7147 | 2661.7147 |  |  |  | 0 | 1 | [10 empty] | 2938 | -261 | 2677 | 2661.7147 | 100.3998 |  |  | #VALUE!
05.06.2008 12:00 | 3600 | 2 | 767.45 | GGB | 765.934 | 778.172 | 771.795 | 260.04 | GGB | 10619.5 | GGB | 9.79 | GGB | 1013.84 | GGB | 63.82 | GGB | 166870.62 | GGB | 135366.82 | GGB | 0 | 0 | 2852 | 3600 | 2836.14 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250582.55 | GGB | 250585.54 | 2575.7849 | 2575.7849 |  |  |  | 1 | 1 |  |  |  |  | 135366.82 | 2575.7849 | 135366.82 | 2575.7849 | 8.9588 |  | 2852 | -261 | 2591 | 2575.7849 | 96.8544 |  |  | #VALUE!
05.06.2008 13:00 | 3600 | 2 | 767.4 | GGB | 765.934 | 779.25 | 771.795 | 258.16 | GGB | 10649.9 | GGB | 9.79 | GGB | 1013.44 | GGB | 64.3 | GGB | 165115.58 | GGB | 133697.59 | GGB | 0 | 0 | 2863 | 3600 | 2847.92 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250621.47 | GGB | 250624.46 | 2586.7759 | 2586.7759 |  |  |  | 0 | 1 | [10 empty] | 2863 | -261 | 2602 | 2586.7759 | 96.0683 |  |  | #VALUE!
05.06.2008 14:00 | 3600 | 2 | 767.13 | GGB | 765.934 | 778.031 | 771.795 | 258.82 | GGB | 10602.6 | GGB | 9.78 | GGB | 1013.01 | GGB | 64.1 | GGB | 166239.03 | GGB | 134629.01 | GGB | 0 | 0 | 2861 | 3600 | 2845.75 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250660.39 | GGB | 250663.38 | 2584.7776 | 2584.7776 |  |  |  | 1 | 1 |  |  |  |  | 134629.01 | 2584.7776 | 134629.01 | 2584.7776 | 8.9411 |  | 2861 | -261 | 2600 | 2584.7776 | 96.6628 |  |  | #VALUE!
05.06.2008 15:00 | 3600 | 2 | 768.18 | GGB | 767.033 | 780 | 772.161 | 258.04 | GGB | 10584.6 | GGB | 9.79 | GGB | 1012.62 | GGB | 63.94 | GGB | 165626.14 | GGB | 134146.16 | GGB | 0 | 0 | 2798 | 3600 | 2782.24 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250699.32 | GGB | 250702.3 | 2521.829 | 2521.829 |  |  |  | 0 | 1 | [10 empty] | 2798 | -261 | 2537 | 2521.829 | 93.9705 |  |  | #VALUE!
05.06.2008 16:00 | 3600 | 2 | 767.99 | GGB | 768.132 | 779.789 | 773.26 | 257.02 | GGB | 10553 | GGB | 9.79 | GGB | 1012.16 | GGB | 64.43 | GGB | 164814.09 | GGB | 133235.1 | GGB | 0 | 0 | 2787 | 3600 | 2771.61 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250738.24 | GGB | 250741.22 | 2510.838 | 2510.838 |  |  |  | 0 | 1 | [10 empty] | 2787 | -261 | 2526 | 2510.838 | 92.9255 |  |  | #VALUE!
05.06.2008 17:00 | 3600 | 2 | 767.81 | GGB | 767.033 | 779.461 | 772.161 | 257.17 | GGB | 10501.8 | GGB | 9.77 | GGB | 1011.81 | GGB | 64.31 | GGB | 165171.7 | GGB | 133523.24 | GGB | 0 | 0 | 2762 | 3600 | 2746.25 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250777.17 | GGB | 250780.14 | 2485.8584 | 2485.8584 |  |  |  | 0 | 1 | [10 empty] | 2762 | -261 | 2501 | 2485.8584 | 92.2 |  |  | #VALUE!
05.06.2008 18:00 | 3600 | 2 | 768.29 | GGB | 764.835 | 777.398 | 770.696 | 256.81 | GGB | 10503.3 | GGB | 9.78 | GGB | 1011.28 | GGB | 64.47 | GGB | 164730.46 | GGB | 133035.74 | GGB | 0 | 0 | 2741 | 3600 | 2725.36 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250816.09 | GGB | 250819.06 | 2464.8755 | 2464.8755 |  |  |  | 1 | 1 |  |  |  |  | 133035.74 | 2464.8755 | 133035.74 | 2464.8755 | 8.4254 |  | 2741 | -261 | 2480 | 2464.8755 | 91.0879 |  |  | #VALUE!
05.06.2008 19:00 | 3600 | 2 | 767.87 | GGB | 765.934 | 778.594 | 771.795 | 255.92 | GGB | 10533.4 | GGB | 9.78 | GGB | 1010.82 | GGB | 65.07 | GGB | 163136.08 | GGB | 131454.72 | GGB | 0 | 0 | 2775 | 3600 | 2760.02 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250855.01 | GGB | 250857.98 | 2498.8478 | 2498.8478 |  |  |  | 1 | 1 |  |  |  |  | 131454.72 | 2498.8478 | 131454.72 | 2498.8478 | 8.44 |  | 2775 | -261 | 2514 | 2498.8478 | 91.2459 |  |  | #VALUE!
05.06.2008 20:00 | 3600 | 2 | 767.53 | GGB | 764.835 | 777.68 | 770.696 | 256.24 | GGB | 10539.1 | GGB | 9.77 | GGB | 1010.83 | GGB | 65.21 | GGB | 163340.74 | GGB | 131564.15 | GGB | 0 | 0 | 2806 | 3600 | 2790.13 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250893.94 | GGB | 250896.9 | 2529.8224 | 2529.8224 |  |  |  | 1 | 1 |  |  |  |  | 131564.15 | 2529.8224 | 131564.15 | 2529.8224 | 8.5517 |  | 2806 | -261 | 2545 | 2529.8224 | 92.4539 |  |  | #VALUE!
05.06.2008 21:00 | 3600 | 2 | 767.21 | GGB | 765.934 | 778.758 | 771.795 | 258.1 | GGB | 10544.3 | GGB | 9.77 | GGB | 1011.3 | GGB | 64.54 | GGB | 165206.91 | GGB | 133392.46 | GGB | 0 | 0 | 2819 | 3600 | 2803.29 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250932.86 | GGB | 250935.82 | 2542.8118 | 2542.8118 |  |  |  | 0 | 1 | [10 empty] | 2819 | -261 | 2558 | 2542.8118 | 94.22 |  |  | #VALUE!
05.06.2008 22:00 | 3600 | 2 | 766.75 | GGB | 764.469 | 776.93 | 769.597 | 259.2 | GGB | 10614.6 | GGB | 9.77 | GGB | 1012.04 | GGB | 64.07 | GGB | 166054.17 | GGB | 134362.36 | GGB | 0 | 0 | 2875 | 3600 | 2859.81 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 250971.79 | GGB | 250974.74 | 2598.7661 | 2598.7661 |  |  |  | 1 | 1 |  |  |  |  | 134362.36 | 2598.7661 | 134362.36 | 2598.7661 | 8.9716 |  | 2875 | -261 | 2614 | 2598.7661 | 96.9934 |  |  | #VALUE!
05.06.2008 23:00 | 3600 | 2 | 765.09 | GGB | 763.37 | 777.047 | 768.498 | 261.21 | GGB | 10724.8 | GGB | 9.76 | GGB | 1013.06 | GGB | 63.75 | GGB | 167555.03 | GGB | 135844.79 | GGB | 0 | 0 | 3006 | 3600 | 2989.95 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 251010.71 | GGB | 251013.66 | 2729.6592 | 2729.6592 |  |  |  | 0 | 1 | [10 empty] | 3006 | -261 | 2745 | 2729.6592 | 103.0028 |  |  | #VALUE!
05.06.2008 24:00 | 3600 | 2 | 764.44 | GGB | 763.37 | 775.734 | 768.498 | 263.68 | GGB | 10810.4 | GGB | 9.76 | GGB | 1014.22 | GGB | 63.13 | GGB | 169820.63 | GGB | 138090.37 | GGB | 0 | 0 | 3090 | 3600 | 3074.74 | GGB | 100 | GGB | 38.92 | GGB | 38.92 | GGB | 251049.63 | GGB | 251052.58 | 2813.5906 | 2736.8165 |  |  |  | 0 | 1 | [10 empty] | 3090 | -261 | 2829 | 2813.5906 | 107.9249 | 2736.8165 |  | 104.98
06.06.2008 01:00 | 3600 | 2 | 763.76 | GGB | 763.37 | 775.664 | 768.132 | 264.9 | GGB | 10882.3 | GGB | 9.76 | GGB | 1015.29 | GGB | 62.46 | GGB | 171953.08 | GGB | 140253.13 | GGB | 0 | 0 | 3149 | 3593 | 3133.01 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251087.8 | GGB | 251090.74 | 2872.5424 | 2694.6137 |  |  |  | 0 | 1 | [10 empty] | 3149 | -261 | 2888 | 2872.5424 | 111.912 | 2694.6137 |  | 104.98
06.06.2008 02:00 | 3600 | 2 | 763.11 | GGB | 763.37 | 775.523 | 768.132 | 268.05 | GGB | 10962.6 | GGB | 9.76 | GGB | 1016.29 | GGB | 62.09 | GGB | 173876.47 | GGB | 142116.64 | GGB | 0 | 0 | 3260 | 3600 | 3244.59 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251125.96 | GGB | 251128.9 | 2983.4518 | 2659.2804 |  |  |  | 0 | 1 | [10 empty] | 3260 | -261 | 2999 | 2983.4518 | 117.7773 | 2659.2804 |  | 104.98
06.06.2008 03:00 | 3600 | 2 | 763.05 | GGB | 762.271 | 773.344 | 767.033 | 269.21 | GGB | 11018.3 | GGB | 9.77 | GGB | 1016.9 | GGB | 61.64 | GGB | 175141.86 | GGB | 143430.96 | GGB | 0 | 0 | 3288 | 3600 | 3272.31 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251164.12 | GGB | 251167.06 | 3011.429 | 2634.9123 |  |  |  | 0 | 1 | [10 empty] | 3288 | -261 | 3027 | 3011.429 | 119.9812 | 2634.9123 |  | 104.98
06.06.2008 04:00 | 3600 | 2 | 762.85 | GGB | 763.37 | 775.313 | 768.132 | 270.27 | GGB | 11070.5 | GGB | 9.78 | GGB | 1017.36 | GGB | 61.19 | GGB | 176516.18 | GGB | 144814.99 | GGB | 0 | 0 | 3326 | 3600 | 3309.68 | GNB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251202.29 | GGB | 251205.22 | 3049.398 | 2609.7298 |  |  |  | 0 | 1 | [10 empty] | 3326 | -261 | 3065 | 3049.398 | 122.6663 | 2609.7298 |  | 104.98
06.06.2008 05:00 | 3600 | 2 | 762.13 | GGB | 763.37 | 774.422 | 768.132 | 270.92 | GGB | 11087.7 | GGB | 9.78 | GGB | 1017.51 | GGB | 60.87 | GGB | 177175.28 | GGB | 145518.74 | GGB | 0 | 0 | 3366 | 3600 | 3349.89 | GNB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251240.45 | GGB | 251243.38 | 3089.3653 | 2597.1088 |  |  |  | 0 | 1 | [10 empty] | 3366 | -261 | 3105 | 3089.3653 | 124.8779 | 2597.1088 |  | 104.98
06.06.2008 06:00 | 3600 | 2 | 762.8 | GGB | 763.37 | 774.539 | 768.132 | 271.33 | GGB | 11123.5 | GGB | 9.79 | GGB | 1017.76 | GGB | 60.72 | GGB | 177732.06 | GGB | 146078.14 | GGB | 0 | 0 | 3356 | 3600 | 3339.58 | GNB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251278.61 | GGB | 251281.54 | 3079.3735 | 2587.1633 |  |  |  | 0 | 1 | [10 empty] | 3356 | -261 | 3095 | 3079.3735 | 124.9525 | 2587.1633 |  | 104.98
06.06.2008 07:00 | 3600 | 2 | 763.58 | GGB | 763.37 | 774.516 | 767.033 | 270.4 | GGB | 11126 | GGB | 9.8 | GGB | 1017.97 | GGB | 60.84 | GGB | 177204.99 | GGB | 145621.35 | GGB | 0 | 0 | 3332 | 3600 | 3316.08 | GNB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251316.77 | GGB | 251319.7 | 3055.3931 | 2595.2788 |  |  |  | 0 | 1 | [10 empty] | 3332 | -261 | 3071 | 3055.3931 | 123.5918 | 2595.2788 |  | 104.98
06.06.2008 08:00 | 3600 | 2 | 764.88 | GGB | 763.37 | 775.664 | 768.498 | 267.47 | GGB | 11049.2 | GGB | 9.82 | GGB | 1017.74 | GGB | 61.59 | GGB | 173808.25 | GGB | 142475.5 | GGB | 0 | 0 | 3210 | 3600 | 3194.44 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251354.94 | GGB | 251357.86 | 2933.4927 | 2652.5824 |  |  |  | 0 | 1 | [10 empty] | 3210 | -261 | 2949 | 2933.4927 | 116.0975 | 2652.5824 |  | 104.98
06.06.2008 09:00 | 3600 | 2 | 765.78 | GGB | 764.835 | 776.906 | 769.597 | 263.58 | GGB | 10906.5 | GGB | 9.82 | GGB | 1017.15 | GGB | 62.55 | GGB | 170024.19 | GGB | 138898.43 | GGB | 0 | 0 | 3010 | 3208 | 2994.45 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251393.1 | GGB | 251396.02 | 2994.45 | 2720.8947 |  |  |  | 1 | 1 |  |  |  |  | 138898.43 | 2720.8947 | 138898.43 | 2720.8947 | 9.9038 | [5 empty] | 115.5346 | 2720.8947 |  | 104.98
06.06.2008 10:00 | 3600 | 2 | 766.56 | GGB | 763.37 | 775.828 | 768.498 | 260.55 | GGB | 10765.5 | GGB | 9.8 | GGB | 1016.07 | GGB | 63.69 | GGB | 166917.94 | GGB | 135755.38 | GGB | 0 | 0 | 2750 | 3600 | 2734.51 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251431.26 | GGB | 251434.18 | 2734.51 | 2734.51 |  |  |  | 0 | 1 | [14 empty] | 103.1179 |  |  | #VALUE!
06.06.2008 11:00 | 3600 | 2 | 766.52 | GGB | 765.934 | 778.711 | 771.795 | 258.34 | GGB | 10646.2 | GGB | 9.8 | GGB | 1015.13 | GGB | 64.65 | GGB | 164841.6 | GGB | 133560.99 | GGB | 0 | 0 | 2645 | 3600 | 2629.81 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251469.43 | GGB | 251472.34 | 2629.81 | 2629.81 |  |  |  | 0 | 1 | [14 empty] | 97.5667 |  |  | #VALUE!
06.06.2008 12:00 | 3600 | 2 | 767.1 | GGB | 768.132 | 780.609 | 773.626 | 256.73 | GGB | 10573.6 | GGB | 9.79 | GGB | 1013.85 | GGB | 64.93 | GGB | 163668.64 | GGB | 132332.17 | GGB | 0 | 0 | 2588 | 3600 | 2572.33 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251507.59 | GGB | 251510.5 | 2572.33 | 2572.33 |  |  |  | 0 | 1 | [14 empty] | 94.5561 |  |  | #VALUE!
06.06.2008 13:00 | 3600 | 2 | 767.35 | GGB | 767.033 | 779.508 | 772.527 | 256.22 | GGB | 10556.9 | GGB | 9.79 | GGB | 1012.95 | GGB | 64.95 | GGB | 163476.08 | GGB | 132052.58 | GGB | 0 | 0 | 2572 | 3600 | 2556.48 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251545.75 | GGB | 251548.66 | 2556.48 | 2556.48 |  |  |  | 0 | 1 | [14 empty] | 93.7749 |  |  | #VALUE!
06.06.2008 14:00 | 3600 | 2 | 767.62 | GGB | 767.033 | 779.156 | 772.527 | 254.87 | GGB | 10509.2 | GGB | 9.78 | GGB | 1012.22 | GGB | 65.26 | GGB | 162247 | GGB | 130844.7 | GGB | 0 | 0 | 2531 | 3600 | 2515.36 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251583.91 | GGB | 251586.82 | 2515.36 | 2515.36 |  |  |  | 0 | 1 | [14 empty] | 91.4226 |  |  | #VALUE!
06.06.2008 15:00 | 3600 | 2 | 767.93 | GGB | 765.934 | 778.898 | 771.429 | 254.11 | GGB | 10472.6 | GGB | 9.78 | GGB | 1011.29 | GGB | 65.71 | GGB | 161669.32 | GGB | 130086.07 | GGB | 0 | 0 | 2496 | 3600 | 2480.79 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251622.08 | GGB | 251624.98 | 2480.79 | 2480.79 |  |  |  | 0 | 1 | [14 empty] | 89.6434 |  |  | #VALUE!
06.06.2008 16:00 | 3600 | 2 | 768.03 | GGB | 767.033 | 779.766 | 772.161 | 253.72 | GGB | 10457.6 | GGB | 9.78 | GGB | 1010.23 | GGB | 65.87 | GGB | 161274.3 | GGB | 129571.4 | GGB | 0 | 0 | 2478 | 3600 | 2462.61 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251660.24 | GGB | 251663.14 | 2462.61 | 2462.61 |  |  |  | 0 | 1 | [14 empty] | 88.6344 |  |  | #VALUE!
06.06.2008 17:00 | 3600 | 2 | 767.69 | GGB | 765.934 | 778.969 | 771.795 | 253.23 | GGB | 10434 | GGB | 9.77 | GGB | 1009.73 | GGB | 66 | GGB | 160809.96 | GGB | 129085.58 | GGB | 0 | 0 | 2475 | 3600 | 2459.7 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251698.4 | GGB | 251701.3 | 2459.7 | 2459.7 |  |  |  | 0 | 1 | [14 empty] | 88.1977 |  |  | #VALUE!
06.06.2008 18:00 | 3600 | 2 | 767.75 | GGB | 765.934 | 779.016 | 772.161 | 253.58 | GGB | 10439.8 | GGB | 9.77 | GGB | 1009.24 | GGB | 65.85 | GGB | 160960.71 | GGB | 129197.64 | GGB | 0 | 0 | 2453 | 3600 | 2438.09 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251736.57 | GGB | 251739.46 | 2438.09 | 2438.09 |  |  |  | 0 | 1 | [14 empty] | 87.4987 |  |  | #VALUE!
06.06.2008 19:00 | 3600 | 2 | 767.87 | GGB | 765.934 | 779.016 | 772.161 | 253.95 | GGB | 10425.6 | GGB | 9.77 | GGB | 1008.8 | GGB | 65.46 | GGB | 161707.84 | GGB | 129891.73 | GGB | 0 | 0 | 2432 | 3600 | 2416.64 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251774.73 | GGB | 251777.62 | 2416.64 | 2416.64 |  |  |  | 0 | 1 | [14 empty] | 87.1949 |  |  | #VALUE!
06.06.2008 20:00 | 3600 | 2 | 767.35 | GGB | 765.934 | 778.992 | 772.161 | 255.16 | GGB | 10419.2 | GGB | 9.76 | GGB | 1008.85 | GGB | 64.94 | GGB | 162710.24 | GGB | 130903.57 | GGB | 0 | 0 | 2428 | 3600 | 2412.59 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251812.89 | GGB | 251815.78 | 2412.59 | 2412.59 |  |  |  | 0 | 1 | [14 empty] | 87.7268 |  |  | #VALUE!
06.06.2008 21:00 | 3600 | 2 | 767.55 | GGB | 767.033 | 780.117 | 773.26 | 255.45 | GGB | 10471.2 | GGB | 9.77 | GGB | 1008.8 | GGB | 64.58 | GGB | 162917.11 | GGB | 131204.6 | GGB | 0 | 0 | 2387 | 3600 | 2372.17 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251851.05 | GGB | 251853.94 | 2372.17 | 2372.17 |  |  |  | 0 | 1 | [14 empty] | 86.4554 |  |  | #VALUE!
06.06.2008 22:00 | 3600 | 2 | 766.21 | GGB | 763.37 | 775.852 | 768.498 | 255.79 | GGB | 10526.9 | GGB | 9.75 | GGB | 1009.36 | GGB | 64.96 | GGB | 162533.09 | GGB | 130819.84 | GGB | 0 | 0 | 2443 | 3600 | 2428.11 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251889.22 | GGB | 251892.1 | 2428.11 | 2428.11 |  |  |  | 0 | 1 | [14 empty] | 88.2347 |  |  | #VALUE!
06.06.2008 23:00 | 3600 | 2 | 765.39 | GGB | 762.271 | 774.703 | 768.498 | 258.72 | GGB | 10594.7 | GGB | 9.75 | GGB | 1010.32 | GGB | 64.41 | GGB | 165023.15 | GGB | 133166.27 | GGB | 0 | 0 | 2526 | 3600 | 2510.4 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251927.38 | GGB | 251930.26 | 2510.4 | 2510.4 |  |  |  | 0 | 1 | [14 empty] | 92.8613 |  |  | #VALUE!
06.06.2008 24:00 | 3600 | 2 | 764.17 | GGB | 762.271 | 774.727 | 767.033 | 262.6 | GGB | 10691.2 | GGB | 9.75 | GGB | 1011.21 | GGB | 62.97 | GGB | 169599.46 | GGB | 137566.62 | GGB | 0 | 0 | 2674 | 3600 | 2658.45 | GGB | 100 | GGB | 38.16 | GGB | 38.16 | GGB | 251965.54 | GGB | 251968.42 | 2658.45 | 2658.45 |  |  |  | 0 | 1 | [14 empty] | 101.5872 |  |  | #VALUE!
07.06.2008 01:00 | 3600 | 2 | 764.22 | GGB | 764.469 | 775.641 | 768.132 | 264.18 | GGB | 10803.9 | GGB | 9.77 | GGB | 1011.95 | GGB | 63.16 | GGB | 169893.25 | GGB | 137831.73 | GGB | 0 | 0 | 2767 | 3600 | 2751.71 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252004.39 | GGB | 252007.27 | 2751.71 | 2741.9521 |  |  |  | 1 | 1 |  |  |  |  | 137831.73 | 2741.9521 | 137831.73 | 2741.9521 | 9.7279 | [5 empty] | 105.3536 | 2741.9521 |  | 104.98
07.06.2008 02:00 | 3600 | 2 | 763.32 | GGB | 764.469 | 775.641 | 768.132 | 266.42 | GGB | 10839.6 | GGB | 9.76 | GGB | 1012.43 | GGB | 62.56 | GGB | 172427.33 | GGB | 140203.18 | GGB | 0 | 0 | 2852 | 3600 | 2836.12 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252043.24 | GGB | 252046.12 | 2836.12 | 2695.5737 |  |  |  | 1 | 1 |  |  |  |  | 140203.18 | 2695.5737 | 140203.18 | 2695.5737 | 9.7279 | [5 empty] | 110.4536 | 2695.5737 |  | 104.98
07.06.2008 03:00 | 3600 | 2 | 763.77 | GGB | 763.37 | 774.469 | 767.033 | 267.82 | GGB | 10887.7 | GGB | 9.77 | GGB | 1013.2 | GGB | 61.96 | GGB | 174165.86 | GGB | 141975.71 | GGB | 0 | 0 | 2873 | 3600 | 2857.6 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252082.09 | GGB | 252084.97 | 2857.6 | 2661.9201 |  |  |  | 0 | 1 | [14 empty] | 112.6972 | 2661.9201 |  | 104.98
07.06.2008 04:00 | 3600 | 2 | 763.37 | GGB | 762.271 | 774.328 | 767.033 | 267.35 | GGB | 10952.1 | GGB | 9.78 | GGB | 1013.44 | GGB | 62.01 | GGB | 173368.12 | GGB | 141340.86 | GGB | 0 | 0 | 2932 | 3600 | 2916.59 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252120.94 | GGB | 252123.82 | 2916.59 | 2673.8765 |  |  |  | 0 | 1 | [14 empty] | 114.5093 | 2673.8765 |  | 104.98
07.06.2008 05:00 | 3600 | 2 | 762.64 | GGB | 762.271 | 774.234 | 767.033 | 269.52 | GGB | 10944.2 | GGB | 9.77 | GGB | 1014.18 | GGB | 61.03 | GGB | 176190.48 | GGB | 144167.08 | GGB | 0 | 0 | 2985 | 3600 | 2968.9 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252159.79 | GGB | 252162.67 | 2968.9 | 2621.4584 |  |  |  | 0 | 1 | [14 empty] | 118.8938 | 2621.4584 |  | 104.98
07.06.2008 06:00 | 3600 | 2 | 763.72 | GGB | 763.37 | 775.523 | 767.033 | 268.5 | GGB | 11006.3 | GGB | 9.8 | GGB | 1014.06 | GGB | 61.43 | GGB | 174805.16 | GGB | 142845.76 | GGB | 0 | 0 | 2970 | 3600 | 2953.94 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252198.64 | GGB | 252201.52 | 2953.94 | 2645.7068 |  |  |  | 0 | 1 | [14 empty] | 117.2105 | 2645.7068 |  | 104.98
07.06.2008 07:00 | 3600 | 2 | 763.52 | GGB | 764.835 | 776.742 | 769.597 | 268.68 | GGB | 10945.1 | GGB | 9.79 | GGB | 1014.12 | GGB | 61.39 | GGB | 175430.15 | GGB | 143381.42 | GGB | 0 | 0 | 2969 | 3600 | 2953.44 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252237.49 | GGB | 252240.37 | 2953.44 | 2635.8227 |  |  |  | 1 | 1 |  |  |  |  | 143381.42 | 2635.8227 | 143381.42 | 2635.8227 | 9.7279 | [5 empty] | 117.6301 | 2635.8227 |  | 104.98
07.06.2008 08:00 | 3600 | 2 | 765.46 | GGB | 765.934 | 777.938 | 770.696 | 265.67 | GGB | 10877.2 | GGB | 9.82 | GGB | 1013.46 | GGB | 61.99 | GGB | 172304.09 | GGB | 140481.66 | GGB | 0 | 0 | 2843 | 3600 | 2827.93 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252276.34 | GGB | 252279.22 | 2827.93 | 2690.2302 |  |  |  | 1 | 1 |  |  |  |  | 140481.66 | 2690.2302 | 140481.66 | 2690.2302 | 9.7279 | [5 empty] | 110.3534 | 2690.2302 |  | 104.98
07.06.2008 09:00 | 3600 | 2 | 766.06 | GGB | 764.835 | 776.953 | 769.597 | 261.21 | GGB | 10762.4 | GGB | 9.81 | GGB | 1012.51 | GGB | 63.3 | GGB | 167560.53 | GGB | 135956.85 | GGB | 0 | 0 | 2751 | 3600 | 2735.3 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252315.19 | GGB | 252318.07 | 2735.3 | 2735.3 |  |  |  | 1 | 1 |  |  |  |  | 135956.85 | 2735.3 | 135956.85 | 2735.3 | 9.5723 | [5 empty] | 103.3008 |  |  | #VALUE!
07.06.2008 10:00 | 3600 | 2 | 766.29 | GGB | 767.033 | 779.156 | 771.795 | 257.77 | GGB | 10622.2 | GGB | 9.8 | GGB | 1011.51 | GGB | 64.83 | GGB | 163794.08 | GGB | 132167.87 | GGB | 0 | 0 | 2676 | 3600 | 2660.78 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252354.04 | GGB | 252356.92 | 2660.78 | 2660.78 |  |  |  | 0 | 1 | [14 empty] | 97.686 |  |  | #VALUE!
07.06.2008 11:00 | 3600 | 2 | 767.14 | GGB | 767.033 | 779.156 | 771.795 | 255.51 | GGB | 10524 | GGB | 9.79 | GGB | 1010.67 | GGB | 65.56 | GGB | 161816.77 | GGB | 130181.58 | GGB | 0 | 0 | 2595 | 3600 | 2579.95 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252392.89 | GGB | 252395.77 | 2579.95 | 2579.95 |  |  |  | 0 | 1 | [14 empty] | 93.295 |  |  | #VALUE!
07.06.2008 12:00 | 3600 | 2 | 767.05 | GGB | 765.934 | 778.102 | 771.795 | 254.47 | GGB | 10475.5 | GGB | 9.78 | GGB | 1009.62 | GGB | 65.76 | GGB | 161247.9 | GGB | 129514.36 | GGB | 0 | 0 | 2551 | 3600 | 2535.78 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252431.74 | GGB | 252434.62 | 2535.78 | 2535.78 |  |  |  | 1 | 1 |  |  |  |  | 129514.36 | 2535.78 | 129514.36 | 2535.78 | 8.4535 | [5 empty] | 91.2278 |  |  | #VALUE!
07.06.2008 13:00 | 3600 | 2 | 767.5 | GGB | 765.934 | 778.945 | 772.161 | 254.89 | GGB | 10426.8 | GGB | 9.78 | GGB | 1008.99 | GGB | 65.48 | GGB | 162160.08 | GGB | 130273.46 | GGB | 0 | 0 | 2517 | 3600 | 2501.65 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252470.59 | GGB | 252473.47 | 2501.65 | 2501.65 |  |  |  | 0 | 1 | [14 empty] | 90.5274 |  |  | #VALUE!
07.06.2008 14:00 | 3600 | 2 | 767.69 | GGB | 764.835 | 778.734 | 770.696 | 253.08 | GGB | 10416.4 | GGB | 9.78 | GGB | 1008.51 | GGB | 65.92 | GGB | 160479.86 | GGB | 128695.1 | GGB | 0 | 0 | 2482 | 3600 | 2466.37 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252509.44 | GGB | 252512.32 | 2466.37 | 2466.37 |  |  |  | 0 | 1 | [14 empty] | 88.1694 |  |  | #VALUE!
07.06.2008 15:00 | 3600 | 2 | 767.72 | GGB | 765.934 | 778.992 | 771.795 | 252.39 | GGB | 10412.2 | GGB | 9.77 | GGB | 1007.72 | GGB | 65.98 | GGB | 159837.26 | GGB | 128053.55 | GGB | 0 | 0 | 2462 | 3600 | 2446.34 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252548.29 | GGB | 252551.17 | 2446.34 | 2446.34 |  |  |  | 0 | 1 | [14 empty] | 87.0174 |  |  | #VALUE!
07.06.2008 16:00 | 3600 | 2 | 767.69 | GGB | 765.934 | 779.063 | 771.795 | 252.1 | GGB | 10405 | GGB | 9.77 | GGB | 1007.46 | GGB | 66.14 | GGB | 159578.68 | GGB | 127754.61 | GGB | 0 | 0 | 2433 | 3600 | 2417.62 | GGB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252587.14 | GGB | 252590.02 | 2417.62 | 2417.62 |  |  |  | 0 | 1 | [14 empty] | 85.795 |  |  | #VALUE!
07.06.2008 17:00 | 3600 | 2 | 767.82 | GGB | 767.033 | 780.117 | 772.161 | 251.67 | GGB | 10393.7 | GGB | 9.77 | GGB | 1007.09 | GGB | 66.3 | GGB | 159309.1 | GGB | 127433.43 | GGB | 0 | 0 | 2402 | 1372 | 1371.88 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252625.99 | GGB | 252628.87 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
07.06.2008 18:00 | 3600 | 2 | 768.01 | GGB | 765.934 | 779.016 | 771.795 | 251.45 | GGB | 10381.8 | GGB | 9.77 | GGB | 1006.33 | GGB | 66.39 | GGB | 158841.46 | GGB | 126927.58 | GGB | 0 | 0 | 0 | 0 | 1377.35 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252664.84 | GGB | 252667.72 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
07.06.2008 19:00 | 3600 | 2 | 767.83 | GGB | 765.934 | 779.016 | 771.795 | 252.15 | GGB | 10380.9 | GGB | 9.76 | GGB | 1006.27 | GGB | 66.11 | GGB | 159269.49 | GGB | 127367.63 | GGB | 0 | 0 | 0 | 0 | 1372.59 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252703.69 | GGB | 252706.57 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
07.06.2008 20:00 | 3600 | 2 | 767.83 | GGB | 765.934 | 778.875 | 771.795 | 252.89 | GGB | 10404.5 | GGB | 9.76 | GGB | 1006.2 | GGB | 65.73 | GGB | 159968.2 | GGB | 128061.98 | GGB | 0 | 0 | 0 | 0 | 1365.15 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252742.54 | GGB | 252745.42 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
07.06.2008 21:00 | 3600 | 2 | 767.49 | GGB | 764.469 | 776.438 | 769.597 | 254.05 | GGB | 10416.8 | GGB | 9.76 | GGB | 1006.59 | GGB | 65.4 | GGB | 161158.77 | GGB | 129191.41 | GGB | 0 | 0 | 0 | 0 | 1353.21 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252781.38 | GGB | 252784.27 | 1353.2246 | 1353.2246 |  |  |  | 1 | 1 |  |  |  |  | 129191.41 | 1353.2246 | 129191.41 |  | 4.5 | 1353.2246 |  |  |  |  | 48.5625 |  |  | #VALUE!
07.06.2008 22:00 | 3600 | 2 | 767.15 | GGB | 763.37 | 776.297 | 768.498 | 256.08 | GGB | 10450.6 | GGB | 9.75 | GGB | 1007.27 | GGB | 64.41 | GGB | 163662.04 | GGB | 131673.06 | GGB | 0 | 0 | 0 | 0 | 1327.71 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252820.23 | GGB | 252823.12 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
07.06.2008 23:00 | 3600 | 2 | 765.95 | GGB | 763.37 | 776.25 | 768.498 | 257.66 | GGB | 10586.8 | GGB | 9.75 | GGB | 1008.42 | GGB | 64.53 | GGB | 164085.67 | GGB | 132115.54 | GGB | 0 | 0 | 0 | 0 | 1323.26 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252859.08 | GGB | 252861.97 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
07.06.2008 24:00 | 3600 | 2 | 764.92 | GGB | 764.469 | 777.445 | 770.696 | 259.52 | GGB | 10682.3 | GGB | 9.76 | GGB | 1009.2 | GGB | 63.83 | GGB | 166309.45 | GGB | 134287.21 | GGB | 0 | 0 | 0 | 0 | 1301.86 | GNB | 100 | GGB | 38.85 | GGB | 38.85 | GGB | 252897.93 | GGB | 252900.82 | 1301.8738 | 1301.8738 |  |  |  | 1 | 1 |  |  |  |  | 134287.21 | 1301.8738 | 134287.21 |  | 4.5 | 1301.8738 |  |  |  |  | 48.5625 |  |  | #VALUE!
08.06.2008 01:00 | 3600 | 2 | 765.3 | GGB | 764.469 | 776.648 | 769.597 | 260.36 | GGB | 10703.7 | GGB | 9.77 | GGB | 1010.1 | GGB | 63.99 | GGB | 166105.89 | GGB | 134178.86 | GGB | 0 | 0 | 0 | 0 | 1311.11 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 252937.03 | GGB | 252939.91 | 1310.974 | 1310.974 |  |  |  | 1 | 1 |  |  |  |  | 134178.86 | 1310.974 | 134178.86 |  | 4.5 | 1310.974 |  |  |  |  | 48.8625 |  |  | #VALUE!
08.06.2008 02:00 | 3600 | 2 | 764.15 | GGB | 763.37 | 775.734 | 768.132 | 261.42 | GGB | 10721.9 | GGB | 9.75 | GGB | 1010.82 | GGB | 63.72 | GGB | 167150.11 | GGB | 135226.05 | GGB | 0 | 0 | 0 | 0 | 1300.96 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 252976.12 | GGB | 252979 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 03:00 | 3600 | 2 | 764.54 | GGB | 762.271 | 774.703 | 767.033 | 262.05 | GGB | 10773.7 | GGB | 9.77 | GGB | 1011.64 | GGB | 63.5 | GGB | 167742.09 | GGB | 135905.92 | GGB | 0 | 0 | 0 | 0 | 1294.45 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253015.22 | GGB | 253018.09 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 04:00 | 3600 | 2 | 763.81 | GGB | 762.271 | 774.375 | 767.033 | 263.4 | GGB | 10804.1 | GGB | 9.76 | GGB | 1012.41 | GGB | 63.04 | GGB | 169514.73 | GGB | 137634.25 | GGB | 0 | 0 | 0 | 0 | 1278.19 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253054.31 | GGB | 253057.18 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 05:00 | 3600 | 2 | 763.41 | GGB | 763.37 | 775.336 | 768.132 | 265.67 | GGB | 10878.2 | GGB | 9.76 | GGB | 1013.07 | GGB | 62.5 | GGB | 171998.2 | GGB | 139967.59 | GGB | 0 | 0 | 0 | 0 | 1256.88 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253093.4 | GGB | 253096.27 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 06:00 | 3600 | 2 | 763.48 | GGB | 763.37 | 775.336 | 768.132 | 268.03 | GGB | 10894.3 | GGB | 9.77 | GGB | 1013.84 | GGB | 61.31 | GGB | 175053.83 | GGB | 143069.17 | GGB | 0 | 0 | 0 | 0 | 1229.64 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253132.5 | GGB | 253135.36 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 07:00 | 3600 | 2 | 765.19 | GGB | 763.37 | 776.391 | 768.498 | 265.65 | GGB | 10926.3 | GGB | 9.81 | GGB | 1014.21 | GGB | 61.77 | GGB | 172608.88 | GGB | 140927.15 | GGB | 0 | 0 | 0 | 0 | 1248.33 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253171.59 | GGB | 253174.45 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 08:00 | 3600 | 2 | 764.64 | GGB | 763.37 | 776.32 | 768.498 | 263.38 | GGB | 10871.5 | GGB | 9.79 | GGB | 1014.17 | GGB | 62.45 | GGB | 170339.99 | GGB | 138787.61 | GGB | 0 | 0 | 0 | 0 | 1267.57 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253210.69 | GGB | 253213.54 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 09:00 | 3600 | 2 | 765.15 | GGB | 763.37 | 776.32 | 768.498 | 262.04 | GGB | 10821.4 | GGB | 9.8 | GGB | 1014.07 | GGB | 62.9 | GGB | 168930.45 | GGB | 137443.14 | GGB | 0 | 0 | 0 | 0 | 1279.97 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253249.78 | GGB | 253252.63 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 10:00 | 3600 | 2 | 765.34 | GGB | 763.37 | 776.18 | 768.498 | 261.07 | GGB | 10759.8 | GGB | 9.79 | GGB | 1013.73 | GGB | 63.49 | GGB | 167684.87 | GGB | 136144.47 | GGB | 0 | 0 | 0 | 0 | 1292.18 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253288.87 | GGB | 253291.72 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 11:00 | 3600 | 2 | 765.87 | GGB | 764.469 | 776.977 | 769.597 | 260.02 | GGB | 10708.9 | GGB | 9.79 | GGB | 1012.99 | GGB | 64.18 | GGB | 166396.38 | GGB | 134722.6 | GGB | 0 | 0 | 0 | 0 | 1305.82 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253327.97 | GGB | 253330.81 | 1305.6829 | 1305.6829 |  |  |  | 1 | 1 |  |  |  |  | 134722.6 | 1305.6829 | 134722.6 |  | 4.5 | 1305.6829 |  |  |  |  | 48.8625 |  |  | #VALUE!
08.06.2008 12:00 | 3600 | 2 | 766.69 | GGB | 764.835 | 778.078 | 770.696 | 258.1 | GGB | 10643.8 | GGB | 9.8 | GGB | 1012.42 | GGB | 64.79 | GGB | 164565.41 | GGB | 132924.51 | GGB | 0 | 0 | 0 | 0 | 1323.48 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253367.06 | GGB | 253369.9 | 1323.3451 | 1323.3451 |  |  |  | 1 | 1 |  |  |  |  | 132924.51 | 1323.3451 | 132924.51 |  | 4.5 | 1323.3451 |  |  |  |  | 48.8625 |  |  | #VALUE!
08.06.2008 13:00 | 3600 | 2 | 766.81 | GGB | 765.934 | 779.25 | 770.696 | 257.5 | GGB | 10546.2 | GGB | 9.78 | GGB | 1012.13 | GGB | 64.85 | GGB | 164222.11 | GGB | 132583.96 | GGB | 0 | 0 | 0 | 0 | 1326.88 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253406.16 | GGB | 253408.99 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 14:00 | 3600 | 2 | 768.04 | GGB | 768.132 | 781.242 | 774.359 | 256.9 | GGB | 10522.6 | GGB | 9.8 | GGB | 1011.57 | GGB | 65.24 | GGB | 163282.42 | GGB | 131602.09 | GGB | 0 | 0 | 0 | 0 | 1336.78 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253445.25 | GGB | 253448.08 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 15:00 | 3600 | 2 | 768.38 | GGB | 767.033 | 779.906 | 773.26 | 254.84 | GGB | 10496.6 | GGB | 9.79 | GGB | 1010.61 | GGB | 66.64 | GGB | 160940.9 | GGB | 129057.76 | GGB | 0 | 0 | 0 | 0 | 1363.13 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253484.34 | GGB | 253487.17 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 16:00 | 3600 | 2 | 768.2 | GGB | 768.132 | 781.055 | 773.26 | 255.02 | GGB | 10485.2 | GGB | 9.79 | GGB | 1009.89 | GGB | 66.63 | GGB | 160904.59 | GGB | 128940.99 | GGB | 0 | 0 | 0 | 0 | 1364.37 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253523.44 | GGB | 253526.26 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 17:00 | 3600 | 2 | 768.67 | GGB | 768.132 | 781.031 | 773.26 | 254.48 | GGB | 10463 | GGB | 9.79 | GGB | 1009.32 | GGB | 67.07 | GGB | 160387.43 | GGB | 128285.92 | GGB | 0 | 0 | 0 | 0 | 1371.34 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253562.53 | GGB | 253565.35 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 18:00 | 3600 | 2 | 768.96 | GGB | 767.033 | 780.047 | 773.626 | 254.31 | GGB | 10448.5 | GGB | 9.79 | GGB | 1008.98 | GGB | 67.05 | GGB | 160189.37 | GGB | 128093.28 | GGB | 0 | 0 | 0 | 0 | 1373.4 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253601.63 | GGB | 253604.44 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 19:00 | 3600 | 2 | 769.07 | GGB | 767.033 | 780 | 772.161 | 255.49 | GGB | 10432.3 | GGB | 9.79 | GGB | 1008.91 | GGB | 66.52 | GGB | 162117.16 | GGB | 129829.79 | GGB | 0 | 0 | 0 | 0 | 1355.03 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253640.72 | GGB | 253643.53 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 20:00 | 3600 | 2 | 768.69 | GGB | 767.033 | 778.875 | 772.161 | 254.76 | GGB | 10463.8 | GGB | 9.78 | GGB | 1008.58 | GGB | 66.47 | GGB | 161078.44 | GGB | 128972.01 | GGB | 0 | 0 | 0 | 0 | 1364.04 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253679.81 | GGB | 253682.62 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 21:00 | 3600 | 2 | 768.05 | GGB | 767.033 | 778.828 | 772.161 | 255.58 | GGB | 10508.6 | GGB | 9.78 | GGB | 1008.67 | GGB | 65.95 | GGB | 161666.02 | GGB | 129653.08 | GGB | 0 | 0 | 0 | 0 | 1356.88 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253718.91 | GGB | 253721.71 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 22:00 | 3600 | 2 | 767.49 | GGB | 765.934 | 778.711 | 770.696 | 256.88 | GGB | 10568.7 | GGB | 9.78 | GGB | 1009.31 | GGB | 65.49 | GGB | 162895.1 | GGB | 130899.36 | GGB | 0 | 0 | 0 | 0 | 1343.96 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253758 | GGB | 253760.8 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
08.06.2008 23:00 | 3600 | 2 | 766.6 | GGB | 764.469 | 777.727 | 770.696 | 259.01 | GGB | 10649.3 | GGB | 9.77 | GGB | 1010.18 | GGB | 64.84 | GGB | 164605.03 | GGB | 132642.41 | GGB | 0 | 0 | 0 | 0 | 1326.3 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253797.1 | GGB | 253799.89 | 1326.1596 | 1326.1596 |  |  |  | 1 | 1 |  |  |  |  | 132642.41 | 1326.1596 | 132642.41 |  | 4.5 | 1326.1596 |  |  |  |  | 48.8625 |  |  | #VALUE!
08.06.2008 24:00 | 3600 | 2 | 765.28 | GGB | 763.37 | 775.453 | 768.132 | 261.68 | GGB | 10742.7 | GGB | 9.76 | GGB | 1010.97 | GGB | 64.11 | GGB | 166917.94 | GGB | 134902.08 | GGB | 0 | 0 | 0 | 0 | 1304.08 | GNB | 100 | GGB | 39.09 | GGB | 39.09 | GGB | 253836.19 | GGB | 253838.98 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
09.06.2008 01:00 | 3600 | 2 | 765.08 | GGB | 764.469 | 776.555 | 768.132 | 263.9 | GGB | 10827.6 | GGB | 9.78 | GGB | 1011.51 | GGB | 63.6 | GGB | 168944.76 | GGB | 136823.79 | GGB | 0 | 0 | 0 | 0 | 1263.96 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 253874.62 | GGB | 253877.41 | 1263.9249 | 1263.9249 |  |  |  | 1 | 1 |  |  |  |  | 136823.79 | 1263.9249 | 136823.79 |  | 4.5 | 1263.9249 |  |  |  |  | 48.0375 |  |  | #VALUE!
09.06.2008 02:00 | 3600 | 2 | 764.88 | GGB | 764.469 | 776.344 | 769.597 | 265.05 | GGB | 10893.9 | GGB | 9.79 | GGB | 1012.03 | GGB | 63.25 | GGB | 170457.72 | GGB | 138263.47 | GGB | 0 | 0 | 0 | 0 | 1250.8 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 253913.05 | GGB | 253915.84 | 1250.7642 | 1250.7642 |  |  |  | 1 | 1 |  |  |  |  | 138263.47 | 1250.7642 | 138263.47 |  | 4.5 | 1250.7642 |  |  |  |  | 48.0375 |  |  | #VALUE!
09.06.2008 03:00 | 3600 | 2 | 764.51 | GGB | 763.37 | 776.203 | 768.132 | 265.82 | GGB | 10919.9 | GGB | 9.79 | GGB | 1012.23 | GGB | 62.93 | GGB | 171284.08 | GGB | 139091.18 | GGB | 0 | 0 | 0 | 0 | 1243.36 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 253951.48 | GGB | 253954.27 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
09.06.2008 04:00 | 3600 | 2 | 764.11 | GGB | 763.37 | 775.195 | 768.132 | 267.27 | GGB | 10941.8 | GGB | 9.79 | GGB | 1012.21 | GGB | 62.42 | GGB | 172948.89 | GGB | 140656.1 | GGB | 0 | 0 | 0 | 0 | 1229.52 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 253989.91 | GGB | 253992.7 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
09.06.2008 05:00 | 3600 | 2 | 764.75 | GGB | 762.271 | 774.211 | 765.934 | 267.9 | GGB | 10954.3 | GGB | 9.8 | GGB | 1011.8 | GGB | 61.95 | GGB | 174091.04 | GGB | 141725.23 | GGB | 0 | 0 | 0 | 0 | 1220.25 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254028.35 | GGB | 254031.13 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
09.06.2008 06:00 | 3600 | 2 | 764.53 | GGB | 764.469 | 775.992 | 768.132 | 268.42 | GGB | 10929.9 | GGB | 9.8 | GGB | 1011.15 | GGB | 61.48 | GGB | 175130.86 | GGB | 142681.22 | GGB | 0 | 0 | 0 | 0 | 1212.07 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254066.78 | GGB | 254069.56 | 1212.0376 | 1212.0376 |  |  |  | 1 | 1 |  |  |  |  | 142681.22 | 1212.0376 | 142681.22 |  | 4.5 | 1212.0376 |  |  |  |  | 48.0375 |  |  | #VALUE!
09.06.2008 07:00 | 3600 | 2 | 766.44 | GGB | 769.597 | 781.313 | 773.626 | 266.32 | GGB | 10927.5 | GGB | 9.84 | GGB | 1009.84 | GGB | 61.86 | GGB | 172915.88 | GGB | 140530.86 | GGB | 0 | 0 | 0 | 0 | 1230.62 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254105.21 | GGB | 254107.99 | 0 | 0 |  |  |  | 0 | 1 | [14 empty] | 0 |  |  | #VALUE!
09.06.2008 08:00 | 3600 | 2 | 766.66 | GGB | 765.934 | 778.195 | 770.33 | 261.32 | GGB | 10813.2 | GGB | 9.83 | GGB | 1009.55 | GGB | 63.47 | GGB | 167243.64 | GGB | 135233.83 | GGB | 0 | 0 | 0 | 0 | 1278.82 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254143.64 | GGB | 254146.42 | 1278.785 | 1278.785 |  |  |  | 1 | 1 |  |  |  |  | 135233.83 | 1278.785 | 135233.83 |  | 4.5 | 1278.785 |  |  |  |  | 48.0375 |  |  | #VALUE!
09.06.2008 09:00 | 3600 | 2 | 766.46 | GGB | 764.835 | 777.141 | 770.33 | 259.79 | GGB | 10696.5 | GGB | 9.81 | GGB | 1009.29 | GGB | 63.84 | GGB | 165954.04 | GGB | 134009.37 | GGB | 0 | 0 | 2668 | 486 | 1290.51 | GNB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254182.07 | GGB | 254184.85 | 1290.4695 | 1290.4695 |  |  |  | 1 | 1 |  |  |  |  | 134009.37 | 1290.4695 | 134009.37 |  | 4.5 | 1290.4695 |  |  |  |  | 48.0375 |  |  | #VALUE!
09.06.2008 10:00 | 3600 | 2 | 767.69 | GGB | 766.667 | 779.836 | 772.527 | 259.16 | GGB | 10625.7 | GGB | 9.81 | GGB | 1008.79 | GGB | 63.86 | GGB | 166306.15 | GGB | 134218.96 | GGB | 0 | 0 | 2581 | 3600 | 2565.67 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254220.5 | GGB | 254223.28 | 2565.67 | 2565.67 |  |  |  | 0 | 1 | [14 empty] | 95.656 |  |  | #VALUE!
09.06.2008 11:00 | 3600 | 2 | 768.64 | GGB | 766.667 | 779.648 | 772.527 | 256.54 | GGB | 10576.1 | GGB | 9.82 | GGB | 1007.49 | GGB | 63.68 | GGB | 164640.24 | GGB | 132772.47 | GGB | 0 | 0 | 2484 | 3600 | 2468.61 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254258.93 | GGB | 254261.71 | 2468.61 | 2468.61 |  |  |  | 0 | 1 | [14 empty] | 91.0454 |  |  | #VALUE!
09.06.2008 12:00 | 3600 | 2 | 768.04 | GGB | 766.667 | 779.648 | 772.527 | 253.63 | GGB | 10517.8 | GGB | 9.81 | GGB | 1006.24 | GGB | 64.74 | GGB | 161566.99 | GGB | 129726.66 | GGB | 0 | 0 | 2497 | 3600 | 2481.45 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254297.36 | GGB | 254300.14 | 2481.45 | 2481.45 |  |  |  | 0 | 1 | [14 empty] | 89.4195 |  |  | #VALUE!
09.06.2008 13:00 | 3600 | 2 | 767.94 | GGB | 766.667 | 779.742 | 772.527 | 253.9 | GGB | 10436.7 | GGB | 9.8 | GGB | 1005.5 | GGB | 64.46 | GGB | 161891.59 | GGB | 130000.21 | GGB | 0 | 0 | 2461 | 3600 | 2445.75 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254335.79 | GGB | 254338.57 | 2445.75 | 2445.75 |  |  |  | 0 | 1 | [14 empty] | 88.3189 |  |  | #VALUE!
09.06.2008 14:00 | 3600 | 2 | 768.34 | GGB | 766.667 | 778.898 | 772.527 | 252.57 | GGB | 10426.3 | GGB | 9.8 | GGB | 1005.06 | GGB | 65.2 | GGB | 159983.61 | GGB | 128126.98 | GGB | 0 | 0 | 2452 | 3600 | 2436.98 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254374.22 | GGB | 254377 | 2436.98 | 2436.98 |  |  |  | 0 | 1 | [14 empty] | 86.7341 |  |  | #VALUE!
09.06.2008 15:00 | 3600 | 2 | 768.11 | GGB | 766.3 | 779.859 | 772.527 | 252.31 | GGB | 10426.9 | GGB | 9.8 | GGB | 1004.87 | GGB | 65.79 | GGB | 159371.82 | GGB | 127392.21 | GGB | 0 | 0 | 2468 | 3600 | 2452.54 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254412.66 | GGB | 254415.43 | 2452.54 | 2452.54 |  |  |  | 0 | 1 | [14 empty] | 86.7874 |  |  | #VALUE!
09.06.2008 16:00 | 3600 | 2 | 768.59 | GGB | 766.667 | 779.789 | 772.527 | 253.79 | GGB | 10405.9 | GGB | 9.8 | GGB | 1005.28 | GGB | 65.35 | GGB | 161179.67 | GGB | 129057.13 | GGB | 0 | 0 | 2443 | 3600 | 2427.8 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254451.09 | GGB | 254453.86 | 2427.8 | 2427.8 |  |  |  | 0 | 1 | [14 empty] | 87.0347 |  |  | #VALUE!
09.06.2008 17:00 | 3600 | 2 | 768.6 | GGB | 766.667 | 779.953 | 772.527 | 254.26 | GGB | 10415.5 | GGB | 9.8 | GGB | 1005.48 | GGB | 64.85 | GGB | 161942.21 | GGB | 129887.73 | GGB | 0 | 0 | 2431 | 3600 | 2416.27 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254489.52 | GGB | 254492.29 | 2416.27 | 2416.27 |  |  |  | 0 | 1 | [14 empty] | 87.1788 |  |  | #VALUE!
09.06.2008 18:00 | 3600 | 2 | 768.22 | GGB | 765.201 | 777.703 | 770.33 | 254.2 | GGB | 10471.9 | GGB | 9.8 | GGB | 1005.56 | GGB | 64.85 | GGB | 161558.19 | GGB | 129588.65 | GGB | 0 | 0 | 2471 | 3600 | 2455.94 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254527.95 | GGB | 254530.72 | 2455.94 | 2455.94 |  |  |  | 1 | 1 |  |  |  |  | 129588.65 | 2455.94 | 129588.65 | 2455.94 | 8.2816 | [5 empty] | 88.4061 |  |  | #VALUE!
09.06.2008 19:00 | 3600 | 2 | 767.18 | GGB | 765.201 | 777.563 | 770.33 | 254.58 | GGB | 10516.9 | GGB | 9.79 | GGB | 1006.07 | GGB | 65.06 | GGB | 161356.83 | GGB | 129410.95 | GGB | 0 | 0 | 2552 | 3600 | 2536.27 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254566.38 | GGB | 254569.15 | 2536.27 | 2536.27 |  |  |  | 1 | 1 |  |  |  |  | 129410.95 | 2536.27 | 129410.95 | 2536.27 | 8.5408 | [5 empty] | 91.1725 |  |  | #VALUE!
09.06.2008 20:00 | 3600 | 2 | 767.1 | GGB | 764.102 | 777.891 | 770.33 | 255.12 | GGB | 10535.1 | GGB | 9.8 | GGB | 1006.13 | GGB | 65.25 | GGB | 161608.81 | GGB | 129547.59 | GGB | 0 | 0 | 2562 | 3600 | 2546.75 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254604.81 | GGB | 254607.58 | 2546.75 | 2546.75 |  |  |  | 1 | 1 |  |  |  |  | 129547.59 | 2546.75 | 129547.59 | 2546.75 | 8.5851 | [5 empty] | 91.6459 |  |  | #VALUE!
09.06.2008 21:00 | 3600 | 2 | 766.94 | GGB | 764.102 | 777.961 | 770.33 | 257.06 | GGB | 10532.4 | GGB | 9.79 | GGB | 1006.27 | GGB | 64.76 | GGB | 163414.46 | GGB | 131206.02 | GGB | 0 | 0 | 2585 | 3600 | 2569.53 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254643.24 | GGB | 254646.01 | 2569.53 | 2569.53 |  |  |  | 1 | 1 |  |  |  |  | 131206.02 | 2569.53 | 131206.02 | 2569.53 | 8.7728 | [5 empty] | 93.6494 |  |  | #VALUE!
09.06.2008 22:00 | 3600 | 2 | 766.8 | GGB | 764.102 | 777.07 | 768.864 | 257.51 | GGB | 10591.5 | GGB | 9.8 | GGB | 1006.78 | GGB | 64.7 | GGB | 163506.89 | GGB | 131368.65 | GGB | 0 | 0 | 2622 | 3600 | 2606.32 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254681.67 | GGB | 254684.44 | 2606.32 | 2606.32 |  |  |  | 1 | 1 |  |  |  |  | 131368.65 | 2606.32 | 131368.65 | 2606.32 | 8.9094 | [5 empty] | 95.108 |  |  | #VALUE!
09.06.2008 23:00 | 3600 | 2 | 765.9 | GGB | 763.004 | 775.734 | 767.766 | 260.35 | GGB | 10614.4 | GGB | 9.78 | GGB | 1007.95 | GGB | 63.93 | GGB | 166211.52 | GGB | 134002.93 | GGB | 0 | 0 | 2688 | 3600 | 2672.54 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254720.1 | GGB | 254722.87 | 2672.54 | 2672.54 |  |  |  | 0 | 1 | [14 empty] | 99.4801 |  |  | #VALUE!
09.06.2008 24:00 | 3600 | 2 | 765.31 | GGB | 764.102 | 776.461 | 767.766 | 259.79 | GGB | 10716.2 | GGB | 9.79 | GGB | 1009.22 | GGB | 63.8 | GGB | 166073.98 | GGB | 134110.14 | GGB | 0 | 0 | 2754 | 3600 | 2738.51 | GGB | 100 | GGB | 38.43 | GGB | 38.43 | GGB | 254758.54 | GGB | 254761.3 | 2738.51 | 2738.51 |  |  |  | 1 | 1 |  |  |  |  | 134110.14 | 2738.51 | 134110.14 | 2738.51 | 9.5566 | [5 empty] | 102.0172 |  |  | #VALUE!
10.06.2008 01:00 | 3600 | 2 | 765.72 | GGB | 763.004 | 775.383 | 767.766 | 262.65 | GGB | 10792.7 | GGB | 9.8 | GGB | 1010.51 | GGB | 63.85 | GGB | 168250.44 | GGB | 136023.67 | GGB | 0 | 0 | 2770 | 3600 | 2754.94 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 254797.36 | GGB | 254800.12 | 2754.94 | 2754.94 |  |  |  | 0 | 1 | [14 empty] | 104.0936 |  |  | #VALUE!
10.06.2008 02:00 | 3600 | 2 | 764.4 | GGB | 763.004 | 774.773 | 767.766 | 266.04 | GGB | 10808.3 | GGB | 9.78 | GGB | 1011.42 | GGB | 62.63 | GGB | 172609.98 | GGB | 140181.52 | GGB | 0 | 0 | 2857 | 3600 | 2841.39 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 254836.18 | GGB | 254838.94 | 2841.39 | 2695.9902 |  |  |  | 0 | 1 | [14 empty] | 110.6418 | 2695.9902 |  | 104.98
10.06.2008 03:00 | 3600 | 2 | 764.35 | GGB | 762.637 | 774.773 | 766.667 | 266.74 | GGB | 10908.5 | GGB | 9.79 | GGB | 1011.9 | GGB | 62.27 | GGB | 173347.21 | GGB | 140998.89 | GGB | 0 | 0 | 2897 | 3600 | 2881.78 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 254875.01 | GGB | 254877.76 | 2881.78 | 2680.3615 |  |  |  | 0 | 1 | [14 empty] | 112.8688 | 2680.3615 |  | 104.98
10.06.2008 04:00 | 3600 | 2 | 764.28 | GGB | 761.538 | 773.859 | 767.766 | 269.02 | GGB | 10938.8 | GGB | 9.8 | GGB | 1012.51 | GGB | 61.2 | GGB | 176015.53 | GGB | 143713.04 | GGB | 0 | 0 | 2909 | 3600 | 2893.46 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 254913.83 | GGB | 254916.58 | 2893.46 | 2629.7405 |  |  |  | 0 | 1 | [14 empty] | 115.5078 | 2629.7405 |  | 104.98
10.06.2008 05:00 | 3600 | 2 | 764.08 | GGB | 761.538 | 772.453 | 766.3 | 268.59 | GGB | 11027.2 | GGB | 9.81 | GGB | 1012.45 | GGB | 61.53 | GGB | 175205.68 | GGB | 142903.83 | GGB | 0 | 0 | 2964 | 3600 | 2948.29 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 254952.66 | GGB | 254955.4 | 2948.29 | 2644.6317 |  |  |  | 0 | 1 | [14 empty] | 117.0339 | 2644.6317 |  | 104.98
10.06.2008 06:00 | 3600 | 2 | 763.54 | GGB | 765.201 | 777.023 | 768.864 | 270.69 | GGB | 11040.1 | GGB | 9.8 | GGB | 1012.96 | GGB | 60.73 | GGB | 177995.04 | GGB | 145597.4 | GGB | 0 | 0 | 3008 | 3600 | 2992.3 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 254991.48 | GGB | 254994.22 | 2992.3 | 2595.7057 |  |  |  | 1 | 1 |  |  |  |  | 145597.4 | 2595.7057 | 145597.4 | 2595.7057 | 9.7354 | [5 empty] | 121.0198 | 2595.7057 |  | 104.98
10.06.2008 07:00 | 3600 | 2 | 765.37 | GGB | 764.102 | 776.063 | 768.864 | 267.81 | GGB | 11060.5 | GGB | 9.84 | GGB | 1012.45 | GGB | 61.28 | GGB | 174492.66 | GGB | 142427.18 | GGB | 0 | 0 | 2912 | 3600 | 2895.97 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255030.31 | GGB | 255033.04 | 2895.97 | 2653.4823 |  |  |  | 1 | 1 |  |  |  |  | 142427.18 | 2653.4823 | 142427.18 | 2653.4823 | 9.7354 | [5 empty] | 114.5736 | 2653.4823 |  | 104.98
10.06.2008 08:00 | 3600 | 2 | 765.84 | GGB | 766.3 | 778.289 | 771.429 | 265.96 | GGB | 10923 | GGB | 9.83 | GGB | 1011.64 | GGB | 61.45 | GGB | 173269.09 | GGB | 141242.88 | GGB | 0 | 0 | 2829 | 3600 | 2813.17 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255069.13 | GGB | 255071.86 | 2813.17 | 2675.7313 |  |  |  | 1 | 1 |  |  |  |  | 141242.88 | 2675.7313 | 141242.88 | 2675.7313 | 9.7354 | [5 empty] | 110.3723 | 2675.7313 |  | 104.98
10.06.2008 09:00 | 3600 | 2 | 766.48 | GGB | 766.3 | 779.438 | 771.429 | 263.33 | GGB | 10817.7 | GGB | 9.83 | GGB | 1011.01 | GGB | 62.32 | GGB | 170182.64 | GGB | 138280.65 | GGB | 0 | 0 | 2750 | 3600 | 2734.55 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255107.96 | GGB | 255110.68 | 2734.55 | 2733.0505 |  |  |  | 0 | 1 | [14 empty] | 105.0376 | 2733.0505 |  | 104.98
10.06.2008 10:00 | 3600 | 2 | 766.36 | GGB | 764.102 | 777.141 | 769.963 | 261.84 | GGB | 10725.4 | GGB | 9.81 | GGB | 1010.17 | GGB | 63.06 | GGB | 168351.68 | GGB | 136380.08 | GGB | 0 | 0 | 2715 | 3600 | 2699.48 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255146.78 | GGB | 255149.5 | 2699.48 | 2699.48 |  |  |  | 1 | 1 |  |  |  |  | 136380.08 | 2699.48 | 136380.08 | 2699.48 | 9.4837 | [5 empty] | 102.2654 |  |  | #VALUE!
10.06.2008 11:00 | 3600 | 2 | 766.98 | GGB | 765.201 | 779.109 | 770.33 | 259.44 | GGB | 10709 | GGB | 9.83 | GGB | 1009.06 | GGB | 64.29 | GGB | 165396.17 | GGB | 133350.36 | GGB | 0 | 0 | 2679 | 3600 | 2663.3 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255185.61 | GGB | 255188.32 | 2663.3 | 2663.3 |  |  |  | 0 | 1 | [14 empty] | 98.6533 |  |  | #VALUE!
10.06.2008 12:00 | 3600 | 2 | 766.32 | GGB | 765.201 | 777.961 | 769.963 | 257.97 | GGB | 10641.8 | GGB | 9.81 | GGB | 1008.02 | GGB | 64.95 | GGB | 163865.6 | GGB | 131722.36 | GGB | 0 | 0 | 2676 | 3600 | 2660.7 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255224.43 | GGB | 255227.14 | 2660.7 | 2660.7 |  |  |  | 1 | 1 |  |  |  |  | 131722.36 | 2660.7 | 131722.36 | 2660.7 | 9.0282 | [5 empty] | 97.3538 |  |  | #VALUE!
10.06.2008 13:00 | 3600 | 2 | 766.65 | GGB | 766.667 | 779.227 | 772.527 | 256.46 | GGB | 10590.3 | GGB | 9.82 | GGB | 1006.66 | GGB | 65.34 | GGB | 162410.95 | GGB | 130224.97 | GGB | 0 | 0 | 2644 | 3600 | 2628.25 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255263.25 | GGB | 255265.96 | 2628.25 | 2628.25 |  |  |  | 0 | 1 | [14 empty] | 95.0733 |  |  | #VALUE!
10.06.2008 14:00 | 3600 | 2 | 767 | GGB | 766.3 | 779.133 | 771.429 | 254.8 | GGB | 10523.2 | GGB | 9.81 | GGB | 1005.71 | GGB | 65.86 | GGB | 160858.38 | GGB | 128660.22 | GGB | 0 | 0 | 2586 | 3600 | 2570.62 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255302.08 | GGB | 255304.78 | 2570.62 | 2570.62 |  |  |  | 0 | 1 | [14 empty] | 91.8713 |  |  | #VALUE!
10.06.2008 15:00 | 3600 | 2 | 767.58 | GGB | 766.667 | 780.258 | 772.527 | 255.33 | GGB | 10452 | GGB | 9.81 | GGB | 1004.68 | GGB | 65.21 | GGB | 162490.18 | GGB | 130083.89 | GGB | 0 | 0 | 2519 | 3600 | 2503.53 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255340.9 | GGB | 255343.6 | 2503.53 | 2503.53 |  |  |  | 0 | 1 | [14 empty] | 90.4636 |  |  | #VALUE!
10.06.2008 16:00 | 3600 | 2 | 767.97 | GGB | 767.766 | 780.352 | 772.527 | 252.81 | GGB | 10451.7 | GGB | 9.81 | GGB | 1003.34 | GGB | 65.75 | GGB | 160125.55 | GGB | 127816.55 | GGB | 0 | 0 | 2481 | 3600 | 2465.78 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255379.73 | GGB | 255382.42 | 2465.78 | 2465.78 |  |  |  | 0 | 1 | [14 empty] | 87.5465 |  |  | #VALUE!
10.06.2008 17:00 | 3600 | 2 | 767.65 | GGB | 766.3 | 780.141 | 772.527 | 252.63 | GGB | 10444.8 | GGB | 9.8 | GGB | 1002.6 | GGB | 65.58 | GGB | 160244.39 | GGB | 127880.38 | GGB | 0 | 0 | 2485 | 3600 | 2469.8 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255418.55 | GGB | 255421.24 | 2469.8 | 2469.8 |  |  |  | 0 | 1 | [14 empty] | 87.733 |  |  | #VALUE!
10.06.2008 18:00 | 3600 | 2 | 767.4 | GGB | 766.667 | 780.188 | 772.527 | 253.25 | GGB | 10462.6 | GGB | 9.8 | GGB | 1002.29 | GGB | 65.52 | GGB | 160187.17 | GGB | 127817.29 | GGB | 0 | 0 | 2510 | 3600 | 2494.49 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255457.38 | GGB | 255460.06 | 2494.49 | 2494.49 |  |  |  | 0 | 1 | [14 empty] | 88.5664 |  |  | #VALUE!
10.06.2008 19:00 | 3600 | 2 | 767.49 | GGB | 766.3 | 779.953 | 771.429 | 253.8 | GGB | 10473.6 | GGB | 9.8 | GGB | 1002.02 | GGB | 65.62 | GGB | 160661.42 | GGB | 128124.35 | GGB | 0 | 0 | 2523 | 3600 | 2508.2 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255496.2 | GGB | 255498.88 | 2508.2 | 2508.2 |  |  |  | 0 | 1 | [14 empty] | 89.2671 |  |  | #VALUE!
10.06.2008 20:00 | 3600 | 2 | 767.6 | GGB | 766.3 | 778.898 | 771.429 | 253.57 | GGB | 10465.1 | GGB | 9.8 | GGB | 1001.36 | GGB | 65.91 | GGB | 160176.17 | GGB | 127544.05 | GGB | 0 | 0 | 2525 | 3600 | 2509.84 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255535.03 | GGB | 255537.7 | 2509.84 | 2509.84 |  |  |  | 0 | 1 | [14 empty] | 88.9209 |  |  | #VALUE!
10.06.2008 21:00 | 3600 | 2 | 767.26 | GGB | 765.201 | 778.875 | 770.33 | 253.74 | GGB | 10461.5 | GGB | 9.8 | GGB | 1000.64 | GGB | 65.83 | GGB | 160199.27 | GGB | 127501.23 | GGB | 0 | 0 | 2538 | 3600 | 2523 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255573.85 | GGB | 255576.52 | 2523 | 2523 |  |  |  | 0 | 1 | [14 empty] | 89.3571 |  |  | #VALUE!
10.06.2008 22:00 | 3600 | 2 | 766.45 | GGB | 765.201 | 778.031 | 770.33 | 255.37 | GGB | 10512.5 | GGB | 9.79 | GGB | 1000.94 | GGB | 65.25 | GGB | 161733.14 | GGB | 128980.95 | GGB | 0 | 0 | 2604 | 3600 | 2588.32 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255612.67 | GGB | 255615.34 | 2588.32 | 2588.32 |  |  |  | 1 | 1 |  |  |  |  | 128980.95 | 2588.32 | 128980.95 | 2588.32 | 8.5998 | [5 empty] | 92.7344 |  |  | #VALUE!
10.06.2008 23:00 | 3600 | 2 | 766.65 | GGB | 766.3 | 778.969 | 771.429 | 257.05 | GGB | 10593.5 | GGB | 9.8 | GGB | 1001.77 | GGB | 64.42 | GGB | 163919.52 | GGB | 131152.1 | GGB | 0 | 0 | 2611 | 3600 | 2595.76 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255651.5 | GGB | 255654.16 | 2595.76 | 2595.76 |  |  |  | 0 | 1 | [14 empty] | 94.5665 |  |  | #VALUE!
10.06.2008 24:00 | 3600 | 2 | 765.67 | GGB | 765.201 | 777.891 | 768.864 | 257.04 | GGB | 10638.4 | GGB | 9.8 | GGB | 1001.81 | GGB | 63.81 | GGB | 164866.91 | GGB | 132155.86 | GGB | 0 | 0 | 2664 | 3600 | 2648.41 | GGB | 100 | GGB | 38.82 | GGB | 38.82 | GGB | 255690.32 | GGB | 255692.98 | 2648.41 | 2648.41 |  |  |  | 1 | 1 |  |  |  |  | 132155.86 | 2648.41 | 132155.86 | 2648.41 | 9.016 | [5 empty] | 97.223 |  |  | #VALUE!
11.06.2008 01:00 | 3600 | 2 | 765.33 | GGB | 765.201 | 777.75 | 768.864 | 258.24 | GGB | 10659.8 | GGB | 9.8 | GGB | 1001.57 | GGB | 63.74 | GGB | 164935.13 | GGB | 132207.28 | GGB | 0 | 0 | 2694 | 3600 | 2678.26 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255729.15 | GGB | 255731.81 | 2678.26 | 2678.26 |  |  |  | 1 | 1 |  |  |  |  | 132207.28 | 2678.26 | 132207.28 | 2678.26 | 9.1189 | [5 empty] | 98.3571 |  |  | #VALUE!
11.06.2008 02:00 | 3600 | 2 | 765.14 | GGB | 764.102 | 776.742 | 768.864 | 260.39 | GGB | 10638.2 | GGB | 9.79 | GGB | 1001.55 | GGB | 63.13 | GGB | 167457.1 | GGB | 134470.69 | GGB | 0 | 0 | 2707 | 3600 | 2691.11 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255767.98 | GGB | 255770.64 | 2691.11 | 2691.11 |  |  |  | 1 | 1 |  |  |  |  | 134470.69 | 2691.11 | 134470.69 | 2691.11 | 9.3195 | [5 empty] | 100.5209 |  |  | #VALUE!
11.06.2008 03:00 | 3600 | 2 | 765.47 | GGB | 764.102 | 776.789 | 769.963 | 260.51 | GGB | 10674.3 | GGB | 9.8 | GGB | 1001.23 | GGB | 63.2 | GGB | 167306.36 | GGB | 134276.8 | GGB | 0 | 0 | 2713 | 3600 | 2697.21 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255806.81 | GGB | 255809.47 | 2697.21 | 2697.21 |  |  |  | 1 | 1 |  |  |  |  | 134276.8 | 2697.21 | 134276.8 | 2697.21 | 9.3271 | [5 empty] | 100.6035 |  |  | #VALUE!
11.06.2008 04:00 | 3600 | 2 | 765.02 | GGB | 764.102 | 775.688 | 768.864 | 259.7 | GGB | 10716.1 | GGB | 9.8 | GGB | 1000.85 | GGB | 63.35 | GGB | 166267.64 | GGB | 133335.4 | GGB | 0 | 0 | 2743 | 3600 | 2727.16 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255845.64 | GGB | 255848.3 | 2727.16 | 2727.16 |  |  |  | 1 | 1 |  |  |  |  | 133335.4 | 2727.16 | 133335.4 | 2727.16 | 9.3646 | [5 empty] | 101.0075 |  |  | #VALUE!
11.06.2008 05:00 | 3600 | 2 | 764.75 | GGB | 763.004 | 775.664 | 767.766 | 260.55 | GGB | 10704 | GGB | 9.8 | GGB | 1000.79 | GGB | 63.07 | GGB | 167441.7 | GGB | 134379.81 | GGB | 0 | 0 | 2762 | 3600 | 2746.63 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255884.47 | GGB | 255887.13 | 2746.63 | 2746.63 |  |  |  | 0 | 1 | [14 empty] | 102.5254 |  |  | #VALUE!
11.06.2008 06:00 | 3600 | 2 | 765.05 | GGB | 765.201 | 776.906 | 769.963 | 261.77 | GGB | 10712.7 | GGB | 9.81 | GGB | 1000.93 | GGB | 62.38 | GGB | 169108.71 | GGB | 136014.75 | GGB | 0 | 0 | 2748 | 3600 | 2732.89 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255923.3 | GGB | 255925.96 | 2732.89 | 2732.89 |  |  |  | 1 | 1 |  |  |  |  | 136014.75 | 2732.89 | 136014.75 | 2732.89 | 9.5728 | [5 empty] | 103.2537 |  |  | #VALUE!
11.06.2008 07:00 | 3600 | 2 | 765.37 | GGB | 765.201 | 777.984 | 771.429 | 261.18 | GGB | 10740.2 | GGB | 9.81 | GGB | 1001.19 | GGB | 62.3 | GGB | 168477.11 | GGB | 135573.77 | GGB | 0 | 0 | 2728 | 3600 | 2712.54 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 255962.13 | GGB | 255964.79 | 2712.54 | 2712.54 |  |  |  | 1 | 1 |  |  |  |  | 135573.77 | 2712.54 | 135573.77 | 2712.54 | 9.4708 | [5 empty] | 102.1526 |  |  | #VALUE!
11.06.2008 08:00 | 3600 | 2 | 765.27 | GGB | 764.102 | 776.93 | 768.864 | 259.95 | GGB | 10746.2 | GGB | 9.81 | GGB | 1001.9 | GGB | 62.99 | GGB | 166875.02 | GGB | 134103.54 | GGB | 0 | 0 | 2743 | 3600 | 2727.7 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256000.96 | GGB | 256003.62 | 2727.7 | 2727.7 |  |  |  | 1 | 1 |  |  |  |  | 134103.54 | 2727.7 | 134103.54 | 2727.7 | 9.4204 | [5 empty] | 101.6095 |  |  | #VALUE!
11.06.2008 09:00 | 3600 | 2 | 765.2 | GGB | 764.102 | 776.93 | 769.963 | 260.18 | GGB | 10707.7 | GGB | 9.8 | GGB | 1001.62 | GGB | 62.82 | GGB | 167772.9 | GGB | 134854.27 | GGB | 0 | 0 | 2733 | 3600 | 2717.22 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256039.78 | GGB | 256042.45 | 2717.22 | 2717.22 |  |  |  | 1 | 1 |  |  |  |  | 134854.27 | 2717.22 | 134854.27 | 2717.22 | 9.4367 | [5 empty] | 101.7858 |  |  | #VALUE!
11.06.2008 10:00 | 3600 | 2 | 766.19 | GGB | 766.3 | 779.391 | 771.429 | 260.12 | GGB | 10709.6 | GGB | 9.82 | GGB | 1001.4 | GGB | 62.64 | GGB | 168013.87 | GGB | 135094.8 | GGB | 0 | 0 | 2680 | 3600 | 2664.47 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256078.61 | GGB | 256081.28 | 2664.47 | 2664.47 |  |  |  | 0 | 1 | [14 empty] | 99.9878 |  |  | #VALUE!
11.06.2008 11:00 | 3600 | 2 | 766.02 | GGB | 765.201 | 777.398 | 770.33 | 258.34 | GGB | 10674.2 | GGB | 9.81 | GGB | 1000.85 | GGB | 63.18 | GGB | 166065.17 | GGB | 133240.6 | GGB | 0 | 0 | 2654 | 3600 | 2638.54 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256117.44 | GGB | 256120.11 | 2638.54 | 2638.54 |  |  |  | 1 | 1 |  |  |  |  | 133240.6 | 2638.54 | 133240.6 | 2638.54 | 9.0538 | [5 empty] | 97.6557 |  |  | #VALUE!
11.06.2008 12:00 | 3600 | 2 | 766.06 | GGB | 766.3 | 778.641 | 771.429 | 259.31 | GGB | 10631.8 | GGB | 9.81 | GGB | 1001.51 | GGB | 62.65 | GGB | 167650.76 | GGB | 134813.19 | GGB | 0 | 0 | 2638 | 3600 | 2622.42 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256156.27 | GGB | 256158.94 | 2622.42 | 2622.42 |  |  |  | 1 | 1 |  |  |  |  | 134813.19 | 2622.42 | 134813.19 | 2622.42 | 9.1047 | [5 empty] | 98.2047 |  |  | #VALUE!
11.06.2008 13:00 | 3600 | 2 | 766.42 | GGB | 765.201 | 778.945 | 771.429 | 257.84 | GGB | 10652.3 | GGB | 9.81 | GGB | 1002.02 | GGB | 63.27 | GGB | 165732.87 | GGB | 133090.41 | GGB | 0 | 0 | 2631 | 3600 | 2615.35 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256195.1 | GGB | 256197.77 | 2615.35 | 2615.35 |  |  |  | 0 | 1 | [14 empty] | 96.6883 |  |  | #VALUE!
11.06.2008 14:00 | 3600 | 2 | 766.22 | GGB | 765.201 | 777.938 | 771.429 | 258.77 | GGB | 10618.7 | GGB | 9.8 | GGB | 1001.92 | GGB | 62.84 | GGB | 166985.06 | GGB | 134257.8 | GGB | 0 | 0 | 2617 | 3600 | 2601.87 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256233.93 | GGB | 256236.6 | 2601.87 | 2601.87 |  |  |  | 1 | 1 |  |  |  |  | 134257.8 | 2601.87 | 134257.8 | 2601.87 | 8.9962 | [5 empty] | 97.0337 |  |  | #VALUE!
11.06.2008 15:00 | 3600 | 2 | 766.66 | GGB | 765.201 | 777.938 | 771.429 | 258.39 | GGB | 10606.5 | GGB | 9.81 | GGB | 1001.47 | GGB | 62.77 | GGB | 167178.72 | GGB | 134379.97 | GGB | 0 | 0 | 2588 | 3600 | 2573.11 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256272.76 | GGB | 256275.43 | 2573.11 | 2573.11 |  |  |  | 1 | 1 |  |  |  |  | 134379.97 | 2573.11 | 134379.97 | 2573.11 | 8.9048 | [5 empty] | 96.0485 |  |  | #VALUE!
11.06.2008 16:00 | 3600 | 2 | 766.76 | GGB | 764.102 | 776.695 | 768.864 | 256.79 | GGB | 10612 | GGB | 9.8 | GGB | 1001.17 | GGB | 63.07 | GGB | 165406.07 | GGB | 132797.17 | GGB | 0 | 0 | 2573 | 3600 | 2558.04 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256311.59 | GGB | 256314.26 | 2558.04 | 2558.04 |  |  |  | 1 | 1 |  |  |  |  | 132797.17 | 2558.04 | 132797.17 | 2558.04 | 8.7484 | [5 empty] | 94.3612 |  |  | #VALUE!
11.06.2008 17:00 | 3600 | 2 | 766.51 | GGB | 765.201 | 778.125 | 770.33 | 257.34 | GGB | 10631.5 | GGB | 9.8 | GGB | 1000.46 | GGB | 62.9 | GGB | 166242.33 | GGB | 133437.78 | GGB | 0 | 0 | 2601 | 3600 | 2585.23 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256350.42 | GGB | 256353.09 | 2585.23 | 2585.23 |  |  |  | 1 | 1 |  |  |  |  | 133437.78 | 2585.23 | 133437.78 | 2585.23 | 8.884 | [5 empty] | 95.8243 |  |  | #VALUE!
11.06.2008 18:00 | 3600 | 2 | 766.68 | GGB | 765.201 | 778.219 | 770.33 | 258.21 | GGB | 10636 | GGB | 9.81 | GGB | 1000.85 | GGB | 62.49 | GGB | 167188.62 | GGB | 134416.51 | GGB | 0 | 0 | 2587 | 3600 | 2571.46 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256389.25 | GGB | 256391.92 | 2571.46 | 2571.46 |  |  |  | 1 | 1 |  |  |  |  | 134416.51 | 2571.46 | 134416.51 | 2571.46 | 8.9015 | [5 empty] | 96.013 |  |  | #VALUE!
11.06.2008 19:00 | 3600 | 2 | 766.18 | GGB | 765.201 | 778.102 | 770.33 | 257.35 | GGB | 10663.9 | GGB | 9.8 | GGB | 1000.92 | GGB | 63.03 | GGB | 165850.61 | GGB | 133133.8 | GGB | 0 | 0 | 2627 | 3600 | 2612.02 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256428.07 | GGB | 256430.75 | 2612.02 | 2612.02 |  |  |  | 1 | 1 |  |  |  |  | 133133.8 | 2612.02 | 133133.8 | 2612.02 | 8.9557 | [5 empty] | 96.5967 |  |  | #VALUE!
11.06.2008 20:00 | 3600 | 2 | 766.24 | GGB | 766.3 | 779.133 | 771.429 | 258.67 | GGB | 10638.7 | GGB | 9.8 | GGB | 1000.81 | GGB | 62.77 | GGB | 167399.88 | GGB | 134467.1 | GGB | 0 | 0 | 2621 | 3600 | 2605.99 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256466.9 | GGB | 256469.58 | 2605.99 | 2605.99 |  |  |  | 0 | 1 | [14 empty] | 97.3389 |  |  | #VALUE!
11.06.2008 21:00 | 3600 | 2 | 765.92 | GGB | 765.201 | 777.141 | 769.963 | 259.72 | GGB | 10638.1 | GGB | 9.8 | GGB | 1000.64 | GGB | 62.28 | GGB | 168284.56 | GGB | 135354.19 | GGB | 0 | 0 | 2628 | 3600 | 2612.24 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256505.73 | GGB | 256508.41 | 2612.24 | 2612.24 |  |  |  | 1 | 1 |  |  |  |  | 135354.19 | 2612.24 | 135354.19 | 2612.24 | 9.1058 | [5 empty] | 98.216 |  |  | #VALUE!
11.06.2008 22:00 | 3600 | 2 | 765.78 | GGB | 763.004 | 776.109 | 768.864 | 260.23 | GGB | 10707.6 | GGB | 9.8 | GGB | 1000.76 | GGB | 62.27 | GGB | 168660.87 | GGB | 135673.89 | GGB | 0 | 0 | 2669 | 3600 | 2653.69 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256544.56 | GGB | 256547.24 | 2653.69 | 2653.69 |  |  |  | 0 | 1 | [14 empty] | 100.0101 |  |  | #VALUE!
11.06.2008 23:00 | 3600 | 2 | 765.37 | GGB | 764.102 | 776.063 | 768.498 | 260.72 | GGB | 10776.7 | GGB | 9.8 | GGB | 1001.13 | GGB | 62.23 | GGB | 169016.28 | GGB | 136029.15 | GGB | 0 | 0 | 2722 | 3600 | 2707.02 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256583.39 | GGB | 256586.07 | 2707.02 | 2707.02 |  |  |  | 1 | 1 |  |  |  |  | 136029.15 | 2707.02 | 136029.15 | 2707.02 | 9.4832 | [5 empty] | 102.2871 |  |  | #VALUE!
11.06.2008 24:00 | 3600 | 2 | 764.94 | GGB | 764.102 | 776.414 | 768.132 | 260.89 | GGB | 10818.6 | GGB | 9.8 | GGB | 1001.46 | GGB | 61.76 | GGB | 170089.11 | GGB | 137128.1 | GGB | 0 | 0 | 2761 | 3600 | 2745.96 | GGB | 100 | GGB | 38.83 | GGB | 38.83 | GGB | 256622.22 | GGB | 256624.9 | 2745.96 | 2745.96 |  |  |  | 1 | 1 |  |  |  |  | 137128.1 | 2745.96 | 137128.1 | 2745.96 | 9.6974 | [5 empty] | 104.5967 |  |  | #VALUE!
12.06.2008 01:00 | 3600 | 2 | 764.81 | GGB | 763.004 | 775.148 | 767.033 | 264.08 | GGB | 10807.6 | GGB | 9.79 | GGB | 1002.2 | GGB | 61 | GGB | 172925.78 | GGB | 139838.77 | GGB | 0 | 0 | 2782 | 3600 | 2766.99 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256660.13 | GGB | 256662.81 | 2766.99 | 2702.5981 |  |  |  | 0 | 1 | [14 empty] | 107.4812 | 2702.5981 |  | 104.98
12.06.2008 02:00 | 3600 | 2 | 765.45 | GGB | 765.201 | 777.281 | 770.696 | 263.86 | GGB | 10864.1 | GGB | 9.82 | GGB | 1002.47 | GGB | 61.14 | GGB | 172377.81 | GGB | 139372.53 | GGB | 0 | 0 | 2766 | 3600 | 2750.62 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256698.05 | GGB | 256700.72 | 2750.62 | 2711.6391 |  |  |  | 1 | 1 |  |  |  |  | 139372.53 | 2711.6391 | 139372.53 | 2711.6391 | 9.9691 | [5 empty] | 106.4891 | 2711.6391 |  | 104.98
12.06.2008 03:00 | 3600 | 2 | 764.04 | GGB | 763.004 | 775.102 | 768.132 | 263.62 | GGB | 10873.6 | GGB | 9.8 | GGB | 1002.17 | GGB | 61.64 | GGB | 171503.04 | GGB | 138416.21 | GGB | 0 | 0 | 2860 | 3600 | 2844.75 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256735.96 | GGB | 256738.63 | 2844.75 | 2730.3738 |  |  |  | 0 | 1 | [14 empty] | 109.3776 | 2730.3738 |  | 104.98
12.06.2008 04:00 | 3600 | 2 | 763.89 | GGB | 761.538 | 774 | 767.033 | 265.08 | GGB | 10888.7 | GGB | 9.8 | GGB | 1001.96 | GGB | 61.22 | GGB | 173267.99 | GGB | 139988.89 | GGB | 0 | 0 | 2883 | 3600 | 2867.41 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256773.87 | GGB | 256776.54 | 2867.41 | 2699.7 |  |  |  | 0 | 1 | [14 empty] | 111.5015 | 2699.7 |  | 104.98
12.06.2008 05:00 | 3600 | 2 | 764.1 | GGB | 765.201 | 777.211 | 769.597 | 266.66 | GGB | 10898.1 | GGB | 9.81 | GGB | 1001.99 | GGB | 60.53 | GGB | 175063.74 | GGB | 141734.41 | GGB | 0 | 0 | 2869 | 3600 | 2852.97 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256811.78 | GGB | 256814.45 | 2852.97 | 2666.452 |  |  |  | 1 | 1 |  |  |  |  | 141734.41 | 2666.452 | 141734.41 | 2666.452 | 9.9691 | [5 empty] | 112.3233 | 2666.452 |  | 104.98
12.06.2008 06:00 | 3600 | 2 | 764.38 | GGB | 764.102 | 775.875 | 768.498 | 265.99 | GGB | 10902.2 | GGB | 9.81 | GGB | 1002.13 | GGB | 60.66 | GGB | 174433.24 | GGB | 141191.04 | GGB | 0 | 0 | 2864 | 3600 | 2848.05 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256849.7 | GGB | 256852.36 | 2848.05 | 2676.7138 |  |  |  | 1 | 1 |  |  |  |  | 141191.04 | 2676.7138 | 141191.04 | 2676.7138 | 9.9691 | [5 empty] | 111.6998 | 2676.7138 |  | 104.98
12.06.2008 07:00 | 3600 | 2 | 764.61 | GGB | 765.201 | 777.07 | 769.597 | 264.35 | GGB | 10923.7 | GGB | 9.82 | GGB | 1002.31 | GGB | 61.37 | GGB | 171894.76 | GGB | 138866.66 | GGB | 0 | 0 | 2870 | 3600 | 2854.34 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256887.61 | GGB | 256890.27 | 2854.34 | 2721.5172 |  |  |  | 1 | 1 |  |  |  |  | 138866.66 | 2721.5172 | 138866.66 | 2721.5172 | 9.9691 | [5 empty] | 110.1035 | 2721.5172 |  | 104.98
12.06.2008 08:00 | 3600 | 2 | 765.28 | GGB | 764.102 | 776.016 | 768.498 | 262.67 | GGB | 10876.5 | GGB | 9.82 | GGB | 1003.04 | GGB | 61.78 | GGB | 169933.96 | GGB | 137210.75 | GGB | 0 | 0 | 2809 | 3600 | 2793.53 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256925.52 | GGB | 256928.18 | 2793.53 | 2754.3614 |  |  |  | 1 | 1 |  |  |  |  | 137210.75 | 2754.3614 | 137210.75 | 2754.3614 | 9.9691 | [5 empty] | 106.4729 | 2754.3614 |  | 104.98
12.06.2008 09:00 | 3600 | 2 | 765.17 | GGB | 763.004 | 776.063 | 768.498 | 262.44 | GGB | 10800.5 | GGB | 9.81 | GGB | 1003.05 | GGB | 61.99 | GGB | 169775.51 | GGB | 136999.47 | GGB | 0 | 0 | 2782 | 3600 | 2766.38 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 256963.44 | GGB | 256966.09 | 2766.38 | 2758.6092 |  |  |  | 0 | 1 | [14 empty] | 105.2757 | 2758.6092 |  | 104.98
12.06.2008 10:00 | 3600 | 2 | 766.38 | GGB | 764.102 | 777.164 | 769.597 | 262.42 | GGB | 10755.1 | GGB | 9.82 | GGB | 1002.35 | GGB | 61.86 | GGB | 170410.41 | GGB | 137469.16 | GGB | 0 | 0 | 2692 | 3600 | 2676.4 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257001.35 | GGB | 257004 | 2676.4 | 2676.4 |  |  |  | 1 | 1 |  |  |  |  | 137469.16 | 2676.4 | 137469.16 | 2676.4 | 9.7052 | [5 empty] | 102.2007 |  |  | #VALUE!
12.06.2008 11:00 | 3600 | 2 | 766.41 | GGB | 766.3 | 779.344 | 771.795 | 261.14 | GGB | 10736.7 | GGB | 9.82 | GGB | 1002.53 | GGB | 62.11 | GGB | 169223.14 | GGB | 136434.18 | GGB | 0 | 0 | 2667 | 3600 | 2651.34 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257039.26 | GGB | 257041.91 | 2651.34 | 2651.34 |  |  |  | 0 | 1 | [14 empty] | 100.4815 |  |  | #VALUE!
12.06.2008 12:00 | 3600 | 2 | 766.14 | GGB | 764.102 | 777.188 | 769.597 | 259.02 | GGB | 10725.9 | GGB | 9.81 | GGB | 1002.2 | GGB | 62.72 | GGB | 166827.71 | GGB | 134214.47 | GGB | 0 | 0 | 2670 | 3600 | 2654.82 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257077.17 | GGB | 257079.82 | 2654.82 | 2654.82 |  |  |  | 1 | 1 |  |  |  |  | 134214.47 | 2654.82 | 134214.47 | 2654.82 | 9.399 | [5 empty] | 98.9765 |  |  | #VALUE!
12.06.2008 13:00 | 3600 | 2 | 766.44 | GGB | 765.201 | 777.234 | 769.597 | 259.19 | GGB | 10682.4 | GGB | 9.81 | GGB | 1001.74 | GGB | 62.64 | GGB | 167268.94 | GGB | 134540.01 | GGB | 0 | 0 | 2642 | 3600 | 2626.47 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257115.09 | GGB | 257117.73 | 2626.47 | 2626.47 |  |  |  | 1 | 1 |  |  |  |  | 134540.01 | 2626.47 | 134540.01 | 2626.47 | 9.3212 | [5 empty] | 98.157 |  |  | #VALUE!
12.06.2008 14:00 | 3600 | 2 | 766.71 | GGB | 765.201 | 778.289 | 770.696 | 258.96 | GGB | 10654 | GGB | 9.81 | GGB | 1000.9 | GGB | 62.36 | GGB | 167654.06 | GGB | 134850.98 | GGB | 0 | 0 | 2607 | 3600 | 2591.56 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257153 | GGB | 257155.64 | 2591.56 | 2591.56 |  |  |  | 1 | 1 |  |  |  |  | 134850.98 | 2591.56 | 134850.98 | 2591.56 | 9.2185 | [5 empty] | 97.0762 |  |  | #VALUE!
12.06.2008 15:00 | 3600 | 2 | 765.79 | GGB | 765.201 | 777.844 | 770.696 | 258.91 | GGB | 10711.5 | GGB | 9.8 | GGB | 1001.61 | GGB | 62.94 | GGB | 166593.34 | GGB | 133860.55 | GGB | 0 | 0 | 2691 | 3600 | 2675.58 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257190.91 | GGB | 257193.55 | 2675.58 | 2675.58 |  |  |  | 1 | 1 |  |  |  |  | 133860.55 | 2675.58 | 133860.55 | 2675.58 | 9.4475 | [5 empty] | 99.4874 |  |  | #VALUE!
12.06.2008 16:00 | 3600 | 2 | 766.5 | GGB | 765.201 | 778.102 | 770.696 | 258.5 | GGB | 10650.9 | GGB | 9.81 | GGB | 1001.29 | GGB | 63.18 | GGB | 166571.33 | GGB | 133702.71 | GGB | 0 | 0 | 2623 | 3600 | 2607.83 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257228.83 | GGB | 257231.46 | 2607.83 | 2607.83 |  |  |  | 1 | 1 |  |  |  |  | 133702.71 | 2607.83 | 133702.71 | 2607.83 | 9.1974 | [5 empty] | 96.8539 |  |  | #VALUE!
12.06.2008 17:00 | 3600 | 2 | 765.2 | GGB | 765.201 | 777.047 | 769.597 | 260.37 | GGB | 10706.7 | GGB | 9.79 | GGB | 1001.02 | GGB | 62.33 | GGB | 168796.21 | GGB | 135797.62 | GGB | 0 | 0 | 2713 | 3600 | 2697.91 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257266.74 | GGB | 257269.37 | 2697.91 | 2697.91 |  |  |  | 1 | 1 |  |  |  |  | 135797.62 | 2697.91 | 135797.62 | 2697.91 | 9.6642 | [5 empty] | 101.7694 |  |  | #VALUE!
12.06.2008 18:00 | 3600 | 2 | 766.58 | GGB | 764.102 | 777.375 | 769.597 | 259.13 | GGB | 10730.3 | GGB | 9.82 | GGB | 1001.37 | GGB | 63.18 | GGB | 167020.27 | GGB | 134075.69 | GGB | 0 | 0 | 2652 | 3600 | 2636.75 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257304.65 | GGB | 257307.28 | 2636.75 | 2636.75 |  |  |  | 1 | 1 |  |  |  |  | 134075.69 | 2636.75 | 134075.69 | 2636.75 | 9.3254 | [5 empty] | 98.2011 |  |  | #VALUE!
12.06.2008 19:00 | 3600 | 2 | 766.36 | GGB | 765.201 | 777.469 | 770.696 | 259.62 | GGB | 10684.5 | GGB | 9.81 | GGB | 1001.41 | GGB | 63.1 | GGB | 167892.84 | GGB | 134810.85 | GGB | 0 | 0 | 2650 | 3600 | 2635 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257342.56 | GGB | 257345.19 | 2635 | 2635 |  |  |  | 1 | 1 |  |  |  |  | 134810.85 | 2635 | 134810.85 | 2635 | 9.3703 | [5 empty] | 98.6741 |  |  | #VALUE!
12.06.2008 20:00 | 3600 | 2 | 765.19 | GGB | 763.004 | 776.531 | 768.498 | 260.34 | GGB | 10745.7 | GGB | 9.79 | GGB | 1001.36 | GGB | 62.32 | GGB | 168434.2 | GGB | 135554.88 | GGB | 0 | 0 | 2734 | 3600 | 2718.85 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257380.48 | GGB | 257383.1 | 2718.85 | 2718.85 |  |  |  | 0 | 1 | [14 empty] | 102.3759 |  |  | #VALUE!
12.06.2008 21:00 | 3600 | 2 | 765.17 | GGB | 764.102 | 776.648 | 769.597 | 261.62 | GGB | 10796.5 | GGB | 9.81 | GGB | 1002.8 | GGB | 62.66 | GGB | 168907.35 | GGB | 135994.01 | GGB | 0 | 0 | 2772 | 3600 | 2756.98 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257418.39 | GGB | 257421.01 | 2756.98 | 2756.98 |  |  |  | 1 | 1 |  |  |  |  | 135994.01 | 2756.98 | 135994.01 | 2756.98 | 9.8901 | [5 empty] | 104.148 |  |  | #VALUE!
12.06.2008 22:00 | 3600 | 2 | 764.9 | GGB | 763.004 | 774.75 | 767.033 | 262.25 | GGB | 10772.4 | GGB | 9.8 | GGB | 1003.05 | GGB | 62.37 | GGB | 169757.91 | GGB | 136828.79 | GGB | 0 | 0 | 2775 | 3600 | 2759.85 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257456.3 | GGB | 257458.92 | 2759.85 | 2759.85 |  |  |  | 0 | 1 | [14 empty] | 104.8964 |  |  | #VALUE!
12.06.2008 23:00 | 3600 | 2 | 765.61 | GGB | 764.102 | 775.758 | 768.498 | 263.61 | GGB | 10815.8 | GGB | 9.81 | GGB | 1003.97 | GGB | 62.06 | GGB | 170949.57 | GGB | 138043.08 | GGB | 0 | 0 | 2762 | 3600 | 2746.73 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257494.22 | GGB | 257496.83 | 2746.73 | 2737.754 |  |  |  | 1 | 1 |  |  |  |  | 138043.08 | 2737.754 | 138043.08 | 2737.754 | 9.9691 | [5 empty] | 105.3242 | 2737.754 |  | 104.98
12.06.2008 24:00 | 3600 | 2 | 764.52 | GGB | 763.004 | 775.57 | 768.498 | 263.75 | GGB | 10853.5 | GGB | 9.8 | GGB | 1004.47 | GGB | 62.27 | GGB | 170929.77 | GGB | 138010.34 | GGB | 0 | 0 | 2845 | 3600 | 2829.26 | GGB | 100 | GGB | 37.91 | GGB | 37.91 | GGB | 257532.13 | GGB | 257534.74 | 2829.26 | 2738.4035 |  |  |  | 0 | 1 | [14 empty] | 108.4631 | 2738.4035 |  | 104.98
13.06.2008 01:00 | 3600 | 2 | 764.46 | GGB | 764.102 | 776.766 | 769.597 | 264.89 | GGB | 10903.6 | GGB | 9.8 | GGB | 1005.13 | GGB | 61.99 | GGB | 172016.9 | GGB | 139098.2 | GGB | 0 | 0 | 2877 | 3600 | 2861.07 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257571.68 | GGB | 257574.29 | 2861.07 | 2716.987 |  |  |  | 1 | 1 |  |  |  |  | 139098.2 | 2716.987 | 139098.2 | 2716.987 | 9.5557 | [5 empty] | 110.5471 | 2716.987 |  | 104.98
13.06.2008 02:00 | 3600 | 2 | 764.03 | GGB | 761.538 | 774.258 | 767.033 | 266 | GGB | 10924.6 | GGB | 9.79 | GGB | 1005.64 | GGB | 61.69 | GGB | 172995.1 | GGB | 140081.6 | GGB | 0 | 0 | 2914 | 3600 | 2898.36 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257611.22 | GGB | 257613.84 | 2898.36 | 2697.9132 |  |  |  | 0 | 1 | [14 empty] | 112.7797 | 2697.9132 |  | 104.98
13.06.2008 03:00 | 3600 | 2 | 763.52 | GGB | 761.538 | 773.156 | 765.934 | 267.25 | GGB | 10972.1 | GGB | 9.8 | GGB | 1005.88 | GGB | 61.35 | GGB | 174315.51 | GGB | 141331.11 | GGB | 0 | 0 | 2956 | 3600 | 2940.87 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257650.77 | GGB | 257653.39 | 2940.87 | 2674.0609 |  |  |  | 0 | 1 | [14 empty] | 115.4546 | 2674.0609 |  | 104.98
13.06.2008 04:00 | 3600 | 2 | 762.81 | GGB | 763.004 | 775.359 | 768.132 | 268.9 | GGB | 11028.4 | GGB | 9.8 | GGB | 1006.45 | GGB | 60.9 | GGB | 175957.21 | GGB | 142934.85 | GGB | 0 | 0 | 3019 | 3600 | 3003.65 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257690.31 | GGB | 257692.94 | 3003.65 | 2644.0578 |  |  |  | 0 | 1 | [14 empty] | 119.2573 | 2644.0578 |  | 104.98
13.06.2008 05:00 | 3600 | 2 | 762.75 | GGB | 761.538 | 773.344 | 765.934 | 269.53 | GGB | 11067.2 | GGB | 9.8 | GGB | 1006.77 | GGB | 60.49 | GGB | 177145.58 | GGB | 144122.49 | GGB | 0 | 0 | 3037 | 3600 | 3021.58 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257729.86 | GGB | 257732.49 | 3021.58 | 2622.2694 |  |  |  | 0 | 1 | [14 empty] | 120.966 | 2622.2694 |  | 104.98
13.06.2008 06:00 | 3600 | 2 | 763.16 | GGB | 762.637 | 774.469 | 767.033 | 269.6 | GGB | 11115.5 | GGB | 9.81 | GGB | 1007.55 | GGB | 60.15 | GGB | 177537.3 | GGB | 144700.3 | GGB | 0 | 0 | 3040 | 3600 | 3024.54 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257769.4 | GGB | 257772.04 | 3024.54 | 2611.7983 |  |  |  | 0 | 1 | [14 empty] | 121.57 | 2611.7983 |  | 104.98
13.06.2008 07:00 | 3600 | 2 | 763.79 | GGB | 764.102 | 775.523 | 768.498 | 268.84 | GGB | 11112.8 | GGB | 9.82 | GGB | 1007.83 | GGB | 60.21 | GGB | 176776.96 | GGB | 144094.62 | GGB | 0 | 0 | 3008 | 3600 | 2992.67 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257808.95 | GGB | 257811.59 | 2992.67 | 2622.7766 |  |  |  | 1 | 1 |  |  |  |  | 144094.62 | 2622.7766 | 144094.62 | 2622.7766 | 9.5557 | [5 empty] | 119.7855 | 2622.7766 |  | 104.98
13.06.2008 08:00 | 3600 | 2 | 764.68 | GGB | 765.201 | 777.633 | 770.696 | 265.96 | GGB | 11031.1 | GGB | 9.84 | GGB | 1007.67 | GGB | 60.9 | GGB | 173463.85 | GGB | 141077.98 | GGB | 0 | 0 | 2918 | 3600 | 2902.16 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257848.5 | GGB | 257851.14 | 2902.16 | 2678.8589 |  |  |  | 1 | 1 |  |  |  |  | 141077.98 | 2678.8589 | 141077.98 | 2678.8589 | 9.5557 | [5 empty] | 113.7308 | 2678.8589 |  | 104.98
13.06.2008 09:00 | 3600 | 2 | 765.12 | GGB | 763.004 | 775.617 | 768.498 | 262.73 | GGB | 10886 | GGB | 9.82 | GGB | 1007.47 | GGB | 62.09 | GGB | 169721.6 | GGB | 137517.07 | GGB | 0 | 0 | 2784 | 3207 | 2768.25 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257888.04 | GGB | 257890.69 | 2768.25 | 2748.2261 |  |  |  | 0 | 1 | [14 empty] | 105.7449 | 2748.2261 |  | 104.98
13.06.2008 10:00 | 3600 | 2 | 766.02 | GGB | 765.201 | 778.641 | 769.597 | 261.65 | GGB | 10814.8 | GGB | 9.82 | GGB | 1006.85 | GGB | 62.85 | GGB | 168537.63 | GGB | 136164.42 | GGB | 0 | 0 | 2685 | 2652 | 2669.73 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257927.59 | GGB | 257930.24 | 2669.73 | 2669.73 |  |  |  | 1 | 1 |  |  |  |  | 136164.42 | 2669.73 | 136164.42 | 2669.73 | 9.1915 | [5 empty] | 100.9784 |  |  | #VALUE!
13.06.2008 11:00 | 3600 | 2 | 766.72 | GGB | 764.102 | 777.469 | 769.597 | 260.18 | GGB | 10750.4 | GGB | 9.82 | GGB | 1005.92 | GGB | 63.41 | GGB | 167296.45 | GGB | 134812.16 | GGB | 0 | 0 | 2645 | 3600 | 2629.51 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 257967.13 | GGB | 257969.79 | 2629.51 | 2629.51 |  |  |  | 1 | 1 |  |  |  |  | 134812.16 | 2629.51 | 134812.16 | 2629.51 | 8.9631 | [5 empty] | 98.4694 |  |  | #VALUE!
13.06.2008 12:00 | 3600 | 2 | 767.08 | GGB | 766.3 | 778.336 | 770.696 | 259.63 | GGB | 10716.8 | GGB | 9.81 | GGB | 1005.76 | GGB | 63.64 | GGB | 166770.49 | GGB | 134275.38 | GGB | 0 | 0 | 2613 | 3600 | 2598.15 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258006.68 | GGB | 258009.34 | 2598.15 | 2598.15 |  |  |  | 1 | 1 |  |  |  |  | 134275.38 | 2598.15 | 134275.38 | 2598.15 | 8.8209 | [5 empty] | 96.9077 |  |  | #VALUE!
13.06.2008 13:00 | 3600 | 2 | 767.04 | GGB | 765.201 | 778.453 | 769.597 | 259.17 | GGB | 10688.4 | GGB | 9.81 | GGB | 1005.88 | GGB | 63.76 | GGB | 166374.37 | GGB | 133924.1 | GGB | 0 | 0 | 2586 | 3600 | 2570.84 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258046.23 | GGB | 258048.89 | 2570.84 | 2570.84 |  |  |  | 1 | 1 |  |  |  |  | 133924.1 | 2570.84 | 133924.1 | 2570.84 | 8.7054 | [5 empty] | 95.6382 |  |  | #VALUE!
13.06.2008 14:00 | 3600 | 2 | 767.16 | GGB | 764.102 | 777.352 | 769.597 | 258.7 | GGB | 10667.2 | GGB | 9.81 | GGB | 1004.93 | GGB | 63.68 | GGB | 165858.31 | GGB | 133414.52 | GGB | 0 | 0 | 2560 | 3600 | 2544.76 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258085.77 | GGB | 258088.44 | 2544.76 | 2544.76 |  |  |  | 1 | 1 |  |  |  |  | 133414.52 | 2544.76 | 133414.52 | 2544.76 | 8.5843 | [5 empty] | 94.3078 |  |  | #VALUE!
13.06.2008 15:00 | 3600 | 2 | 767.16 | GGB | 765.201 | 778.383 | 771.795 | 258.62 | GGB | 10662.4 | GGB | 9.81 | GGB | 1004.78 | GGB | 63.92 | GGB | 165707.56 | GGB | 133178.28 | GGB | 0 | 0 | 2559 | 3600 | 2543.96 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258125.32 | GGB | 258127.99 | 2543.96 | 2543.96 |  |  |  | 1 | 1 |  |  |  |  | 133178.28 | 2543.96 | 133178.28 | 2543.96 | 8.5664 | [5 empty] | 94.1112 |  |  | #VALUE!
13.06.2008 16:00 | 3600 | 2 | 767.18 | GGB | 766.3 | 779.602 | 771.795 | 258 | GGB | 10638 | GGB | 9.81 | GGB | 1004.34 | GGB | 64.23 | GGB | 165338.95 | GGB | 132704.33 | GGB | 0 | 0 | 2544 | 3600 | 2528.86 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258164.86 | GGB | 258167.54 | 2528.86 | 2528.86 |  |  |  | 0 | 1 | [14 empty] | 93.2196 |  |  | #VALUE!
13.06.2008 17:00 | 3600 | 2 | 767.7 | GGB | 766.667 | 778.828 | 770.696 | 256.81 | GGB | 10596.5 | GGB | 9.81 | GGB | 1003.6 | GGB | 64.52 | GGB | 164203.4 | GGB | 131582.64 | GGB | 0 | 0 | 2498 | 3600 | 2483.13 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258204.41 | GGB | 258207.09 | 2483.13 | 2483.13 |  |  |  | 0 | 1 | [14 empty] | 90.7602 |  |  | #VALUE!
13.06.2008 18:00 | 3600 | 2 | 767.35 | GGB | 765.201 | 777.75 | 770.33 | 255.98 | GGB | 10559.8 | GGB | 9.8 | GGB | 1003.18 | GGB | 64.75 | GGB | 163483.78 | GGB | 130862 | GGB | 0 | 0 | 2502 | 3600 | 2487.01 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258243.96 | GGB | 258246.64 | 2487.01 | 2487.01 |  |  |  | 1 | 1 |  |  |  |  | 130862 | 2487.01 | 130862 | 2487.01 | 8.229 | [5 empty] | 90.4042 |  |  | #VALUE!
13.06.2008 19:00 | 3600 | 2 | 767.7 | GGB | 766.3 | 778.969 | 771.429 | 255.52 | GGB | 10545.4 | GGB | 9.81 | GGB | 1002.47 | GGB | 64.98 | GGB | 162949.02 | GGB | 130254.17 | GGB | 0 | 0 | 2474 | 3600 | 2458.97 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258283.5 | GGB | 258286.19 | 2458.97 | 2458.97 |  |  |  | 0 | 1 | [14 empty] | 88.9697 |  |  | #VALUE!
13.06.2008 20:00 | 3600 | 2 | 767.27 | GGB | 765.201 | 778.969 | 770.33 | 257.09 | GGB | 10512 | GGB | 9.8 | GGB | 1002.58 | GGB | 64.46 | GGB | 164687.55 | GGB | 131860.53 | GGB | 0 | 0 | 2485 | 3600 | 2470.24 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258323.05 | GGB | 258325.74 | 2470.24 | 2470.24 |  |  |  | 0 | 1 | [14 empty] | 90.4798 |  |  | #VALUE!
13.06.2008 21:00 | 3600 | 2 | 767.51 | GGB | 767.766 | 780.398 | 772.527 | 257.49 | GGB | 10542.9 | GGB | 9.81 | GGB | 1002.64 | GGB | 64.18 | GGB | 164868.01 | GGB | 132120.49 | GGB | 0 | 0 | 2480 | 3600 | 2464.61 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258362.59 | GGB | 258365.29 | 2464.61 | 2464.61 |  |  |  | 0 | 1 | [14 empty] | 90.4515 |  |  | #VALUE!
13.06.2008 22:00 | 3600 | 2 | 766.53 | GGB | 765.201 | 778.172 | 769.963 | 257.44 | GGB | 10576.3 | GGB | 9.79 | GGB | 1002.62 | GGB | 64.73 | GGB | 163831.49 | GGB | 131073.46 | GGB | 0 | 0 | 2557 | 3600 | 2541.94 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258402.14 | GGB | 258404.84 | 2541.94 | 2541.94 |  |  |  | 1 | 1 |  |  |  |  | 131073.46 | 2541.94 | 131073.46 | 2541.94 | 8.4243 | [5 empty] | 92.5502 |  |  | #VALUE!
13.06.2008 23:00 | 3600 | 2 | 766.06 | GGB | 764.102 | 777.961 | 769.597 | 259.18 | GGB | 10630.2 | GGB | 9.79 | GGB | 1003.05 | GGB | 64.37 | GGB | 166453.59 | GGB | 133373.67 | GGB | 0 | 0 | 2614 | 3600 | 2598.45 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258441.68 | GGB | 258444.39 | 2598.45 | 2598.45 |  |  |  | 1 | 1 |  |  |  |  | 133373.67 | 2598.45 | 133373.67 | 2598.45 | 8.7627 | [5 empty] | 96.268 |  |  | #VALUE!
13.06.2008 24:00 | 3600 | 2 | 766.1 | GGB | 766.3 | 778.922 | 770.696 | 261.04 | GGB | 10676.3 | GGB | 9.8 | GGB | 1003.03 | GGB | 63.27 | GGB | 167932.45 | GGB | 134996.42 | GGB | 0 | 0 | 2622 | 3600 | 2607 | GGB | 100 | GGB | 39.55 | GGB | 39.55 | GGB | 258481.23 | GGB | 258483.94 | 2607 | 2607 |  |  |  | 0 | 1 | [14 empty] | 97.7599 |  |  | #VALUE!
14.06.2008 01:00 | 3600 | 2 | 765.45 | GGB | 765.201 | 777.867 | 769.597 | 260.87 | GGB | 10734.4 | GGB | 9.8 | GGB | 1002.82 | GGB | 63.52 | GGB | 167436.19 | GGB | 134464.37 | GGB | 0 | 0 | 2681 | 3600 | 2665.2 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258522.1 | GGB | 258524.81 | 2665.2 | 2665.2 |  |  |  | 1 | 1 |  |  |  |  | 134464.37 | 2665.2 | 134464.37 | 2665.2 | 8.7686 | [5 empty] | 99.5485 |  |  | #VALUE!
14.06.2008 02:00 | 3600 | 2 | 764.99 | GGB | 764.102 | 775.711 | 768.498 | 261.49 | GGB | 10756.3 | GGB | 9.8 | GGB | 1002.77 | GGB | 63.3 | GGB | 168392.39 | GGB | 135314.34 | GGB | 0 | 0 | 2722 | 3600 | 2707.04 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258562.97 | GGB | 258565.68 | 2707.04 | 2707.04 |  |  |  | 1 | 1 |  |  |  |  | 135314.34 | 2707.04 | 135314.34 | 2707.04 | 8.9626 | [5 empty] | 101.7504 |  |  | #VALUE!
14.06.2008 03:00 | 3600 | 2 | 765 | GGB | 763.004 | 775.664 | 768.132 | 262.26 | GGB | 10794.6 | GGB | 9.8 | GGB | 1002.9 | GGB | 63 | GGB | 169048.19 | GGB | 135982.42 | GGB | 0 | 0 | 2735 | 3600 | 2719.88 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258603.83 | GGB | 258606.55 | 2719.88 | 2719.88 |  |  |  | 0 | 1 | [14 empty] | 102.7377 |  |  | #VALUE!
14.06.2008 04:00 | 3600 | 2 | 765 | GGB | 764.102 | 776.648 | 769.597 | 262.61 | GGB | 10817.8 | GGB | 9.81 | GGB | 1002.64 | GGB | 62.8 | GGB | 169417.9 | GGB | 136326.94 | GGB | 0 | 0 | 2751 | 3600 | 2735.59 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258644.7 | GGB | 258647.42 | 2735.59 | 2735.59 |  |  |  | 1 | 1 |  |  |  |  | 136326.94 | 2735.59 | 136326.94 | 2735.59 | 9.1249 | [5 empty] | 103.5929 |  |  | #VALUE!
14.06.2008 05:00 | 3600 | 2 | 764.84 | GGB | 764.102 | 775.664 | 768.132 | 262.14 | GGB | 10806.4 | GGB | 9.81 | GGB | 1002.9 | GGB | 62.89 | GGB | 168770.9 | GGB | 135802.79 | GGB | 0 | 0 | 2760 | 3600 | 2744.18 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258685.57 | GGB | 258688.29 | 2744.18 | 2744.18 |  |  |  | 1 | 1 |  |  |  |  | 135802.79 | 2744.18 | 135802.79 | 2744.18 | 9.1184 | [5 empty] | 103.5187 |  |  | #VALUE!
14.06.2008 06:00 | 3600 | 2 | 764.61 | GGB | 761.538 | 773.578 | 765.934 | 262.82 | GGB | 10803.4 | GGB | 9.8 | GGB | 1003.01 | GGB | 62.98 | GGB | 168736.79 | GGB | 135755.46 | GGB | 0 | 0 | 2784 | 3600 | 2768.98 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258726.44 | GGB | 258729.16 | 2768.98 | 2768.98 |  |  |  | 0 | 1 | [14 empty] | 104.4178 |  |  | #VALUE!
14.06.2008 07:00 | 3600 | 2 | 764.96 | GGB | 764.102 | 775.664 | 768.498 | 262.87 | GGB | 10826.7 | GGB | 9.82 | GGB | 1003.08 | GGB | 62.98 | GGB | 168693.88 | GGB | 135729.87 | GGB | 0 | 0 | 2798 | 3600 | 2782.42 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258767.3 | GGB | 258770.03 | 2782.42 | 2782.42 |  |  |  | 1 | 1 |  |  |  |  | 135729.87 | 2782.42 | 135729.87 | 2782.42 | 9.2405 | [5 empty] | 104.9049 |  |  | #VALUE!
14.06.2008 08:00 | 3600 | 2 | 764.64 | GGB | 764.102 | 775.641 | 768.132 | 262.87 | GGB | 10812.5 | GGB | 9.81 | GGB | 1002.72 | GGB | 63.08 | GGB | 168540.93 | GGB | 135517.23 | GGB | 0 | 0 | 2815 | 3600 | 2799.05 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258808.17 | GGB | 258810.9 | 2799.05 | 2788.7819 |  |  |  | 1 | 1 |  |  |  |  | 135517.23 | 2788.7819 | 135517.23 | 2788.7819 | 9.2471 | [5 empty] | 105.3665 | 2788.7819 |  | 104.98
14.06.2008 09:00 | 3600 | 2 | 764.93 | GGB | 764.102 | 775.945 | 768.132 | 262.28 | GGB | 10779.9 | GGB | 9.81 | GGB | 1002.33 | GGB | 63.28 | GGB | 167663.96 | GGB | 134680.97 | GGB | 0 | 0 | 2786 | 3600 | 2770.83 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258849.04 | GGB | 258851.77 | 2770.83 | 2770.83 |  |  |  | 1 | 1 |  |  |  |  | 134680.97 | 2770.83 | 134680.97 | 2770.83 | 9.1309 | [5 empty] | 103.6606 |  |  | #VALUE!
14.06.2008 10:00 | 3600 | 2 | 764.87 | GGB | 763.004 | 775.758 | 767.766 | 263.1 | GGB | 10731.3 | GGB | 9.81 | GGB | 1002.56 | GGB | 62.82 | GGB | 168809.42 | GGB | 135816.38 | GGB | 0 | 0 | 2768 | 3600 | 2752.67 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258889.91 | GGB | 258892.64 | 2752.67 | 2752.67 |  |  |  | 0 | 1 | [14 empty] | 103.8494 |  |  | #VALUE!
14.06.2008 11:00 | 3600 | 2 | 765.05 | GGB | 765.201 | 777.82 | 769.963 | 263 | GGB | 10736.1 | GGB | 9.81 | GGB | 1002.18 | GGB | 63.2 | GGB | 168207.53 | GGB | 135128.35 | GGB | 0 | 0 | 2762 | 3600 | 2746.58 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258930.77 | GGB | 258933.51 | 2746.58 | 2746.58 |  |  |  | 1 | 1 |  |  |  |  | 135128.35 | 2746.58 | 135128.35 | 2746.58 | 9.081 | [5 empty] | 103.0947 |  |  | #VALUE!
14.06.2008 12:00 | 3600 | 2 | 765.04 | GGB | 765.201 | 777.727 | 768.864 | 262.02 | GGB | 10759.8 | GGB | 9.81 | GGB | 1001.74 | GGB | 63.51 | GGB | 166683.56 | GGB | 133721.67 | GGB | 0 | 0 | 2785 | 3600 | 2769.72 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 258971.64 | GGB | 258974.38 | 2769.72 | 2769.72 |  |  |  | 1 | 1 |  |  |  |  | 133721.67 | 2769.72 | 133721.67 | 2769.72 | 9.0622 | [5 empty] | 102.881 |  |  | #VALUE!
14.06.2008 13:00 | 3600 | 2 | 764.72 | GGB | 764.102 | 775.453 | 767.766 | 261.3 | GGB | 10739.3 | GGB | 9.8 | GGB | 1000.85 | GGB | 63.38 | GGB | 166383.17 | GGB | 133413.97 | GGB | 0 | 0 | 2808 | 3600 | 2792.4 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259012.51 | GGB | 259015.25 | 2792.4 | 2792.4 |  |  |  | 1 | 1 |  |  |  |  | 133413.97 | 2792.4 | 133413.97 | 2792.4 | 9.1154 | [5 empty] | 103.4848 |  |  | #VALUE!
14.06.2008 14:00 | 3600 | 2 | 764.53 | GGB | 764.102 | 776.508 | 768.864 | 262.41 | GGB | 10775.8 | GGB | 9.8 | GGB | 1001.73 | GGB | 62.85 | GGB | 167617.75 | GGB | 134733.18 | GGB | 0 | 0 | 2839 | 3600 | 2823.66 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259053.38 | GGB | 259056.12 | 2823.66 | 2805.0106 |  |  |  | 1 | 1 |  |  |  |  | 134733.18 | 2805.0106 | 134733.18 | 2805.0106 | 9.2471 | [5 empty] | 105.678 | 2805.0106 |  | 104.98
14.06.2008 15:00 | 3600 | 2 | 764.94 | GGB | 763.004 | 775.641 | 767.766 | 262.42 | GGB | 10780.6 | GGB | 9.81 | GGB | 1002.35 | GGB | 63.29 | GGB | 167690.37 | GGB | 134700.55 | GGB | 0 | 0 | 2798 | 3600 | 2782.9 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259094.24 | GGB | 259096.99 | 2782.9 | 2782.9 |  |  |  | 0 | 1 | [14 empty] | 104.1273 |  |  | #VALUE!
14.06.2008 16:00 | 3600 | 2 | 764.96 | GGB | 765.201 | 777.797 | 768.864 | 262.05 | GGB | 10765.8 | GGB | 9.81 | GGB | 1002.19 | GGB | 63.55 | GGB | 167136.9 | GGB | 134130.88 | GGB | 0 | 0 | 2779 | 3600 | 2763.7 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259135.11 | GGB | 259137.86 | 2763.7 | 2763.7 |  |  |  | 1 | 1 |  |  |  |  | 134130.88 | 2763.7 | 134130.88 | 2763.7 | 9.0702 | [5 empty] | 102.9715 |  |  | #VALUE!
14.06.2008 17:00 | 3600 | 2 | 766.2 | GGB | 765.201 | 777.82 | 769.963 | 260.54 | GGB | 10715.9 | GGB | 9.82 | GGB | 1001.7 | GGB | 64.37 | GGB | 165557.92 | GGB | 132474.67 | GGB | 0 | 0 | 2699 | 3600 | 2683.61 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259175.98 | GGB | 259178.73 | 2683.61 | 2683.61 |  |  |  | 1 | 1 |  |  |  |  | 132474.67 | 2683.61 | 132474.67 | 2683.61 | 8.6986 | [5 empty] | 98.7529 |  |  | #VALUE!
14.06.2008 18:00 | 3600 | 2 | 766.21 | GGB | 761.538 | 774.234 | 766.667 | 259.09 | GGB | 10639.3 | GGB | 9.81 | GGB | 1000.85 | GGB | 65.01 | GGB | 164327.74 | GGB | 131132.14 | GGB | 0 | 0 | 2665 | 3600 | 2649.31 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259216.85 | GGB | 259219.6 | 2649.31 | 2649.31 |  |  |  | 0 | 1 | [14 empty] | 96.5027 |  |  | #VALUE!
14.06.2008 19:00 | 3600 | 2 | 765.12 | GGB | 763.004 | 776.555 | 768.864 | 260.39 | GGB | 10683.4 | GGB | 9.8 | GGB | 1001.38 | GGB | 64.11 | GGB | 165869.31 | GGB | 132785.99 | GGB | 0 | 0 | 2746 | 3600 | 2730.19 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259257.72 | GGB | 259260.47 | 2730.19 | 2730.19 |  |  |  | 0 | 1 | [14 empty] | 100.7031 |  |  | #VALUE!
14.06.2008 20:00 | 3600 | 2 | 765.52 | GGB | 764.102 | 776.508 | 768.864 | 260.9 | GGB | 10716.3 | GGB | 9.81 | GGB | 1002.19 | GGB | 63.77 | GGB | 166013.46 | GGB | 133140.97 | GGB | 0 | 0 | 2728 | 3600 | 2712.24 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259298.58 | GGB | 259301.34 | 2712.24 | 2712.24 |  |  |  | 1 | 1 |  |  |  |  | 133140.97 | 2712.24 | 133140.97 | 2712.24 | 8.8356 | [5 empty] | 100.3084 |  |  | #VALUE!
14.06.2008 21:00 | 3600 | 2 | 765.29 | GGB | 763.004 | 775.711 | 767.766 | 261.46 | GGB | 10731.2 | GGB | 9.8 | GGB | 1002.63 | GGB | 63.64 | GGB | 166602.14 | GGB | 133724.94 | GGB | 0 | 0 | 2737 | 3600 | 2721.48 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259339.45 | GGB | 259342.21 | 2721.48 | 2721.48 |  |  |  | 0 | 1 | [14 empty] | 101.0916 |  |  | #VALUE!
14.06.2008 22:00 | 3600 | 2 | 764.96 | GGB | 763.004 | 775.875 | 767.766 | 261.93 | GGB | 10741.9 | GGB | 9.8 | GGB | 1003.17 | GGB | 63.53 | GGB | 167285.45 | GGB | 134389.27 | GGB | 0 | 0 | 2747 | 3600 | 2731.71 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259380.32 | GGB | 259383.08 | 2731.71 | 2731.71 |  |  |  | 0 | 1 | [14 empty] | 101.9757 |  |  | #VALUE!
14.06.2008 23:00 | 3600 | 2 | 764.52 | GGB | 764.102 | 775.781 | 767.766 | 263.61 | GGB | 10790.6 | GGB | 9.79 | GGB | 1003.82 | GGB | 63.19 | GGB | 169039.39 | GGB | 136022.28 | GGB | 0 | 0 | 2799 | 3600 | 2783.09 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259421.19 | GGB | 259423.95 | 2783.09 | 2778.4272 |  |  |  | 1 | 1 |  |  |  |  | 136022.28 | 2778.4272 | 136022.28 | 2778.4272 | 9.2471 | [5 empty] | 105.1562 | 2778.4272 |  | 104.98
14.06.2008 24:00 | 3600 | 2 | 764.68 | GGB | 763.004 | 774.727 | 767.766 | 264.38 | GGB | 10858.4 | GGB | 9.8 | GGB | 1004.81 | GGB | 62.76 | GGB | 170788.92 | GGB | 137741.17 | GGB | 0 | 0 | 2819 | 3600 | 2803.05 | GGB | 100 | GGB | 40.87 | GGB | 40.87 | GGB | 259462.05 | GGB | 259464.82 | 2803.05 | 2743.7548 |  |  |  | 0 | 1 | [14 empty] | 107.2487 | 2743.7548 |  | 104.98
15.06.2008 01:00 | 3600 | 2 | 764.11 | GGB | 763.004 | 775.852 | 767.766 | 265.62 | GGB | 10893.8 | GGB | 9.79 | GGB | 1004.69 | GGB | 62.02 | GGB | 171829.84 | GGB | 138871.47 | GGB | 0 | 0 | 2858 | 3600 | 2842.94 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259500.76 | GGB | 259503.52 | 2842.94 | 2721.4229 |  |  |  | 0 | 1 | [14 empty] | 109.6676 | 2721.4229 |  | 104.98
15.06.2008 02:00 | 3600 | 2 | 764.39 | GGB | 763.004 | 774.844 | 767.766 | 266.57 | GGB | 10936.9 | GGB | 9.81 | GGB | 1005.19 | GGB | 61.96 | GGB | 172709.01 | GGB | 139676.54 | GGB | 0 | 0 | 2871 | 3600 | 2855.32 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259539.46 | GGB | 259542.22 | 2855.32 | 2705.7371 |  |  |  | 0 | 1 | [14 empty] | 110.7837 | 2705.7371 |  | 104.98
15.06.2008 03:00 | 3600 | 2 | 763.91 | GGB | 764.102 | 775.992 | 768.132 | 266.85 | GGB | 10955.5 | GGB | 9.8 | GGB | 1005.44 | GGB | 61.67 | GGB | 173271.29 | GGB | 140285.95 | GGB | 0 | 0 | 2896 | 3600 | 2880.71 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259578.17 | GGB | 259580.92 | 2880.71 | 2693.9833 |  |  |  | 1 | 1 |  |  |  |  | 140285.95 | 2693.9833 | 140285.95 | 2693.9833 | 9.7656 | [5 empty] | 112.2564 | 2693.9833 |  | 104.98
15.06.2008 04:00 | 3600 | 2 | 763.93 | GGB | 761.538 | 774.609 | 767.033 | 267.44 | GGB | 10971.5 | GGB | 9.81 | GGB | 1006.15 | GGB | 61.57 | GGB | 173693.82 | GGB | 140769.87 | GGB | 0 | 0 | 2909 | 3600 | 2893.73 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259616.87 | GGB | 259619.62 | 2893.73 | 2684.7222 |  |  |  | 0 | 1 | [14 empty] | 113.1528 | 2684.7222 |  | 104.98
15.06.2008 05:00 | 3600 | 2 | 763.45 | GGB | 762.637 | 774.609 | 767.033 | 267.85 | GGB | 10979.2 | GGB | 9.8 | GGB | 1006.31 | GGB | 61.4 | GGB | 174014.01 | GGB | 141125.39 | GGB | 0 | 0 | 2941 | 3600 | 2925.88 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259655.57 | GGB | 259658.32 | 2925.88 | 2677.9589 |  |  |  | 0 | 1 | [14 empty] | 114.6989 | 2677.9589 |  | 104.98
15.06.2008 06:00 | 3600 | 2 | 763.33 | GGB | 762.637 | 774.586 | 767.033 | 268.52 | GGB | 11000.1 | GGB | 9.8 | GGB | 1006.57 | GGB | 61.21 | GGB | 174720.43 | GGB | 141814.83 | GGB | 0 | 0 | 2958 | 3600 | 2942.4 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259694.28 | GGB | 259697.02 | 2942.4 | 2664.9399 |  |  |  | 0 | 1 | [14 empty] | 115.91 | 2664.9399 |  | 104.98
15.06.2008 07:00 | 3600 | 2 | 764.26 | GGB | 761.538 | 773.32 | 767.033 | 267.89 | GGB | 11010.8 | GGB | 9.82 | GGB | 1006.93 | GGB | 61.35 | GGB | 173932.59 | GGB | 141168.26 | GGB | 0 | 0 | 2916 | 3600 | 2900.13 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259732.98 | GGB | 259735.72 | 2900.13 | 2677.1457 |  |  |  | 0 | 1 | [14 empty] | 113.724 | 2677.1457 |  | 104.98
15.06.2008 08:00 | 3600 | 2 | 764.68 | GGB | 764.102 | 775.922 | 768.132 | 266.86 | GGB | 10979.8 | GGB | 9.82 | GGB | 1007.46 | GGB | 61.69 | GGB | 172765.13 | GGB | 140152.4 | GGB | 0 | 0 | 2882 | 3600 | 2866.48 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259771.69 | GGB | 259774.42 | 2866.48 | 2696.5503 |  |  |  | 1 | 1 |  |  |  |  | 140152.4 | 2696.5503 | 140152.4 | 2696.5503 | 9.7656 | [5 empty] | 111.5956 | 2696.5503 |  | 104.98
15.06.2008 09:00 | 3600 | 2 | 765.44 | GGB | 765.201 | 777.117 | 769.597 | 266.86 | GGB | 10893.7 | GGB | 9.82 | GGB | 1007.39 | GGB | 61.37 | GGB | 173330.7 | GGB | 140734.03 | GGB | 0 | 0 | 2788 | 3600 | 2773.02 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259810.39 | GGB | 259813.12 | 2773.02 | 2685.4059 |  |  |  | 1 | 1 |  |  |  |  | 140734.03 | 2685.4059 | 140734.03 | 2685.4059 | 9.7656 | [5 empty] | 108.4051 | 2685.4059 |  | 104.98
15.06.2008 10:00 | 3600 | 2 | 766.26 | GGB | 765.201 | 777.375 | 769.597 | 264.41 | GGB | 10864.8 | GGB | 9.82 | GGB | 1007.36 | GGB | 62.24 | GGB | 170580.96 | GGB | 138140.08 | GGB | 0 | 0 | 2726 | 3600 | 2710.26 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259849.09 | GGB | 259851.82 | 2710.26 | 2710.26 |  |  |  | 1 | 1 |  |  |  |  | 138140.08 | 2710.26 | 138140.08 | 2710.26 | 9.6743 | [5 empty] | 103.9988 |  |  | #VALUE!
15.06.2008 11:00 | 3600 | 2 | 766.35 | GGB | 765.201 | 778.641 | 770.696 | 263 | GGB | 10809.3 | GGB | 9.81 | GGB | 1006.58 | GGB | 63.28 | GGB | 168971.17 | GGB | 136306.14 | GGB | 0 | 0 | 2703 | 3600 | 2687.67 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259887.8 | GGB | 259890.52 | 2687.67 | 2687.67 |  |  |  | 1 | 1 |  |  |  |  | 136306.14 | 2687.67 | 136306.14 | 2687.67 | 9.4663 | [5 empty] | 101.7628 |  |  | #VALUE!
15.06.2008 12:00 | 3600 | 2 | 766.19 | GGB | 765.201 | 777.797 | 769.597 | 263.71 | GGB | 10748.2 | GGB | 9.8 | GGB | 1006.43 | GGB | 62.85 | GGB | 170445.62 | GGB | 137652.03 | GGB | 0 | 0 | 2666 | 3600 | 2650.71 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259926.5 | GGB | 259929.22 | 2650.71 | 2650.71 |  |  |  | 1 | 1 |  |  |  |  | 137652.03 | 2650.71 | 137652.03 | 2650.71 | 9.4283 | [5 empty] | 101.3543 |  |  | #VALUE!
15.06.2008 13:00 | 3600 | 2 | 767.12 | GGB | 766.3 | 780.023 | 771.795 | 260.95 | GGB | 10753.3 | GGB | 9.82 | GGB | 1005.83 | GGB | 63.59 | GGB | 167298.65 | GGB | 134730.84 | GGB | 0 | 0 | 2606 | 3600 | 2590.9 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 259965.21 | GGB | 259967.92 | 2590.9 | 2590.9 |  |  |  | 0 | 1 | [14 empty] | 96.965 |  |  | #VALUE!
15.06.2008 14:00 | 3600 | 2 | 767.05 | GGB | 766.3 | 779.133 | 771.795 | 260.19 | GGB | 10713 | GGB | 9.81 | GGB | 1005.49 | GGB | 63.96 | GGB | 167067.58 | GGB | 134353.41 | GGB | 0 | 0 | 2602 | 3600 | 2586.74 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260003.91 | GGB | 260006.62 | 2586.74 | 2586.74 |  |  |  | 0 | 1 | [14 empty] | 96.5381 |  |  | #VALUE!
15.06.2008 15:00 | 3600 | 2 | 767.23 | GGB | 766.3 | 778.336 | 771.795 | 258.9 | GGB | 10656.5 | GGB | 9.81 | GGB | 1005.11 | GGB | 64.44 | GGB | 165914.43 | GGB | 133183.74 | GGB | 0 | 0 | 2566 | 3600 | 2550.42 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260042.61 | GGB | 260045.32 | 2550.42 | 2550.42 |  |  |  | 1 | 1 |  |  |  |  | 133183.74 | 2550.42 | 133183.74 | 2550.42 | 8.7771 | [5 empty] | 94.354 |  |  | #VALUE!
15.06.2008 16:00 | 3600 | 2 | 767.34 | GGB | 767.766 | 780.469 | 773.26 | 260.35 | GGB | 10618.1 | GGB | 9.81 | GGB | 1004.65 | GGB | 63.91 | GGB | 167776.2 | GGB | 134829.98 | GGB | 0 | 0 | 2549 | 3600 | 2533.46 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260081.32 | GGB | 260084.02 | 2533.46 | 2533.46 |  |  |  | 0 | 1 | [14 empty] | 94.8851 |  |  | #VALUE!
15.06.2008 17:00 | 3600 | 2 | 767.61 | GGB | 766.3 | 778.805 | 771.795 | 258.47 | GGB | 10618 | GGB | 9.81 | GGB | 1004.14 | GGB | 64.24 | GGB | 165744.98 | GGB | 132998.54 | GGB | 0 | 0 | 2520 | 3600 | 2504.39 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260120.02 | GGB | 260122.72 | 2504.39 | 2504.39 |  |  |  | 0 | 1 | [14 empty] | 92.5223 |  |  | #VALUE!
15.06.2008 18:00 | 3600 | 2 | 767.4 | GGB | 765.201 | 777.82 | 771.795 | 258.07 | GGB | 10619.2 | GGB | 9.81 | GGB | 1003.84 | GGB | 64.41 | GGB | 165408.27 | GGB | 132623.32 | GGB | 0 | 0 | 2524 | 3600 | 2508.67 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260158.73 | GGB | 260161.42 | 2508.67 | 2508.67 |  |  |  | 1 | 1 |  |  |  |  | 132623.32 | 2508.67 | 132623.32 | 2508.67 | 8.5971 | [5 empty] | 92.4189 |  |  | #VALUE!
15.06.2008 19:00 | 3600 | 2 | 767.65 | GGB | 766.667 | 779.836 | 772.161 | 258 | GGB | 10609.4 | GGB | 9.81 | GGB | 1003.79 | GGB | 64.45 | GGB | 165072.67 | GGB | 132332.7 | GGB | 0 | 0 | 2506 | 3600 | 2490.97 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260197.43 | GGB | 260200.12 | 2490.97 | 2490.97 |  |  |  | 0 | 1 | [14 empty] | 91.5658 |  |  | #VALUE!
15.06.2008 20:00 | 3600 | 2 | 766.59 | GGB | 760.44 | 773.039 | 765.934 | 258.24 | GGB | 10607.5 | GGB | 9.79 | GGB | 1003.8 | GGB | 64.08 | GGB | 165571.12 | GGB | 132877.37 | GGB | 0 | 0 | 2555 | 3600 | 2540.11 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260236.13 | GGB | 260238.82 | 2540.11 | 2540.11 |  |  |  | 0 | 1 | [14 empty] | 93.7564 |  |  | #VALUE!
15.06.2008 21:00 | 3600 | 2 | 767.55 | GGB | 767.766 | 780.398 | 772.161 | 258.61 | GGB | 10666.7 | GGB | 9.82 | GGB | 1004.21 | GGB | 63.75 | GGB | 165717.47 | GGB | 133179.8 | GGB | 0 | 0 | 2542 | 3600 | 2526.43 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260274.84 | GGB | 260277.52 | 2526.43 | 2526.43 |  |  |  | 0 | 1 | [14 empty] | 93.4637 |  |  | #VALUE!
15.06.2008 22:00 | 3600 | 2 | 766.11 | GGB | 764.102 | 777 | 769.597 | 259.34 | GGB | 10674.7 | GGB | 9.79 | GGB | 1004.55 | GGB | 63.63 | GGB | 166265.44 | GGB | 133714.53 | GGB | 0 | 0 | 2611 | 3600 | 2595.95 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260313.54 | GGB | 260316.22 | 2595.95 | 2595.95 |  |  |  | 1 | 1 |  |  |  |  | 133714.53 | 2595.95 | 133714.53 | 2595.95 | 8.9694 | [5 empty] | 96.4212 |  |  | #VALUE!
15.06.2008 23:00 | 3600 | 2 | 765.7 | GGB | 764.102 | 776.977 | 768.498 | 260.8 | GGB | 10716.8 | GGB | 9.8 | GGB | 1005.24 | GGB | 63.48 | GGB | 167196.32 | GGB | 134616.59 | GGB | 0 | 0 | 2664 | 3600 | 2648.76 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260352.25 | GGB | 260354.92 | 2648.76 | 2648.76 |  |  |  | 1 | 1 |  |  |  |  | 134616.59 | 2648.76 | 134616.59 | 2648.76 | 9.2136 | [5 empty] | 99.0464 |  |  | #VALUE!
15.06.2008 24:00 | 3600 | 2 | 764.35 | GGB | 762.637 | 774.469 | 767.033 | 262.72 | GGB | 10788.6 | GGB | 9.78 | GGB | 1006.17 | GGB | 63 | GGB | 169372.79 | GGB | 136686.14 | GGB | 0 | 0 | 2777 | 3600 | 2761.63 | GGB | 100 | GGB | 38.7 | GGB | 38.7 | GGB | 260390.95 | GGB | 260393.62 | 2761.63 | 2761.63 |  |  |  | 0 | 1 | [14 empty] | 104.8546 |  |  | #VALUE!
16.06.2008 01:00 | 3600 | 2 | 764.24 | GGB | 761.538 | 773.227 | 765.934 | 265.41 | GGB | 10859.8 | GGB | 9.79 | GGB | 1006.65 | GGB | 62.95 | GGB | 171056.31 | GGB | 138134.45 | GGB | 0 | 0 | 2842 | 3600 | 2826.51 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260428.94 | GGB | 260431.61 | 2826.51 | 2735.9431 |  |  |  | 0 | 1 | [14 empty] | 108.4551 | 2735.9431 |  | 104.98
16.06.2008 02:00 | 3600 | 2 | 764.24 | GGB | 764.102 | 776.484 | 769.597 | 266.5 | GGB | 10919.9 | GGB | 9.81 | GGB | 1007.52 | GGB | 62.6 | GGB | 172280.98 | GGB | 139385.65 | GGB | 0 | 0 | 2874 | 3600 | 2858.54 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260466.93 | GGB | 260469.6 | 2858.54 | 2711.3838 |  |  |  | 1 | 1 |  |  |  |  | 139385.65 | 2711.3838 | 139385.65 | 2711.3838 | 9.9481 | [5 empty] | 110.6776 | 2711.3838 |  | 104.98
16.06.2008 03:00 | 3600 | 2 | 763.8 | GGB | 763.004 | 775.43 | 767.033 | 266.87 | GGB | 10937.2 | GGB | 9.8 | GGB | 1007.52 | GGB | 62.34 | GGB | 172842.15 | GGB | 139950.49 | GGB | 0 | 0 | 2895 | 3600 | 2879.14 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260504.92 | GGB | 260507.59 | 2879.14 | 2700.4407 |  |  |  | 0 | 1 | [14 empty] | 111.927 | 2700.4407 |  | 104.98
16.06.2008 04:00 | 3600 | 2 | 763.32 | GGB | 761.538 | 773.461 | 766.667 | 267.66 | GGB | 10962.6 | GGB | 9.8 | GGB | 1007.84 | GGB | 62.01 | GGB | 173978.8 | GGB | 141055.49 | GGB | 0 | 0 | 2938 | 3600 | 2922.48 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260542.91 | GGB | 260545.58 | 2922.48 | 2679.286 |  |  |  | 0 | 1 | [14 empty] | 114.5088 | 2679.286 |  | 104.98
16.06.2008 05:00 | 3600 | 2 | 763.44 | GGB | 761.172 | 773.555 | 766.3 | 268.13 | GGB | 10994.9 | GGB | 9.8 | GGB | 1007.7 | GGB | 61.63 | GGB | 174304.5 | GGB | 141459.53 | GGB | 0 | 0 | 2941 | 3600 | 2925.76 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260580.9 | GGB | 260583.57 | 2925.76 | 2671.6334 |  |  |  | 0 | 1 | [14 empty] | 114.9657 | 2671.6334 |  | 104.98
16.06.2008 06:00 | 3600 | 2 | 763.36 | GGB | 763.37 | 775.945 | 767.766 | 268.83 | GGB | 11026.9 | GGB | 9.81 | GGB | 1008.02 | GGB | 61.21 | GGB | 175134.16 | GGB | 142357.02 | GGB | 0 | 0 | 2960 | 3600 | 2943.95 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260618.88 | GGB | 260621.56 | 2943.95 | 2654.79 |  |  |  | 0 | 1 | [14 empty] | 116.4144 | 2654.79 |  | 104.98
16.06.2008 07:00 | 3600 | 2 | 764.07 | GGB | 763.37 | 775.195 | 768.132 | 267.75 | GGB | 11021.7 | GGB | 9.82 | GGB | 1008.01 | GGB | 61.36 | GGB | 174184.57 | GGB | 141519.72 | GGB | 0 | 0 | 2929 | 3600 | 2913.85 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260656.87 | GGB | 260659.55 | 2913.85 | 2670.4971 |  |  |  | 0 | 1 | [14 empty] | 114.5465 | 2670.4971 |  | 104.98
16.06.2008 08:00 | 3600 | 2 | 765 | GGB | 764.469 | 776.555 | 768.498 | 265.41 | GGB | 10960.4 | GGB | 9.83 | GGB | 1007.9 | GGB | 62.05 | GGB | 171564.66 | GGB | 139088.64 | GGB | 0 | 0 | 2854 | 3600 | 2838.58 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260694.86 | GGB | 260697.54 | 2838.58 | 2717.1737 |  |  |  | 1 | 1 |  |  |  |  | 139088.64 | 2717.1737 | 139088.64 | 2717.1737 | 9.9481 | [5 empty] | 109.6706 | 2717.1737 |  | 104.98
16.06.2008 09:00 | 3600 | 2 | 766.57 | GGB | 765.934 | 778.5 | 770.696 | 261.38 | GGB | 10812.5 | GGB | 9.83 | GGB | 1007.4 | GGB | 63.3 | GGB | 167449.4 | GGB | 135181.99 | GGB | 0 | 0 | 2699 | 3600 | 2683.17 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260732.85 | GGB | 260735.53 | 2683.17 | 2683.17 |  |  |  | 1 | 1 |  |  |  |  | 135181.99 | 2683.17 | 135181.99 | 2683.17 | 9.5477 | [5 empty] | 100.7545 |  |  | #VALUE!
16.06.2008 10:00 | 3600 | 2 | 766.99 | GGB | 765.934 | 778.617 | 770.696 | 259.27 | GGB | 10685 | GGB | 9.82 | GGB | 1006.7 | GGB | 64.28 | GGB | 165376.36 | GGB | 133024.9 | GGB | 0 | 0 | 2613 | 3600 | 2597.89 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260770.84 | GGB | 260773.52 | 2597.89 | 2597.89 |  |  |  | 1 | 1 |  |  |  |  | 133024.9 | 2597.89 | 133024.9 | 2597.89 | 9.0967 | [5 empty] | 95.9956 |  |  | #VALUE!
16.06.2008 11:00 | 3600 | 2 | 767.22 | GGB | 765.934 | 778.688 | 770.696 | 258.48 | GGB | 10616.3 | GGB | 9.81 | GGB | 1006.57 | GGB | 64.88 | GGB | 164389.36 | GGB | 131980.87 | GGB | 0 | 0 | 2566 | 3600 | 2551.17 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260808.83 | GGB | 260811.51 | 2551.17 | 2551.17 |  |  |  | 1 | 1 |  |  |  |  | 131980.87 | 2551.17 | 131980.87 | 2551.17 | 8.863 | [5 empty] | 93.5293 |  |  | #VALUE!
16.06.2008 12:00 | 3600 | 2 | 767.55 | GGB | 765.934 | 778.547 | 770.696 | 258.04 | GGB | 10572.3 | GGB | 9.81 | GGB | 1005.45 | GGB | 64.91 | GGB | 164585.22 | GGB | 131977.01 | GGB | 0 | 0 | 2524 | 3600 | 2508.65 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260846.82 | GGB | 260849.5 | 2508.65 | 2508.65 |  |  |  | 1 | 1 |  |  |  |  | 131977.01 | 2508.65 | 131977.01 | 2508.65 | 8.715 | [5 empty] | 91.9678 |  |  | #VALUE!
16.06.2008 13:00 | 3600 | 2 | 768.1 | GGB | 765.934 | 778.641 | 770.696 | 258.7 | GGB | 10535.3 | GGB | 9.81 | GGB | 1005.08 | GGB | 64.17 | GGB | 165848.41 | GGB | 133235.53 | GGB | 0 | 0 | 2469 | 3600 | 2453.81 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260884.81 | GGB | 260887.49 | 2453.81 | 2453.81 |  |  |  | 1 | 1 |  |  |  |  | 133235.53 | 2453.81 | 133235.53 | 2453.81 | 8.6058 | [5 empty] | 90.8152 |  |  | #VALUE!
16.06.2008 14:00 | 3600 | 2 | 768.72 | GGB | 767.033 | 780.961 | 773.26 | 257.18 | GGB | 10523.3 | GGB | 9.82 | GGB | 1004.67 | GGB | 64.64 | GGB | 164622.63 | GGB | 132013.29 | GGB | 0 | 0 | 2440 | 3600 | 2424.63 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260922.8 | GGB | 260925.48 | 2424.63 | 2424.63 |  |  |  | 0 | 1 | [14 empty] | 88.9121 |  |  | #VALUE!
16.06.2008 15:00 | 3600 | 2 | 768.21 | GGB | 765.934 | 778.805 | 771.795 | 255.31 | GGB | 10505.8 | GGB | 9.8 | GGB | 1004.06 | GGB | 65.26 | GGB | 162397.75 | GGB | 129912.34 | GGB | 0 | 0 | 2449 | 3600 | 2433.85 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260960.79 | GGB | 260963.47 | 2433.85 | 2433.85 |  |  |  | 0 | 1 | [14 empty] | 87.8298 |  |  | #VALUE!
16.06.2008 16:00 | 3600 | 2 | 768.54 | GGB | 767.033 | 780.844 | 773.26 | 254.81 | GGB | 10493.1 | GGB | 9.81 | GGB | 1003.31 | GGB | 65.73 | GGB | 161779.36 | GGB | 129139.01 | GGB | 0 | 0 | 2434 | 3600 | 2418.75 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 260998.78 | GGB | 261001.46 | 2418.75 | 2418.75 |  |  |  | 0 | 1 | [14 empty] | 86.7653 |  |  | #VALUE!
16.06.2008 17:00 | 3600 | 2 | 767.94 | GGB | 765.934 | 779.813 | 771.795 | 254.86 | GGB | 10436.6 | GGB | 9.8 | GGB | 1002.56 | GGB | 65.58 | GGB | 162205.19 | GGB | 129439.05 | GGB | 0 | 0 | 2434 | 3600 | 2418.66 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261036.77 | GGB | 261039.45 | 2418.66 | 2418.66 |  |  |  | 0 | 1 | [14 empty] | 86.9636 |  |  | #VALUE!
16.06.2008 18:00 | 3600 | 2 | 768.78 | GGB | 767.033 | 779.836 | 772.161 | 254.49 | GGB | 10452.4 | GGB | 9.81 | GGB | 1002.13 | GGB | 65.52 | GGB | 161598.9 | GGB | 128925.63 | GGB | 0 | 0 | 2394 | 3600 | 2379.04 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261074.75 | GGB | 261077.44 | 2379.04 | 2379.04 |  |  |  | 0 | 1 | [14 empty] | 85.1998 |  |  | #VALUE!
16.06.2008 19:00 | 3600 | 2 | 768.18 | GGB | 767.033 | 779.813 | 772.161 | 254.44 | GGB | 10456.9 | GGB | 9.8 | GGB | 1001.93 | GGB | 66.06 | GGB | 161286.41 | GGB | 128445.06 | GGB | 0 | 0 | 2441 | 3600 | 2425.86 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261112.74 | GGB | 261115.43 | 2425.86 | 2425.86 |  |  |  | 0 | 1 | [14 empty] | 86.5527 |  |  | #VALUE!
16.06.2008 20:00 | 3600 | 2 | 767.76 | GGB | 764.835 | 778.617 | 770.696 | 255.03 | GGB | 10461.8 | GGB | 9.79 | GGB | 1002.03 | GGB | 66.02 | GGB | 161693.53 | GGB | 128796.97 | GGB | 0 | 0 | 2464 | 3600 | 2449.14 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261150.73 | GGB | 261153.42 | 2449.14 | 2449.14 |  |  |  | 1 | 1 |  |  |  |  | 128796.97 | 2449.14 | 128796.97 | 2449.14 | 8.3033 | [5 empty] | 87.6227 |  |  | #VALUE!
16.06.2008 21:00 | 3600 | 2 | 767.45 | GGB | 767.033 | 779.555 | 771.795 | 256.16 | GGB | 10508.5 | GGB | 9.8 | GGB | 1002.76 | GGB | 65.57 | GGB | 162350.43 | GGB | 129583.81 | GGB | 0 | 0 | 2486 | 3600 | 2470.69 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261188.72 | GGB | 261191.41 | 2470.69 | 2470.69 |  |  |  | 0 | 1 | [14 empty] | 88.9337 |  |  | #VALUE!
16.06.2008 22:00 | 3600 | 2 | 766.9 | GGB | 765.934 | 778.523 | 770.696 | 257.25 | GGB | 10555.7 | GGB | 9.79 | GGB | 1002.85 | GGB | 65.24 | GGB | 163353.94 | GGB | 130525.31 | GGB | 0 | 0 | 2551 | 3600 | 2536.05 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261226.71 | GGB | 261229.4 | 2536.05 | 2536.05 |  |  |  | 1 | 1 |  |  |  |  | 130525.31 | 2536.05 | 130525.31 | 2536.05 | 8.7133 | [5 empty] | 91.9496 |  |  | #VALUE!
16.06.2008 23:00 | 3600 | 2 | 766.18 | GGB | 764.835 | 777.281 | 769.597 | 258.6 | GGB | 10627.9 | GGB | 9.8 | GGB | 1003.62 | GGB | 64.77 | GGB | 165074.87 | GGB | 132184.59 | GGB | 0 | 0 | 2618 | 3600 | 2603.02 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261264.7 | GGB | 261267.39 | 2603.02 | 2603.02 |  |  |  | 1 | 1 |  |  |  |  | 132184.59 | 2603.02 | 132184.59 | 2603.02 | 9.0571 | [5 empty] | 95.5775 |  |  | #VALUE!
16.06.2008 24:00 | 3600 | 2 | 765.62 | GGB | 763.37 | 776.32 | 768.498 | 259.98 | GGB | 10661.6 | GGB | 9.79 | GGB | 1004.05 | GGB | 64.47 | GGB | 165680.06 | GGB | 132844.31 | GGB | 0 | 0 | 2659 | 3600 | 2643.57 | GGB | 100 | GGB | 37.99 | GGB | 37.99 | GGB | 261302.69 | GGB | 261305.38 | 2643.57 | 2643.57 |  |  |  | 0 | 1 | [14 empty] | 97.5509 |  |  | #VALUE!
17.06.2008 01:00 | 3600 | 2 | 764.87 | GGB | 762.271 | 775.242 | 768.132 | 261.85 | GGB | 10725.4 | GGB | 9.79 | GGB | 1004.32 | GGB | 63.99 | GGB | 167601.25 | GGB | 134611.32 | GGB | 0 | 0 | 2744 | 3600 | 2728.21 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261341.9 | GGB | 261344.59 | 2728.21 | 2728.21 |  |  |  | 0 | 1 | [14 empty] | 102.0133 |  |  | #VALUE!
17.06.2008 02:00 | 3600 | 2 | 765.24 | GGB | 764.469 | 777.516 | 769.597 | 262.64 | GGB | 10778.6 | GGB | 9.81 | GGB | 1004.48 | GGB | 63.38 | GGB | 168248.24 | GGB | 135400.1 | GGB | 0 | 0 | 2729 | 3600 | 2713.87 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261381.11 | GGB | 261383.8 | 2713.87 | 2713.87 |  |  |  | 1 | 1 |  |  |  |  | 135400.1 | 2713.87 | 135400.1 | 2713.87 | 9.3715 | [5 empty] | 102.0717 |  |  | #VALUE!
17.06.2008 03:00 | 3600 | 2 | 764.77 | GGB | 764.469 | 776.508 | 768.132 | 262.97 | GGB | 10788.7 | GGB | 9.8 | GGB | 1004.24 | GGB | 63.09 | GGB | 168722.49 | GGB | 135864.06 | GGB | 0 | 0 | 2760 | 3600 | 2744.99 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261420.32 | GGB | 261423.01 | 2744.99 | 2744.99 |  |  |  | 1 | 1 |  |  |  |  | 135864.06 | 2744.99 | 135864.06 | 2744.99 | 9.5115 | [5 empty] | 103.596 |  |  | #VALUE!
17.06.2008 04:00 | 3600 | 2 | 764.82 | GGB | 762.271 | 775.336 | 767.033 | 263.28 | GGB | 10800.2 | GGB | 9.8 | GGB | 1004.24 | GGB | 63.1 | GGB | 168836.92 | GGB | 135955.23 | GGB | 0 | 0 | 2762 | 3600 | 2746.08 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261459.53 | GGB | 261462.22 | 2746.08 | 2746.08 |  |  |  | 0 | 1 | [14 empty] | 103.7066 |  |  | #VALUE!
17.06.2008 05:00 | 3600 | 2 | 764.84 | GGB | 764.469 | 777.328 | 769.597 | 263.66 | GGB | 10821.6 | GGB | 9.81 | GGB | 1004.34 | GGB | 63.04 | GGB | 169296.87 | GGB | 136362.81 | GGB | 0 | 0 | 2781 | 3600 | 2765.17 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261498.74 | GGB | 261501.43 | 2765.17 | 2765.17 |  |  |  | 1 | 1 |  |  |  |  | 136362.81 | 2765.17 | 136362.81 | 2765.17 | 9.6166 | [5 empty] | 104.7407 |  |  | #VALUE!
17.06.2008 06:00 | 3600 | 2 | 764.87 | GGB | 764.835 | 777.375 | 769.597 | 264.27 | GGB | 10833.2 | GGB | 9.81 | GGB | 1004.17 | GGB | 63.13 | GGB | 169765.61 | GGB | 136679.05 | GGB | 0 | 0 | 2803 | 3600 | 2787.84 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261537.95 | GGB | 261540.64 | 2787.84 | 2765.0763 |  |  |  | 1 | 1 |  |  |  |  | 136679.05 | 2765.0763 | 136679.05 | 2765.0763 | 9.6386 | [5 empty] | 105.8443 | 2765.0763 |  | 104.98
17.06.2008 07:00 | 3600 | 2 | 765.01 | GGB | 763.37 | 775.242 | 767.033 | 263.44 | GGB | 10814.2 | GGB | 9.81 | GGB | 1004.4 | GGB | 63.33 | GGB | 169132.92 | GGB | 136119.04 | GGB | 0 | 0 | 2788 | 3600 | 2772.09 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261577.16 | GGB | 261579.85 | 2772.09 | 2772.09 |  |  |  | 0 | 1 | [14 empty] | 104.8151 |  |  | #VALUE!
17.06.2008 08:00 | 3600 | 2 | 765.22 | GGB | 764.469 | 777.422 | 768.498 | 262.76 | GGB | 10800.7 | GGB | 9.82 | GGB | 1004.68 | GGB | 63.48 | GGB | 168080.99 | GGB | 135250.9 | GGB | 0 | 0 | 2762 | 3600 | 2746.88 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261616.37 | GGB | 261619.06 | 2746.88 | 2746.88 |  |  |  | 1 | 1 |  |  |  |  | 135250.9 | 2746.88 | 135250.9 | 2746.88 | 9.4751 | [5 empty] | 103.1994 |  |  | #VALUE!
17.06.2008 09:00 | 3600 | 2 | 764.82 | GGB | 762.271 | 775.031 | 767.033 | 262.02 | GGB | 10762.6 | GGB | 9.8 | GGB | 1004.76 | GGB | 63.23 | GGB | 167161.11 | GGB | 134620.34 | GGB | 0 | 0 | 2770 | 3600 | 2754.1 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261655.58 | GGB | 261658.27 | 2754.1 | 2754.1 |  |  |  | 0 | 1 | [14 empty] | 102.9883 |  |  | #VALUE!
17.06.2008 10:00 | 3600 | 2 | 765.37 | GGB | 763.37 | 776.109 | 768.498 | 262.27 | GGB | 10780 | GGB | 9.82 | GGB | 1004.38 | GGB | 63.43 | GGB | 167002.66 | GGB | 134363.92 | GGB | 0 | 0 | 2763 | 3600 | 2747.23 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261694.79 | GGB | 261697.48 | 2747.23 | 2747.23 |  |  |  | 0 | 1 | [14 empty] | 102.5357 |  |  | #VALUE!
17.06.2008 11:00 | 3600 | 2 | 764.66 | GGB | 763.37 | 776.086 | 768.498 | 262.69 | GGB | 10769 | GGB | 9.8 | GGB | 1004.63 | GGB | 63.37 | GGB | 167246.94 | GGB | 134615.5 | GGB | 0 | 0 | 2806 | 3600 | 2790.11 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261734 | GGB | 261736.69 | 2790.11 | 2790.11 |  |  |  | 0 | 1 | [14 empty] | 104.3311 |  |  | #VALUE!
17.06.2008 12:00 | 3600 | 2 | 765.19 | GGB | 764.835 | 777.727 | 769.597 | 262.85 | GGB | 10780.6 | GGB | 9.81 | GGB | 1003.96 | GGB | 63.44 | GGB | 167475.81 | GGB | 134684.16 | GGB | 0 | 0 | 2787 | 3600 | 2771.58 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261773.21 | GGB | 261775.9 | 2771.58 | 2771.58 |  |  |  | 1 | 1 |  |  |  |  | 134684.16 | 2771.58 | 134684.16 | 2771.58 | 9.5202 | [5 empty] | 103.6911 |  |  | #VALUE!
17.06.2008 13:00 | 3600 | 2 | 765.32 | GGB | 763.37 | 776.719 | 769.597 | 262.82 | GGB | 10757.8 | GGB | 9.81 | GGB | 1003.76 | GGB | 64.13 | GGB | 167334.96 | GGB | 134268.28 | GGB | 0 | 0 | 2773 | 3600 | 2757.64 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261812.42 | GGB | 261815.11 | 2757.64 | 2757.64 |  |  |  | 0 | 1 | [14 empty] | 102.851 |  |  | #VALUE!
17.06.2008 14:00 | 3600 | 2 | 765.07 | GGB | 763.37 | 776.625 | 768.498 | 263.45 | GGB | 10714.3 | GGB | 9.8 | GGB | 1003.5 | GGB | 62.76 | GGB | 168754.4 | GGB | 135926.23 | GGB | 0 | 0 | 2753 | 3600 | 2738.02 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261851.63 | GGB | 261854.32 | 2738.02 | 2738.02 |  |  |  | 0 | 1 | [14 empty] | 103.3802 |  |  | #VALUE!
17.06.2008 15:00 | 3600 | 2 | 764.33 | GGB | 764.469 | 776.672 | 769.597 | 264.56 | GGB | 10785.7 | GGB | 9.79 | GGB | 1004.44 | GGB | 60.97 | GGB | 170544.65 | GGB | 138232.4 | GGB | 0 | 0 | 2813 | 3600 | 2797.9 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261890.84 | GGB | 261893.53 | 2797.9 | 2734.0045 |  |  |  | 1 | 1 |  |  |  |  | 138232.4 | 2734.0045 | 138232.4 | 2734.0045 | 9.6386 | [5 empty] | 107.4335 | 2734.0045 |  | 104.98
17.06.2008 16:00 | 3600 | 2 | 765.15 | GGB | 764.469 | 777.703 | 769.597 | 263.89 | GGB | 10832.2 | GGB | 9.82 | GGB | 1004.9 | GGB | 62.96 | GGB | 168780.81 | GGB | 136053.33 | GGB | 0 | 0 | 2795 | 3600 | 2779.74 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261930.05 | GGB | 261932.74 | 2779.74 | 2777.7931 |  |  |  | 1 | 1 |  |  |  |  | 136053.33 | 2777.7931 | 136053.33 | 2777.7931 | 9.6386 | [5 empty] | 105.0536 | 2777.7931 |  | 104.98
17.06.2008 17:00 | 3600 | 2 | 765.25 | GGB | 764.835 | 777.68 | 769.597 | 263.64 | GGB | 10801.9 | GGB | 9.81 | GGB | 1005.1 | GGB | 63.28 | GGB | 168708.19 | GGB | 135892.59 | GGB | 0 | 0 | 2779 | 3600 | 2763.65 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 261969.26 | GGB | 261971.95 | 2763.65 | 2763.65 |  |  |  | 1 | 1 |  |  |  |  | 135892.59 | 2763.65 | 135892.59 | 2763.65 | 9.5782 | [5 empty] | 104.3221 |  |  | #VALUE!
17.06.2008 18:00 | 3600 | 2 | 765.05 | GGB | 761.172 | 773.438 | 765.934 | 263.57 | GGB | 10761.3 | GGB | 9.79 | GGB | 1005.07 | GGB | 62.79 | GGB | 169391.5 | GGB | 136636.28 | GGB | 0 | 0 | 2756 | 3600 | 2740.73 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262008.47 | GGB | 262011.16 | 2740.73 | 2740.73 |  |  |  | 0 | 1 | [14 empty] | 104.0231 |  |  | #VALUE!
17.06.2008 19:00 | 3600 | 2 | 765.89 | GGB | 763.37 | 775.781 | 768.498 | 265.57 | GGB | 10830 | GGB | 9.82 | GGB | 1005.91 | GGB | 61.65 | GGB | 172086.22 | GGB | 139399.77 | GGB | 0 | 0 | 2748 | 3600 | 2732.95 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262047.68 | GGB | 262050.37 | 2732.95 | 2711.1092 |  |  |  | 0 | 1 | [14 empty] | 105.8257 | 2711.1092 |  | 104.98
17.06.2008 20:00 | 3600 | 2 | 765.24 | GGB | 763.37 | 776.742 | 768.498 | 265.74 | GGB | 10801.3 | GGB | 9.8 | GGB | 1006.09 | GGB | 62.78 | GGB | 171804.54 | GGB | 138730.23 | GGB | 0 | 0 | 2777 | 3600 | 2761.38 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262086.89 | GGB | 262089.58 | 2761.38 | 2724.1936 |  |  |  | 0 | 1 | [14 empty] | 106.413 | 2724.1936 |  | 104.98
17.06.2008 21:00 | 3600 | 2 | 765.24 | GGB | 764.469 | 776.906 | 769.597 | 263.99 | GGB | 10838.1 | GGB | 9.81 | GGB | 1005.42 | GGB | 63.31 | GGB | 169551.04 | GGB | 136605.61 | GGB | 0 | 0 | 2782 | 3600 | 2766.8 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262126.1 | GGB | 262128.79 | 2766.8 | 2766.5628 |  |  |  | 1 | 1 |  |  |  |  | 136605.61 | 2766.5628 | 136605.61 | 2766.5628 | 9.6386 | [5 empty] | 104.989 | 2766.5628 |  | 104.98
17.06.2008 22:00 | 3600 | 2 | 764.44 | GGB | 763.37 | 775.805 | 767.033 | 264.69 | GGB | 10838.3 | GGB | 9.8 | GGB | 1005.95 | GGB | 63.11 | GGB | 169972.47 | GGB | 137097.08 | GGB | 0 | 0 | 2827 | 3600 | 2811.77 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262165.31 | GGB | 262168 | 2811.77 | 2756.6451 |  |  |  | 0 | 1 | [14 empty] | 107.0793 | 2756.6451 |  | 104.98
17.06.2008 23:00 | 3600 | 2 | 764.27 | GGB | 764.469 | 775.945 | 769.597 | 266.66 | GGB | 10853.3 | GGB | 9.8 | GGB | 1007.05 | GGB | 62.46 | GGB | 172095.02 | GGB | 139227.85 | GGB | 0 | 0 | 2852 | 3600 | 2836.18 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262204.52 | GGB | 262207.21 | 2836.18 | 2714.4569 |  |  |  | 1 | 1 |  |  |  |  | 139227.85 | 2714.4569 | 139227.85 | 2714.4569 | 9.6386 | [5 empty] | 109.6876 | 2714.4569 |  | 104.98
17.06.2008 24:00 | 3600 | 2 | 765.1 | GGB | 763.37 | 775.922 | 768.132 | 266.87 | GGB | 10910.9 | GGB | 9.81 | GGB | 1007.22 | GGB | 62.29 | GGB | 172042.21 | GGB | 139279.42 | GGB | 0 | 0 | 2831 | 3600 | 2815.03 | GGB | 100 | GGB | 39.21 | GGB | 39.21 | GGB | 262243.73 | GGB | 262246.42 | 2815.03 | 2713.4519 |  |  |  | 0 | 1 | [14 empty] | 108.9099 | 2713.4519 |  | 104.98
18.06.2008 01:00 | 3600 | 2 | 764.33 | GGB | 764.469 | 775.875 | 768.132 | 268.3 | GGB | 10900.1 | GGB | 9.79 | GGB | 1008.01 | GGB | 61.77 | GGB | 174087.74 | GGB | 141266.19 | GGB | 0 | 0 | 2873 | 3600 | 2857.75 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262282.52 | GGB | 262285.22 | 2857.75 | 2675.2898 |  |  |  | 1 | 1 |  |  |  |  | 141266.19 | 2675.2898 | 141266.19 | 2675.2898 | 9.7404 | [5 empty] | 112.1398 | 2675.2898 |  | 104.98
18.06.2008 02:00 | 3600 | 2 | 764.71 | GGB | 763.37 | 774.563 | 768.132 | 267.87 | GGB | 10969.5 | GGB | 9.81 | GGB | 1008.28 | GGB | 61.89 | GGB | 173380.22 | GGB | 140679.41 | GGB | 0 | 0 | 2879 | 3600 | 2863.09 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262321.31 | GGB | 262324.02 | 2863.09 | 2686.4486 |  |  |  | 0 | 1 | [14 empty] | 111.8827 | 2686.4486 |  | 104.98
18.06.2008 03:00 | 3600 | 2 | 764.32 | GGB | 763.37 | 775.664 | 768.498 | 268.03 | GGB | 10984.2 | GGB | 9.81 | GGB | 1008.59 | GGB | 61.63 | GGB | 173481.45 | GGB | 140915.84 | GGB | 0 | 0 | 2905 | 3600 | 2889.02 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262360.11 | GGB | 262362.82 | 2889.02 | 2681.9412 |  |  |  | 0 | 1 | [14 empty] | 113.0857 | 2681.9412 |  | 104.98
18.06.2008 04:00 | 3600 | 2 | 764.52 | GGB | 764.469 | 775.547 | 768.132 | 267.52 | GGB | 10984.6 | GGB | 9.81 | GGB | 1008.27 | GGB | 61.64 | GGB | 173171.16 | GGB | 140612.29 | GGB | 0 | 0 | 2889 | 3600 | 2873.68 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262398.9 | GGB | 262401.62 | 2873.68 | 2687.7309 |  |  |  | 1 | 1 |  |  |  |  | 140612.29 | 2687.7309 | 140612.29 | 2687.7309 | 9.7404 | [5 empty] | 112.243 | 2687.7309 |  | 104.98
18.06.2008 05:00 | 3600 | 2 | 764.6 | GGB | 763.37 | 775.43 | 767.033 | 266.9 | GGB | 10971.1 | GGB | 9.81 | GGB | 1007.99 | GGB | 61.54 | GGB | 172625.39 | GGB | 140174.51 | GGB | 0 | 0 | 2872 | 3600 | 2856.51 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262437.7 | GGB | 262440.42 | 2856.51 | 2696.125 |  |  |  | 0 | 1 | [14 empty] | 111.225 | 2696.125 |  | 104.98
18.06.2008 06:00 | 3600 | 2 | 763.92 | GGB | 763.37 | 775.5 | 768.498 | 268.57 | GGB | 10922.8 | GGB | 9.8 | GGB | 1008.58 | GGB | 60.93 | GGB | 174937.2 | GGB | 142394.42 | GGB | 0 | 0 | 2882 | 3600 | 2866.72 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262476.49 | GGB | 262479.22 | 2866.72 | 2654.0928 |  |  |  | 0 | 1 | [14 empty] | 113.3903 | 2654.0928 |  | 104.98
18.06.2008 07:00 | 3600 | 2 | 764.91 | GGB | 764.469 | 777.609 | 770.696 | 268.38 | GGB | 10930.1 | GGB | 9.81 | GGB | 1009.29 | GGB | 61.08 | GGB | 174563.08 | GGB | 142123.29 | GGB | 0 | 0 | 2839 | 3600 | 2823.29 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262515.29 | GGB | 262518.02 | 2823.29 | 2659.156 |  |  |  | 1 | 1 |  |  |  |  | 142123.29 | 2659.156 | 142123.29 | 2659.156 | 9.7404 | [5 empty] | 111.4598 | 2659.156 |  | 104.98
18.06.2008 08:00 | 3600 | 2 | 765.93 | GGB | 764.469 | 776.484 | 769.597 | 265.53 | GGB | 10932 | GGB | 9.83 | GGB | 1009.31 | GGB | 62.09 | GGB | 171119.03 | GGB | 138903.16 | GGB | 0 | 0 | 2786 | 3600 | 2770.26 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262554.08 | GGB | 262556.82 | 2770.26 | 2720.802 |  |  |  | 1 | 1 |  |  |  |  | 138903.16 | 2720.802 | 138903.16 | 2720.802 | 9.7404 | [5 empty] | 106.8883 | 2720.802 |  | 104.98
18.06.2008 09:00 | 3600 | 2 | 765.68 | GGB | 764.835 | 778.055 | 769.963 | 264.15 | GGB | 10867.9 | GGB | 9.82 | GGB | 1009.34 | GGB | 62.85 | GGB | 169446.51 | GGB | 137237.85 | GGB | 0 | 0 | 2777 | 3600 | 2761.64 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262592.88 | GGB | 262595.62 | 2761.64 | 2753.8176 |  |  |  | 1 | 1 |  |  |  |  | 137237.85 | 2753.8176 | 137237.85 | 2753.8176 | 9.7404 | [5 empty] | 105.2782 | 2753.8176 |  | 104.98
18.06.2008 10:00 | 3600 | 2 | 765.96 | GGB | 764.835 | 778.195 | 769.963 | 264.89 | GGB | 10790.1 | GGB | 9.81 | GGB | 1009.82 | GGB | 62.67 | GGB | 170544.65 | GGB | 138269.4 | GGB | 0 | 0 | 2733 | 3600 | 2717.21 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262631.67 | GGB | 262634.42 | 2717.21 | 2717.21 |  |  |  | 1 | 1 |  |  |  |  | 138269.4 | 2717.21 | 138269.4 | 2717.21 | 9.6832 | [5 empty] | 104.3631 |  |  | #VALUE!
18.06.2008 11:00 | 3600 | 2 | 766.15 | GGB | 764.835 | 777.445 | 768.864 | 262.02 | GGB | 10775.5 | GGB | 9.82 | GGB | 1009.31 | GGB | 63.74 | GGB | 167127 | GGB | 134996.46 | GGB | 0 | 0 | 2659 | 3600 | 2643.45 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262670.47 | GGB | 262673.22 | 2643.45 | 2643.45 |  |  |  | 1 | 1 |  |  |  |  | 134996.46 | 2643.45 | 134996.46 | 2643.45 | 9.1973 | [5 empty] | 99.1268 |  |  | #VALUE!
18.06.2008 12:00 | 3600 | 2 | 765.72 | GGB | 764.835 | 777.68 | 768.864 | 261.24 | GGB | 10708 | GGB | 9.81 | GGB | 1008.73 | GGB | 64.16 | GGB | 166876.12 | GGB | 134549.33 | GGB | 0 | 0 | 2642 | 3600 | 2626.85 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262709.26 | GGB | 262712.02 | 2626.85 | 2626.85 |  |  |  | 1 | 1 |  |  |  |  | 134549.33 | 2626.85 | 134549.33 | 2626.85 | 9.1093 | [5 empty] | 98.178 |  |  | #VALUE!
18.06.2008 13:00 | 3600 | 2 | 766.64 | GGB | 765.934 | 778.852 | 770.33 | 260.42 | GGB | 10675.6 | GGB | 9.82 | GGB | 1008.35 | GGB | 64.04 | GGB | 166324.85 | GGB | 134104.13 | GGB | 0 | 0 | 2574 | 3600 | 2558.53 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262748.06 | GGB | 262750.82 | 2558.53 | 2558.53 |  |  |  | 0 | 1 | [14 empty] | 95.3082 |  |  | #VALUE!
18.06.2008 14:00 | 3600 | 2 | 766.44 | GGB | 764.835 | 777.563 | 770.33 | 258.86 | GGB | 10629.8 | GGB | 9.81 | GGB | 1008.25 | GGB | 64.71 | GGB | 164842.7 | GGB | 132630.65 | GGB | 0 | 0 | 2555 | 3600 | 2539.35 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262786.85 | GGB | 262789.62 | 2539.35 | 2539.35 |  |  |  | 1 | 1 |  |  |  |  | 132630.65 | 2539.35 | 132630.65 | 2539.35 | 8.6803 | [5 empty] | 93.5543 |  |  | #VALUE!
18.06.2008 15:00 | 3600 | 2 | 766.84 | GGB | 764.835 | 777.563 | 769.963 | 258.35 | GGB | 10631.1 | GGB | 9.81 | GGB | 1008.34 | GGB | 64.79 | GGB | 164347.55 | GGB | 132213.8 | GGB | 0 | 0 | 2548 | 3600 | 2533.17 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262825.65 | GGB | 262828.42 | 2533.17 | 2533.17 |  |  |  | 1 | 1 |  |  |  |  | 132213.8 | 2533.17 | 132213.8 | 2533.17 | 8.632 | [5 empty] | 93.0333 |  |  | #VALUE!
18.06.2008 16:00 | 3600 | 2 | 766.1 | GGB | 765.934 | 778.617 | 770.696 | 259.83 | GGB | 10593.1 | GGB | 9.8 | GGB | 1008.52 | GGB | 64.32 | GGB | 166100.38 | GGB | 133835.13 | GGB | 0 | 0 | 2570 | 3600 | 2555.11 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262864.44 | GGB | 262867.22 | 2555.11 | 2555.11 |  |  |  | 1 | 1 |  |  |  |  | 133835.13 | 2555.11 | 133835.13 | 2555.11 | 8.8135 | [5 empty] | 94.9899 |  |  | #VALUE!
18.06.2008 17:00 | 3600 | 2 | 766.94 | GGB | 765.934 | 777.75 | 770.696 | 257.82 | GGB | 10604 | GGB | 9.81 | GGB | 1008.22 | GGB | 64.93 | GGB | 163604.82 | GGB | 131545.16 | GGB | 0 | 0 | 2529 | 3600 | 2513.78 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262903.23 | GGB | 262906.02 | 2513.78 | 2513.78 |  |  |  | 1 | 1 |  |  |  |  | 131545.16 | 2513.78 | 131545.16 | 2513.78 | 8.5226 | [5 empty] | 91.8543 |  |  | #VALUE!
18.06.2008 18:00 | 3600 | 2 | 767.07 | GGB | 765.934 | 778.852 | 770.696 | 257.73 | GGB | 10586.7 | GGB | 9.8 | GGB | 1008.07 | GGB | 64.9 | GGB | 163910.71 | GGB | 131784.67 | GGB | 0 | 0 | 2499 | 3600 | 2483.59 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262942.03 | GGB | 262944.82 | 2483.59 | 2483.59 |  |  |  | 0 | 1 | [14 empty] | 90.9164 |  |  | #VALUE!
18.06.2008 19:00 | 3600 | 2 | 767.17 | GGB | 765.934 | 778.875 | 770.696 | 257.56 | GGB | 10587.6 | GGB | 9.8 | GGB | 1007.92 | GGB | 65 | GGB | 164090.07 | GGB | 131869.55 | GGB | 0 | 0 | 2502 | 3600 | 2486.86 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 262980.82 | GGB | 262983.62 | 2486.86 | 2486.86 |  |  |  | 0 | 1 | [14 empty] | 91.0948 |  |  | #VALUE!
18.06.2008 20:00 | 3600 | 2 | 766.84 | GGB | 765.934 | 777.938 | 770.696 | 258.37 | GGB | 10611.4 | GGB | 9.8 | GGB | 1007.93 | GGB | 64.63 | GGB | 165034.16 | GGB | 132774.17 | GGB | 0 | 0 | 2521 | 3600 | 2506.15 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 263019.62 | GGB | 263022.42 | 2506.15 | 2506.15 |  |  |  | 1 | 1 |  |  |  |  | 132774.17 | 2506.15 | 132774.17 | 2506.15 | 8.5761 | [5 empty] | 92.4311 |  |  | #VALUE!
18.06.2008 21:00 | 3600 | 2 | 766.3 | GGB | 764.835 | 778.828 | 770.696 | 260.34 | GGB | 10622 | GGB | 9.79 | GGB | 1008.24 | GGB | 63.95 | GGB | 167270.04 | GGB | 134886.19 | GGB | 0 | 0 | 2550 | 3600 | 2534.41 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 263058.41 | GGB | 263061.22 | 2534.41 | 2534.41 |  |  |  | 0 | 1 | [14 empty] | 94.9603 |  |  | #VALUE!
18.06.2008 22:00 | 3600 | 2 | 766.27 | GGB | 764.835 | 777.914 | 769.597 | 260.98 | GGB | 10688.3 | GGB | 9.8 | GGB | 1008.76 | GGB | 63.53 | GGB | 167452.7 | GGB | 135272.59 | GGB | 0 | 0 | 2579 | 3600 | 2563.94 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 263097.21 | GGB | 263100.02 | 2563.94 | 2563.94 |  |  |  | 1 | 1 |  |  |  |  | 135272.59 | 2563.94 | 135272.59 | 2563.94 | 8.9389 | [5 empty] | 96.3419 |  |  | #VALUE!
18.06.2008 23:00 | 3600 | 2 | 764.9 | GGB | 763.37 | 775.5 | 768.132 | 262.22 | GGB | 10738.6 | GGB | 9.78 | GGB | 1009.75 | GGB | 63.54 | GGB | 168368.18 | GGB | 136142.15 | GGB | 0 | 0 | 2686 | 3600 | 2670.16 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 263136 | GGB | 263138.82 | 2670.16 | 2670.16 |  |  |  | 0 | 1 | [14 empty] | 100.9781 |  |  | #VALUE!
18.06.2008 24:00 | 3600 | 2 | 764.41 | GGB | 762.271 | 774.352 | 767.033 | 264.01 | GGB | 10829.5 | GGB | 9.79 | GGB | 1010.89 | GGB | 62.7 | GGB | 170547.95 | GGB | 138406.49 | GGB | 0 | 0 | 2747 | 3600 | 2731.48 | GGB | 100 | GGB | 38.8 | GGB | 38.8 | GGB | 263174.8 | GGB | 263177.62 | 2731.48 | 2730.5656 |  |  |  | 0 | 1 | [14 empty] | 105.0152 | 2730.5656 |  | 104.98
19.06.2008 01:00 | 3600 | 2 | 763.91 | GGB | 763.37 | 775.477 | 768.132 | 267.01 | GGB | 10908.5 | GGB | 9.79 | GGB | 1011.34 | GGB | 62.47 | GGB | 172587.98 | GGB | 140219.06 | GGB | 0 | 0 | 2847 | 3600 | 2831.08 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263213.12 | GGB | 263215.94 | 2831.08 | 2695.2684 |  |  |  | 0 | 1 | [14 empty] | 110.2698 | 2695.2684 |  | 104.98
19.06.2008 02:00 | 3600 | 2 | 763.51 | GGB | 761.172 | 773.461 | 765.934 | 267.86 | GGB | 10953.3 | GGB | 9.8 | GGB | 1011.59 | GGB | 62.26 | GGB | 173525.46 | GGB | 141103.6 | GGB | 0 | 0 | 2886 | 3600 | 2870 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263251.44 | GGB | 263254.26 | 2870 | 2678.3725 |  |  |  | 0 | 1 | [14 empty] | 112.4909 | 2678.3725 |  | 104.98
19.06.2008 03:00 | 3600 | 2 | 763.64 | GGB | 764.469 | 776.695 | 768.498 | 268.53 | GGB | 10997.5 | GGB | 9.81 | GGB | 1011.96 | GGB | 62.04 | GGB | 174220.88 | GGB | 141815.28 | GGB | 0 | 0 | 2906 | 3600 | 2890.88 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263289.76 | GGB | 263292.58 | 2890.88 | 2664.9315 |  |  |  | 1 | 1 |  |  |  |  | 141815.28 | 2664.9315 | 141815.28 | 2664.9315 | 9.8624 | [5 empty] | 113.8808 | 2664.9315 |  | 104.98
19.06.2008 04:00 | 3600 | 2 | 762.34 | GGB | 763.37 | 774.469 | 768.132 | 270.23 | GGB | 10978.9 | GGB | 9.79 | GGB | 1012.04 | GGB | 61.3 | GGB | 176395.14 | GGB | 143915.32 | GGB | 0 | 0 | 2951 | 3600 | 2934.98 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263328.09 | GGB | 263330.9 | 2934.98 | 2626.0443 |  |  |  | 0 | 1 | [14 empty] | 117.3302 | 2626.0443 |  | 104.98
19.06.2008 05:00 | 3600 | 2 | 764.15 | GGB | 763.37 | 774.539 | 767.033 | 269.14 | GGB | 11030.1 | GGB | 9.82 | GGB | 1011.74 | GGB | 61.38 | GGB | 175178.17 | GGB | 142846.44 | GGB | 0 | 0 | 2884 | 3600 | 2868.14 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263366.41 | GGB | 263369.22 | 2868.14 | 2645.6942 |  |  |  | 0 | 1 | [14 empty] | 113.8066 | 2645.6942 |  | 104.98
19.06.2008 06:00 | 3600 | 2 | 763.09 | GGB | 764.469 | 775.453 | 768.132 | 269.68 | GGB | 10986.2 | GGB | 9.8 | GGB | 1011.71 | GGB | 61.19 | GGB | 176203.69 | GGB | 143757.75 | GGB | 0 | 0 | 2925 | 3600 | 2909.79 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263404.73 | GGB | 263407.54 | 2909.79 | 2628.9226 |  |  |  | 1 | 1 |  |  |  |  | 143757.75 | 2628.9226 | 143757.75 | 2628.9226 | 9.8624 | [5 empty] | 116.1958 | 2628.9226 |  | 104.98
19.06.2008 07:00 | 3600 | 2 | 763.99 | GGB | 764.469 | 776.555 | 769.597 | 269.79 | GGB | 10988.1 | GGB | 9.82 | GGB | 1011.66 | GGB | 61.06 | GGB | 176247.7 | GGB | 143844.96 | GGB | 0 | 0 | 2876 | 3600 | 2860.18 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263443.05 | GGB | 263445.86 | 2860.18 | 2627.3288 |  |  |  | 1 | 1 |  |  |  |  | 143844.96 | 2627.3288 | 143844.96 | 2627.3288 | 9.8624 | [5 empty] | 114.284 | 2627.3288 |  | 104.98
19.06.2008 08:00 | 3600 | 2 | 766.14 | GGB | 765.934 | 777.867 | 770.696 | 265.53 | GGB | 10956.1 | GGB | 9.85 | GGB | 1011.36 | GGB | 62.62 | GGB | 171179.54 | GGB | 139016.51 | GGB | 0 | 0 | 2747 | 3600 | 2731.69 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263481.38 | GGB | 263484.18 | 2731.69 | 2718.5836 |  |  |  | 1 | 1 |  |  |  |  | 139016.51 | 2718.5836 | 139016.51 | 2718.5836 | 9.8624 | [5 empty] | 105.4861 | 2718.5836 |  | 104.98
19.06.2008 09:00 | 3600 | 2 | 766.13 | GGB | 764.835 | 776.977 | 769.597 | 261.95 | GGB | 10789.7 | GGB | 9.82 | GGB | 1011.66 | GGB | 63.31 | GGB | 167868.63 | GGB | 136087.12 | GGB | 0 | 0 | 2661 | 3600 | 2645.55 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263519.7 | GGB | 263522.5 | 2645.55 | 2645.55 |  |  |  | 1 | 1 |  |  |  |  | 136087.12 | 2645.55 | 136087.12 | 2645.55 | 9.3952 | [5 empty] | 100.007 |  |  | #VALUE!
19.06.2008 10:00 | 3600 | 2 | 766.92 | GGB | 767.033 | 778.781 | 770.696 | 259.34 | GGB | 10705.1 | GGB | 9.82 | GGB | 1010.92 | GGB | 64.16 | GGB | 165099.08 | GGB | 133407.66 | GGB | 0 | 0 | 2583 | 3600 | 2567.99 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263558.02 | GGB | 263560.82 | 2567.99 | 2567.99 |  |  |  | 0 | 1 | [14 empty] | 95.1638 |  |  | #VALUE!
19.06.2008 11:00 | 3600 | 2 | 766.49 | GGB | 765.934 | 777.727 | 770.696 | 259.04 | GGB | 10622.6 | GGB | 9.81 | GGB | 1010.55 | GGB | 64.47 | GGB | 164915.32 | GGB | 133087.27 | GGB | 0 | 0 | 2567 | 3600 | 2551.51 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263596.34 | GGB | 263599.14 | 2551.51 | 2551.51 |  |  |  | 1 | 1 |  |  |  |  | 133087.27 | 2551.51 | 133087.27 | 2551.51 | 8.8615 | [5 empty] | 94.326 |  |  | #VALUE!
19.06.2008 12:00 | 3600 | 2 | 767.63 | GGB | 767.033 | 779.906 | 772.161 | 258.17 | GGB | 10558.7 | GGB | 9.82 | GGB | 1010.25 | GGB | 64.91 | GGB | 164101.07 | GGB | 132220.21 | GGB | 0 | 0 | 2479 | 3600 | 2464.22 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263634.67 | GGB | 263637.46 | 2464.22 | 2464.22 |  |  |  | 0 | 1 | [14 empty] | 90.5055 |  |  | #VALUE!
19.06.2008 13:00 | 3600 | 2 | 767.48 | GGB | 767.033 | 779.836 | 772.161 | 255.68 | GGB | 10517.1 | GGB | 9.81 | GGB | 1009.65 | GGB | 66.05 | GGB | 161382.14 | GGB | 129513.46 | GGB | 0 | 0 | 2476 | 3600 | 2460.84 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263672.99 | GGB | 263675.78 | 2460.84 | 2460.84 |  |  |  | 0 | 1 | [14 empty] | 88.5311 |  |  | #VALUE!
19.06.2008 14:00 | 3600 | 2 | 767.97 | GGB | 767.033 | 780.68 | 772.161 | 254.55 | GGB | 10473 | GGB | 9.81 | GGB | 1008.77 | GGB | 66.28 | GGB | 160582.19 | GGB | 128672.13 | GGB | 0 | 0 | 2430 | 3600 | 2414.68 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263711.31 | GGB | 263714.1 | 2414.68 | 2414.68 |  |  |  | 0 | 1 | [14 empty] | 86.3061 |  |  | #VALUE!
19.06.2008 15:00 | 3600 | 2 | 768.02 | GGB | 767.033 | 779.672 | 772.161 | 254.53 | GGB | 10460.4 | GGB | 9.8 | GGB | 1008.22 | GGB | 66.28 | GGB | 160648.21 | GGB | 128656.23 | GGB | 0 | 0 | 2425 | 3600 | 2410.25 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263749.63 | GGB | 263752.42 | 2410.25 | 2410.25 |  |  |  | 0 | 1 | [14 empty] | 86.1371 |  |  | #VALUE!
19.06.2008 16:00 | 3600 | 2 | 767.93 | GGB | 765.934 | 779.883 | 771.795 | 254.6 | GGB | 10465.8 | GGB | 9.8 | GGB | 1008.22 | GGB | 66.2 | GGB | 160644.91 | GGB | 128681.33 | GGB | 0 | 0 | 2422 | 3600 | 2406.61 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263787.95 | GGB | 263790.74 | 2406.61 | 2406.61 |  |  |  | 0 | 1 | [14 empty] | 86.0238 |  |  | #VALUE!
19.06.2008 17:00 | 3600 | 2 | 767.94 | GGB | 765.934 | 778.758 | 771.795 | 254.59 | GGB | 10440.6 | GGB | 9.8 | GGB | 1008.04 | GGB | 66.18 | GGB | 160892.49 | GGB | 128866.5 | GGB | 0 | 0 | 2410 | 3600 | 2395.02 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263826.28 | GGB | 263829.06 | 2395.02 | 2395.02 |  |  |  | 0 | 1 | [14 empty] | 85.7327 |  |  | #VALUE!
19.06.2008 18:00 | 3600 | 2 | 768.66 | GGB | 767.033 | 780.867 | 772.161 | 255.15 | GGB | 10410.9 | GGB | 9.8 | GGB | 1008.14 | GGB | 65.7 | GGB | 161755.15 | GGB | 129751.1 | GGB | 0 | 0 | 2370 | 3600 | 2354.52 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263864.6 | GGB | 263867.38 | 2354.52 | 2354.52 |  |  |  | 0 | 1 | [14 empty] | 84.8615 |  |  | #VALUE!
19.06.2008 19:00 | 3600 | 2 | 768.18 | GGB | 768.132 | 779.836 | 773.26 | 255.27 | GGB | 10434.8 | GGB | 9.8 | GGB | 1008.17 | GGB | 65.64 | GGB | 161700.13 | GGB | 129734.11 | GGB | 0 | 0 | 2401 | 3600 | 2385.81 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263902.92 | GGB | 263905.7 | 2385.81 | 2385.81 |  |  |  | 0 | 1 | [14 empty] | 85.978 |  |  | #VALUE!
19.06.2008 20:00 | 3600 | 2 | 767.73 | GGB | 765.934 | 778.711 | 770.696 | 254.61 | GGB | 10459.8 | GGB | 9.8 | GGB | 1007.99 | GGB | 66.23 | GGB | 160282.9 | GGB | 128350.2 | GGB | 0 | 0 | 2430 | 3600 | 2414.67 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263941.24 | GGB | 263944.02 | 2414.67 | 2414.67 |  |  |  | 0 | 1 | [14 empty] | 86.0898 |  |  | #VALUE!
19.06.2008 21:00 | 3600 | 2 | 767.35 | GGB | 765.934 | 779.016 | 771.795 | 255.7 | GGB | 10476.3 | GGB | 9.8 | GGB | 1008.06 | GGB | 66.24 | GGB | 161340.32 | GGB | 129203.11 | GGB | 0 | 0 | 2480 | 3600 | 2464.47 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 263979.57 | GGB | 263982.34 | 2464.47 | 2464.47 |  |  |  | 0 | 1 | [14 empty] | 88.4492 |  |  | #VALUE!
19.06.2008 22:00 | 3600 | 2 | 766.71 | GGB | 764.835 | 778.219 | 769.597 | 258.56 | GGB | 10507.8 | GGB | 9.79 | GGB | 1008.36 | GGB | 65.07 | GGB | 164128.58 | GGB | 131930.17 | GGB | 0 | 0 | 2518 | 3600 | 2502.79 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 264017.89 | GGB | 264020.66 | 2502.79 | 2502.79 |  |  |  | 1 | 1 |  |  |  |  | 131930.17 | 2502.79 | 131930.17 | 2502.79 | 8.6167 | [5 empty] | 91.7204 |  |  | #VALUE!
19.06.2008 23:00 | 3600 | 2 | 766.23 | GGB | 764.469 | 777.234 | 769.597 | 259.4 | GGB | 10577.2 | GGB | 9.79 | GGB | 1008.42 | GGB | 64.99 | GGB | 164546.71 | GGB | 132307.36 | GGB | 0 | 0 | 2588 | 3600 | 2572.29 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 264056.21 | GGB | 264058.98 | 2572.29 | 2572.29 |  |  |  | 1 | 1 |  |  |  |  | 132307.36 | 2572.29 | 132307.36 | 2572.29 | 8.8813 | [5 empty] | 94.5369 |  |  | #VALUE!
19.06.2008 24:00 | 3600 | 2 | 766.5 | GGB | 767.033 | 779.719 | 771.795 | 260 | GGB | 10603.8 | GGB | 9.81 | GGB | 1008.19 | GGB | 64.5 | GGB | 166459.1 | GGB | 134007.3 | GGB | 0 | 0 | 2567 | 3600 | 2551.46 | GGB | 100 | GGB | 38.32 | GGB | 38.32 | GGB | 264094.53 | GGB | 264097.3 | 2551.46 | 2551.46 |  |  |  | 0 | 1 | [14 empty] | 94.9762 |  |  | #VALUE!
20.06.2008 01:00 | 3600 | 2 | 765.61 | GGB | 764.469 | 777.68 | 769.597 | 260.01 | GGB | 10642.7 | GGB | 9.79 | GGB | 1008.16 | GGB | 64.63 | GGB | 165235.52 | GGB | 132967.21 | GGB | 0 | 0 | 2622 | 3600 | 2606.46 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264134.06 | GGB | 264136.83 | 2606.46 | 2606.46 |  |  |  | 1 | 1 |  |  |  |  | 132967.21 | 2606.46 | 132967.21 | 2606.46 | 8.7674 | [5 empty] | 96.2705 |  |  | #VALUE!
20.06.2008 02:00 | 3600 | 2 | 764.82 | GGB | 764.469 | 776.836 | 769.963 | 263.25 | GGB | 10688.2 | GGB | 9.78 | GGB | 1008.86 | GGB | 63.93 | GGB | 168780.81 | GGB | 136198.45 | GGB | 0 | 0 | 2706 | 3600 | 2690.69 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264173.59 | GGB | 264176.36 | 2690.69 | 2690.69 |  |  |  | 1 | 1 |  |  |  |  | 136198.45 | 2690.69 | 136198.45 | 2690.69 | 9.2706 | [5 empty] | 101.7966 |  |  | #VALUE!
20.06.2008 03:00 | 3600 | 2 | 765.61 | GGB | 765.934 | 777.586 | 770.33 | 263.91 | GGB | 10755.6 | GGB | 9.8 | GGB | 1009.15 | GGB | 63.39 | GGB | 169496.03 | GGB | 137032.32 | GGB | 0 | 0 | 2682 | 3600 | 2666.56 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264213.12 | GGB | 264215.89 | 2666.56 | 2666.56 |  |  |  | 1 | 1 |  |  |  |  | 137032.32 | 2666.56 | 137032.32 | 2666.56 | 9.2437 | [5 empty] | 101.5014 |  |  | #VALUE!
20.06.2008 04:00 | 3600 | 2 | 764.17 | GGB | 761.172 | 773.508 | 765.201 | 265.18 | GGB | 10799.9 | GGB | 9.79 | GGB | 1009.06 | GGB | 63.39 | GGB | 170583.16 | GGB | 137898.47 | GGB | 0 | 0 | 2787 | 3600 | 2771.95 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264252.65 | GGB | 264255.42 | 2771.95 | 2740.625 |  |  |  | 0 | 1 | [14 empty] | 106.1799 | 2740.625 |  | 104.98
20.06.2008 05:00 | 3600 | 2 | 764.7 | GGB | 764.469 | 776.766 | 768.864 | 267.13 | GGB | 10828.2 | GGB | 9.8 | GGB | 1009.14 | GGB | 62.7 | GGB | 172992.9 | GGB | 140147.64 | GGB | 0 | 0 | 2796 | 3600 | 2780.99 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264292.18 | GGB | 264294.95 | 2780.99 | 2696.6419 |  |  |  | 1 | 1 |  |  |  |  | 140147.64 | 2696.6419 | 140147.64 | 2696.6419 | 9.5605 | [5 empty] | 108.2637 | 2696.6419 |  | 104.98
20.06.2008 06:00 | 3600 | 2 | 765.82 | GGB | 765.934 | 777.773 | 770.33 | 265.46 | GGB | 10866.1 | GGB | 9.82 | GGB | 1009.06 | GGB | 63.02 | GGB | 171097.02 | GGB | 138467.39 | GGB | 0 | 0 | 2748 | 3600 | 2732.9 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264331.7 | GGB | 264334.48 | 2732.9 | 2729.3647 |  |  |  | 1 | 1 |  |  |  |  | 138467.39 | 2729.3647 | 138467.39 | 2729.3647 | 9.5605 | [5 empty] | 105.116 | 2729.3647 |  | 104.98
20.06.2008 07:00 | 3600 | 2 | 765.39 | GGB | 765.934 | 779.063 | 770.33 | 263.82 | GGB | 10832.9 | GGB | 9.82 | GGB | 1008.75 | GGB | 63.36 | GGB | 169643.47 | GGB | 137111.56 | GGB | 0 | 0 | 2759 | 3600 | 2743.52 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264371.23 | GGB | 264374.01 | 2743.52 | 2743.52 |  |  |  | 0 | 1 | [14 empty] | 104.4912 |  |  | #VALUE!
20.06.2008 08:00 | 3600 | 2 | 766.07 | GGB | 764.835 | 777.445 | 769.963 | 263.08 | GGB | 10748.1 | GGB | 9.82 | GGB | 1009.02 | GGB | 63.39 | GGB | 169290.26 | GGB | 136847.22 | GGB | 0 | 0 | 2672 | 3600 | 2656.26 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264410.76 | GGB | 264413.54 | 2656.26 | 2656.26 |  |  |  | 1 | 1 |  |  |  |  | 136847.22 | 2656.26 | 136847.22 | 2656.26 | 9.1956 | [5 empty] | 100.9727 |  |  | #VALUE!
20.06.2008 09:00 | 3600 | 2 | 766.53 | GGB | 765.934 | 778.617 | 770.33 | 259.52 | GGB | 10695.9 | GGB | 9.82 | GGB | 1008.28 | GGB | 64.57 | GGB | 165078.17 | GGB | 132879.75 | GGB | 0 | 0 | 2647 | 3209 | 2632.03 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264450.29 | GGB | 264453.07 | 2632.03 | 2632.03 |  |  |  | 1 | 1 |  |  |  |  | 132879.75 | 2632.03 | 132879.75 | 2632.03 | 8.8475 | [5 empty] | 97.151 |  |  | #VALUE!
20.06.2008 10:00 | 3600 | 2 | 766.76 | GGB | 764.835 | 777.633 | 770.33 | 257.9 | GGB | 10581.5 | GGB | 9.81 | GGB | 1008.06 | GGB | 65.43 | GGB | 163408.96 | GGB | 131174.07 | GGB | 0 | 0 | 2640 | 3600 | 2624.88 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264489.82 | GGB | 264492.6 | 2624.88 | 2624.88 |  |  |  | 1 | 1 |  |  |  |  | 131174.07 | 2624.88 | 131174.07 | 2624.88 | 8.7103 | [5 empty] | 95.6434 |  |  | #VALUE!
20.06.2008 11:00 | 3600 | 2 | 767.78 | GGB | 767.033 | 779.836 | 771.795 | 256.35 | GGB | 10461.3 | GGB | 9.82 | GGB | 1007.29 | GGB | 65.81 | GGB | 161831.07 | GGB | 129661.94 | GGB | 0 | 0 | 2526 | 3600 | 2510.49 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264529.35 | GGB | 264532.13 | 2510.49 | 2510.49 |  |  |  | 0 | 1 | [14 empty] | 90.4208 |  |  | #VALUE!
20.06.2008 12:00 | 3600 | 2 | 767.86 | GGB | 767.033 | 779.836 | 772.161 | 253.41 | GGB | 10417.2 | GGB | 9.81 | GGB | 1005.76 | GGB | 67 | GGB | 158561.97 | GGB | 126404.6 | GGB | 0 | 0 | 2483 | 3600 | 2467.72 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264568.87 | GGB | 264571.66 | 2467.72 | 2467.72 |  |  |  | 0 | 1 | [14 empty] | 86.6475 |  |  | #VALUE!
20.06.2008 13:00 | 3600 | 2 | 767.91 | GGB | 765.934 | 778.641 | 772.161 | 253.25 | GGB | 10351.5 | GGB | 9.8 | GGB | 1005.02 | GGB | 67.19 | GGB | 158724.82 | GGB | 126370.07 | GGB | 0 | 0 | 2471 | 3600 | 2455.91 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264608.4 | GGB | 264611.19 | 2455.91 | 2455.91 |  |  |  | 1 | 1 |  |  |  |  | 126370.07 | 2455.91 | 126370.07 | 2455.91 | 7.8511 | [5 empty] | 86.2093 |  |  | #VALUE!
20.06.2008 14:00 | 3600 | 2 | 767.92 | GGB | 765.934 | 779.953 | 771.429 | 254.41 | GGB | 10343.8 | GGB | 9.8 | GGB | 1004.55 | GGB | 66.5 | GGB | 160102.44 | GGB | 127669.31 | GGB | 0 | 0 | 2453 | 3600 | 2437.94 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264647.93 | GGB | 264650.72 | 2437.94 | 2437.94 |  |  |  | 0 | 1 | [14 empty] | 86.4584 |  |  | #VALUE!
20.06.2008 15:00 | 3600 | 2 | 767.29 | GGB | 759.707 | 773.461 | 765.201 | 253.3 | GGB | 10385.4 | GGB | 9.78 | GGB | 1004.02 | GGB | 66.24 | GGB | 158783.14 | GGB | 126644.52 | GGB | 0 | 0 | 2493 | 3600 | 2477.9 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264687.46 | GGB | 264690.25 | 2477.9 | 2477.9 |  |  |  | 0 | 1 | [14 empty] | 87.1701 |  |  | #VALUE!
20.06.2008 16:00 | 3600 | 2 | 764.62 | GGB | 763.37 | 776.648 | 768.864 | 259.93 | GGB | 10626.5 | GGB | 9.79 | GGB | 1006.52 | GGB | 64.59 | GGB | 164361.85 | GGB | 132063.59 | GGB | 0 | 0 | 2802 | 3600 | 2786.12 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264726.99 | GGB | 264729.78 | 2786.12 | 2786.12 |  |  |  | 0 | 1 | [14 empty] | 102.2069 |  |  | #VALUE!
20.06.2008 17:00 | 3600 | 2 | 764.92 | GGB | 765.934 | 777.844 | 770.696 | 261.19 | GGB | 10639.2 | GGB | 9.8 | GGB | 1007.67 | GGB | 63.91 | GGB | 165129.89 | GGB | 133103.21 | GGB | 0 | 0 | 2787 | 3600 | 2771.76 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264766.52 | GGB | 264769.31 | 2771.76 | 2771.76 |  |  |  | 1 | 1 |  |  |  |  | 133103.21 | 2771.76 | 133103.21 | 2771.76 | 9.3329 | [5 empty] | 102.4806 |  |  | #VALUE!
20.06.2008 18:00 | 3600 | 2 | 765.52 | GGB | 764.835 | 777.141 | 768.498 | 260.91 | GGB | 10643.1 | GGB | 9.81 | GGB | 1007.91 | GGB | 65.21 | GGB | 164218.81 | GGB | 131890.83 | GGB | 0 | 0 | 2772 | 3600 | 2756.92 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264806.05 | GGB | 264808.84 | 2756.92 | 2756.92 |  |  |  | 1 | 1 |  |  |  |  | 131890.83 | 2756.92 | 131890.83 | 2756.92 | 9.1984 | [5 empty] | 101.0035 |  |  | #VALUE!
20.06.2008 19:00 | 3600 | 2 | 764.72 | GGB | 763.37 | 776.109 | 768.132 | 259.91 | GGB | 10616.8 | GGB | 9.8 | GGB | 1007.34 | GGB | 65.97 | GGB | 162887.4 | GGB | 130454.52 | GGB | 0 | 0 | 2814 | 3600 | 2798.36 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264845.57 | GGB | 264848.37 | 2798.36 | 2798.36 |  |  |  | 0 | 1 | [14 empty] | 101.4052 |  |  | #VALUE!
20.06.2008 20:00 | 3600 | 2 | 765.58 | GGB | 764.835 | 777.188 | 768.498 | 260.46 | GGB | 10630.9 | GGB | 9.81 | GGB | 1007.47 | GGB | 65.93 | GGB | 163502.49 | GGB | 130978.07 | GGB | 0 | 0 | 2781 | 3600 | 2765.53 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264885.1 | GGB | 264887.9 | 2765.53 | 2765.53 |  |  |  | 1 | 1 |  |  |  |  | 130978.07 | 2765.53 | 130978.07 | 2765.53 | 9.1633 | [5 empty] | 100.6177 |  |  | #VALUE!
20.06.2008 21:00 | 3600 | 2 | 765.33 | GGB | 764.469 | 777.281 | 768.864 | 260.68 | GGB | 10631.9 | GGB | 9.8 | GGB | 1007.57 | GGB | 65.73 | GGB | 163854.6 | GGB | 131349.88 | GGB | 0 | 0 | 2797 | 3600 | 2781.56 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264924.63 | GGB | 264927.43 | 2781.56 | 2781.56 |  |  |  | 1 | 1 |  |  |  |  | 131349.88 | 2781.56 | 131349.88 | 2781.56 | 9.2425 | [5 empty] | 101.4882 |  |  | #VALUE!
20.06.2008 22:00 | 3600 | 2 | 765.31 | GGB | 763.37 | 776.156 | 767.766 | 260.59 | GGB | 10636 | GGB | 9.8 | GGB | 1008.09 | GGB | 65.77 | GGB | 163835.89 | GGB | 131386.73 | GGB | 0 | 0 | 2800 | 3600 | 2784.22 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 264964.16 | GGB | 264966.96 | 2784.22 | 2784.22 |  |  |  | 0 | 1 | [14 empty] | 101.6138 |  |  | #VALUE!
20.06.2008 23:00 | 3600 | 2 | 765.05 | GGB | 763.37 | 776.086 | 767.766 | 261.49 | GGB | 10664.1 | GGB | 9.8 | GGB | 1008.53 | GGB | 65.6 | GGB | 164584.12 | GGB | 132112.09 | GGB | 0 | 0 | 2838 | 3600 | 2822.85 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 265003.69 | GGB | 265006.49 | 2822.85 | 2822.85 |  |  |  | 0 | 1 | [14 empty] | 103.5924 |  |  | #VALUE!
20.06.2008 24:00 | 3600 | 2 | 764.64 | GGB | 762.271 | 773.063 | 766.3 | 262.36 | GGB | 10687.9 | GGB | 9.79 | GGB | 1008.85 | GGB | 64.9 | GGB | 166319.35 | GGB | 133825.12 | GGB | 0 | 0 | 2857 | 3600 | 2841.1 | GGB | 100 | GGB | 39.53 | GGB | 39.53 | GGB | 265043.22 | GGB | 265046.02 | 2841.1 | 2824.0438 |  |  |  | 0 | 1 | [14 empty] | 105.614 | 2824.0438 |  | 104.98
21.06.2008 01:00 | 3600 | 2 | 764.88 | GGB | 764.469 | 776.203 | 769.597 | 264.31 | GGB | 10755.7 | GGB | 9.8 | GGB | 1009.66 | GGB | 64.29 | GGB | 168203.13 | GGB | 135693.22 | GGB | 0 | 0 | 2881 | 3600 | 2865.11 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265082.99 | GGB | 265085.79 | 2865.11 | 2785.1649 |  |  |  | 1 | 1 |  |  |  |  | 135693.22 | 2785.1649 | 135693.22 | 2785.1649 | 9.5028 | [5 empty] | 107.9933 | 2785.1649 |  | 104.98
21.06.2008 02:00 | 3600 | 2 | 764.59 | GGB | 763.37 | 775.172 | 767.033 | 265.79 | GGB | 10790.2 | GGB | 9.79 | GGB | 1010.61 | GGB | 63.71 | GGB | 170210.15 | GGB | 137679.22 | GGB | 0 | 0 | 2885 | 3600 | 2869.12 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265122.76 | GGB | 265125.56 | 2869.12 | 2744.9894 |  |  |  | 0 | 1 | [14 empty] | 109.7273 | 2744.9894 |  | 104.98
21.06.2008 03:00 | 3600 | 2 | 764.97 | GGB | 764.469 | 775.969 | 768.498 | 266.96 | GGB | 10837.1 | GGB | 9.8 | GGB | 1011.08 | GGB | 62.97 | GGB | 172106.03 | GGB | 139581.69 | GGB | 0 | 0 | 2883 | 3600 | 2867.7 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265162.53 | GGB | 265165.33 | 2867.7 | 2707.5758 |  |  |  | 1 | 1 |  |  |  |  | 139581.69 | 2707.5758 | 139581.69 | 2707.5758 | 9.5028 | [5 empty] | 111.1884 | 2707.5758 |  | 104.98
21.06.2008 04:00 | 3600 | 2 | 764.57 | GGB | 763.37 | 775.195 | 768.498 | 266.32 | GGB | 10891.8 | GGB | 9.81 | GGB | 1010.85 | GGB | 63.22 | GGB | 171282.98 | GGB | 138782.71 | GGB | 0 | 0 | 2922 | 3600 | 2905.91 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265202.3 | GGB | 265205.1 | 2905.91 | 2723.1634 |  |  |  | 0 | 1 | [14 empty] | 112.025 | 2723.1634 |  | 104.98
21.06.2008 05:00 | 3600 | 2 | 764.19 | GGB | 764.469 | 776.297 | 768.132 | 267 | GGB | 10908.4 | GGB | 9.8 | GGB | 1011.22 | GGB | 63.02 | GGB | 171913.47 | GGB | 139424.45 | GGB | 0 | 0 | 2962 | 3600 | 2946.39 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265242.07 | GGB | 265244.87 | 2946.39 | 2710.6293 |  |  |  | 1 | 1 |  |  |  |  | 139424.45 | 2710.6293 | 139424.45 | 2710.6293 | 9.5028 | [5 empty] | 114.1108 | 2710.6293 |  | 104.98
21.06.2008 06:00 | 3600 | 2 | 764.6 | GGB | 762.271 | 774.234 | 767.033 | 267.15 | GGB | 10926.1 | GGB | 9.81 | GGB | 1011.19 | GGB | 62.87 | GGB | 172054.31 | GGB | 139599.55 | GGB | 0 | 0 | 2941 | 3600 | 2925.29 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265281.83 | GGB | 265284.64 | 2925.29 | 2707.2294 |  |  |  | 0 | 1 | [14 empty] | 113.4359 | 2707.2294 |  | 104.98
21.06.2008 07:00 | 3600 | 2 | 764.59 | GGB | 765.934 | 777.563 | 769.597 | 267.06 | GGB | 10932.2 | GGB | 9.81 | GGB | 1011.61 | GGB | 62.76 | GGB | 171953.08 | GGB | 139619.04 | GGB | 0 | 0 | 2934 | 3600 | 2918.61 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265321.6 | GGB | 265324.41 | 2918.61 | 2706.8514 |  |  |  | 1 | 1 |  |  |  |  | 139619.04 | 2706.8514 | 139619.04 | 2706.8514 | 9.5028 | [5 empty] | 113.1926 | 2706.8514 |  | 104.98
21.06.2008 08:00 | 3600 | 2 | 766.15 | GGB | 768.132 | 779.766 | 772.161 | 266.16 | GGB | 10887.4 | GGB | 9.83 | GGB | 1011.79 | GGB | 63 | GGB | 171354.5 | GGB | 139060.72 | GGB | 0 | 0 | 2824 | 3600 | 2808.32 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265361.37 | GGB | 265364.18 | 2808.32 | 2717.7193 |  |  |  | 0 | 1 | [14 empty] | 108.4797 | 2717.7193 |  | 104.98
21.06.2008 09:00 | 3600 | 2 | 766.2 | GGB | 764.835 | 778.336 | 770.696 | 263.42 | GGB | 10806.9 | GGB | 9.82 | GGB | 1011.45 | GGB | 63.78 | GGB | 168205.33 | GGB | 136141.84 | GGB | 0 | 0 | 2773 | 3600 | 2757.89 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265401.14 | GGB | 265403.95 | 2757.89 | 2757.89 |  |  |  | 1 | 1 |  |  |  |  | 136141.84 | 2757.89 | 136141.84 | 2757.89 | 9.4409 | [5 empty] | 104.2956 |  |  | #VALUE!
21.06.2008 10:00 | 3600 | 2 | 766.72 | GGB | 765.934 | 778.641 | 771.795 | 261.59 | GGB | 10724 | GGB | 9.82 | GGB | 1010.96 | GGB | 64.82 | GGB | 166236.83 | GGB | 134068.88 | GGB | 0 | 0 | 2712 | 3600 | 2696.76 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265440.91 | GGB | 265443.72 | 2696.76 | 2696.76 |  |  |  | 1 | 1 |  |  |  |  | 134068.88 | 2696.76 | 134068.88 | 2696.76 | 9.0911 | [5 empty] | 100.431 |  |  | #VALUE!
21.06.2008 11:00 | 3600 | 2 | 767.22 | GGB | 767.033 | 779.672 | 771.795 | 261.62 | GGB | 10607.4 | GGB | 9.81 | GGB | 1010.15 | GGB | 65.22 | GGB | 166525.12 | GGB | 134033.52 | GGB | 0 | 0 | 2635 | 3600 | 2619.92 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265480.68 | GGB | 265483.49 | 2619.92 | 2619.92 |  |  |  | 0 | 1 | [14 empty] | 97.5436 |  |  | #VALUE!
21.06.2008 12:00 | 3600 | 2 | 767.6 | GGB | 765.934 | 778.43 | 770.696 | 259.8 | GGB | 10576.4 | GGB | 9.82 | GGB | 1009.24 | GGB | 65.99 | GGB | 164617.13 | GGB | 132080.68 | GGB | 0 | 0 | 2590 | 3600 | 2574.57 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265520.45 | GGB | 265523.26 | 2574.57 | 2574.57 |  |  |  | 1 | 1 |  |  |  |  | 132080.68 | 2574.57 | 132080.68 | 2574.57 | 8.5504 | [5 empty] | 94.4586 |  |  | #VALUE!
21.06.2008 13:00 | 3600 | 2 | 766.77 | GGB | 763.37 | 776.086 | 768.498 | 258.35 | GGB | 10545.9 | GGB | 9.8 | GGB | 1008.19 | GGB | 66.17 | GGB | 163125.07 | GGB | 130676.71 | GGB | 0 | 0 | 2618 | 3600 | 2602.82 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265560.22 | GGB | 265563.03 | 2602.82 | 2602.82 |  |  |  | 0 | 1 | [14 empty] | 94.48 |  |  | #VALUE!
21.06.2008 14:00 | 3600 | 2 | 767.01 | GGB | 765.934 | 779.25 | 770.696 | 259.22 | GGB | 10584.1 | GGB | 9.82 | GGB | 1008.08 | GGB | 66.58 | GGB | 163050.25 | GGB | 130444.42 | GGB | 0 | 0 | 2659 | 3600 | 2644.05 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265599.99 | GGB | 265602.8 | 2644.05 | 2644.05 |  |  |  | 0 | 1 | [14 empty] | 95.806 |  |  | #VALUE!
21.06.2008 15:00 | 3600 | 2 | 765.29 | GGB | 763.37 | 776.133 | 768.864 | 259.61 | GGB | 10539.4 | GGB | 9.78 | GGB | 1007.72 | GGB | 66.1 | GGB | 163313.23 | GGB | 130793.08 | GGB | 0 | 0 | 2725 | 3600 | 2709.57 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265639.76 | GGB | 265642.57 | 2709.57 | 2709.57 |  |  |  | 0 | 1 | [14 empty] | 98.4425 |  |  | #VALUE!
21.06.2008 16:00 | 3600 | 2 | 764.65 | GGB | 764.835 | 778.172 | 770.33 | 264.41 | GGB | 10653.3 | GGB | 9.78 | GGB | 1009.19 | GGB | 64.05 | GGB | 168381.39 | GGB | 135870.07 | GGB | 0 | 0 | 2832 | 3600 | 2816.83 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265679.53 | GGB | 265682.34 | 2816.83 | 2781.5397 |  |  |  | 1 | 1 |  |  |  |  | 135870.07 | 2781.5397 | 135870.07 | 2781.5397 | 9.5028 | [5 empty] | 106.3119 | 2781.5397 |  | 104.98
21.06.2008 17:00 | 3600 | 2 | 766.3 | GGB | 765.934 | 778.242 | 771.429 | 263.18 | GGB | 10737 | GGB | 9.83 | GGB | 1009.49 | GGB | 64.83 | GGB | 165948.54 | GGB | 133638.79 | GGB | 0 | 0 | 2764 | 3600 | 2748.34 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265719.3 | GGB | 265722.11 | 2748.34 | 2748.34 |  |  |  | 1 | 1 |  |  |  |  | 133638.79 | 2748.34 | 133638.79 | 2748.34 | 9.2352 | [5 empty] | 102.0236 |  |  | #VALUE!
21.06.2008 18:00 | 3600 | 2 | 764.85 | GGB | 763.37 | 776.109 | 768.864 | 262.92 | GGB | 10679.6 | GGB | 9.79 | GGB | 1009.41 | GGB | 65.29 | GGB | 165717.47 | GGB | 133262.42 | GGB | 0 | 0 | 2847 | 3600 | 2831.48 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265759.07 | GGB | 265761.88 | 2831.48 | 2831.48 |  |  |  | 0 | 1 | [14 empty] | 104.8139 |  |  | #VALUE!
21.06.2008 19:00 | 3600 | 2 | 765.04 | GGB | 764.835 | 777.258 | 769.963 | 263.91 | GGB | 10737.9 | GGB | 9.81 | GGB | 1008.71 | GGB | 65.15 | GGB | 166404.08 | GGB | 133775.64 | GGB | 0 | 0 | 2865 | 3600 | 2848.99 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265798.84 | GGB | 265801.65 | 2848.99 | 2825.0883 |  |  |  | 1 | 1 |  |  |  |  | 133775.64 | 2825.0883 | 133775.64 | 2825.0883 | 9.5028 | [5 empty] | 105.8682 | 2825.0883 |  | 104.98
21.06.2008 20:00 | 3600 | 2 | 763.13 | GGB | 763.37 | 776.016 | 767.766 | 266.12 | GGB | 10811.3 | GGB | 9.77 | GGB | 1010.57 | GGB | 62.84 | GGB | 169603.86 | GGB | 137538.64 | GGB | 0 | 0 | 2982 | 3600 | 2965.92 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265838.61 | GGB | 265841.42 | 2965.92 | 2747.7951 |  |  |  | 0 | 1 | [14 empty] | 113.3135 | 2747.7951 |  | 104.98
21.06.2008 21:00 | 3600 | 2 | 764.21 | GGB | 763.37 | 774.891 | 766.667 | 268.63 | GGB | 10850.2 | GGB | 9.8 | GGB | 1011.09 | GGB | 63.6 | GGB | 172027.9 | GGB | 139258.81 | GGB | 0 | 0 | 2947 | 3600 | 2931.86 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265878.38 | GGB | 265881.19 | 2931.86 | 2713.8534 |  |  |  | 0 | 1 | [14 empty] | 113.4131 | 2713.8534 |  | 104.98
21.06.2008 22:00 | 3600 | 2 | 764.81 | GGB | 761.172 | 773.391 | 765.201 | 268.15 | GGB | 10892.5 | GGB | 9.81 | GGB | 1011.38 | GGB | 63.25 | GGB | 171915.67 | GGB | 139353.83 | GGB | 0 | 0 | 2913 | 3600 | 2896.99 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265918.15 | GGB | 265920.96 | 2896.99 | 2712.003 |  |  |  | 0 | 1 | [14 empty] | 112.1407 | 2712.003 |  | 104.98
21.06.2008 23:00 | 3600 | 2 | 764.61 | GGB | 763.37 | 775.547 | 767.766 | 268.45 | GGB | 10928.4 | GGB | 9.81 | GGB | 1011.84 | GGB | 63.33 | GGB | 172264.48 | GGB | 139665.94 | GGB | 0 | 0 | 2950 | 3600 | 2934.44 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265957.92 | GGB | 265960.73 | 2934.44 | 2705.9425 |  |  |  | 0 | 1 | [14 empty] | 113.8448 | 2705.9425 |  | 104.98
21.06.2008 24:00 | 3600 | 2 | 763.67 | GGB | 763.37 | 775.383 | 767.766 | 270.59 | GGB | 10901 | GGB | 9.79 | GGB | 1013.14 | GGB | 62.6 | GGB | 174925.09 | GGB | 142316.6 | GGB | 0 | 0 | 3005 | 3600 | 2989.72 | GGB | 100 | GGB | 39.77 | GGB | 39.77 | GGB | 265997.69 | GGB | 266000.5 | 2989.72 | 2655.544 |  |  |  | 0 | 1 | [14 empty] | 118.1908 | 2655.544 |  | 104.98
22.06.2008 01:00 | 3600 | 2 | 764.85 | GGB | 762.271 | 774.023 | 766.667 | 268.94 | GGB | 10989.8 | GGB | 9.82 | GGB | 1012.8 | GGB | 62.8 | GGB | 173692.72 | GGB | 141181.3 | GGB | 0 | 0 | 2953 | 3600 | 2937.59 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266035.89 | GGB | 266038.7 | 2937.59 | 2676.8984 |  |  |  | 0 | 1 | [14 empty] | 115.2035 | 2676.8984 |  | 104.98
22.06.2008 02:00 | 3600 | 2 | 764.32 | GGB | 763.37 | 775.219 | 767.766 | 269.59 | GGB | 10980.2 | GGB | 9.81 | GGB | 1013 | GGB | 62.94 | GGB | 173884.17 | GGB | 141305.96 | GGB | 0 | 0 | 3007 | 3600 | 2991.24 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266074.09 | GGB | 266076.9 | 2991.24 | 2674.5369 |  |  |  | 0 | 1 | [14 empty] | 117.4111 | 2674.5369 |  | 104.98
22.06.2008 03:00 | 3600 | 2 | 764.29 | GGB | 763.37 | 775.359 | 767.766 | 269.64 | GGB | 10990.6 | GGB | 9.81 | GGB | 1013.3 | GGB | 62.85 | GGB | 173875.37 | GGB | 141379.98 | GGB | 0 | 0 | 3003 | 3600 | 2987.11 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266112.29 | GGB | 266115.1 | 2987.11 | 2673.1366 |  |  |  | 0 | 1 | [14 empty] | 117.3104 | 2673.1366 |  | 104.98
22.06.2008 04:00 | 3600 | 2 | 764.14 | GGB | 764.469 | 776.297 | 768.864 | 269.84 | GGB | 11000.6 | GGB | 9.81 | GGB | 1013.19 | GGB | 62.64 | GGB | 174198.87 | GGB | 141716.96 | GGB | 0 | 0 | 3001 | 3600 | 2985.72 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266150.48 | GGB | 266153.3 | 2985.72 | 2666.7803 |  |  |  | 1 | 1 |  |  |  |  | 141716.96 | 2666.7803 | 141716.96 | 2666.7803 | 9.8934 | [5 empty] | 117.5353 | 2666.7803 |  | 104.98
22.06.2008 05:00 | 3600 | 2 | 763.8 | GGB | 762.271 | 773.906 | 766.3 | 270.45 | GGB | 10987.5 | GGB | 9.8 | GGB | 1013.24 | GGB | 62.41 | GGB | 174975.71 | GGB | 142449.89 | GGB | 0 | 0 | 3016 | 3600 | 3000.21 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266188.68 | GGB | 266191.5 | 3000.21 | 2653.0593 |  |  |  | 0 | 1 | [14 empty] | 118.7166 | 2653.0593 |  | 104.98
22.06.2008 06:00 | 3600 | 2 | 764.49 | GGB | 763.37 | 775.922 | 767.766 | 271.45 | GGB | 10981 | GGB | 9.81 | GGB | 1013.42 | GGB | 61.89 | GGB | 176501.88 | GGB | 143940.97 | GGB | 0 | 0 | 2978 | 3600 | 2962.26 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266226.88 | GGB | 266229.7 | 2962.26 | 2625.5763 |  |  |  | 0 | 1 | [14 empty] | 118.4418 | 2625.5763 |  | 104.98
22.06.2008 07:00 | 3600 | 2 | 765.04 | GGB | 764.469 | 775.898 | 768.864 | 269.45 | GGB | 11007.9 | GGB | 9.82 | GGB | 1013.59 | GGB | 62.6 | GGB | 173547.47 | GGB | 141255.19 | GGB | 0 | 0 | 2950 | 3600 | 2934.09 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266265.08 | GGB | 266267.9 | 2934.09 | 2675.4982 |  |  |  | 1 | 1 |  |  |  |  | 141255.19 | 2675.4982 | 141255.19 | 2675.4982 | 9.8934 | [5 empty] | 115.1265 | 2675.4982 |  | 104.98
22.06.2008 08:00 | 3600 | 2 | 765.23 | GGB | 764.835 | 776.977 | 768.864 | 268.5 | GGB | 10970.7 | GGB | 9.82 | GGB | 1013.52 | GGB | 63.05 | GGB | 172312.89 | GGB | 140054.22 | GGB | 0 | 0 | 2932 | 3600 | 2916.29 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266303.28 | GGB | 266306.1 | 2916.29 | 2698.4406 |  |  |  | 1 | 1 |  |  |  |  | 140054.22 | 2698.4406 | 140054.22 | 2698.4406 | 9.8934 | [5 empty] | 113.4552 | 2698.4406 |  | 104.98
22.06.2008 09:00 | 3600 | 2 | 765.57 | GGB | 763.37 | 776.438 | 768.864 | 266.62 | GGB | 10901.8 | GGB | 9.82 | GGB | 1013.64 | GGB | 63.73 | GGB | 169949.37 | GGB | 137872.67 | GGB | 0 | 0 | 2880 | 3600 | 2864.78 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266341.48 | GGB | 266344.3 | 2864.78 | 2741.1379 |  |  |  | 0 | 1 | [14 empty] | 109.7152 | 2741.1379 |  | 104.98
22.06.2008 10:00 | 3600 | 2 | 765.72 | GGB | 765.934 | 778.875 | 771.429 | 265.01 | GGB | 10821.1 | GGB | 9.81 | GGB | 1013.76 | GGB | 64.33 | GGB | 168027.08 | GGB | 136086.69 | GGB | 0 | 0 | 2855 | 3600 | 2839.55 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266379.68 | GGB | 266382.5 | 2839.55 | 2777.1121 |  |  |  | 0 | 1 | [14 empty] | 107.3403 | 2777.1121 |  | 104.98
22.06.2008 11:00 | 3600 | 2 | 766.54 | GGB | 765.934 | 777.797 | 770.33 | 264.1 | GGB | 10778.4 | GGB | 9.82 | GGB | 1013.28 | GGB | 64.76 | GGB | 167315.16 | GGB | 135271.07 | GGB | 0 | 0 | 2776 | 3600 | 2760.48 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266417.87 | GGB | 266420.7 | 2760.48 | 2760.48 |  |  |  | 1 | 1 |  |  |  |  | 135271.07 | 2760.48 | 135271.07 | 2760.48 | 9.7752 | [5 empty] | 103.7259 |  |  | #VALUE!
22.06.2008 12:00 | 3600 | 2 | 767.01 | GGB | 765.934 | 778.758 | 770.33 | 263.01 | GGB | 10729.9 | GGB | 9.82 | GGB | 1013.05 | GGB | 65.01 | GGB | 166637.35 | GGB | 134593.49 | GGB | 0 | 0 | 2723 | 3600 | 2707.58 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266456.07 | GGB | 266458.9 | 2707.58 | 2707.58 |  |  |  | 0 | 1 | [14 empty] | 101.2285 |  |  | #VALUE!
22.06.2008 13:00 | 3600 | 2 | 767.24 | GGB | 765.934 | 778.688 | 770.33 | 261.85 | GGB | 10685.7 | GGB | 9.81 | GGB | 1012.63 | GGB | 65.34 | GGB | 165653.65 | GGB | 133616.11 | GGB | 0 | 0 | 2679 | 3600 | 2663.81 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266494.27 | GGB | 266497.1 | 2663.81 | 2663.81 |  |  |  | 1 | 1 |  |  |  |  | 133616.11 | 2663.81 | 133616.11 | 2663.81 | 9.3175 | [5 empty] | 98.8689 |  |  | #VALUE!
22.06.2008 14:00 | 3600 | 2 | 767.34 | GGB | 765.934 | 778.781 | 770.33 | 260.96 | GGB | 10641.8 | GGB | 9.81 | GGB | 1012.32 | GGB | 65.61 | GGB | 164807.49 | GGB | 132785.5 | GGB | 0 | 0 | 2652 | 3600 | 2636.22 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266532.47 | GGB | 266535.3 | 2636.22 | 2636.22 |  |  |  | 0 | 1 | [14 empty] | 97.2366 |  |  | #VALUE!
22.06.2008 15:00 | 3600 | 2 | 767.49 | GGB | 765.934 | 778.758 | 771.429 | 261.38 | GGB | 10571 | GGB | 9.81 | GGB | 1011.74 | GGB | 65.31 | GGB | 165726.27 | GGB | 133567.29 | GGB | 0 | 0 | 2607 | 3600 | 2591.56 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266570.67 | GGB | 266573.5 | 2591.56 | 2591.56 |  |  |  | 0 | 1 | [14 empty] | 96.1521 |  |  | #VALUE!
22.06.2008 16:00 | 3600 | 2 | 768.05 | GGB | 768.132 | 780.938 | 772.527 | 260.8 | GGB | 10569.9 | GGB | 9.81 | GGB | 1010.68 | GGB | 65.52 | GGB | 165352.16 | GGB | 133044.55 | GGB | 0 | 0 | 2581 | 3600 | 2566.19 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266608.87 | GGB | 266611.7 | 2566.19 | 2566.19 |  |  |  | 0 | 1 | [14 empty] | 94.8382 |  |  | #VALUE!
22.06.2008 17:00 | 3600 | 2 | 767.82 | GGB | 765.934 | 778.875 | 771.429 | 259.25 | GGB | 10564.6 | GGB | 9.81 | GGB | 1010.35 | GGB | 66.29 | GGB | 163506.89 | GGB | 131217.42 | GGB | 0 | 0 | 2574 | 3600 | 2558.63 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266647.07 | GGB | 266649.9 | 2558.63 | 2558.63 |  |  |  | 0 | 1 | [14 empty] | 93.2602 |  |  | #VALUE!
22.06.2008 18:00 | 3600 | 2 | 767.78 | GGB | 765.934 | 778.992 | 771.429 | 259.14 | GGB | 10561.6 | GGB | 9.81 | GGB | 1010.04 | GGB | 66.27 | GGB | 163742.36 | GGB | 131374.79 | GGB | 0 | 0 | 2571 | 3600 | 2555.8 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266685.26 | GGB | 266688.1 | 2555.8 | 2555.8 |  |  |  | 0 | 1 | [14 empty] | 93.2688 |  |  | #VALUE!
22.06.2008 19:00 | 3600 | 2 | 767.72 | GGB | 765.934 | 778.992 | 771.429 | 259.48 | GGB | 10571.9 | GGB | 9.8 | GGB | 1010.05 | GGB | 65.94 | GGB | 164216.61 | GGB | 131885.25 | GGB | 0 | 0 | 2586 | 3600 | 2570.67 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266723.46 | GGB | 266726.3 | 2570.67 | 2570.67 |  |  |  | 0 | 1 | [14 empty] | 94.176 |  |  | #VALUE!
22.06.2008 20:00 | 3600 | 2 | 767.37 | GGB | 767.033 | 780.094 | 771.429 | 260.33 | GGB | 10605.6 | GGB | 9.8 | GGB | 1010.57 | GGB | 65.52 | GGB | 164844.9 | GGB | 132622.94 | GGB | 0 | 0 | 2607 | 3600 | 2591.86 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266761.66 | GGB | 266764.5 | 2591.86 | 2591.86 |  |  |  | 0 | 1 | [14 empty] | 95.4834 |  |  | #VALUE!
22.06.2008 21:00 | 3600 | 2 | 767.41 | GGB | 765.934 | 778.805 | 771.429 | 260.65 | GGB | 10620.1 | GGB | 9.8 | GGB | 1010.8 | GGB | 65.4 | GGB | 164789.88 | GGB | 132655.42 | GGB | 0 | 0 | 2611 | 3600 | 2595.73 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266799.86 | GGB | 266802.7 | 2595.73 | 2595.73 |  |  |  | 0 | 1 | [14 empty] | 95.6493 |  |  | #VALUE!
22.06.2008 22:00 | 3600 | 2 | 766.79 | GGB | 764.469 | 776.742 | 768.864 | 260.79 | GGB | 10624.9 | GGB | 9.8 | GGB | 1010.5 | GGB | 65.51 | GGB | 164831.7 | GGB | 132605.31 | GGB | 0 | 0 | 2654 | 3600 | 2638.98 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266838.06 | GGB | 266840.9 | 2638.98 | 2638.98 |  |  |  | 1 | 1 |  |  |  |  | 132605.31 | 2638.98 | 132605.31 | 2638.98 | 9.1608 | [5 empty] | 97.2063 |  |  | #VALUE!
22.06.2008 23:00 | 3600 | 2 | 766.51 | GGB | 764.835 | 778.102 | 768.864 | 261.37 | GGB | 10665.2 | GGB | 9.81 | GGB | 1010.31 | GGB | 65.5 | GGB | 165357.66 | GGB | 133005.9 | GGB | 0 | 0 | 2703 | 3600 | 2687.58 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266876.26 | GGB | 266879.1 | 2687.58 | 2687.58 |  |  |  | 1 | 1 |  |  |  |  | 133005.9 | 2687.58 | 133005.9 | 2687.58 | 9.3577 | [5 empty] | 99.2956 |  |  | #VALUE!
22.06.2008 24:00 | 3600 | 2 | 765.7 | GGB | 764.469 | 777.141 | 769.963 | 262.74 | GGB | 10685.7 | GGB | 9.8 | GGB | 1009.9 | GGB | 65.28 | GGB | 166197.21 | GGB | 133716.12 | GGB | 0 | 0 | 2769 | 3600 | 2753.26 | GGB | 100 | GGB | 38.2 | GGB | 38.2 | GGB | 266914.46 | GGB | 266917.3 | 2753.26 | 2753.26 |  |  |  | 1 | 1 |  |  |  |  | 133716.12 | 2753.26 | 133716.12 | 2753.26 | 9.6376 | [5 empty] | 102.2653 |  |  | #VALUE!
23.06.2008 01:00 | 3600 | 2 | 766.42 | GGB | 764.835 | 777.07 | 769.963 | 262.77 | GGB | 10700.3 | GGB | 9.81 | GGB | 1009.58 | GGB | 65.22 | GGB | 166128.99 | GGB | 133641.58 | GGB | 0 | 0 | 2732 | 3600 | 2716.9 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 266952.48 | GGB | 266955.33 | 2716.9 | 2716.9 |  |  |  | 1 | 1 |  |  |  |  | 133641.58 | 2716.9 | 133641.58 | 2716.9 | 9.5475 | [5 empty] | 100.8586 |  |  | #VALUE!
23.06.2008 02:00 | 3600 | 2 | 766.03 | GGB | 764.835 | 778.219 | 769.963 | 262.11 | GGB | 10711.7 | GGB | 9.81 | GGB | 1009.01 | GGB | 64.98 | GGB | 166402.98 | GGB | 133880.42 | GGB | 0 | 0 | 2761 | 3600 | 2745.32 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 266990.51 | GGB | 266993.36 | 2745.32 | 2745.32 |  |  |  | 1 | 1 |  |  |  |  | 133880.42 | 2745.32 | 133880.42 | 2745.32 | 9.6646 | [5 empty] | 102.0957 |  |  | #VALUE!
23.06.2008 03:00 | 3600 | 2 | 765.55 | GGB | 765.934 | 778.336 | 769.963 | 263.8 | GGB | 10675.8 | GGB | 9.8 | GGB | 1008.17 | GGB | 64.86 | GGB | 167692.57 | GGB | 134853.4 | GGB | 0 | 0 | 2802 | 3600 | 2786.5 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267028.54 | GGB | 267031.39 | 2786.5 | 2786.5 |  |  |  | 1 | 1 |  |  |  |  | 134853.4 | 2786.5 | 134853.4 | 2786.5 | 9.8809 | [5 empty] | 104.3803 |  |  | #VALUE!
23.06.2008 04:00 | 3600 | 2 | 766.19 | GGB | 765.934 | 778.758 | 770.33 | 264.05 | GGB | 10683.1 | GGB | 9.81 | GGB | 1007.59 | GGB | 64.7 | GGB | 167987.46 | GGB | 135077.65 | GGB | 0 | 0 | 2761 | 3600 | 2745.76 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267066.57 | GGB | 267069.42 | 2745.76 | 2745.76 |  |  |  | 0 | 1 | [14 empty] | 103.0252 |  |  | #VALUE!
23.06.2008 05:00 | 3600 | 2 | 765.96 | GGB | 764.835 | 777.539 | 769.597 | 262.82 | GGB | 10694.2 | GGB | 9.81 | GGB | 1006.77 | GGB | 64.97 | GGB | 166474.5 | GGB | 133643.55 | GGB | 0 | 0 | 2745 | 3600 | 2729.87 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267104.6 | GGB | 267107.45 | 2729.87 | 2729.87 |  |  |  | 1 | 1 |  |  |  |  | 133643.55 | 2729.87 | 133643.55 | 2729.87 | 9.5932 | [5 empty] | 101.3415 |  |  | #VALUE!
23.06.2008 06:00 | 3600 | 2 | 765.94 | GGB | 764.835 | 777.516 | 770.696 | 262.73 | GGB | 10691.5 | GGB | 9.81 | GGB | 1006.16 | GGB | 65.05 | GGB | 166416.18 | GGB | 133484.62 | GGB | 0 | 0 | 2753 | 3600 | 2737.88 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267142.63 | GGB | 267145.48 | 2737.88 | 2737.88 |  |  |  | 1 | 1 |  |  |  |  | 133484.62 | 2737.88 | 133484.62 | 2737.88 | 9.6099 | [5 empty] | 101.518 |  |  | #VALUE!
23.06.2008 07:00 | 3600 | 2 | 765.96 | GGB | 764.469 | 777.539 | 769.597 | 262.46 | GGB | 10680.2 | GGB | 9.81 | GGB | 1005.27 | GGB | 65.12 | GGB | 166288.54 | GGB | 133236.61 | GGB | 0 | 0 | 2744 | 3600 | 2728.9 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267180.65 | GGB | 267183.51 | 2728.9 | 2728.9 |  |  |  | 1 | 1 |  |  |  |  | 133236.61 | 2728.9 | 133236.61 | 2728.9 | 9.5606 | [5 empty] | 100.9971 |  |  | #VALUE!
23.06.2008 08:00 | 3600 | 2 | 766.32 | GGB | 764.835 | 777.727 | 769.597 | 261.79 | GGB | 10663.2 | GGB | 9.81 | GGB | 1005.3 | GGB | 65.21 | GGB | 165555.72 | GGB | 132618.13 | GGB | 0 | 0 | 2717 | 3600 | 2701.42 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267218.68 | GGB | 267221.54 | 2701.42 | 2701.42 |  |  |  | 1 | 1 |  |  |  |  | 132618.13 | 2701.42 | 132618.13 | 2701.42 | 9.4204 | [5 empty] | 99.5159 |  |  | #VALUE!
23.06.2008 09:00 | 3600 | 2 | 765.19 | GGB | 762.271 | 775.734 | 767.033 | 262.24 | GGB | 10672.9 | GGB | 9.8 | GGB | 1004.77 | GGB | 64.79 | GGB | 165925.43 | GGB | 133008.62 | GGB | 0 | 0 | 2788 | 3600 | 2772.02 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267256.71 | GGB | 267259.57 | 2772.02 | 2772.02 |  |  |  | 0 | 1 | [14 empty] | 102.4174 |  |  | #VALUE!
23.06.2008 10:00 | 3600 | 2 | 765.04 | GGB | 763.37 | 775.781 | 768.132 | 263.51 | GGB | 10683.2 | GGB | 9.8 | GGB | 1003.97 | GGB | 64.66 | GGB | 167305.25 | GGB | 134062.6 | GGB | 0 | 0 | 2827 | 3600 | 2811.01 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267294.74 | GGB | 267297.6 | 2811.01 | 2811.01 |  |  |  | 0 | 1 | [14 empty] | 104.6809 |  |  | #VALUE!
23.06.2008 11:00 | 3600 | 2 | 765.73 | GGB | 764.835 | 777.656 | 769.597 | 263.86 | GGB | 10655.6 | GGB | 9.82 | GGB | 1003.18 | GGB | 64.68 | GGB | 167548.43 | GGB | 134142.95 | GGB | 0 | 0 | 2783 | 3600 | 2767.08 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267332.77 | GGB | 267335.63 | 2767.08 | 2767.08 |  |  |  | 1 | 1 |  |  |  |  | 134142.95 | 2767.08 | 134142.95 | 2767.08 | 9.7603 | [5 empty] | 103.1067 |  |  | #VALUE!
23.06.2008 12:00 | 3600 | 2 | 767.02 | GGB | 764.835 | 777.656 | 769.597 | 259.91 | GGB | 10612.2 | GGB | 9.83 | GGB | 1002.29 | GGB | 66.03 | GGB | 163130.57 | GGB | 129970.93 | GGB | 0 | 0 | 2687 | 3600 | 2671.75 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267370.79 | GGB | 267373.66 | 2671.75 | 2671.75 |  |  |  | 1 | 1 |  |  |  |  | 129970.93 | 2671.75 | 129970.93 | 2671.75 | 9.1309 | [5 empty] | 96.4583 |  |  | #VALUE!
23.06.2008 13:00 | 3600 | 2 | 766.41 | GGB | 767.033 | 779.977 | 771.795 | 258.66 | GGB | 10535.5 | GGB | 9.82 | GGB | 1001.47 | GGB | 66.65 | GGB | 162103.96 | GGB | 128811.24 | GGB | 0 | 0 | 2694 | 3600 | 2678.68 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267408.82 | GGB | 267411.69 | 2678.68 | 2678.68 |  |  |  | 0 | 1 | [14 empty] | 95.8456 |  |  | #VALUE!
23.06.2008 14:00 | 3600 | 2 | 767.25 | GGB | 764.835 | 777.891 | 769.597 | 255.68 | GGB | 10434.5 | GGB | 9.82 | GGB | 1000.16 | GGB | 67.43 | GGB | 159246.38 | GGB | 126084.4 | GGB | 0 | 0 | 2609 | 3600 | 2593.5 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267446.85 | GGB | 267449.72 | 2593.5 | 2593.5 |  |  |  | 1 | 1 |  |  |  |  | 126084.4 | 2593.5 | 126084.4 | 2593.5 | 8.5985 | [5 empty] | 90.8333 |  |  | #VALUE!
23.06.2008 15:00 | 3600 | 2 | 766.38 | GGB | 764.835 | 777.891 | 769.597 | 255.76 | GGB | 10400.2 | GGB | 9.8 | GGB | 999.19 | GGB | 67.71 | GGB | 158506.95 | GGB | 125277.02 | GGB | 0 | 0 | 2653 | 3600 | 2637.93 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267484.88 | GGB | 267487.75 | 2637.93 | 2637.93 |  |  |  | 1 | 1 |  |  |  |  | 125277.02 | 2637.93 |  | 2637.93 | 8.6898 | [5 empty] | 91.7978 |  |  | #VALUE!
23.06.2008 16:00 | 3600 | 2 | 765.41 | GGB | 763.37 | 776.672 | 768.132 | 257.15 | GGB | 10467.9 | GGB | 9.79 | GGB | 1000.11 | GGB | 66.66 | GGB | 159502.76 | GGB | 126568.77 | GGB | 0 | 0 | 2760 | 3600 | 2744.9 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267522.91 | GGB | 267525.78 | 2744.9 | 2744.9 |  |  |  | 0 | 1 | [14 empty] | 96.5052 |  |  | #VALUE!
23.06.2008 17:00 | 3600 | 2 | 766.17 | GGB | 763.37 | 776.461 | 768.498 | 257.57 | GGB | 10456.2 | GGB | 9.8 | GGB | 1000.73 | GGB | 67.91 | GGB | 159317.9 | GGB | 126035.4 | GGB | 0 | 0 | 2737 | 3600 | 2721.37 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267560.94 | GGB | 267563.81 | 2721.37 | 2721.37 |  |  |  | 0 | 1 | [14 empty] | 95.2747 |  |  | #VALUE!
23.06.2008 18:00 | 3600 | 2 | 766.88 | GGB | 764.469 | 777.609 | 769.597 | 256.99 | GGB | 10434.4 | GGB | 9.8 | GGB | 1000.5 | GGB | 67.63 | GGB | 159621.6 | GGB | 126350.64 | GGB | 0 | 0 | 2664 | 3600 | 2648.79 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267598.96 | GGB | 267601.84 | 2648.79 | 2648.79 |  |  |  | 1 | 1 |  |  |  |  | 126350.64 | 2648.79 | 126350.64 | 2648.79 | 8.8003 | [5 empty] | 92.9656 |  |  | #VALUE!
23.06.2008 19:00 | 3600 | 2 | 767.1 | GGB | 764.835 | 777.586 | 769.597 | 257.67 | GGB | 10462.9 | GGB | 9.8 | GGB | 1001.13 | GGB | 67.06 | GGB | 161087.25 | GGB | 127805.55 | GGB | 0 | 0 | 2646 | 3600 | 2630.27 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267636.99 | GGB | 267639.87 | 2630.27 | 2630.27 |  |  |  | 1 | 1 |  |  |  |  | 127805.55 | 2630.27 | 127805.55 | 2630.27 | 8.8394 | [5 empty] | 93.3786 |  |  | #VALUE!
23.06.2008 20:00 | 3600 | 2 | 767.2 | GGB | 764.835 | 778.148 | 770.696 | 257.85 | GGB | 10474.3 | GGB | 9.8 | GGB | 1001.5 | GGB | 66.55 | GGB | 161907 | GGB | 128697.61 | GGB | 0 | 0 | 2613 | 3600 | 2597.68 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267675.02 | GGB | 267677.9 | 2597.68 | 2597.68 |  |  |  | 1 | 1 |  |  |  |  | 128697.61 | 2597.68 | 128697.61 | 2597.68 | 8.7908 | [5 empty] | 92.8653 |  |  | #VALUE!
23.06.2008 21:00 | 3600 | 2 | 767.01 | GGB | 764.835 | 778.102 | 770.696 | 258.49 | GGB | 10523.6 | GGB | 9.8 | GGB | 1001.8 | GGB | 65.93 | GGB | 163151.48 | GGB | 129961.89 | GGB | 0 | 0 | 2632 | 3600 | 2616.17 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267713.05 | GGB | 267715.93 | 2616.17 | 2616.17 |  |  |  | 1 | 1 |  |  |  |  | 129961.89 | 2616.17 | 129961.89 | 2616.17 | 8.9404 | [5 empty] | 94.4451 |  |  | #VALUE!
23.06.2008 22:00 | 3600 | 2 | 765.98 | GGB | 764.835 | 777.07 | 769.597 | 260.35 | GGB | 10584.2 | GGB | 9.79 | GGB | 1002.9 | GGB | 65.21 | GGB | 164957.13 | GGB | 131824.37 | GGB | 0 | 0 | 2699 | 3600 | 2683.61 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267751.08 | GGB | 267753.96 | 2683.61 | 2683.61 |  |  |  | 1 | 1 |  |  |  |  | 131824.37 | 2683.61 | 131824.37 | 2683.61 | 9.3023 | [5 empty] | 98.2681 |  |  | #VALUE!
23.06.2008 23:00 | 3600 | 2 | 765.87 | GGB | 764.835 | 777.891 | 768.498 | 263.18 | GGB | 10623.1 | GGB | 9.79 | GGB | 1003.6 | GGB | 64.06 | GGB | 168119.5 | GGB | 134903.2 | GGB | 0 | 0 | 2727 | 3600 | 2711.15 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267789.1 | GGB | 267791.99 | 2711.15 | 2711.15 |  |  |  | 1 | 1 |  |  |  |  | 134903.2 | 2711.15 | 134903.2 | 2711.15 | 9.6172 | [5 empty] | 101.5952 |  |  | #VALUE!
23.06.2008 24:00 | 3600 | 2 | 765.71 | GGB | 763.37 | 776.648 | 768.498 | 263.68 | GGB | 10656.8 | GGB | 9.8 | GGB | 1003.9 | GGB | 63.73 | GGB | 168565.14 | GGB | 135432.95 | GGB | 0 | 0 | 2746 | 3600 | 2731.05 | GGB | 100 | GGB | 38.03 | GGB | 38.03 | GGB | 267827.13 | GGB | 267830.02 | 2731.05 | 2731.05 |  |  |  | 0 | 1 | [14 empty] | 102.7428 |  |  | #VALUE!
24.06.2008 01:00 | 3600 | 2 | 765.9 | GGB | 763.37 | 776.695 | 768.132 | 261.76 | GGB | 10702.6 | GGB | 9.81 | GGB | 1003.79 | GGB | 64.14 | GGB | 166561.43 | GGB | 133646.66 | GGB | 0 | 0 | 2751 | 3600 | 2735.17 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 267865.46 | GGB | 267868.35 | 2735.17 | 2735.17 |  |  |  | 0 | 1 | [14 empty] | 101.5406 |  |  | #VALUE!
24.06.2008 02:00 | 3600 | 2 | 765.46 | GGB | 762.271 | 775.57 | 767.033 | 262.44 | GGB | 10687.2 | GGB | 9.8 | GGB | 1003.99 | GGB | 64.45 | GGB | 166424.98 | GGB | 133439.9 | GGB | 0 | 0 | 2799 | 3600 | 2783.88 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 267903.79 | GGB | 267906.68 | 2783.88 | 2783.88 |  |  |  | 0 | 1 | [14 empty] | 103.1891 |  |  | #VALUE!
24.06.2008 03:00 | 3600 | 2 | 765.22 | GGB | 763.37 | 775.805 | 767.033 | 263.24 | GGB | 10709.5 | GGB | 9.8 | GGB | 1003.84 | GGB | 64.56 | GGB | 166895.93 | GGB | 133754.75 | GGB | 0 | 0 | 2827 | 3600 | 2811.01 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 267942.12 | GGB | 267945.01 | 2811.01 | 2811.01 |  |  |  | 0 | 1 | [14 empty] | 104.4405 |  |  | #VALUE!
24.06.2008 04:00 | 3600 | 2 | 765.41 | GGB | 764.469 | 776.906 | 769.597 | 263.09 | GGB | 10714.2 | GGB | 9.81 | GGB | 1003.61 | GGB | 64.28 | GGB | 167004.86 | GGB | 133925.22 | GGB | 0 | 0 | 2807 | 3600 | 2791.14 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 267980.44 | GGB | 267983.34 | 2791.14 | 2791.14 |  |  |  | 1 | 1 |  |  |  |  | 133925.22 | 2791.14 | 133925.22 | 2791.14 | 9.7523 | [5 empty] | 103.8345 |  |  | #VALUE!
24.06.2008 05:00 | 3600 | 2 | 764.97 | GGB | 764.469 | 776.883 | 768.498 | 263.48 | GGB | 10726 | GGB | 9.8 | GGB | 1003.76 | GGB | 63.99 | GGB | 167612.25 | GGB | 134548.14 | GGB | 0 | 0 | 2833 | 3600 | 2817.25 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268018.77 | GGB | 268021.67 | 2817.25 | 2808.8683 |  |  |  | 1 | 1 |  |  |  |  | 134548.14 | 2808.8683 | 134548.14 | 2808.8683 | 9.8598 | [5 empty] | 105.2933 | 2808.8683 |  | 104.98
24.06.2008 06:00 | 3600 | 2 | 765.09 | GGB | 763.37 | 775.852 | 768.132 | 263.7 | GGB | 10750.2 | GGB | 9.81 | GGB | 1003.63 | GGB | 63.69 | GGB | 168148.11 | GGB | 135080.36 | GGB | 0 | 0 | 2837 | 3600 | 2821.25 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268057.1 | GGB | 268060 | 2821.25 | 2797.8012 |  |  |  | 0 | 1 | [14 empty] | 105.8599 | 2797.8012 |  | 104.98
24.06.2008 07:00 | 3600 | 2 | 765.08 | GGB | 763.37 | 775.875 | 767.033 | 263.95 | GGB | 10766.8 | GGB | 9.81 | GGB | 1004.03 | GGB | 63.45 | GGB | 168411.09 | GGB | 135442.18 | GGB | 0 | 0 | 2836 | 3600 | 2820.04 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268095.43 | GGB | 268098.33 | 2820.04 | 2790.3272 |  |  |  | 0 | 1 | [14 empty] | 106.0979 | 2790.3272 |  | 104.98
24.06.2008 08:00 | 3600 | 2 | 764.55 | GGB | 763.37 | 776.25 | 768.498 | 265.05 | GGB | 10777.8 | GGB | 9.8 | GGB | 1004.82 | GGB | 63.21 | GGB | 169555.45 | GGB | 136565.41 | GGB | 0 | 0 | 2871 | 3600 | 2855.26 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268133.75 | GGB | 268136.66 | 2855.26 | 2767.3772 |  |  |  | 0 | 1 | [14 empty] | 108.3138 | 2767.3772 |  | 104.98
24.06.2008 09:00 | 3600 | 2 | 765.38 | GGB | 764.835 | 777.281 | 769.597 | 265.02 | GGB | 10743.1 | GGB | 9.81 | GGB | 1004.68 | GGB | 62.67 | GGB | 170183.74 | GGB | 137275.12 | GGB | 0 | 0 | 2789 | 3600 | 2773.27 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268172.08 | GGB | 268174.99 | 2773.27 | 2753.0699 |  |  |  | 1 | 1 |  |  |  |  | 137275.12 | 2753.0699 | 137275.12 | 2753.0699 | 9.8598 | [5 empty] | 105.7503 | 2753.0699 |  | 104.98
24.06.2008 10:00 | 3600 | 2 | 765.96 | GGB | 764.469 | 777.328 | 768.498 | 262.86 | GGB | 10748.9 | GGB | 9.82 | GGB | 1005.01 | GGB | 63.65 | GGB | 167715.68 | GGB | 134934.53 | GGB | 0 | 0 | 2756 | 3600 | 2740.08 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268210.41 | GGB | 268213.32 | 2740.08 | 2740.08 |  |  |  | 1 | 1 |  |  |  |  | 134934.53 | 2740.08 | 134934.53 | 2740.08 | 9.646 | [5 empty] | 102.7032 |  |  | #VALUE!
24.06.2008 11:00 | 3600 | 2 | 765.93 | GGB | 764.835 | 777.328 | 768.498 | 262.35 | GGB | 10726.4 | GGB | 9.81 | GGB | 1004.31 | GGB | 63.61 | GGB | 167581.44 | GGB | 134749.41 | GGB | 0 | 0 | 2747 | 3600 | 2731.99 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268248.74 | GGB | 268251.65 | 2731.99 | 2731.99 |  |  |  | 1 | 1 |  |  |  |  | 134749.41 | 2731.99 | 134749.41 | 2731.99 | 9.6043 | [5 empty] | 102.2595 |  |  | #VALUE!
24.06.2008 12:00 | 3600 | 2 | 765.98 | GGB | 764.835 | 777.352 | 769.597 | 261.88 | GGB | 10717.1 | GGB | 9.81 | GGB | 1004.14 | GGB | 63.56 | GGB | 167471.41 | GGB | 134655.51 | GGB | 0 | 0 | 2721 | 3600 | 2705.25 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268287.06 | GGB | 268289.98 | 2705.25 | 2705.25 |  |  |  | 1 | 1 |  |  |  |  | 134655.51 | 2705.25 | 134655.51 | 2705.25 | 9.5037 | [5 empty] | 101.188 |  |  | #VALUE!
24.06.2008 13:00 | 3600 | 2 | 766.17 | GGB | 764.835 | 777.164 | 768.498 | 261.6 | GGB | 10703.6 | GGB | 9.81 | GGB | 1004.13 | GGB | 63.56 | GGB | 167416.39 | GGB | 134611.77 | GGB | 0 | 0 | 2701 | 3600 | 2685.5 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268325.39 | GGB | 268328.31 | 2685.5 | 2685.5 |  |  |  | 1 | 1 |  |  |  |  | 134611.77 | 2685.5 | 134611.77 | 2685.5 | 9.4313 | [5 empty] | 100.4166 |  |  | #VALUE!
24.06.2008 14:00 | 3600 | 2 | 766.19 | GGB | 764.835 | 777.07 | 769.597 | 261.33 | GGB | 10697.3 | GGB | 9.81 | GGB | 1004.05 | GGB | 63.49 | GGB | 167465.9 | GGB | 134666.78 | GGB | 0 | 0 | 2690 | 3600 | 2674.54 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268363.72 | GGB | 268366.64 | 2674.54 | 2674.54 |  |  |  | 1 | 1 |  |  |  |  | 134666.78 | 2674.54 | 134666.78 | 2674.54 | 9.3966 | [5 empty] | 100.0477 |  |  | #VALUE!
24.06.2008 15:00 | 3600 | 2 | 766.56 | GGB | 764.835 | 777.211 | 769.597 | 261.22 | GGB | 10701.1 | GGB | 9.81 | GGB | 1004.39 | GGB | 63.53 | GGB | 167522.02 | GGB | 134742.31 | GGB | 0 | 0 | 2679 | 3600 | 2663.29 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268402.05 | GGB | 268404.97 | 2663.29 | 2663.29 |  |  |  | 1 | 1 |  |  |  |  | 134742.31 | 2663.29 | 134742.31 | 2663.29 | 9.3623 | [5 empty] | 99.6827 |  |  | #VALUE!
24.06.2008 16:00 | 3600 | 2 | 766.8 | GGB | 767.033 | 779.273 | 771.795 | 261.2 | GGB | 10711 | GGB | 9.81 | GGB | 1004.44 | GGB | 63.42 | GGB | 167562.73 | GGB | 134825.67 | GGB | 0 | 0 | 2674 | 3600 | 2658.4 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268440.38 | GGB | 268443.3 | 2658.4 | 2658.4 |  |  |  | 0 | 1 | [14 empty] | 99.5613 |  |  | #VALUE!
24.06.2008 17:00 | 3600 | 2 | 766.14 | GGB | 764.469 | 777.328 | 769.597 | 261.56 | GGB | 10713.7 | GGB | 9.8 | GGB | 1004.94 | GGB | 63.19 | GGB | 167969.86 | GGB | 135311.66 | GGB | 0 | 0 | 2709 | 3600 | 2693.72 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268478.7 | GGB | 268481.63 | 2693.72 | 2693.72 |  |  |  | 1 | 1 |  |  |  |  | 135311.66 | 2693.72 | 135311.66 | 2693.72 | 9.5093 | [5 empty] | 101.2477 |  |  | #VALUE!
24.06.2008 18:00 | 3600 | 2 | 766.46 | GGB | 763.37 | 777.328 | 768.498 | 261.5 | GGB | 10721.4 | GGB | 9.81 | GGB | 1004.84 | GGB | 63.4 | GGB | 167904.94 | GGB | 135164.61 | GGB | 0 | 0 | 2691 | 3600 | 2675.44 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268517.03 | GGB | 268519.96 | 2675.44 | 2675.44 |  |  |  | 0 | 1 | [14 empty] | 100.4513 |  |  | #VALUE!
24.06.2008 19:00 | 3600 | 2 | 765.46 | GGB | 763.37 | 776.227 | 768.498 | 262.94 | GGB | 10755 | GGB | 9.79 | GGB | 1005.44 | GGB | 62.98 | GGB | 168996.47 | GGB | 136295.29 | GGB | 0 | 0 | 2766 | 3600 | 2750.86 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268555.36 | GGB | 268558.29 | 2750.86 | 2750.86 |  |  |  | 0 | 1 | [14 empty] | 104.147 |  |  | #VALUE!
24.06.2008 20:00 | 3600 | 2 | 765.4 | GGB | 764.469 | 776.18 | 769.597 | 263.7 | GGB | 10810.5 | GGB | 9.8 | GGB | 1006.35 | GGB | 62.71 | GGB | 169941.66 | GGB | 137292.04 | GGB | 0 | 0 | 2798 | 3600 | 2782.56 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268593.69 | GGB | 268596.62 | 2782.56 | 2752.7306 |  |  |  | 1 | 1 |  |  |  |  | 137292.04 | 2752.7306 | 137292.04 | 2752.7306 | 9.8598 | [5 empty] | 106.1176 | 2752.7306 |  | 104.98
24.06.2008 21:00 | 3600 | 2 | 765.32 | GGB | 764.469 | 777.023 | 768.498 | 263.58 | GGB | 10845 | GGB | 9.81 | GGB | 1006.81 | GGB | 62.43 | GGB | 170503.94 | GGB | 137922.83 | GGB | 0 | 0 | 2819 | 3600 | 2803.76 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268632.01 | GGB | 268634.95 | 2803.76 | 2740.141 |  |  |  | 1 | 1 |  |  |  |  | 137922.83 | 2740.141 | 137922.83 | 2740.141 | 9.8598 | [5 empty] | 107.4174 | 2740.141 |  | 104.98
24.06.2008 22:00 | 3600 | 2 | 765.2 | GGB | 763.37 | 776.016 | 768.132 | 263.34 | GGB | 10868.1 | GGB | 9.81 | GGB | 1007.36 | GGB | 62.02 | GGB | 170719.6 | GGB | 138341.9 | GGB | 0 | 0 | 2826 | 3600 | 2810.98 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268670.34 | GGB | 268673.28 | 2810.98 | 2731.8405 |  |  |  | 0 | 1 | [14 empty] | 108.0212 | 2731.8405 |  | 104.98
24.06.2008 23:00 | 3600 | 2 | 765.21 | GGB | 764.469 | 777.281 | 769.597 | 262.64 | GGB | 10893.1 | GGB | 9.82 | GGB | 1007.4 | GGB | 61.61 | GGB | 171202.65 | GGB | 138907.66 | GGB | 0 | 0 | 2822 | 3600 | 2806.32 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268708.67 | GGB | 268711.61 | 2806.32 | 2720.7139 |  |  |  | 1 | 1 |  |  |  |  | 138907.66 | 2720.7139 | 138907.66 | 2720.7139 | 9.8598 | [5 empty] | 108.2832 | 2720.7139 |  | 104.98
24.06.2008 24:00 | 3600 | 2 | 764.03 | GGB | 763.37 | 775.992 | 768.498 | 263.33 | GGB | 10873.6 | GGB | 9.79 | GGB | 1007.52 | GGB | 61.18 | GGB | 171005.69 | GGB | 138943.34 | GGB | 0 | 0 | 2874 | 3600 | 2858.42 | GGB | 100 | GGB | 38.33 | GGB | 38.33 | GGB | 268747 | GGB | 268749.94 | 2858.42 | 2720.0152 |  |  |  | 0 | 1 | [14 empty] | 110.3218 | 2720.0152 |  | 104.98
25.06.2008 01:00 | 3600 | 2 | 764.76 | GGB | 763.37 | 775.992 | 768.498 | 263.28 | GGB | 10898 | GGB | 9.81 | GGB | 1007.59 | GGB | 61.32 | GGB | 170946.27 | GGB | 138845.86 | GGB | 0 | 0 | 2854 | 3600 | 2838.78 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 268785.66 | GGB | 268788.6 | 2838.78 | 2721.9249 |  |  |  | 0 | 1 | [14 empty] | 109.4869 | 2721.9249 |  | 104.98
25.06.2008 02:00 | 3600 | 2 | 763.9 | GGB | 763.37 | 775.945 | 768.132 | 265.84 | GGB | 10859.2 | GGB | 9.79 | GGB | 1008.08 | GGB | 60.58 | GGB | 173797.25 | GGB | 141544.19 | GGB | 0 | 0 | 2891 | 3600 | 2875.41 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 268824.32 | GGB | 268827.26 | 2875.41 | 2670.0354 |  |  |  | 0 | 1 | [14 empty] | 113.0549 | 2670.0354 |  | 104.98
25.06.2008 03:00 | 3600 | 2 | 764.31 | GGB | 763.37 | 775.781 | 768.132 | 267.28 | GGB | 10908.2 | GGB | 9.8 | GGB | 1008.53 | GGB | 60.48 | GGB | 174915.19 | GGB | 142560.1 | GGB | 0 | 0 | 2900 | 3600 | 2884.12 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 268862.98 | GGB | 268865.92 | 2884.12 | 2651.0082 |  |  |  | 0 | 1 | [14 empty] | 114.2112 | 2651.0082 |  | 104.98
25.06.2008 04:00 | 3600 | 2 | 764.3 | GGB | 763.37 | 775.523 | 768.132 | 266.61 | GGB | 10973 | GGB | 9.81 | GGB | 1008.72 | GGB | 60.95 | GGB | 173642.1 | GGB | 141349.75 | GGB | 0 | 0 | 2942 | 3600 | 2926.81 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 268901.64 | GGB | 268904.58 | 2926.81 | 2673.7083 |  |  |  | 0 | 1 | [14 empty] | 114.9177 | 2673.7083 |  | 104.98
25.06.2008 05:00 | 3600 | 2 | 763.28 | GGB | 764.469 | 776.789 | 768.498 | 268.22 | GGB | 10950.5 | GGB | 9.79 | GGB | 1008.34 | GGB | 60.38 | GGB | 175821.87 | GGB | 143316.23 | GGB | 0 | 0 | 2978 | 3600 | 2961.99 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 268940.3 | GGB | 268943.24 | 2961.99 | 2637.0216 |  |  |  | 1 | 1 |  |  |  |  | 143316.23 | 2637.0216 | 143316.23 | 2637.0216 | 9.7757 | [5 empty] | 117.917 | 2637.0216 |  | 104.98
25.06.2008 06:00 | 3600 | 2 | 763.98 | GGB | 764.469 | 775.734 | 769.597 | 268.76 | GGB | 10971.4 | GGB | 9.81 | GGB | 1008.57 | GGB | 60.05 | GGB | 176557.99 | GGB | 144090.83 | GGB | 0 | 0 | 2959 | 3600 | 2943.1 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 268978.95 | GGB | 268981.9 | 2943.1 | 2622.8456 |  |  |  | 1 | 1 |  |  |  |  | 144090.83 | 2622.8456 | 144090.83 | 2622.8456 | 9.7757 | [5 empty] | 117.7983 | 2622.8456 |  | 104.98
25.06.2008 07:00 | 3600 | 2 | 762.47 | GGB | 757.143 | 770.32 | 762.271 | 268.25 | GGB | 10918.2 | GGB | 9.77 | GGB | 1008.71 | GGB | 59.98 | GGB | 176125.56 | GGB | 143787.39 | GGB | 0 | 0 | 3032 | 3600 | 3016.7 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269017.61 | GGB | 269020.56 | 3016.7 | 2628.3807 |  |  |  | 0 | 1 | [14 empty] | 120.4898 | 2628.3807 |  | 104.98
25.06.2008 08:00 | 3600 | 2 | 767.18 | GGB | 765.934 | 778.477 | 769.597 | 265.58 | GGB | 10999.1 | GGB | 9.87 | GGB | 1008.99 | GGB | 61.12 | GGB | 171694.5 | GGB | 139731.44 | GGB | 0 | 0 | 2808 | 3600 | 2792.18 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269056.27 | GGB | 269059.22 | 2792.18 | 2704.6741 |  |  |  | 1 | 1 |  |  |  |  | 139731.44 | 2704.6741 | 139731.44 | 2704.6741 | 9.7757 | [5 empty] | 108.3765 | 2704.6741 |  | 104.98
25.06.2008 09:00 | 3600 | 2 | 764.73 | GGB | 764.835 | 777.539 | 769.597 | 266.6 | GGB | 10859.4 | GGB | 9.81 | GGB | 1009.5 | GGB | 61.03 | GGB | 172602.28 | GGB | 140578.08 | GGB | 0 | 0 | 2868 | 3600 | 2852.51 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269094.93 | GGB | 269097.88 | 2852.51 | 2688.385 |  |  |  | 1 | 1 |  |  |  |  | 140578.08 | 2688.385 | 140578.08 | 2688.385 | 9.7757 | [5 empty] | 111.389 | 2688.385 |  | 104.98
25.06.2008 10:00 | 3600 | 2 | 765.99 | GGB | 764.835 | 777.609 | 769.597 | 265.41 | GGB | 10816.3 | GGB | 9.82 | GGB | 1009.46 | GGB | 61.58 | GGB | 171682.4 | GGB | 139593.7 | GGB | 0 | 0 | 2774 | 3600 | 2758.61 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269133.59 | GGB | 269136.54 | 2758.61 | 2707.3428 |  |  |  | 1 | 1 |  |  |  |  | 139593.7 | 2707.3428 | 139593.7 | 2707.3428 | 9.7757 | [5 empty] | 106.9679 | 2707.3428 |  | 104.98
25.06.2008 11:00 | 3600 | 2 | 766.7 | GGB | 765.934 | 778.617 | 770.696 | 264.6 | GGB | 10767.8 | GGB | 9.81 | GGB | 1009.21 | GGB | 61.96 | GGB | 171026.6 | GGB | 138867.96 | GGB | 0 | 0 | 2722 | 3600 | 2706.73 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269172.25 | GGB | 269175.2 | 2706.73 | 2706.73 |  |  |  | 1 | 1 |  |  |  |  | 138867.96 | 2706.73 | 138867.96 | 2706.73 | 9.7227 | [5 empty] | 104.4106 |  |  | #VALUE!
25.06.2008 12:00 | 3600 | 2 | 767.29 | GGB | 765.934 | 778.477 | 770.696 | 263.4 | GGB | 10728.9 | GGB | 9.81 | GGB | 1008.88 | GGB | 62.15 | GGB | 170187.04 | GGB | 138063.7 | GGB | 0 | 0 | 2667 | 3600 | 2651.2 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269210.91 | GGB | 269213.86 | 2651.2 | 2651.2 |  |  |  | 1 | 1 |  |  |  |  | 138063.7 | 2651.2 | 138063.7 | 2651.2 | 9.468 | [5 empty] | 101.6762 |  |  | #VALUE!
25.06.2008 13:00 | 3600 | 2 | 767.67 | GGB | 767.033 | 779.883 | 770.696 | 262.53 | GGB | 10707.6 | GGB | 9.82 | GGB | 1008.89 | GGB | 62.52 | GGB | 169075.7 | GGB | 137013.44 | GGB | 0 | 0 | 2635 | 3600 | 2619.3 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269249.57 | GGB | 269252.52 | 2619.3 | 2619.3 |  |  |  | 0 | 1 | [14 empty] | 99.6887 |  |  | #VALUE!
25.06.2008 14:00 | 3600 | 2 | 767.88 | GGB | 768.132 | 780.164 | 773.26 | 261.36 | GGB | 10680.1 | GGB | 9.82 | GGB | 1008.56 | GGB | 62.71 | GGB | 168101.9 | GGB | 136103.01 | GGB | 0 | 0 | 2612 | 3600 | 2596.27 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269288.23 | GGB | 269291.18 | 2596.27 | 2596.27 |  |  |  | 0 | 1 | [14 empty] | 98.1556 |  |  | #VALUE!
25.06.2008 15:00 | 3600 | 2 | 767.73 | GGB | 767.033 | 780.07 | 773.26 | 259.14 | GGB | 10668.6 | GGB | 9.81 | GGB | 1008.16 | GGB | 63.51 | GGB | 166002.45 | GGB | 134027.11 | GGB | 0 | 0 | 2605 | 3600 | 2589.59 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269326.89 | GGB | 269329.84 | 2589.59 | 2589.59 |  |  |  | 0 | 1 | [14 empty] | 96.4098 |  |  | #VALUE!
25.06.2008 16:00 | 3600 | 2 | 767.54 | GGB | 767.033 | 779.297 | 771.795 | 260.4 | GGB | 10609.7 | GGB | 9.8 | GGB | 1008.02 | GGB | 63.07 | GGB | 167515.42 | GGB | 135407.84 | GGB | 0 | 0 | 2602 | 3600 | 2586.56 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269365.55 | GGB | 269368.5 | 2586.56 | 2586.56 |  |  |  | 0 | 1 | [14 empty] | 97.289 |  |  | #VALUE!
25.06.2008 17:00 | 3600 | 2 | 767.71 | GGB | 764.469 | 777 | 768.132 | 260.02 | GGB | 10587.4 | GGB | 9.8 | GGB | 1007.7 | GGB | 63.19 | GGB | 167208.43 | GGB | 135071.11 | GGB | 0 | 0 | 2570 | 3600 | 2554.37 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269404.21 | GGB | 269407.16 | 2554.37 | 2554.37 |  |  |  | 1 | 1 |  |  |  |  | 135071.11 | 2554.37 | 135071.11 | 2554.37 | 8.9245 | [5 empty] | 95.8393 |  |  | #VALUE!
25.06.2008 18:00 | 3600 | 2 | 769 | GGB | 768.132 | 780.469 | 773.26 | 259.65 | GGB | 10616.9 | GGB | 9.82 | GGB | 1007.52 | GGB | 63.42 | GGB | 166428.29 | GGB | 134324.32 | GGB | 0 | 0 | 2534 | 3600 | 2518.76 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269442.87 | GGB | 269445.82 | 2518.76 | 2518.76 |  |  |  | 0 | 1 | [14 empty] | 93.9808 |  |  | #VALUE!
25.06.2008 19:00 | 3600 | 2 | 767.64 | GGB | 761.172 | 773.273 | 765.934 | 258.59 | GGB | 10604.5 | GGB | 9.8 | GGB | 1007.12 | GGB | 64.06 | GGB | 165088.07 | GGB | 132937.25 | GGB | 0 | 0 | 2594 | 3600 | 2578.41 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269481.53 | GGB | 269484.48 | 2578.41 | 2578.41 |  |  |  | 0 | 1 | [14 empty] | 95.213 |  |  | #VALUE!
25.06.2008 20:00 | 3600 | 2 | 768.03 | GGB | 768.132 | 781.242 | 773.26 | 259.05 | GGB | 10634.9 | GGB | 9.81 | GGB | 1006.77 | GGB | 63.9 | GGB | 165506.2 | GGB | 133291.23 | GGB | 0 | 0 | 2611 | 3600 | 2595.2 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269520.19 | GGB | 269523.14 | 2595.2 | 2595.2 |  |  |  | 0 | 1 | [14 empty] | 96.0882 |  |  | #VALUE!
25.06.2008 21:00 | 3600 | 2 | 767.66 | GGB | 763.37 | 775.805 | 767.033 | 260.7 | GGB | 10619.2 | GGB | 9.79 | GGB | 1007 | GGB | 63.35 | GGB | 167187.52 | GGB | 134894.08 | GGB | 0 | 0 | 2605 | 3600 | 2589.67 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269558.85 | GGB | 269561.8 | 2589.67 | 2589.67 |  |  |  | 0 | 1 | [14 empty] | 97.0364 |  |  | #VALUE!
25.06.2008 22:00 | 3600 | 2 | 766.99 | GGB | 768.498 | 781.43 | 773.26 | 262.17 | GGB | 10647.7 | GGB | 9.8 | GGB | 1007.66 | GGB | 62.57 | GGB | 168675.18 | GGB | 136499.38 | GGB | 0 | 0 | 2670 | 3600 | 2654.95 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269597.51 | GGB | 269600.46 | 2654.95 | 2654.95 |  |  |  | 0 | 1 | [14 empty] | 100.6664 |  |  | #VALUE!
25.06.2008 23:00 | 3600 | 2 | 766.27 | GGB | 757.509 | 769.711 | 761.538 | 263.77 | GGB | 10693.1 | GGB | 9.78 | GGB | 1008.45 | GGB | 62.61 | GGB | 169537.84 | GGB | 137289.01 | GGB | 0 | 0 | 2741 | 3600 | 2725.61 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269636.17 | GGB | 269639.12 | 2725.61 | 2725.61 |  |  |  | 0 | 1 | [14 empty] | 103.9434 |  |  | #VALUE!
25.06.2008 24:00 | 3600 | 2 | 765.34 | GGB | 761.172 | 773.156 | 765.201 | 265.19 | GGB | 10838.8 | GGB | 9.8 | GGB | 1008.63 | GGB | 62.6 | GGB | 170292.67 | GGB | 137928.76 | GGB | 0 | 0 | 2888 | 3600 | 2872.57 | GGB | 100 | GGB | 38.66 | GGB | 38.66 | GGB | 269674.83 | GGB | 269677.78 | 2872.57 | 2740.0232 |  |  |  | 0 | 1 | [14 empty] | 110.0583 | 2740.0232 |  | 104.98
26.06.2008 01:00 | 3600 | 2 | 764.38 | GGB | 763.37 | 776.039 | 768.864 | 267.18 | GGB | 10895.4 | GGB | 9.79 | GGB | 1008.87 | GGB | 62.1 | GGB | 172308.49 | GGB | 139803.05 | GGB | 0 | 0 | 2973 | 3600 | 2957.64 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269714.69 | GGB | 269717.64 | 2957.64 | 2703.2887 |  |  |  | 0 | 1 | [14 empty] | 114.8575 | 2703.2887 |  | 104.98
26.06.2008 02:00 | 3600 | 2 | 764.26 | GGB | 771.795 | 783.68 | 776.923 | 269.24 | GGB | 10922.4 | GGB | 9.79 | GGB | 1009.34 | GGB | 61.34 | GGB | 174909.69 | GGB | 142304.19 | GGB | 0 | 0 | 2997 | 3600 | 2981.11 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269754.56 | GGB | 269757.5 | 2981.11 | 2655.7756 |  |  |  | 0 | 1 | [14 empty] | 117.8401 | 2655.7756 |  | 104.98
26.06.2008 03:00 | 3600 | 2 | 764.66 | GGB | 764.835 | 776.836 | 768.498 | 269.65 | GGB | 10926.9 | GGB | 9.8 | GGB | 1009.26 | GGB | 60.83 | GGB | 175410.34 | GGB | 142917.43 | GGB | 0 | 0 | 2954 | 3600 | 2938.69 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269794.42 | GGB | 269797.36 | 2938.69 | 2644.38 |  |  |  | 1 | 1 |  |  |  |  | 142917.43 | 2644.38 | 142917.43 | 2644.38 | 9.4814 | [5 empty] | 116.6639 | 2644.38 |  | 104.98
26.06.2008 04:00 | 3600 | 2 | 764.36 | GGB | 764.835 | 777.539 | 769.597 | 269.11 | GGB | 10924 | GGB | 9.81 | GGB | 1008.92 | GGB | 60.63 | GGB | 175129.76 | GGB | 142725.84 | GGB | 0 | 0 | 2955 | 3600 | 2938.98 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269834.28 | GGB | 269837.22 | 2938.98 | 2647.9298 |  |  |  | 1 | 1 |  |  |  |  | 142725.84 | 2647.9298 | 142725.84 | 2647.9298 | 9.4814 | [5 empty] | 116.519 | 2647.9298 |  | 104.98
26.06.2008 05:00 | 3600 | 2 | 765.13 | GGB | 763.37 | 775.406 | 768.132 | 267.09 | GGB | 10962.2 | GGB | 9.82 | GGB | 1007.78 | GGB | 61.26 | GGB | 172692.51 | GGB | 140318.16 | GGB | 0 | 0 | 2938 | 3600 | 2922.43 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269874.15 | GGB | 269877.08 | 2922.43 | 2693.3649 |  |  |  | 0 | 1 | [14 empty] | 113.9083 | 2693.3649 |  | 104.98
26.06.2008 06:00 | 3600 | 2 | 764.64 | GGB | 763.37 | 775.992 | 768.498 | 266.5 | GGB | 10934.4 | GGB | 9.81 | GGB | 1007.07 | GGB | 61.4 | GGB | 172158.84 | GGB | 139726.67 | GGB | 0 | 0 | 2955 | 3600 | 2938.97 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269914.01 | GGB | 269916.94 | 2938.97 | 2704.7664 |  |  |  | 0 | 1 | [14 empty] | 114.0701 | 2704.7664 |  | 104.98
26.06.2008 07:00 | 3600 | 2 | 764.65 | GGB | 765.934 | 776.813 | 769.597 | 267.57 | GGB | 10873.8 | GGB | 9.8 | GGB | 1007.33 | GGB | 60.96 | GGB | 173462.74 | GGB | 141006.05 | GGB | 0 | 0 | 2934 | 3600 | 2918.08 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269953.88 | GGB | 269956.8 | 2918.08 | 2680.2254 |  |  |  | 1 | 1 |  |  |  |  | 141006.05 | 2680.2254 | 141006.05 | 2680.2254 | 9.4814 | [5 empty] | 114.2964 | 2680.2254 |  | 104.98
26.06.2008 08:00 | 3600 | 2 | 765.41 | GGB | 764.469 | 776.555 | 769.597 | 266.69 | GGB | 10851.7 | GGB | 9.81 | GGB | 1007.5 | GGB | 61.06 | GGB | 172410.82 | GGB | 140132.7 | GGB | 0 | 0 | 2869 | 3600 | 2853.17 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 269993.74 | GGB | 269996.66 | 2853.17 | 2696.9294 |  |  |  | 1 | 1 |  |  |  |  | 140132.7 | 2696.9294 | 140132.7 | 2696.9294 | 9.4814 | [5 empty] | 111.0618 | 2696.9294 |  | 104.98
26.06.2008 09:00 | 3600 | 2 | 765.59 | GGB | 765.934 | 777.797 | 770.33 | 266.74 | GGB | 10821 | GGB | 9.81 | GGB | 1007.32 | GGB | 61.82 | GGB | 171611.98 | GGB | 139140.52 | GGB | 0 | 0 | 2866 | 3600 | 2850.68 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270033.61 | GGB | 270036.52 | 2850.68 | 2716.1606 |  |  |  | 1 | 1 |  |  |  |  | 139140.52 | 2716.1606 | 139140.52 | 2716.1606 | 9.4814 | [5 empty] | 110.1792 | 2716.1606 |  | 104.98
26.06.2008 10:00 | 3600 | 2 | 766.44 | GGB | 765.934 | 778.078 | 770.33 | 264.22 | GGB | 10794.6 | GGB | 9.82 | GGB | 1007.09 | GGB | 63.47 | GGB | 167964.36 | GGB | 135483.6 | GGB | 0 | 0 | 2825 | 3600 | 2809.57 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270073.47 | GGB | 270076.38 | 2809.57 | 2789.4742 |  |  |  | 1 | 1 |  |  |  |  | 135483.6 | 2789.4742 | 135483.6 | 2789.4742 | 9.4814 | [5 empty] | 105.7363 | 2789.4742 |  | 104.98
26.06.2008 11:00 | 3600 | 2 | 766.4 | GGB | 767.033 | 779.039 | 771.429 | 264.92 | GGB | 10701.1 | GGB | 9.81 | GGB | 1007.9 | GGB | 63.85 | GGB | 168429.8 | GGB | 135818.03 | GGB | 0 | 0 | 2788 | 3600 | 2772.64 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270113.33 | GGB | 270116.24 | 2772.64 | 2772.64 |  |  |  | 0 | 1 | [14 empty] | 104.604 |  |  | #VALUE!
26.06.2008 12:00 | 3600 | 2 | 767.45 | GGB | 765.934 | 778.195 | 769.963 | 263.87 | GGB | 10629.2 | GGB | 9.81 | GGB | 1006.9 | GGB | 64.34 | GGB | 167538.53 | GGB | 134768.06 | GGB | 0 | 0 | 2689 | 3600 | 2673.29 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270153.2 | GGB | 270156.1 | 2673.29 | 2673.29 |  |  |  | 1 | 1 |  |  |  |  | 134768.06 | 2673.29 | 134768.06 | 2673.29 | 9.0385 | [5 empty] | 100.0761 |  |  | #VALUE!
26.06.2008 13:00 | 3600 | 2 | 768.46 | GGB | 764.469 | 777.141 | 768.498 | 261.29 | GGB | 10616.8 | GGB | 9.82 | GGB | 1005.93 | GGB | 65.13 | GGB | 164969.24 | GGB | 132264.95 | GGB | 0 | 0 | 2631 | 3600 | 2615.76 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270193.06 | GGB | 270195.96 | 2615.76 | 2615.76 |  |  |  | 1 | 1 |  |  |  |  | 132264.95 | 2615.76 | 132264.95 | 2615.76 | 8.6797 | [5 empty] | 96.1037 |  |  | #VALUE!
26.06.2008 14:00 | 3600 | 2 | 768.26 | GGB | 765.934 | 779.414 | 770.696 | 259.1 | GGB | 10597.1 | GGB | 9.82 | GGB | 1005.3 | GGB | 65.32 | GGB | 163856.8 | GGB | 131214.51 | GGB | 0 | 0 | 2611 | 3600 | 2595.98 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270232.93 | GGB | 270235.82 | 2595.98 | 2595.98 |  |  |  | 0 | 1 | [14 empty] | 94.6195 |  |  | #VALUE!
26.06.2008 15:00 | 3600 | 2 | 767.78 | GGB | 764.835 | 777.281 | 769.597 | 258.57 | GGB | 10539.1 | GGB | 9.8 | GGB | 1005.47 | GGB | 65.05 | GGB | 164367.35 | GGB | 131752.45 | GGB | 0 | 0 | 2620 | 3600 | 2604.31 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270272.79 | GGB | 270275.68 | 2604.31 | 2604.31 |  |  |  | 1 | 1 |  |  |  |  | 131752.45 | 2604.31 | 131752.45 | 2604.31 | 8.6082 | [5 empty] | 95.3123 |  |  | #VALUE!
26.06.2008 16:00 | 3600 | 2 | 768.66 | GGB | 767.033 | 780.352 | 771.795 | 258.09 | GGB | 10530.6 | GGB | 9.82 | GGB | 1005.2 | GGB | 64.74 | GGB | 164578.62 | GGB | 132005.64 | GGB | 0 | 0 | 2552 | 3600 | 2537.01 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270312.65 | GGB | 270315.54 | 2537.01 | 2537.01 |  |  |  | 0 | 1 | [14 empty] | 93.0277 |  |  | #VALUE!
26.06.2008 17:00 | 3600 | 2 | 768.08 | GGB | 767.033 | 780.422 | 771.795 | 256.32 | GGB | 10526.7 | GGB | 9.81 | GGB | 1004.98 | GGB | 64.83 | GGB | 162879.7 | GGB | 130579.75 | GGB | 0 | 0 | 2562 | 3600 | 2547.15 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270352.52 | GGB | 270355.4 | 2547.15 | 2547.15 |  |  |  | 0 | 1 | [14 empty] | 92.3906 |  |  | #VALUE!
26.06.2008 18:00 | 3600 | 2 | 767.82 | GGB | 767.033 | 779.602 | 772.161 | 256.82 | GGB | 10475.4 | GGB | 9.79 | GGB | 1004.69 | GGB | 64.75 | GGB | 163638.93 | GGB | 131182.62 | GGB | 0 | 0 | 2540 | 3600 | 2524.62 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270392.38 | GGB | 270395.26 | 2524.62 | 2524.62 |  |  |  | 0 | 1 | [14 empty] | 91.9962 |  |  | #VALUE!
26.06.2008 19:00 | 3600 | 2 | 769.06 | GGB | 767.033 | 779.508 | 772.161 | 257.6 | GGB | 10502.8 | GGB | 9.81 | GGB | 1005.08 | GGB | 64.25 | GGB | 165006.65 | GGB | 132525.98 | GGB | 0 | 0 | 2486 | 3600 | 2470.61 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270432.25 | GGB | 270435.12 | 2470.61 | 2470.61 |  |  |  | 0 | 1 | [14 empty] | 90.95 |  |  | #VALUE!
26.06.2008 20:00 | 3600 | 2 | 768.22 | GGB | 765.934 | 778.664 | 771.795 | 257.14 | GGB | 10540.6 | GGB | 9.8 | GGB | 1005.68 | GGB | 64.19 | GGB | 164676.55 | GGB | 132363.37 | GGB | 0 | 0 | 2531 | 3600 | 2515.54 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270472.11 | GGB | 270474.98 | 2515.54 | 2515.54 |  |  |  | 1 | 1 |  |  |  |  | 132363.37 | 2515.54 | 132363.37 | 2515.54 | 8.3534 | [5 empty] | 92.4904 |  |  | #VALUE!
26.06.2008 21:00 | 3600 | 2 | 767.45 | GGB | 765.934 | 778.805 | 770.696 | 258.73 | GGB | 10570.2 | GGB | 9.79 | GGB | 1006.19 | GGB | 63.82 | GGB | 166242.33 | GGB | 133838.84 | GGB | 0 | 0 | 2581 | 3600 | 2566.13 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270511.98 | GGB | 270514.84 | 2566.13 | 2566.13 |  |  |  | 0 | 1 | [14 empty] | 95.4022 |  |  | #VALUE!
26.06.2008 22:00 | 3600 | 2 | 767.64 | GGB | 767.033 | 779.578 | 770.696 | 260.85 | GGB | 10669.6 | GGB | 9.8 | GGB | 1007.06 | GGB | 62.87 | GGB | 168288.96 | GGB | 135983.74 | GGB | 0 | 0 | 2609 | 3600 | 2593.3 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270551.84 | GGB | 270554.7 | 2593.3 | 2593.3 |  |  |  | 0 | 1 | [14 empty] | 97.9574 |  |  | #VALUE!
26.06.2008 23:00 | 3600 | 2 | 766.5 | GGB | 765.934 | 777.492 | 769.597 | 261.62 | GGB | 10749 | GGB | 9.79 | GGB | 1008.18 | GGB | 62.95 | GGB | 168725.79 | GGB | 136458.52 | GGB | 0 | 0 | 2724 | 3600 | 2708.44 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270591.7 | GGB | 270594.56 | 2708.44 | 2708.44 |  |  |  | 1 | 1 |  |  |  |  | 136458.52 | 2708.44 | 136458.52 | 2708.44 | 9.2722 | [5 empty] | 102.6638 |  |  | #VALUE!
26.06.2008 24:00 | 3600 | 2 | 766.39 | GGB | 764.835 | 777.375 | 769.597 | 262.74 | GGB | 10822.2 | GGB | 9.8 | GGB | 1009.12 | GGB | 62.37 | GGB | 170435.72 | GGB | 138209.42 | GGB | 0 | 0 | 2760 | 3600 | 2744.51 | GGB | 100 | GGB | 39.86 | GGB | 39.86 | GGB | 270631.57 | GGB | 270634.42 | 2744.51 | 2734.4591 |  |  |  | 1 | 1 |  |  |  |  | 138209.42 | 2734.4591 | 138209.42 | 2734.4591 | 9.4814 | [5 empty] | 105.3659 | 2734.4591 |  | 104.98
27.06.2008 01:00 | 3600 | 2 | 765.55 | GGB | 764.835 | 777.07 | 769.597 | 265.8 | GGB | 10824.3 | GGB | 9.79 | GGB | 1010 | GGB | 61.56 | GGB | 173239.38 | GGB | 140944.63 | GGB | 0 | 0 | 2827 | 3600 | 2811.73 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270670.64 | GGB | 270673.49 | 2811.73 | 2681.3934 |  |  |  | 1 | 1 |  |  |  |  | 140944.63 | 2681.3934 | 140944.63 | 2681.3934 | 9.6731 | [5 empty] | 110.0828 | 2681.3934 |  | 104.98
27.06.2008 02:00 | 3600 | 2 | 766.07 | GGB | 765.934 | 777.094 | 769.597 | 265.24 | GGB | 10901.1 | GGB | 9.81 | GGB | 1010.42 | GGB | 61.77 | GGB | 172463.64 | GGB | 140281.39 | GGB | 0 | 0 | 2838 | 3600 | 2822.59 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270709.71 | GGB | 270712.56 | 2822.59 | 2694.0708 |  |  |  | 1 | 1 |  |  |  |  | 140281.39 | 2694.0708 | 140281.39 | 2694.0708 | 9.6731 | [5 empty] | 109.988 | 2694.0708 |  | 104.98
27.06.2008 03:00 | 3600 | 2 | 765.09 | GGB | 763.37 | 776.133 | 768.498 | 265.8 | GGB | 10915.3 | GGB | 9.8 | GGB | 1010.68 | GGB | 61.67 | GGB | 173005 | GGB | 140804.47 | GGB | 0 | 0 | 2895 | 3600 | 2879.82 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270748.79 | GGB | 270751.63 | 2879.82 | 2684.0625 |  |  |  | 0 | 1 | [14 empty] | 112.6365 | 2684.0625 |  | 104.98
27.06.2008 04:00 | 3600 | 2 | 764.76 | GGB | 763.37 | 775.078 | 768.132 | 267.12 | GGB | 10949 | GGB | 9.8 | GGB | 1011.22 | GGB | 61.38 | GGB | 174029.42 | GGB | 141835.67 | GGB | 0 | 0 | 2954 | 3600 | 2938.6 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270787.86 | GGB | 270790.7 | 2938.6 | 2664.5483 |  |  |  | 0 | 1 | [14 empty] | 115.7773 | 2664.5483 |  | 104.98
27.06.2008 05:00 | 3600 | 2 | 765.14 | GGB | 763.37 | 775.336 | 767.033 | 267.41 | GGB | 10971.9 | GGB | 9.8 | GGB | 1011.23 | GGB | 61.29 | GGB | 174140.55 | GGB | 141966.12 | GGB | 0 | 0 | 2947 | 3600 | 2931.36 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270826.93 | GGB | 270829.77 | 2931.36 | 2662.0999 |  |  |  | 0 | 1 | [14 empty] | 115.5983 | 2662.0999 |  | 104.98
27.06.2008 06:00 | 3600 | 2 | 764.49 | GGB | 764.469 | 776.367 | 768.498 | 269.5 | GGB | 10956.6 | GGB | 9.79 | GGB | 1011.32 | GGB | 60.66 | GGB | 176709.84 | GGB | 144342.65 | GGB | 0 | 0 | 2969 | 3600 | 2953.84 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270866 | GGB | 270868.84 | 2953.84 | 2618.2698 |  |  |  | 1 | 1 |  |  |  |  | 144342.65 | 2618.2698 | 144342.65 | 2618.2698 | 9.6731 | [5 empty] | 118.4347 | 2618.2698 |  | 104.98
27.06.2008 07:00 | 3600 | 2 | 765.89 | GGB | 762.271 | 774.914 | 767.033 | 267.26 | GGB | 11007.4 | GGB | 9.83 | GGB | 1011.17 | GGB | 61.36 | GGB | 173929.29 | GGB | 141754.58 | GGB | 0 | 0 | 2920 | 3600 | 2904.41 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270905.07 | GGB | 270907.91 | 2904.41 | 2666.0726 |  |  |  | 0 | 1 | [14 empty] | 114.3648 | 2666.0726 |  | 104.98
27.06.2008 08:00 | 3600 | 2 | 766.43 | GGB | 764.835 | 776.813 | 769.597 | 265.15 | GGB | 10949.9 | GGB | 9.83 | GGB | 1011.08 | GGB | 61.86 | GGB | 171964.08 | GGB | 139930.49 | GGB | 0 | 0 | 2862 | 3600 | 2846.51 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270944.15 | GGB | 270946.98 | 2846.51 | 2700.8267 |  |  |  | 1 | 1 |  |  |  |  | 139930.49 | 2700.8267 | 139930.49 | 2700.8267 | 9.6731 | [5 empty] | 110.6426 | 2700.8267 |  | 104.98
27.06.2008 09:00 | 3600 | 2 | 766.79 | GGB | 765.934 | 777.773 | 769.597 | 263.13 | GGB | 10856.5 | GGB | 9.82 | GGB | 1010.67 | GGB | 62.47 | GGB | 170075.91 | GGB | 138085.77 | GGB | 0 | 0 | 2794 | 3207 | 2778.35 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 270983.22 | GGB | 270986.05 | 2471.8698 | 2471.8698 |  |  |  | 1 | 1 |  |  |  |  | 138085.77 | 2471.8698 | 138085.77 | 2471.8698 | 8.7364 |  | 2794 | -307 | 2487 | 2471.8698 | 94.8139 |  |  | #VALUE!
27.06.2008 10:00 | 3600 | 2 | 767.51 | GGB | 765.934 | 778.875 | 770.696 | 262.15 | GGB | 10728.9 | GGB | 9.82 | GGB | 1010 | GGB | 62.67 | GGB | 169672.08 | GGB | 137587.17 | GGB | 0 | 0 | 2671 | 3600 | 2655.8 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271022.29 | GGB | 271025.12 | 2348.9702 | 2348.9702 |  |  |  | 0 | 1 | [10 empty] | 2671 | -307 | 2364 | 2348.9702 | 89.7745 |  |  | #VALUE!
27.06.2008 11:00 | 3600 | 2 | 768.26 | GGB | 767.033 | 780.469 | 772.527 | 259.73 | GGB | 10683.4 | GGB | 9.82 | GGB | 1009.04 | GGB | 63.6 | GGB | 166668.16 | GGB | 134649.93 | GGB | 0 | 0 | 2614 | 3600 | 2599.12 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271061.36 | GGB | 271064.19 | 2292.0167 | 2292.0167 |  |  |  | 0 | 1 | [10 empty] | 2614 | -307 | 2307 | 2292.0167 | 85.7277 |  |  | #VALUE!
27.06.2008 12:00 | 3600 | 2 | 767.11 | GGB | 764.835 | 778.383 | 770.33 | 258.15 | GGB | 10635.4 | GGB | 9.81 | GGB | 1008.53 | GGB | 64.6 | GGB | 164859.2 | GGB | 132726.22 | GGB | 0 | 0 | 2626 | 3600 | 2610.17 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271100.44 | GGB | 271103.26 | 2304.0069 | 2304.0069 |  |  |  | 1 | 1 |  |  |  |  | 132726.22 | 2304.0069 | 132726.22 |  | 7.827 |  | 2626 | -307 | 2319 | 2304.0069 | 84.945 |  |  | #VALUE!
27.06.2008 13:00 | 3600 | 2 | 767.35 | GGB | 765.934 | 779.156 | 771.429 | 258.76 | GGB | 10570.5 | GGB | 9.81 | GGB | 1008.6 | GGB | 64.54 | GGB | 165743.88 | GGB | 133472.03 | GGB | 0 | 0 | 2574 | 3600 | 2558.36 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271139.51 | GGB | 271142.33 | 2252.0494 | 2252.0494 |  |  |  | 0 | 1 | [10 empty] | 2574 | -307 | 2267 | 2252.0494 | 83.496 |  |  | #VALUE!
27.06.2008 14:00 | 3600 | 2 | 768.04 | GGB | 765.934 | 779.273 | 771.429 | 257.31 | GGB | 10562.6 | GGB | 9.81 | GGB | 1008.82 | GGB | 64.99 | GGB | 163893.11 | GGB | 131832.38 | GGB | 0 | 0 | 2534 | 3600 | 2518.72 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271178.58 | GGB | 271181.4 | 2212.082 | 2212.082 |  |  |  | 0 | 1 | [10 empty] | 2534 | -307 | 2227 | 2212.082 | 81.0067 |  |  | #VALUE!
27.06.2008 15:00 | 3600 | 2 | 767.89 | GGB | 765.934 | 779.32 | 771.429 | 255.76 | GGB | 10532.9 | GGB | 9.8 | GGB | 1007.13 | GGB | 65.49 | GGB | 162452.77 | GGB | 130261.26 | GGB | 0 | 0 | 2532 | 3600 | 2516.64 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271217.65 | GGB | 271220.47 | 2210.0837 | 2210.0837 |  |  |  | 0 | 1 | [10 empty] | 2532 | -307 | 2225 | 2210.0837 | 79.969 |  |  | #VALUE!
27.06.2008 16:00 | 3600 | 2 | 768.18 | GGB | 765.934 | 779.109 | 771.429 | 254.83 | GGB | 10498.7 | GGB | 9.8 | GGB | 1006.07 | GGB | 65.75 | GGB | 161715.54 | GGB | 129433.41 | GGB | 0 | 0 | 2504 | 3600 | 2488.89 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271256.73 | GGB | 271259.54 | 2182.1065 | 2182.1065 |  |  |  | 0 | 1 | [10 empty] | 2504 | -307 | 2197 | 2182.1065 | 78.4549 |  |  | #VALUE!
27.06.2008 17:00 | 3600 | 2 | 768.56 | GGB | 768.132 | 780.211 | 772.527 | 254.49 | GGB | 10481.2 | GGB | 9.81 | GGB | 1005.08 | GGB | 65.9 | GGB | 161519.68 | GGB | 129092.14 | GGB | 0 | 0 | 2476 | 3600 | 2461.22 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271295.8 | GGB | 271298.61 | 2154.1294 | 2154.1294 |  |  |  | 0 | 1 | [10 empty] | 2476 | -307 | 2169 | 2154.1294 | 77.2448 |  |  | #VALUE!
27.06.2008 18:00 | 3600 | 2 | 768.49 | GGB | 765.934 | 779.156 | 771.429 | 254.13 | GGB | 10464 | GGB | 9.8 | GGB | 1004.31 | GGB | 66 | GGB | 161287.51 | GGB | 128771.61 | GGB | 0 | 0 | 2468 | 3600 | 2452.69 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271334.87 | GGB | 271337.68 | 2146.1359 | 2146.1359 |  |  |  | 0 | 1 | [10 empty] | 2468 | -307 | 2161 | 2146.1359 | 76.767 |  |  | #VALUE!
27.06.2008 19:00 | 3600 | 2 | 768.34 | GGB | 767.033 | 779.156 | 771.429 | 254.33 | GGB | 10470.8 | GGB | 9.8 | GGB | 1003.89 | GGB | 65.74 | GGB | 161394.24 | GGB | 128901.8 | GGB | 0 | 0 | 2476 | 3600 | 2461.06 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271373.94 | GGB | 271376.75 | 2154.1294 | 2154.1294 |  |  |  | 0 | 1 | [10 empty] | 2476 | -307 | 2169 | 2154.1294 | 77.1309 |  |  | #VALUE!
27.06.2008 20:00 | 3600 | 2 | 767.75 | GGB | 764.835 | 776.977 | 768.864 | 255.28 | GGB | 10468.5 | GGB | 9.79 | GGB | 1003.66 | GGB | 65.47 | GGB | 162398.85 | GGB | 129778.31 | GGB | 0 | 0 | 2498 | 3600 | 2482.91 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271413.01 | GGB | 271415.82 | 2176.1114 | 2176.1114 |  |  |  | 1 | 1 |  |  |  |  | 129778.31 | 2176.1114 | 129778.31 |  | 7.2284 |  | 2498 | -307 | 2191 | 2176.1114 | 78.4478 |  |  | #VALUE!
27.06.2008 21:00 | 3600 | 2 | 768.5 | GGB | 770.696 | 783.891 | 776.19 | 256.22 | GGB | 10475.2 | GGB | 9.81 | GGB | 1003.39 | GGB | 64.68 | GGB | 163413.36 | GGB | 130858.12 | GGB | 0 | 0 | 2479 | 3600 | 2463.33 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271452.09 | GGB | 271454.89 | 2157.1269 | 2157.1269 |  |  |  | 0 | 1 | [10 empty] | 2479 | -307 | 2172 | 2157.1269 | 78.4104 |  |  | #VALUE!
27.06.2008 22:00 | 3600 | 2 | 767.01 | GGB | 767.033 | 780.422 | 772.161 | 256.44 | GGB | 10504.3 | GGB | 9.79 | GGB | 1002.64 | GGB | 64.67 | GGB | 162920.41 | GGB | 130370.67 | GGB | 0 | 0 | 2565 | 3600 | 2549.32 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271491.16 | GGB | 271493.96 | 2243.0567 | 2243.0567 |  |  |  | 0 | 1 | [10 empty] | 2565 | -307 | 2258 | 2243.0567 | 81.2302 |  |  | #VALUE!
27.06.2008 23:00 | 3600 | 2 | 765.96 | GGB | 765.934 | 779.203 | 771.795 | 259.18 | GGB | 10588.4 | GGB | 9.79 | GGB | 1002.95 | GGB | 64.3 | GGB | 165559.02 | GGB | 132666.93 | GGB | 0 | 0 | 2687 | 3600 | 2671.52 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271530.23 | GGB | 271533.03 | 2364.9571 | 2364.9571 |  |  |  | 0 | 1 | [10 empty] | 2687 | -307 | 2380 | 2364.9571 | 87.1532 |  |  | #VALUE!
27.06.2008 24:00 | 3600 | 2 | 765.9 | GGB | 765.934 | 778.055 | 770.696 | 258.62 | GGB | 10653.9 | GGB | 9.8 | GGB | 1002.47 | GGB | 64.28 | GGB | 165581.03 | GGB | 132629.33 | GGB | 0 | 0 | 2709 | 3600 | 2693.21 | GGB | 100 | GGB | 39.07 | GGB | 39.07 | GGB | 271569.3 | GGB | 271572.1 | 2386.9392 | 2386.9392 |  |  |  | 1 | 1 |  |  |  |  | 132629.33 | 2386.9392 | 132629.33 | 2386.9392 | 8.1028 |  | 2709 | -307 | 2402 | 2386.9392 | 87.9384 |  |  | #VALUE!
28.06.2008 01:00 | 3600 | 2 | 765.95 | GGB | 763.37 | 775.758 | 767.033 | 259.27 | GGB | 10648.5 | GGB | 9.8 | GGB | 1001.88 | GGB | 63.99 | GGB | 165994.75 | GGB | 132999.52 | GGB | 0 | 0 | 2692 | 3600 | 2677.06 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271608.07 | GGB | 271610.86 | 2369.9531 | 2369.9531 |  |  |  | 0 | 1 | [10 empty] | 2692 | -307 | 2385 | 2369.9531 | 87.5563 |  |  | #VALUE!
28.06.2008 02:00 | 3600 | 2 | 766.68 | GGB | 765.934 | 777.844 | 769.597 | 259.44 | GGB | 10626.9 | GGB | 9.81 | GGB | 1002.36 | GGB | 63.47 | GGB | 166664.86 | GGB | 133806.18 | GGB | 0 | 0 | 2645 | 3600 | 2630.11 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271646.83 | GGB | 271649.62 | 2322.9914 | 2322.9914 |  |  |  | 1 | 1 |  |  |  |  | 133806.18 | 2322.9914 | 133806.18 | 2322.9914 | 8.0194 |  | 2645 | -307 | 2338 | 2322.9914 | 86.3418 |  |  | #VALUE!
28.06.2008 03:00 | 3600 | 2 | 765.42 | GGB | 763.37 | 775.664 | 768.132 | 259.69 | GGB | 10676.9 | GGB | 9.79 | GGB | 1001.94 | GGB | 63.71 | GGB | 166057.47 | GGB | 133167.75 | GGB | 0 | 0 | 2738 | 3600 | 2722.11 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271685.59 | GGB | 271688.38 | 2415.9155 | 2415.9155 |  |  |  | 0 | 1 | [10 empty] | 2738 | -307 | 2431 | 2415.9155 | 89.3672 |  |  | #VALUE!
28.06.2008 04:00 | 3600 | 2 | 765.72 | GGB | 764.835 | 777.797 | 769.597 | 260.57 | GGB | 10739.7 | GGB | 9.81 | GGB | 1001.74 | GGB | 63.16 | GGB | 167116 | GGB | 134208.43 | GGB | 0 | 0 | 2746 | 3600 | 2730.68 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271724.35 | GGB | 271727.14 | 2423.909 | 2423.909 |  |  |  | 1 | 1 |  |  |  |  | 134208.43 | 2423.909 | 134208.43 | 2423.909 | 8.3929 |  | 2746 | -307 | 2439 | 2423.909 | 90.3636 |  |  | #VALUE!
28.06.2008 05:00 | 3600 | 2 | 764.67 | GGB | 763.37 | 775.57 | 768.132 | 261.32 | GGB | 10767.1 | GGB | 9.79 | GGB | 1002.54 | GGB | 62.73 | GGB | 168008.37 | GGB | 135205.52 | GGB | 0 | 0 | 2820 | 3600 | 2804.06 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271763.11 | GGB | 271765.9 | 2497.8486 | 2497.8486 |  |  |  | 0 | 1 | [10 empty] | 2820 | -307 | 2513 | 2497.8486 | 93.8119 |  |  | #VALUE!
28.06.2008 06:00 | 3600 | 2 | 764.67 | GGB | 763.37 | 775.617 | 768.132 | 262.36 | GGB | 10792.8 | GGB | 9.8 | GGB | 1003.03 | GGB | 62.8 | GGB | 168599.25 | GGB | 135721.24 | GGB | 0 | 0 | 2841 | 3600 | 2825.01 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271801.87 | GGB | 271804.66 | 2518.8314 | 2518.8314 |  |  |  | 0 | 1 | [10 empty] | 2841 | -307 | 2534 | 2518.8314 | 94.9608 |  |  | #VALUE!
28.06.2008 07:00 | 3600 | 2 | 764.91 | GGB | 763.37 | 775.594 | 768.132 | 262.52 | GGB | 10802.5 | GGB | 9.8 | GGB | 1003.71 | GGB | 62.99 | GGB | 168851.23 | GGB | 135939.08 | GGB | 0 | 0 | 2842 | 3600 | 2826.87 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271840.64 | GGB | 271843.42 | 2519.8306 | 2519.8306 |  |  |  | 0 | 1 | [10 empty] | 2842 | -307 | 2535 | 2519.8306 | 95.151 |  |  | #VALUE!
28.06.2008 08:00 | 3600 | 2 | 765.06 | GGB | 764.835 | 776.438 | 768.498 | 263.84 | GGB | 10782 | GGB | 9.8 | GGB | 1004.02 | GGB | 62.6 | GGB | 170251.96 | GGB | 137265.48 | GGB | 0 | 0 | 2826 | 3600 | 2810.18 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271879.4 | GGB | 271882.18 | 2503.8437 | 2503.8437 |  |  |  | 1 | 1 |  |  |  |  | 137265.48 | 2503.8437 | 137265.48 | 2503.8437 | 8.8672 |  | 2826 | -307 | 2519 | 2503.8437 | 95.4698 |  |  | #VALUE!
28.06.2008 09:00 | 3600 | 2 | 765.68 | GGB | 763.37 | 776.461 | 768.498 | 262.98 | GGB | 10804.1 | GGB | 9.82 | GGB | 1004.43 | GGB | 62.8 | GGB | 169054.79 | GGB | 136275.54 | GGB | 0 | 0 | 2805 | 3600 | 2789.22 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271918.16 | GGB | 271920.94 | 2482.8608 | 2482.8608 |  |  |  | 0 | 1 | [10 empty] | 2805 | -307 | 2498 | 2482.8608 | 93.987 |  |  | #VALUE!
28.06.2008 10:00 | 3600 | 2 | 765.04 | GGB | 763.37 | 776.25 | 768.498 | 263.15 | GGB | 10788.3 | GGB | 9.8 | GGB | 1004.75 | GGB | 62.91 | GGB | 168913.95 | GGB | 136162.33 | GGB | 0 | 0 | 2851 | 3600 | 2835.7 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271956.92 | GGB | 271959.7 | 2528.8233 | 2528.8233 |  |  |  | 0 | 1 | [10 empty] | 2851 | -307 | 2544 | 2528.8233 | 95.6474 |  |  | #VALUE!
28.06.2008 11:00 | 3600 | 2 | 765.06 | GGB | 765.934 | 777.141 | 769.597 | 264.37 | GGB | 10761.3 | GGB | 9.81 | GGB | 1004.71 | GGB | 62.67 | GGB | 170348.79 | GGB | 137409.96 | GGB | 0 | 0 | 2815 | 3600 | 2799.52 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 271995.68 | GGB | 271998.46 | 2492.8527 | 2492.8527 |  |  |  | 1 | 1 |  |  |  |  | 137409.96 | 2492.8527 | 137409.96 | 2492.8527 | 8.8375 |  | 2815 | -307 | 2508 | 2492.8527 | 95.1508 |  |  | #VALUE!
28.06.2008 12:00 | 3600 | 2 | 766.94 | GGB | 764.835 | 777.984 | 769.597 | 261.73 | GGB | 10741.8 | GGB | 9.83 | GGB | 1004.6 | GGB | 63.6 | GGB | 167583.64 | GGB | 134790.09 | GGB | 0 | 0 | 2705 | 3600 | 2689.19 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272034.44 | GGB | 272037.22 | 2382.9424 | 2382.9424 |  |  |  | 1 | 1 |  |  |  |  | 134790.09 | 2382.9424 | 134790.09 | 2382.9424 | 8.2868 |  | 2705 | -307 | 2398 | 2382.9424 | 89.2214 |  |  | #VALUE!
28.06.2008 13:00 | 3600 | 2 | 766.34 | GGB | 764.835 | 777 | 768.498 | 259.35 | GGB | 10663.3 | GGB | 9.81 | GGB | 1003.65 | GGB | 64.37 | GGB | 165431.38 | GGB | 132632.32 | GGB | 0 | 0 | 2704 | 3600 | 2688.21 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272073.21 | GGB | 272075.98 | 2381.9433 | 2381.9433 |  |  |  | 1 | 1 |  |  |  |  | 132632.32 | 2381.9433 | 132632.32 | 2381.9433 | 8.1507 |  | 2704 | -307 | 2397 | 2381.9433 | 87.7563 |  |  | #VALUE!
28.06.2008 14:00 | 3600 | 2 | 766.11 | GGB | 764.469 | 777.023 | 769.597 | 259.23 | GGB | 10674.4 | GGB | 9.81 | GGB | 1003.69 | GGB | 64.05 | GGB | 165615.14 | GGB | 132908.39 | GGB | 0 | 0 | 2715 | 3600 | 2699.31 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272111.97 | GGB | 272114.74 | 2392.9343 | 2392.9343 |  |  |  | 1 | 1 |  |  |  |  | 132908.39 | 2392.9343 | 132908.39 | 2392.9343 | 8.2054 |  | 2715 | -307 | 2408 | 2392.9343 | 88.3447 |  |  | #VALUE!
28.06.2008 15:00 | 3600 | 2 | 766.63 | GGB | 764.835 | 776.977 | 769.597 | 258.78 | GGB | 10681.9 | GGB | 9.81 | GGB | 1004.07 | GGB | 64.02 | GGB | 165655.85 | GGB | 133007.73 | GGB | 0 | 0 | 2688 | 3600 | 2672.8 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272150.73 | GGB | 272153.5 | 2365.9563 | 2365.9563 |  |  |  | 1 | 1 |  |  |  |  | 133007.73 | 2365.9563 | 133007.73 | 2365.9563 | 8.1189 |  | 2688 | -307 | 2381 | 2365.9563 | 87.414 |  |  | #VALUE!
28.06.2008 16:00 | 3600 | 2 | 766.35 | GGB | 765.934 | 777.867 | 769.597 | 259.01 | GGB | 10704.2 | GGB | 9.82 | GGB | 1004.72 | GGB | 63.73 | GGB | 165982.65 | GGB | 133467.85 | GGB | 0 | 0 | 2724 | 3600 | 2709 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272189.49 | GGB | 272192.26 | 2401.9269 | 2401.9269 |  |  |  | 1 | 1 |  |  |  |  | 133467.85 | 2401.9269 | 133467.85 | 2401.9269 | 8.2709 |  | 2724 | -307 | 2417 | 2401.9269 | 89.05 |  |  | #VALUE!
28.06.2008 17:00 | 3600 | 2 | 766.73 | GGB | 765.934 | 777.891 | 770.696 | 256.96 | GGB | 10628.3 | GGB | 9.81 | GGB | 1004 | GGB | 64.4 | GGB | 164345.35 | GGB | 131795.63 | GGB | 0 | 0 | 2663 | 3600 | 2647.84 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272228.25 | GGB | 272231.02 | 2340.9767 | 2340.9767 |  |  |  | 1 | 1 |  |  |  |  | 131795.63 | 2340.9767 | 131795.63 | 2340.9767 | 7.96 |  | 2663 | -307 | 2356 | 2340.9767 | 85.7029 |  |  | #VALUE!
28.06.2008 18:00 | 3600 | 2 | 766.91 | GGB | 767.033 | 780 | 770.696 | 257.86 | GGB | 10575 | GGB | 9.81 | GGB | 1003.64 | GGB | 63.8 | GGB | 165900.12 | GGB | 133231.73 | GGB | 0 | 0 | 2615 | 3600 | 2599.9 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272267.01 | GGB | 272269.78 | 2293.0159 | 2293.0159 |  |  |  | 0 | 1 | [10 empty] | 2615 | -307 | 2308 | 2293.0159 | 84.8618 |  |  | #VALUE!
28.06.2008 19:00 | 3600 | 2 | 767.22 | GGB | 762.271 | 775.758 | 767.033 | 256.89 | GGB | 10589.8 | GGB | 9.8 | GGB | 1003.98 | GGB | 64.07 | GGB | 164940.63 | GGB | 132397.31 | GGB | 0 | 0 | 2602 | 3600 | 2586.6 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272305.78 | GGB | 272308.54 | 2280.0265 | 2280.0265 |  |  |  | 0 | 1 | [10 empty] | 2602 | -307 | 2295 | 2280.0265 | 83.8526 |  |  | #VALUE!
28.06.2008 20:00 | 3600 | 2 | 767.02 | GGB | 765.934 | 777.938 | 769.597 | 257.37 | GGB | 10626.8 | GGB | 9.8 | GGB | 1004.23 | GGB | 63.81 | GGB | 165649.25 | GGB | 133103.77 | GGB | 0 | 0 | 2618 | 3600 | 2602.83 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272344.54 | GGB | 272347.3 | 2296.0135 | 2296.0135 |  |  |  | 1 | 1 |  |  |  |  | 133103.77 | 2296.0135 | 133103.77 |  | 7.8846 |  | 2618 | -307 | 2311 | 2296.0135 | 84.8911 |  |  | #VALUE!
28.06.2008 21:00 | 3600 | 2 | 766.06 | GGB | 764.835 | 777.539 | 769.597 | 259.88 | GGB | 10633.6 | GGB | 9.79 | GGB | 1005.14 | GGB | 62.94 | GGB | 168488.12 | GGB | 135860.36 | GGB | 0 | 0 | 2653 | 3600 | 2637.88 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272383.3 | GGB | 272386.06 | 2330.9849 | 2330.9849 |  |  |  | 1 | 1 |  |  |  |  | 135860.36 | 2330.9849 | 135860.36 | 2330.9849 | 8.1705 |  | 2653 | -307 | 2346 | 2330.9849 | 87.969 |  |  | #VALUE!
28.06.2008 22:00 | 3600 | 2 | 766.41 | GGB | 764.469 | 777.656 | 768.498 | 260.49 | GGB | 10716 | GGB | 9.8 | GGB | 1005.7 | GGB | 62.6 | GGB | 168632.26 | GGB | 136189.47 | GGB | 0 | 0 | 2670 | 3600 | 2654.13 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272422.06 | GGB | 272424.82 | 2347.971 | 2347.971 |  |  |  | 1 | 1 |  |  |  |  | 136189.47 | 2347.971 | 136189.47 | 2347.971 | 8.25 |  | 2670 | -307 | 2363 | 2347.971 | 88.8247 |  |  | #VALUE!
28.06.2008 23:00 | 3600 | 2 | 765.79 | GGB | 764.835 | 777.352 | 769.597 | 261.29 | GGB | 10770.8 | GGB | 9.8 | GGB | 1006.59 | GGB | 62.68 | GGB | 168814.92 | GGB | 136425.83 | GGB | 0 | 0 | 2738 | 3600 | 2722.31 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272460.82 | GGB | 272463.58 | 2415.9155 | 2415.9155 |  |  |  | 1 | 1 |  |  |  |  | 136425.83 | 2415.9155 | 136425.83 | 2415.9155 | 8.5034 |  | 2738 | -307 | 2431 | 2415.9155 | 91.5537 |  |  | #VALUE!
28.06.2008 24:00 | 3600 | 2 | 765.45 | GGB | 763.37 | 776.039 | 768.132 | 261.5 | GGB | 10788.8 | GGB | 9.8 | GGB | 1007.05 | GGB | 62.58 | GGB | 169304.57 | GGB | 136922.22 | GGB | 0 | 0 | 2790 | 3600 | 2774.14 | GGB | 100 | GGB | 38.76 | GGB | 38.76 | GGB | 272499.58 | GGB | 272502.34 | 2467.8731 | 2467.8731 |  |  |  | 0 | 1 | [10 empty] | 2790 | -307 | 2483 | 2467.8731 | 93.863 |  |  | #VALUE!
29.06.2008 01:00 | 3600 | 2 | 766 | GGB | 763.37 | 776.414 | 768.498 | 261.57 | GGB | 10801.2 | GGB | 9.81 | GGB | 1007.24 | GGB | 62.52 | GGB | 169172.53 | GGB | 136866.3 | GGB | 0 | 0 | 2763 | 3600 | 2747.24 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272538.25 | GGB | 272541.01 | 2440.8951 | 2440.8951 |  |  |  | 0 | 1 | [10 empty] | 2763 | -307 | 2456 | 2440.8951 | 92.799 |  |  | #VALUE!
29.06.2008 02:00 | 3600 | 2 | 765.43 | GGB | 763.37 | 776.461 | 768.132 | 262.27 | GGB | 10824.1 | GGB | 9.8 | GGB | 1007.41 | GGB | 62.5 | GGB | 169489.43 | GGB | 137154.94 | GGB | 0 | 0 | 2804 | 3600 | 2788.8 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272576.93 | GGB | 272579.68 | 2481.8616 | 2481.8616 |  |  |  | 0 | 1 | [10 empty] | 2804 | -307 | 2497 | 2481.8616 | 94.5554 |  |  | #VALUE!
29.06.2008 03:00 | 3600 | 2 | 765.92 | GGB | 763.37 | 776.648 | 768.498 | 262.09 | GGB | 10832 | GGB | 9.81 | GGB | 1007.39 | GGB | 62.47 | GGB | 169341.98 | GGB | 137047.06 | GGB | 0 | 0 | 2787 | 3600 | 2771.27 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272615.6 | GGB | 272618.35 | 2464.8755 | 2464.8755 |  |  |  | 0 | 1 | [10 empty] | 2787 | -307 | 2480 | 2464.8755 | 93.8344 |  |  | #VALUE!
29.06.2008 04:00 | 3600 | 2 | 764.81 | GGB | 762.271 | 775.594 | 767.033 | 262.57 | GGB | 10845 | GGB | 9.8 | GGB | 1007.26 | GGB | 61.91 | GGB | 169773.31 | GGB | 137606.21 | GGB | 0 | 0 | 2859 | 3600 | 2843.3 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272654.27 | GGB | 272657.02 | 2536.8167 | 2536.8167 |  |  |  | 0 | 1 | [10 empty] | 2859 | -307 | 2552 | 2536.8167 | 96.9671 |  |  | #VALUE!
29.06.2008 05:00 | 3600 | 2 | 764.7 | GGB | 764.835 | 777.586 | 769.597 | 263.49 | GGB | 10875.7 | GGB | 9.8 | GGB | 1007.41 | GGB | 61.66 | GGB | 170267.36 | GGB | 138129.15 | GGB | 0 | 0 | 2886 | 3600 | 2870 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272692.94 | GGB | 272695.69 | 2563.7947 | 2563.7947 |  |  |  | 1 | 1 |  |  |  |  | 138129.15 | 2563.7947 | 138129.15 | 2563.7947 | 9.1579 |  | 2886 | -307 | 2579 | 2563.7947 | 98.3708 |  |  | #VALUE!
29.06.2008 06:00 | 3600 | 2 | 764.87 | GGB | 764.469 | 777.469 | 769.597 | 263.91 | GGB | 10888.9 | GGB | 9.81 | GGB | 1007.69 | GGB | 62.05 | GGB | 170476.43 | GGB | 138175.07 | GGB | 0 | 0 | 2883 | 3600 | 2867.79 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272731.61 | GGB | 272734.36 | 2560.7971 | 2560.7971 |  |  |  | 1 | 1 |  |  |  |  | 138175.07 | 2560.7971 | 138175.07 | 2560.7971 | 9.1502 |  | 2883 | -307 | 2576 | 2560.7971 | 98.2884 |  |  | #VALUE!
29.06.2008 07:00 | 3600 | 2 | 764.91 | GGB | 764.469 | 776.484 | 768.498 | 264 | GGB | 10885.4 | GGB | 9.81 | GGB | 1007.56 | GGB | 62.24 | GGB | 170770.22 | GGB | 138317.92 | GGB | 0 | 0 | 2886 | 3600 | 2870.49 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272770.28 | GGB | 272773.03 | 2563.7947 | 2563.7947 |  |  |  | 1 | 1 |  |  |  |  | 138317.92 | 2563.7947 | 138317.92 | 2563.7947 | 9.1704 |  | 2886 | -307 | 2579 | 2563.7947 | 98.5052 |  |  | #VALUE!
29.06.2008 08:00 | 3600 | 2 | 764.97 | GGB | 764.469 | 776.461 | 768.498 | 263.73 | GGB | 10886.6 | GGB | 9.81 | GGB | 1007.35 | GGB | 62.37 | GGB | 170593.06 | GGB | 138095.27 | GGB | 0 | 0 | 2884 | 3600 | 2868.27 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272808.95 | GGB | 272811.7 | 2561.7963 | 2561.7963 |  |  |  | 1 | 1 |  |  |  |  | 138095.27 | 2561.7963 | 138095.27 | 2561.7963 | 9.1485 |  | 2884 | -307 | 2577 | 2561.7963 | 98.27 |  |  | #VALUE!
29.06.2008 09:00 | 3600 | 2 | 764.98 | GGB | 764.469 | 776.32 | 768.132 | 263.79 | GGB | 10842.2 | GGB | 9.81 | GGB | 1007.39 | GGB | 62.46 | GGB | 170652.48 | GGB | 138111.56 | GGB | 0 | 0 | 2864 | 3600 | 2848.92 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272847.62 | GGB | 272850.37 | 2541.8127 | 2541.8127 |  |  |  | 1 | 1 |  |  |  |  | 138111.56 | 2541.8127 | 138111.56 | 2541.8127 | 9.0782 |  | 2864 | -307 | 2557 | 2541.8127 | 97.5149 |  |  | #VALUE!
29.06.2008 10:00 | 3600 | 2 | 766.27 | GGB | 765.934 | 778.336 | 769.597 | 263.63 | GGB | 10800.7 | GGB | 9.82 | GGB | 1007.29 | GGB | 62.26 | GGB | 170805.43 | GGB | 138301.03 | GGB | 0 | 0 | 2770 | 3600 | 2754.61 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272886.29 | GGB | 272889.04 | 2447.8894 | 2447.8894 |  |  |  | 1 | 1 |  |  |  |  | 138301.03 | 2447.8894 | 138301.03 | 2447.8894 | 8.7547 |  | 2770 | -307 | 2463 | 2447.8894 | 94.0405 |  |  | #VALUE!
29.06.2008 11:00 | 3600 | 2 | 766.33 | GGB | 764.469 | 776.156 | 769.597 | 262.22 | GGB | 10793.4 | GGB | 9.82 | GGB | 1007.05 | GGB | 62.84 | GGB | 169249.55 | GGB | 136774.08 | GGB | 0 | 0 | 2755 | 3600 | 2739.7 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272924.96 | GGB | 272927.71 | 2432.9016 | 2432.9016 |  |  |  | 1 | 1 |  |  |  |  | 136774.08 | 2432.9016 | 136774.08 | 2432.9016 | 8.6051 |  | 2755 | -307 | 2448 | 2432.9016 | 92.4327 |  |  | #VALUE!
29.06.2008 12:00 | 3600 | 2 | 766.4 | GGB | 767.033 | 779.063 | 770.696 | 260.46 | GGB | 10750.4 | GGB | 9.82 | GGB | 1006.57 | GGB | 63.61 | GGB | 167480.21 | GGB | 134968.74 | GGB | 0 | 0 | 2717 | 3600 | 2701.33 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 272963.63 | GGB | 272966.38 | 2394.9327 | 2394.9327 |  |  |  | 0 | 1 | [10 empty] | 2717 | -307 | 2410 | 2394.9327 | 89.7892 |  |  | #VALUE!
29.06.2008 13:00 | 3600 | 2 | 767.05 | GGB | 767.033 | 779.227 | 770.696 | 258.58 | GGB | 10679 | GGB | 9.81 | GGB | 1005.86 | GGB | 64.18 | GGB | 165928.73 | GGB | 133398.7 | GGB | 0 | 0 | 2647 | 3600 | 2631.6 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273002.3 | GGB | 273005.05 | 2324.9898 | 2324.9898 |  |  |  | 0 | 1 | [10 empty] | 2647 | -307 | 2340 | 2324.9898 | 86.1529 |  |  | #VALUE!
29.06.2008 14:00 | 3600 | 2 | 766.96 | GGB | 767.033 | 779.039 | 771.795 | 258.24 | GGB | 10656.7 | GGB | 9.81 | GGB | 1005.47 | GGB | 64.23 | GGB | 165782.39 | GGB | 133208.67 | GGB | 0 | 0 | 2646 | 3600 | 2630.55 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273040.97 | GGB | 273043.72 | 2323.9906 | 2323.9906 |  |  |  | 0 | 1 | [10 empty] | 2646 | -307 | 2339 | 2323.9906 | 85.9932 |  |  | #VALUE!
29.06.2008 15:00 | 3600 | 2 | 767.18 | GGB | 765.934 | 779.039 | 770.696 | 257.23 | GGB | 10629.5 | GGB | 9.81 | GGB | 1005.42 | GGB | 64.3 | GGB | 164950.53 | GGB | 132508.65 | GGB | 0 | 0 | 2617 | 3600 | 2601.24 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273079.64 | GGB | 273082.39 | 2295.0143 | 2295.0143 |  |  |  | 0 | 1 | [10 empty] | 2617 | -307 | 2310 | 2295.0143 | 84.4748 |  |  | #VALUE!
29.06.2008 16:00 | 3600 | 2 | 766.78 | GGB | 765.934 | 777.914 | 769.597 | 257.3 | GGB | 10628.3 | GGB | 9.8 | GGB | 1005.44 | GGB | 64.18 | GGB | 164957.13 | GGB | 132561.53 | GGB | 0 | 0 | 2636 | 3600 | 2620.48 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273118.31 | GGB | 273121.06 | 2313.9988 | 2313.9988 |  |  |  | 1 | 1 |  |  |  |  | 132561.53 | 2313.9988 | 132561.53 | 2313.9988 | 7.9324 |  | 2636 | -307 | 2329 | 2313.9988 | 85.2076 |  |  | #VALUE!
29.06.2008 17:00 | 3600 | 2 | 766.69 | GGB | 765.934 | 777.844 | 769.597 | 258.03 | GGB | 10649.1 | GGB | 9.8 | GGB | 1005.58 | GGB | 63.95 | GGB | 165186 | GGB | 132855.64 | GGB | 0 | 0 | 2662 | 3600 | 2647.02 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273156.98 | GGB | 273159.73 | 2339.9776 | 2339.9776 |  |  |  | 1 | 1 |  |  |  |  | 132855.64 | 2339.9776 | 132855.64 | 2339.9776 | 8.0393 |  | 2662 | -307 | 2355 | 2339.9776 | 86.3553 |  |  | #VALUE!
29.06.2008 18:00 | 3600 | 2 | 767.34 | GGB | 767.033 | 778.945 | 771.795 | 257.09 | GGB | 10622.5 | GGB | 9.81 | GGB | 1005.7 | GGB | 64.61 | GGB | 164261.72 | GGB | 131868.32 | GGB | 0 | 0 | 2617 | 3600 | 2601.59 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273195.65 | GGB | 273198.4 | 2295.0143 | 2295.0143 |  |  |  | 0 | 1 | [10 empty] | 2617 | -307 | 2310 | 2295.0143 | 84.0666 |  |  | #VALUE!
29.06.2008 19:00 | 3600 | 2 | 767.05 | GGB | 765.934 | 777.938 | 770.696 | 256.87 | GGB | 10600.5 | GGB | 9.8 | GGB | 1005.74 | GGB | 64.64 | GGB | 164081.27 | GGB | 131716.88 | GGB | 0 | 0 | 2619 | 3600 | 2603.73 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273234.32 | GGB | 273237.07 | 2297.0127 | 2297.0127 |  |  |  | 1 | 1 |  |  |  |  | 131716.88 | 2297.0127 | 131716.88 |  | 7.824 |  | 2619 | -307 | 2312 | 2297.0127 | 84.0431 |  |  | #VALUE!
29.06.2008 20:00 | 3600 | 2 | 766.93 | GGB | 764.835 | 778.172 | 769.597 | 257.73 | GGB | 10593.7 | GGB | 9.8 | GGB | 1006.13 | GGB | 64.5 | GGB | 164587.42 | GGB | 132227.68 | GGB | 0 | 0 | 2632 | 3600 | 2616.28 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273272.99 | GGB | 273275.74 | 2310.002 | 2310.002 |  |  |  | 1 | 1 |  |  |  |  | 132227.68 | 2310.002 | 132227.68 | 2310.002 | 7.8988 |  | 2632 | -307 | 2325 | 2310.002 | 84.8462 |  |  | #VALUE!
29.06.2008 21:00 | 3600 | 2 | 766.75 | GGB | 764.835 | 777.375 | 769.597 | 259.28 | GGB | 10601 | GGB | 9.8 | GGB | 1006.71 | GGB | 63.79 | GGB | 166233.53 | GGB | 133911.78 | GGB | 0 | 0 | 2640 | 3600 | 2624.28 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273311.66 | GGB | 273314.41 | 2317.9955 | 2317.9955 |  |  |  | 1 | 1 |  |  |  |  | 133911.78 | 2317.9955 | 133911.78 | 2317.9955 | 8.0271 |  | 2640 | -307 | 2333 | 2317.9955 | 86.2241 |  |  | #VALUE!
29.06.2008 22:00 | 3600 | 2 | 766.8 | GGB | 765.934 | 778.336 | 770.696 | 258.76 | GGB | 10652.6 | GGB | 9.81 | GGB | 1006.71 | GGB | 64.49 | GGB | 164859.2 | GGB | 132529.72 | GGB | 0 | 0 | 2671 | 3600 | 2655.54 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273350.33 | GGB | 273353.08 | 2348.9702 | 2348.9702 |  |  |  | 1 | 1 |  |  |  |  | 132529.72 | 2348.9702 | 132529.72 | 2348.9702 | 8.0504 |  | 2671 | -307 | 2364 | 2348.9702 | 86.4745 |  |  | #VALUE!
29.06.2008 23:00 | 3600 | 2 | 766.24 | GGB | 765.934 | 778.219 | 769.597 | 259.64 | GGB | 10674.9 | GGB | 9.8 | GGB | 1008.07 | GGB | 64.18 | GGB | 165482 | GGB | 133332.35 | GGB | 0 | 0 | 2714 | 3600 | 2698.47 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273389 | GGB | 273391.75 | 2391.9351 | 2391.9351 |  |  |  | 1 | 1 |  |  |  |  | 133332.35 | 2391.9351 | 133332.35 | 2391.9351 | 8.2473 |  | 2714 | -307 | 2407 | 2391.9351 | 88.5895 |  |  | #VALUE!
29.06.2008 24:00 | 3600 | 2 | 765.68 | GGB | 764.835 | 777 | 768.498 | 260.94 | GGB | 10723.2 | GGB | 9.8 | GGB | 1008.5 | GGB | 63.96 | GGB | 166664.86 | GGB | 134431.36 | GGB | 0 | 0 | 2771 | 3600 | 2755.31 | GGB | 100 | GGB | 38.67 | GGB | 38.67 | GGB | 273427.67 | GGB | 273430.42 | 2448.8886 | 2448.8886 |  |  |  | 1 | 1 |  |  |  |  | 134431.36 | 2448.8886 | 134431.36 | 2448.8886 | 8.5133 |  | 2771 | -307 | 2464 | 2448.8886 | 91.4465 |  |  | #VALUE!
30.06.2008 01:00 | 3600 | 2 | 765.39 | GGB | 763.37 | 776.016 | 768.132 | 260.74 | GGB | 10763.5 | GGB | 9.8 | GGB | 1008.51 | GGB | 63.53 | GGB | 167702.48 | GGB | 135439.31 | GGB | 0 | 0 | 2799 | 3600 | 2783.87 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273465.86 | GGB | 273468.61 | 2476.8657 | 2476.8657 |  |  |  | 0 | 1 | [10 empty] | 2799 | -307 | 2492 | 2476.8657 | 93.1847 |  |  | #VALUE!
30.06.2008 02:00 | 3600 | 2 | 765.46 | GGB | 764.835 | 777.164 | 768.498 | 262.3 | GGB | 10782.8 | GGB | 9.8 | GGB | 1009.1 | GGB | 63.43 | GGB | 167965.46 | GGB | 135772.6 | GGB | 0 | 0 | 2816 | 3600 | 2800.73 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273504.04 | GGB | 273506.8 | 2493.8518 | 2493.8518 |  |  |  | 1 | 1 |  |  |  |  | 135772.6 | 2493.8518 | 135772.6 | 2493.8518 | 8.8661 |  | 2816 | -307 | 2509 | 2493.8518 | 94.0547 |  |  | #VALUE!
30.06.2008 03:00 | 3600 | 2 | 765.25 | GGB | 764.469 | 776.016 | 768.498 | 263.25 | GGB | 10808.5 | GGB | 9.8 | GGB | 1009.34 | GGB | 63.27 | GGB | 168839.13 | GGB | 136574.26 | GGB | 0 | 0 | 2845 | 3600 | 2829.77 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273542.23 | GGB | 273544.99 | 2522.8282 | 2522.8282 |  |  |  | 1 | 1 |  |  |  |  | 136574.26 | 2522.8282 | 136574.26 | 2522.8282 | 9.0221 |  | 2845 | -307 | 2538 | 2522.8282 | 95.7093 |  |  | #VALUE!
30.06.2008 04:00 | 3600 | 2 | 765.25 | GGB | 764.835 | 776.039 | 768.498 | 263.66 | GGB | 10839 | GGB | 9.8 | GGB | 1009.52 | GGB | 63.03 | GGB | 169504.83 | GGB | 137239.42 | GGB | 0 | 0 | 2862 | 3600 | 2846.02 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273580.41 | GGB | 273583.18 | 2539.8143 | 2539.8143 |  |  |  | 1 | 1 |  |  |  |  | 137239.42 | 2539.8143 | 137239.42 | 2539.8143 | 9.1271 |  | 2862 | -307 | 2555 | 2539.8143 | 96.823 |  |  | #VALUE!
30.06.2008 05:00 | 3600 | 2 | 765.13 | GGB | 764.835 | 777.516 | 769.597 | 265.16 | GGB | 10837.1 | GGB | 9.8 | GGB | 1010.2 | GGB | 62.48 | GGB | 171372.1 | GGB | 139068.17 | GGB | 0 | 0 | 2869 | 3600 | 2853.78 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273618.6 | GGB | 273621.37 | 2546.8086 | 2546.8086 |  |  |  | 1 | 1 |  |  |  |  | 139068.17 | 2546.8086 | 139068.17 | 2546.8086 | 9.2742 |  | 2869 | -307 | 2562 | 2546.8086 | 98.3833 |  |  | #VALUE!
30.06.2008 06:00 | 3600 | 2 | 765.55 | GGB | 763.37 | 775.383 | 768.498 | 264.33 | GGB | 10879 | GGB | 9.81 | GGB | 1010.24 | GGB | 62.91 | GGB | 170232.15 | GGB | 137971.92 | GGB | 0 | 0 | 2867 | 3600 | 2851.27 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273656.78 | GGB | 273659.56 | 2544.8102 | 2544.8102 |  |  |  | 0 | 1 | [10 empty] | 2867 | -307 | 2560 | 2544.8102 | 97.5312 |  |  | #VALUE!
30.06.2008 07:00 | 3600 | 2 | 765.05 | GGB | 764.469 | 776.391 | 768.498 | 264.56 | GGB | 10886.7 | GGB | 9.8 | GGB | 1010.76 | GGB | 62.7 | GGB | 170775.72 | GGB | 138573.05 | GGB | 0 | 0 | 2899 | 3600 | 2883.41 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273694.97 | GGB | 273697.75 | 2576.7841 | 2576.7841 |  |  |  | 1 | 1 |  |  |  |  | 138573.05 | 2576.7841 | 138573.05 | 2576.7841 | 9.3499 |  | 2899 | -307 | 2592 | 2576.7841 | 99.1869 |  |  | #VALUE!
30.06.2008 08:00 | 3600 | 2 | 765.35 | GGB | 764.469 | 776.414 | 769.597 | 264.04 | GGB | 10891.9 | GGB | 9.81 | GGB | 1011.03 | GGB | 62.71 | GGB | 170267.36 | GGB | 138191.54 | GGB | 0 | 0 | 2882 | 3600 | 2866.48 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273733.15 | GGB | 273735.94 | 2559.798 | 2559.798 |  |  |  | 1 | 1 |  |  |  |  | 138191.54 | 2559.798 | 138191.54 | 2559.798 | 9.2627 |  | 2882 | -307 | 2575 | 2559.798 | 98.2618 |  |  | #VALUE!
30.06.2008 09:00 | 3600 | 2 | 765.17 | GGB | 765.934 | 777.727 | 770.696 | 264.77 | GGB | 10851.9 | GGB | 9.8 | GGB | 1011.23 | GGB | 62.5 | GGB | 171422.72 | GGB | 139243.36 | GGB | 0 | 0 | 2875 | 3600 | 2859.42 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273771.34 | GGB | 273774.13 | 2552.8037 | 2552.8037 |  |  |  | 1 | 1 |  |  |  |  | 139243.36 | 2552.8037 | 139243.36 | 2552.8037 | 9.3077 |  | 2875 | -307 | 2568 | 2552.8037 | 98.7392 |  |  | #VALUE!
30.06.2008 10:00 | 3600 | 2 | 766.79 | GGB | 767.033 | 778.641 | 771.795 | 263.82 | GGB | 10819.8 | GGB | 9.83 | GGB | 1011.21 | GGB | 62.88 | GGB | 170233.25 | GGB | 138117.51 | GGB | 0 | 0 | 2774 | 3600 | 2758.26 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273809.52 | GGB | 273812.32 | 2451.8861 | 2451.8861 |  |  |  | 1 | 1 |  |  |  |  | 138117.51 | 2451.8861 | 138117.51 | 2451.8861 | 8.8675 |  | 2774 | -307 | 2467 | 2451.8861 | 94.069 |  |  | #VALUE!
30.06.2008 11:00 | 3600 | 2 | 766.55 | GGB | 764.835 | 776.602 | 769.597 | 260.52 | GGB | 10752.2 | GGB | 9.82 | GGB | 1010.22 | GGB | 64.36 | GGB | 166714.37 | GGB | 134539.23 | GGB | 0 | 0 | 2730 | 3600 | 2714.43 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273847.7 | GGB | 273850.51 | 2407.922 | 2407.922 |  |  |  | 1 | 1 |  |  |  |  | 134539.23 | 2407.922 | 134539.23 | 2407.922 | 8.4828 |  | 2730 | -307 | 2423 | 2407.922 | 89.9889 |  |  | #VALUE!
30.06.2008 12:00 | 3600 | 2 | 767.04 | GGB | 767.033 | 780.094 | 772.161 | 259.41 | GGB | 10652.6 | GGB | 9.82 | GGB | 1008.9 | GGB | 64.61 | GGB | 165866.01 | GGB | 133581.72 | GGB | 0 | 0 | 2651 | 3600 | 2635.66 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273885.89 | GGB | 273888.7 | 2328.9865 | 2328.9865 |  |  |  | 0 | 1 | [10 empty] | 2651 | -307 | 2344 | 2328.9865 | 86.4195 |  |  | #VALUE!
30.06.2008 13:00 | 3600 | 2 | 767.25 | GGB | 765.934 | 778.969 | 770.696 | 258.4 | GGB | 10577.2 | GGB | 9.81 | GGB | 1008.13 | GGB | 64.73 | GGB | 165364.26 | GGB | 133026.83 | GGB | 0 | 0 | 2624 | 3312 | 2608.25 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273924.07 | GGB | 273926.89 | 2302.0086 | 2302.0086 |  |  |  | 0 | 1 | [10 empty] | 2624 | -307 | 2317 | 2302.0086 | 85.0636 |  |  | #VALUE!
30.06.2008 14:00 | 3600 | 2 | 768.19 | GGB | 768.132 | 780.094 | 773.26 | 255.68 | GGB | 10558.7 | GGB | 9.82 | GGB | 1007.41 | GGB | 65.28 | GGB | 162899.5 | GGB | 130740.04 | GGB | 0 | 0 | 2855 | 3600 | 2839.75 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 273962.26 | GGB | 273965.08 | 2532.82 | 2532.82 |  |  |  | 0 | 1 | [10 empty] | 2855 | -307 | 2548 | 2532.82 | 91.9836 |  |  | #VALUE!
30.06.2008 15:00 | 3600 | 2 | 767.71 | GGB | 767.033 | 780.07 | 771.795 | 255.53 | GGB | 10488.9 | GGB | 9.8 | GGB | 1007.24 | GGB | 65.39 | GGB | 162979.83 | GGB | 130736.82 | GGB | 0 | 0 | 2840 | 3600 | 2824.63 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274000.44 | GGB | 274003.27 | 2517.8322 | 2517.8322 |  |  |  | 0 | 1 | [10 empty] | 2840 | -307 | 2533 | 2517.8322 | 91.4371 |  |  | #VALUE!
30.06.2008 16:00 | 3600 | 2 | 768.33 | GGB | 767.033 | 779.203 | 771.795 | 255.16 | GGB | 10452 | GGB | 9.8 | GGB | 1006.39 | GGB | 65.57 | GGB | 162579.3 | GGB | 130237.16 | GGB | 0 | 0 | 2792 | 3600 | 2776.6 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274038.63 | GGB | 274041.46 | 2469.8714 | 2469.8714 |  |  |  | 0 | 1 | [10 empty] | 2792 | -307 | 2485 | 2469.8714 | 89.3525 |  |  | #VALUE!
30.06.2008 17:00 | 3600 | 2 | 768.58 | GGB | 767.033 | 779.297 | 771.795 | 253.25 | GGB | 10443.8 | GGB | 9.8 | GGB | 1004.51 | GGB | 66.34 | GGB | 160510.67 | GGB | 128050.46 | GGB | 0 | 0 | 2783 | 3600 | 2767.04 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274076.81 | GGB | 274079.65 | 2460.8788 | 2460.8788 |  |  |  | 0 | 1 | [10 empty] | 2783 | -307 | 2476 | 2460.8788 | 87.5324 |  |  | #VALUE!
30.06.2008 18:00 | 3600 | 2 | 768.23 | GGB | 767.033 | 779.227 | 771.429 | 253.65 | GGB | 10460.1 | GGB | 9.8 | GGB | 1004.58 | GGB | 66.17 | GGB | 160652.61 | GGB | 128237 | GGB | 0 | 0 | 2811 | 3600 | 2795.15 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274115 | GGB | 274117.84 | 2488.8559 | 2488.8559 |  |  |  | 0 | 1 | [10 empty] | 2811 | -307 | 2504 | 2488.8559 | 88.6565 |  |  | #VALUE!
30.06.2008 19:00 | 3600 | 2 | 766.89 | GGB | 763.37 | 776.086 | 767.766 | 254.76 | GGB | 10500.1 | GGB | 9.78 | GGB | 1004.86 | GGB | 65.17 | GGB | 161454.76 | GGB | 129291.29 | GGB | 0 | 0 | 2890 | 3600 | 2874.18 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274153.18 | GGB | 274156.03 | 2567.7914 | 2567.7914 |  |  |  | 0 | 1 | [10 empty] | 2890 | -307 | 2583 | 2567.7914 | 92.2203 |  |  | #VALUE!
30.06.2008 20:00 | 3600 | 2 | 764.37 | GGB | 760.806 | 772.359 | 764.469 | 260.72 | GGB | 10649.5 | GGB | 9.76 | GGB | 1006.48 | GGB | 63 | GGB | 167008.16 | GGB | 134820.36 | GGB | 0 | 0 | 3103 | 3600 | 3087.19 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274191.37 | GGB | 274194.22 | 2780.6176 | 2780.6176 |  |  |  | 0 | 1 | [10 empty] | 3103 | -307 | 2796 | 2780.6176 | 104.1344 |  |  | #VALUE!
30.06.2008 21:00 | 3600 | 2 | 766.65 | GGB | 773.26 | 785.531 | 776.923 | 262.01 | GGB | 10752.8 | GGB | 9.83 | GGB | 1007.6 | GGB | 63.41 | GGB | 167782.8 | GGB | 135432.65 | GGB | 0 | 0 | 3053 | 3600 | 3037.75 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274229.55 | GGB | 274232.41 | 2730.6584 | 2730.6584 |  |  |  | 0 | 1 | [10 empty] | 3053 | -307 | 2746 | 2730.6584 | 102.7279 |  |  | #VALUE!
30.06.2008 22:00 | 3600 | 2 | 764.89 | GGB | 761.172 | 772.828 | 764.835 | 260.65 | GGB | 10718 | GGB | 9.78 | GGB | 1007.33 | GGB | 63.94 | GGB | 166410.68 | GGB | 134077.43 | GGB | 0 | 0 | 3122 | 3600 | 3106.09 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274267.73 | GGB | 274270.6 | 2799.602 | 2799.602 |  |  |  | 0 | 1 | [10 empty] | 3122 | -307 | 2815 | 2799.602 | 104.2676 |  |  | #VALUE!
30.06.2008 23:00 | 3600 | 2 | 765.3 | GGB | 759.707 | 772.688 | 763.37 | 260.84 | GGB | 10743 | GGB | 9.8 | GGB | 1007.52 | GGB | 64.01 | GGB | 166470.1 | GGB | 134121.66 | GGB | 0 | 0 | 3121 | 3600 | 3104.92 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274305.92 | GGB | 274308.79 | 2798.6029 | 2798.6029 |  |  |  | 0 | 1 | [10 empty] | 3121 | -307 | 2814 | 2798.6029 | 104.2648 |  |  | #VALUE!
30.06.2008 24:00 | 3600 | 2 | 765.52 | GGB | 764.835 | 776.484 | 769.597 | 261.29 | GGB | 10792.4 | GGB | 9.8 | GGB | 1007.96 | GGB | 63.56 | GGB | 167599.04 | GGB | 135272.25 | GGB | 0 | 0 | 3121 | 3600 | 3105.17 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274344.1 | GGB | 274346.98 | 2798.6029 | 2793.8324 |  |  |  | 1 | 1 |  |  |  |  | 135272.25 | 2793.8324 | 135272.25 | 2793.8324 | 9.896 |  | 3121 | -307 | 2814 | 2798.6029 | 105.1593 | 2793.8324 |  | 104.98
01.07.2008 01:00 | 3600 | 2 | 764.27 | GGB | 765.934 | 777.539 | 769.597 | 264.3 | GGB | 10782.3 | GGB | 9.77 | GGB | 1008.62 | GGB | 62.36 | GGB | 170809.83 | GGB | 138449.1 | GGB | 0 | 0 | 3171 | 3600 | 3154.86 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274382.3 | GGB | 274385.17 | 2848.562 | 2729.7252 |  |  |  | 1 | 1 |  |  |  |  | 138449.1 | 2729.7252 | 138449.1 | 2729.7252 | 9.896 |  | 3171 | -307 | 2864 | 2848.562 | 109.5502 | 2729.7252 |  | 104.98
01.07.2008 02:00 | 3600 | 2 | 765.68 | GGB | 765.934 | 776.484 | 769.597 | 264.72 | GGB | 10833.1 | GGB | 9.8 | GGB | 1009.24 | GGB | 62.09 | GGB | 172092.82 | GGB | 139684.54 | GGB | 0 | 0 | 3099 | 3600 | 3083.22 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274420.49 | GGB | 274423.36 | 2776.6208 | 2705.5822 |  |  |  | 1 | 1 |  |  |  |  | 139684.54 | 2705.5822 | 139684.54 | 2705.5822 | 9.896 |  | 3099 | -307 | 2792 | 2776.6208 | 107.7364 | 2705.5822 |  | 104.98
01.07.2008 03:00 | 3600 | 2 | 765.06 | GGB | 763.37 | 775.383 | 768.132 | 264.03 | GGB | 10876.1 | GGB | 9.79 | GGB | 1009.41 | GGB | 62.79 | GGB | 170350.99 | GGB | 138007.05 | GGB | 0 | 0 | 3155 | 3600 | 3139.11 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274458.69 | GGB | 274461.55 | 2832.5751 | 2738.4688 |  |  |  | 0 | 1 | [10 empty] | 3155 | -307 | 2848 | 2832.5751 | 108.5876 | 2738.4688 |  | 104.98
01.07.2008 04:00 | 3600 | 2 | 765.22 | GGB | 764.469 | 775.57 | 768.132 | 264.31 | GGB | 10897.6 | GGB | 9.8 | GGB | 1009.58 | GGB | 62.52 | GGB | 171011.19 | GGB | 138678.16 | GGB | 0 | 0 | 3154 | 3600 | 3138.5 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274496.88 | GGB | 274499.74 | 2831.5759 | 2725.2164 |  |  |  | 1 | 1 |  |  |  |  | 138678.16 | 2725.2164 | 138678.16 | 2725.2164 | 9.896 |  | 3154 | -307 | 2847 | 2831.5759 | 109.0771 | 2725.2164 |  | 104.98
01.07.2008 05:00 | 3600 | 2 | 765.24 | GGB | 764.469 | 775.852 | 768.498 | 264.34 | GGB | 10899.6 | GGB | 9.8 | GGB | 1009.51 | GGB | 62.54 | GGB | 171276.37 | GGB | 138875.2 | GGB | 0 | 0 | 3166 | 3600 | 3150.49 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274535.08 | GGB | 274537.93 | 2843.5661 | 2721.3498 |  |  |  | 1 | 1 |  |  |  |  | 138875.2 | 2721.3498 | 138875.2 | 2721.3498 | 9.896 |  | 3166 | -307 | 2859 | 2843.5661 | 109.6947 | 2721.3498 |  | 104.98
01.07.2008 06:00 | 3600 | 2 | 765.41 | GGB | 764.835 | 776.813 | 768.498 | 264.02 | GGB | 10904.4 | GGB | 9.81 | GGB | 1009.68 | GGB | 62.6 | GGB | 170999.09 | GGB | 138648.72 | GGB | 0 | 0 | 3158 | 3600 | 3142.05 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274573.27 | GGB | 274576.12 | 2835.5727 | 2725.7951 |  |  |  | 1 | 1 |  |  |  |  | 138648.72 | 2725.7951 | 138648.72 | 2725.7951 | 9.896 |  | 3158 | -307 | 2851 | 2835.5727 | 109.2079 | 2725.7951 |  | 104.98
01.07.2008 07:00 | 3600 | 2 | 765.18 | GGB | 764.835 | 776.695 | 768.498 | 263.51 | GGB | 10887.1 | GGB | 9.81 | GGB | 1009.81 | GGB | 62.61 | GGB | 170628.27 | GGB | 138358.2 | GGB | 0 | 0 | 3164 | 3600 | 3147.79 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274611.46 | GGB | 274614.31 | 2841.5678 | 2731.5186 |  |  |  | 1 | 1 |  |  |  |  | 138358.2 | 2731.5186 | 138358.2 | 2731.5186 | 9.896 |  | 3164 | -307 | 2857 | 2841.5678 | 109.2095 | 2731.5186 |  | 104.98
01.07.2008 08:00 | 3600 | 2 | 765.32 | GGB | 764.469 | 776.859 | 769.597 | 263.17 | GGB | 10871.9 | GGB | 9.81 | GGB | 1009.91 | GGB | 62.61 | GGB | 169924.06 | GGB | 137802.63 | GGB | 0 | 0 | 3147 | 3600 | 3130.94 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274649.66 | GGB | 274652.5 | 2824.5816 | 2742.5311 |  |  |  | 1 | 1 |  |  |  |  | 137802.63 | 2742.5311 | 137802.63 | 2742.5311 | 9.896 |  | 3147 | -307 | 2840 | 2824.5816 | 108.1208 | 2742.5311 |  | 104.98
01.07.2008 09:00 | 3600 | 2 | 765.68 | GGB | 764.469 | 775.641 | 768.498 | 262.6 | GGB | 10848.1 | GGB | 9.81 | GGB | 1010.22 | GGB | 62.66 | GGB | 169472.92 | GGB | 137457.4 | GGB | 0 | 0 | 3123 | 3600 | 3106.95 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274687.85 | GGB | 274690.69 | 2800.6012 | 2749.4191 |  |  |  | 1 | 1 |  |  |  |  | 137457.4 | 2749.4191 | 137457.4 | 2749.4191 | 9.896 |  | 3123 | -307 | 2816 | 2800.6012 | 106.9343 | 2749.4191 |  | 104.98
01.07.2008 10:00 | 3600 | 2 | 766.4 | GGB | 765.934 | 777.867 | 770.696 | 261.81 | GGB | 10824.4 | GGB | 9.82 | GGB | 1010.25 | GGB | 63.28 | GGB | 168029.28 | GGB | 136039.49 | GGB | 0 | 0 | 3080 | 3600 | 3064.7 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274726.05 | GGB | 274728.88 | 2757.6363 | 2757.6363 |  |  |  | 1 | 1 |  |  |  |  | 136039.49 | 2757.6363 | 136039.49 | 2757.6363 | 9.8232 |  | 3080 | -307 | 2773 | 2757.6363 | 104.2076 |  |  | #VALUE!
01.07.2008 11:00 | 3600 | 2 | 767.11 | GGB | 767.033 | 779.953 | 770.696 | 259.94 | GGB | 10745.9 | GGB | 9.82 | GGB | 1009.8 | GGB | 64.06 | GGB | 166274.24 | GGB | 134247.69 | GGB | 0 | 0 | 3002 | 3600 | 2986.1 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274764.24 | GGB | 274767.07 | 2679.7 | 2679.7 |  |  |  | 0 | 1 | [10 empty] | 3002 | -307 | 2695 | 2679.7 | 99.9288 |  |  | #VALUE!
01.07.2008 12:00 | 3600 | 2 | 767.35 | GGB | 767.033 | 779.813 | 771.795 | 258.71 | GGB | 10668.3 | GGB | 9.81 | GGB | 1008.79 | GGB | 64.51 | GGB | 165071.57 | GGB | 132967.83 | GGB | 0 | 0 | 2955 | 3600 | 2939.49 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274802.44 | GGB | 274805.26 | 2632.7384 | 2632.7384 |  |  |  | 0 | 1 | [10 empty] | 2955 | -307 | 2648 | 2632.7384 | 97.2415 |  |  | #VALUE!
01.07.2008 13:00 | 3600 | 2 | 767.57 | GGB | 767.033 | 779.695 | 771.795 | 257.87 | GGB | 10631.7 | GGB | 9.8 | GGB | 1008.31 | GGB | 64.5 | GGB | 164803.09 | GGB | 132690.61 | GGB | 0 | 0 | 2911 | 3600 | 2895.72 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274840.63 | GGB | 274843.45 | 2588.7743 | 2588.7743 |  |  |  | 0 | 1 | [10 empty] | 2911 | -307 | 2604 | 2588.7743 | 95.4183 |  |  | #VALUE!
01.07.2008 14:00 | 3600 | 2 | 767.24 | GGB | 765.934 | 777.305 | 769.597 | 257.95 | GGB | 10638.3 | GGB | 9.8 | GGB | 1008.57 | GGB | 64.45 | GGB | 164958.23 | GGB | 132868.65 | GGB | 0 | 0 | 2935 | 3600 | 2919.32 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274878.83 | GGB | 274881.64 | 2612.7547 | 2612.7547 |  |  |  | 1 | 1 |  |  |  |  | 132868.65 | 2612.7547 | 132868.65 | 2612.7547 | 9.0902 |  | 2935 | -307 | 2628 | 2612.7547 | 96.4314 |  |  | #VALUE!
01.07.2008 15:00 | 3600 | 2 | 767.96 | GGB | 765.934 | 778.406 | 770.696 | 257.5 | GGB | 10621.8 | GGB | 9.81 | GGB | 1008.55 | GGB | 64.29 | GGB | 164814.09 | GGB | 132814.84 | GGB | 0 | 0 | 2888 | 3600 | 2871.98 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274917.02 | GGB | 274919.83 | 2565.7931 | 2565.7931 |  |  |  | 1 | 1 |  |  |  |  | 132814.84 | 2565.7931 | 132814.84 | 2565.7931 | 8.9232 |  | 2888 | -307 | 2581 | 2565.7931 | 94.6598 |  |  | #VALUE!
01.07.2008 16:00 | 3600 | 2 | 767.49 | GGB | 765.934 | 778.523 | 770.696 | 258.82 | GGB | 10589.8 | GGB | 9.8 | GGB | 1008.57 | GGB | 63.64 | GGB | 166410.68 | GGB | 134362.72 | GGB | 0 | 0 | 2898 | 3600 | 2882.86 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274955.21 | GGB | 274958.02 | 2575.7849 | 2575.7849 |  |  |  | 1 | 1 |  |  |  |  | 134362.72 | 2575.7849 | 134362.72 | 2575.7849 | 9.0623 |  | 2898 | -307 | 2591 | 2575.7849 | 96.136 |  |  | #VALUE!
01.07.2008 17:00 | 3600 | 2 | 767.85 | GGB | 767.033 | 779.719 | 770.696 | 256.87 | GGB | 10619.1 | GGB | 9.81 | GGB | 1008 | GGB | 64.34 | GGB | 164432.27 | GGB | 132413.61 | GGB | 0 | 0 | 2873 | 3600 | 2857 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 274993.41 | GGB | 274996.21 | 2550.8053 | 2550.8053 |  |  |  | 0 | 1 | [10 empty] | 2873 | -307 | 2566 | 2550.8053 | 93.8226 |  |  | #VALUE!
01.07.2008 18:00 | 3600 | 2 | 767.76 | GGB | 768.132 | 780.914 | 773.26 | 256.63 | GGB | 10614.4 | GGB | 9.8 | GGB | 1007.96 | GGB | 64.51 | GGB | 164317.84 | GGB | 132250.07 | GGB | 0 | 0 | 2874 | 3600 | 2858.22 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275031.6 | GGB | 275034.4 | 2551.8045 | 2551.8045 |  |  |  | 0 | 1 | [10 empty] | 2874 | -307 | 2567 | 2551.8045 | 93.7434 |  |  | #VALUE!
01.07.2008 19:00 | 3600 | 2 | 767.41 | GGB | 765.934 | 778.875 | 770.696 | 256.86 | GGB | 10614.7 | GGB | 9.8 | GGB | 1007.96 | GGB | 64.52 | GGB | 164324.44 | GGB | 132249.71 | GGB | 0 | 0 | 2903 | 3600 | 2887.13 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275069.8 | GGB | 275072.59 | 2580.7808 | 2580.7808 |  |  |  | 0 | 1 | [10 empty] | 2903 | -307 | 2596 | 2580.7808 | 94.8076 |  |  | #VALUE!
01.07.2008 20:00 | 3600 | 2 | 767.37 | GGB | 765.934 | 778.828 | 770.696 | 257.28 | GGB | 10623.9 | GGB | 9.8 | GGB | 1007.91 | GGB | 64.65 | GGB | 164345.35 | GGB | 132210.59 | GGB | 0 | 0 | 2910 | 3600 | 2894.77 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275107.99 | GGB | 275110.78 | 2587.7751 | 2587.7751 |  |  |  | 0 | 1 | [10 empty] | 2910 | -307 | 2603 | 2587.7751 | 95.0365 |  |  | #VALUE!
01.07.2008 21:00 | 3600 | 2 | 767.44 | GGB | 767.033 | 778.781 | 770.696 | 259.68 | GGB | 10603.9 | GGB | 9.79 | GGB | 1008.45 | GGB | 63.88 | GGB | 166812.3 | GGB | 134574.18 | GGB | 0 | 0 | 2905 | 3600 | 2889.43 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275146.19 | GGB | 275148.97 | 2582.7792 | 2582.7792 |  |  |  | 0 | 1 | [10 empty] | 2905 | -307 | 2598 | 2582.7792 | 96.5487 |  |  | #VALUE!
01.07.2008 22:00 | 3600 | 2 | 766.98 | GGB | 764.835 | 776.625 | 768.498 | 259.79 | GGB | 10675.2 | GGB | 9.79 | GGB | 1009.03 | GGB | 63.88 | GGB | 166307.25 | GGB | 134241.69 | GGB | 0 | 0 | 2951 | 3600 | 2935.77 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275184.38 | GGB | 275187.16 | 2628.7416 | 2628.7416 |  |  |  | 1 | 1 |  |  |  |  | 134241.69 | 2628.7416 | 134241.69 | 2628.7416 | 9.2403 |  | 2951 | -307 | 2644 | 2628.7416 | 98.0241 |  |  | #VALUE!
01.07.2008 23:00 | 3600 | 2 | 766.36 | GGB | 765.934 | 777.75 | 770.696 | 261 | GGB | 10738 | GGB | 9.79 | GGB | 1009.68 | GGB | 63.64 | GGB | 167112.7 | GGB | 135077.98 | GGB | 0 | 0 | 3025 | 3600 | 3009.08 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275222.58 | GGB | 275225.35 | 2702.6812 | 2702.6812 |  |  |  | 1 | 1 |  |  |  |  | 135077.98 | 2702.6812 | 135077.98 | 2702.6812 | 9.5594 |  | 3025 | -307 | 2718 | 2702.6812 | 101.4091 |  |  | #VALUE!
01.07.2008 24:00 | 3600 | 2 | 766.29 | GGB | 765.934 | 778.688 | 770.696 | 261.78 | GGB | 10777.5 | GGB | 9.8 | GGB | 1010.59 | GGB | 63.34 | GGB | 168385.79 | GGB | 136349.04 | GGB | 0 | 0 | 3035 | 3600 | 3019.48 | GGB | 100 | GGB | 38.19 | GGB | 38.19 | GGB | 275260.77 | GGB | 275263.54 | 2712.6731 | 2712.6731 |  |  |  | 1 | 1 |  |  |  |  | 136349.04 | 2712.6731 | 136349.04 | 2712.6731 | 9.685 |  | 3035 | -307 | 2728 | 2712.6731 | 102.7418 |  |  | #VALUE!
02.07.2008 01:00 | 3600 | 2 | 765.52 | GGB | 764.835 | 776.672 | 768.498 | 264.62 | GGB | 10762.7 | GGB | 9.78 | GGB | 1011.49 | GGB | 62.68 | GGB | 171070.61 | GGB | 138917.43 | GGB | 0 | 0 | 3093 | 3600 | 3077.31 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275299.21 | GGB | 275301.98 | 2770.6257 | 2720.5225 |  |  |  | 1 | 1 |  |  |  |  | 138917.43 | 2720.5225 | 138917.43 | 2720.5225 | 9.8316 |  | 3093 | -307 | 2786 | 2770.6257 | 106.9134 | 2720.5225 |  | 104.98
02.07.2008 02:00 | 3600 | 2 | 765.58 | GGB | 764.835 | 777.703 | 768.498 | 265.63 | GGB | 10818.3 | GGB | 9.8 | GGB | 1011.85 | GGB | 62.34 | GGB | 172079.62 | GGB | 139930.6 | GGB | 0 | 0 | 3097 | 3600 | 3081.21 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275337.66 | GGB | 275340.42 | 2774.6224 | 2700.8246 |  |  |  | 1 | 1 |  |  |  |  | 139930.6 | 2700.8246 | 139930.6 | 2700.8246 | 9.8316 |  | 3097 | -307 | 2790 | 2774.6224 | 107.8485 | 2700.8246 |  | 104.98
02.07.2008 03:00 | 3600 | 2 | 765.76 | GGB | 763.37 | 776.648 | 768.498 | 265.59 | GGB | 10881.9 | GGB | 9.8 | GGB | 1012.03 | GGB | 62.39 | GGB | 171859.55 | GGB | 139756.12 | GGB | 0 | 0 | 3123 | 3600 | 3107.45 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275376.1 | GGB | 275378.86 | 2800.6012 | 2704.1964 |  |  |  | 0 | 1 | [10 empty] | 3123 | -307 | 2816 | 2800.6012 | 108.7225 | 2704.1964 |  | 104.98
02.07.2008 04:00 | 3600 | 2 | 765.04 | GGB | 763.37 | 775.547 | 767.033 | 265.84 | GGB | 10894.7 | GGB | 9.79 | GGB | 1012.23 | GGB | 62.34 | GGB | 172207.26 | GGB | 140085.73 | GGB | 0 | 0 | 3168 | 3600 | 3152.28 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275414.54 | GGB | 275417.3 | 2845.5645 | 2697.8337 |  |  |  | 0 | 1 | [10 empty] | 3168 | -307 | 2861 | 2845.5645 | 110.7286 | 2697.8337 |  | 104.98
02.07.2008 05:00 | 3600 | 2 | 765.04 | GGB | 764.469 | 776.625 | 768.498 | 267.58 | GGB | 10905.4 | GGB | 9.8 | GGB | 1012.58 | GGB | 61.44 | GGB | 174708.33 | GGB | 142553.86 | GGB | 0 | 0 | 3182 | 3600 | 3166.43 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275452.99 | GGB | 275455.74 | 2859.5531 | 2651.1243 |  |  |  | 1 | 1 |  |  |  |  | 142553.86 | 2651.1243 | 142553.86 | 2651.1243 | 9.8316 |  | 3182 | -307 | 2875 | 2859.5531 | 113.2334 | 2651.1243 |  | 104.98
02.07.2008 06:00 | 3600 | 2 | 765.32 | GGB | 763.37 | 775.453 | 767.033 | 267.63 | GGB | 10920.5 | GGB | 9.8 | GGB | 1012.51 | GGB | 61.26 | GGB | 174829.36 | GGB | 142718.98 | GGB | 0 | 0 | 3169 | 3600 | 3152.88 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275491.43 | GGB | 275494.18 | 2846.5637 | 2648.057 |  |  |  | 0 | 1 | [10 empty] | 3169 | -307 | 2862 | 2846.5637 | 112.8496 | 2648.057 |  | 104.98
02.07.2008 07:00 | 3600 | 2 | 766.2 | GGB | 764.835 | 777.656 | 769.597 | 266.31 | GGB | 10957.8 | GGB | 9.83 | GGB | 1012.9 | GGB | 61.74 | GGB | 173071.02 | GGB | 141136 | GGB | 0 | 0 | 3143 | 3600 | 3127.29 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275529.88 | GGB | 275532.62 | 2820.5849 | 2677.7576 |  |  |  | 1 | 1 |  |  |  |  | 141136 | 2677.7576 | 141136 | 2677.7576 | 9.8316 |  | 3143 | -307 | 2836 | 2820.5849 | 110.5795 | 2677.7576 |  | 104.98
02.07.2008 08:00 | 3600 | 2 | 765.53 | GGB | 764.835 | 777.609 | 768.498 | 264.88 | GGB | 10928.8 | GGB | 9.81 | GGB | 1013.27 | GGB | 62.51 | GGB | 170897.86 | GGB | 139092.53 | GGB | 0 | 0 | 3174 | 3600 | 3157.69 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275568.32 | GGB | 275571.06 | 2851.5596 | 2717.0977 |  |  |  | 1 | 1 |  |  |  |  | 139092.53 | 2717.0977 | 139092.53 | 2717.0977 | 9.8316 |  | 3174 | -307 | 2867 | 2851.5596 | 110.1752 | 2717.0977 |  | 104.98
02.07.2008 09:00 | 3600 | 2 | 766.16 | GGB | 765.934 | 778.547 | 770.696 | 264.91 | GGB | 10860.5 | GGB | 9.81 | GGB | 1013.08 | GGB | 62.42 | GGB | 171176.24 | GGB | 139330.74 | GGB | 0 | 0 | 3107 | 3600 | 3091.53 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275606.76 | GGB | 275609.5 | 2784.6143 | 2712.4524 |  |  |  | 1 | 1 |  |  |  |  | 139330.74 | 2712.4524 | 139330.74 | 2712.4524 | 9.8316 |  | 3107 | -307 | 2800 | 2784.6143 | 107.7729 | 2712.4524 |  | 104.98
02.07.2008 10:00 | 3600 | 2 | 766.72 | GGB | 764.835 | 777.375 | 770.696 | 264.14 | GGB | 10804.6 | GGB | 9.81 | GGB | 1012.65 | GGB | 62.98 | GGB | 170331.18 | GGB | 138355.6 | GGB | 0 | 0 | 3069 | 2664 | 3053.5 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275645.21 | GGB | 275647.94 | 2746.6453 | 2731.57 |  |  |  | 1 | 1 |  |  |  |  | 138355.6 | 2731.57 | 138355.6 | 2731.57 | 9.8316 |  | 3069 | -307 | 2762 | 2746.6453 | 105.5594 | 2731.57 |  | 104.98
02.07.2008 11:00 | 3600 | 2 | 766.49 | GGB | 764.835 | 777.867 | 768.498 | 262.26 | GGB | 10799.4 | GGB | 9.81 | GGB | 1012.18 | GGB | 63.85 | GGB | 167909.34 | GGB | 135972.14 | GGB | 0 | 0 | 3076 | 3600 | 3060.22 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275683.65 | GGB | 275686.38 | 2753.6396 | 2753.6396 |  |  |  | 1 | 1 |  |  |  |  | 135972.14 | 2753.6396 | 135972.14 | 2753.6396 | 9.7403 |  | 3076 | -307 | 2769 | 2753.6396 | 104.0051 |  |  | #VALUE!
02.07.2008 12:00 | 3600 | 2 | 767.38 | GGB | 768.132 | 781.336 | 773.26 | 262.24 | GGB | 10732.1 | GGB | 9.82 | GGB | 1012.87 | GGB | 65.67 | GGB | 167468.1 | GGB | 134979.32 | GGB | 0 | 0 | 3009 | 2218 | 1281.65 | GNB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275722.09 | GGB | 275724.82 | 0 | 0 |  |  |  | 0 | 1 | [10 empty] | 3009 | -307 | 2702 | 2686.6943 | 0 |  |  | #VALUE!
02.07.2008 13:00 | 3600 | 2 | 767.76 | GGB | 767.033 | 779.063 | 771.795 | 261.59 | GGB | 10658.7 | GGB | 9.81 | GGB | 1011.45 | GGB | 64.15 | GGB | 168235.04 | GGB | 136016.68 | GGB | 0 | 0 | 2972 | 3600 | 2956.47 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275760.54 | GGB | 275763.26 | 2649.7245 | 2649.7245 |  |  |  | 0 | 1 | [10 empty] | 2972 | -307 | 2665 | 2649.7245 | 100.113 |  |  | #VALUE!
02.07.2008 14:00 | 3600 | 2 | 767.79 | GGB | 767.033 | 780.117 | 771.795 | 260.76 | GGB | 10637.1 | GGB | 9.81 | GGB | 1011.07 | GGB | 64.83 | GGB | 167213.93 | GGB | 134866.72 | GGB | 0 | 0 | 2949 | 3405 | 2933.38 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275798.98 | GGB | 275801.7 | 2626.7433 | 2626.7433 |  |  |  | 0 | 1 | [10 empty] | 2949 | -307 | 2642 | 2626.7433 | 98.4056 |  |  | #VALUE!
02.07.2008 15:00 | 3600 | 2 | 767.87 | GGB | 768.132 | 780.117 | 773.26 | 260.2 | GGB | 10607.1 | GGB | 9.81 | GGB | 1010.67 | GGB | 64.52 | GGB | 166767.19 | GGB | 134577.11 | GGB | 0 | 0 | 2917 | 3600 | 2901.45 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275837.43 | GGB | 275840.14 | 2594.7694 | 2594.7694 |  |  |  | 0 | 1 | [10 empty] | 2917 | -307 | 2610 | 2594.7694 | 96.999 |  |  | #VALUE!
02.07.2008 16:00 | 3600 | 2 | 768.54 | GGB | 767.033 | 780.211 | 772.161 | 259.27 | GGB | 10569.4 | GGB | 9.81 | GGB | 1009.94 | GGB | 64.69 | GGB | 165958.44 | GGB | 133761.42 | GGB | 0 | 0 | 2871 | 3600 | 2855.62 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275875.87 | GGB | 275878.58 | 2548.8069 | 2548.8069 |  |  |  | 0 | 1 | [10 empty] | 2871 | -307 | 2564 | 2548.8069 | 94.7033 |  |  | #VALUE!
02.07.2008 17:00 | 3600 | 2 | 768.86 | GGB | 767.033 | 780.211 | 772.161 | 258.08 | GGB | 10535.1 | GGB | 9.81 | GGB | 1009.34 | GGB | 64.91 | GGB | 165235.52 | GGB | 133011.52 | GGB | 0 | 0 | 2840 | 3600 | 2824.57 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275914.31 | GGB | 275917.02 | 2517.8322 | 2517.8322 |  |  |  | 0 | 1 | [10 empty] | 2840 | -307 | 2533 | 2517.8322 | 93.028 |  |  | #VALUE!
02.07.2008 18:00 | 3600 | 2 | 769.26 | GGB | 768.132 | 780.211 | 773.26 | 257.35 | GGB | 10521.9 | GGB | 9.81 | GGB | 1008.63 | GGB | 65.09 | GGB | 164671.05 | GGB | 132395.27 | GGB | 0 | 0 | 2823 | 3600 | 2807.16 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275952.76 | GGB | 275955.46 | 2500.8461 | 2500.8461 |  |  |  | 0 | 1 | [10 empty] | 2823 | -307 | 2516 | 2500.8461 | 91.9723 |  |  | #VALUE!
02.07.2008 19:00 | 3600 | 2 | 768.52 | GGB | 767.033 | 780.211 | 772.161 | 257.6 | GGB | 10510 | GGB | 9.8 | GGB | 1008.52 | GGB | 64.96 | GGB | 164660.04 | GGB | 132421.49 | GGB | 0 | 0 | 2843 | 3600 | 2827.36 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 275991.2 | GGB | 275993.9 | 2520.8298 | 2520.8298 |  |  |  | 0 | 1 | [10 empty] | 2843 | -307 | 2536 | 2520.8298 | 92.7256 |  |  | #VALUE!
02.07.2008 20:00 | 3600 | 2 | 768.73 | GGB | 767.033 | 779.836 | 771.795 | 256.06 | GGB | 10536.1 | GGB | 9.81 | GGB | 1007.88 | GGB | 65.66 | GGB | 162490.18 | GGB | 130322.88 | GGB | 0 | 0 | 2853 | 3600 | 2837.22 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 276029.64 | GGB | 276032.34 | 2530.8216 | 2530.8216 |  |  |  | 0 | 1 | [10 empty] | 2853 | -307 | 2546 | 2530.8216 | 91.6178 |  |  | #VALUE!
02.07.2008 21:00 | 3600 | 2 | 768.09 | GGB | 767.033 | 779.953 | 771.795 | 257.55 | GGB | 10504.3 | GGB | 9.8 | GGB | 1008.69 | GGB | 65.31 | GGB | 164197.9 | GGB | 131937.96 | GGB | 0 | 0 | 2871 | 3600 | 2854.99 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 276068.09 | GGB | 276070.78 | 2548.8069 | 2548.8069 |  |  |  | 0 | 1 | [10 empty] | 2871 | -307 | 2564 | 2548.8069 | 93.4123 |  |  | #VALUE!
02.07.2008 22:00 | 3600 | 2 | 768.02 | GGB | 767.033 | 780 | 772.161 | 258.8 | GGB | 10538.5 | GGB | 9.8 | GGB | 1009.02 | GGB | 64.9 | GGB | 165385.17 | GGB | 133093.03 | GGB | 0 | 0 | 2904 | 3600 | 2888.24 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 276106.53 | GGB | 276109.22 | 2581.78 | 2581.78 |  |  |  | 0 | 1 | [10 empty] | 2904 | -307 | 2597 | 2581.78 | 95.4491 |  |  | #VALUE!
02.07.2008 23:00 | 3600 | 2 | 767.37 | GGB | 764.835 | 777.797 | 769.597 | 258.35 | GGB | 10609 | GGB | 9.79 | GGB | 1008.82 | GGB | 65.08 | GGB | 164252.92 | GGB | 132085.79 | GGB | 0 | 0 | 2959 | 3600 | 2943.55 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 276144.97 | GGB | 276147.66 | 2636.7351 | 2636.7351 |  |  |  | 1 | 1 |  |  |  |  | 132085.79 | 2636.7351 | 132085.79 | 2636.7351 | 9.0602 |  | 2959 | -307 | 2652 | 2636.7351 | 96.7431 |  |  | #VALUE!
02.07.2008 24:00 | 3600 | 2 | 765.73 | GGB | 765.934 | 777.773 | 769.597 | 261.84 | GGB | 10706.6 | GGB | 9.78 | GGB | 1009.91 | GGB | 64.65 | GGB | 166892.63 | GGB | 134525.72 | GGB | 0 | 0 | 3105 | 3600 | 3089.45 | GGB | 100 | GGB | 38.44 | GGB | 38.44 | GGB | 276183.42 | GGB | 276186.1 | 2782.6159 | 2782.6159 |  |  |  | 1 | 1 |  |  |  |  | 134525.72 | 2782.6159 | 134525.72 | 2782.6159 | 9.7381 |  | 3105 | -307 | 2798 | 2782.6159 | 103.9815 |  |  | #VALUE!
03.07.2008 01:00 | 3600 | 2 | 765.55 | GGB | 763.37 | 776.531 | 768.498 | 265.17 | GGB | 10752.2 | GGB | 9.78 | GGB | 1010.9 | GGB | 63.51 | GGB | 170607.37 | GGB | 138121.63 | GGB | 0 | 0 | 3147 | 3600 | 3131.12 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276222.35 | GGB | 276225.03 | 2824.5816 | 2736.1971 |  |  |  | 0 | 1 | [10 empty] | 3147 | -307 | 2840 | 2824.5816 | 108.3711 | 2736.1971 |  | 104.98
03.07.2008 02:00 | 3600 | 2 | 765.93 | GGB | 765.934 | 777.563 | 769.597 | 266.31 | GGB | 10814.9 | GGB | 9.8 | GGB | 1011.32 | GGB | 63.09 | GGB | 172112.63 | GGB | 139570.11 | GGB | 0 | 0 | 3160 | 3600 | 3144 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276261.29 | GGB | 276263.96 | 2837.571 | 2707.8004 |  |  |  | 1 | 1 |  |  |  |  | 139570.11 | 2707.8004 | 139570.11 | 2707.8004 | 9.7079 |  | 3160 | -307 | 2853 | 2837.571 | 110.0111 | 2707.8004 |  | 104.98
03.07.2008 03:00 | 3600 | 2 | 766.52 | GGB | 764.469 | 776.156 | 768.498 | 263.8 | GGB | 10884.2 | GGB | 9.82 | GGB | 1011.19 | GGB | 63.07 | GGB | 170514.94 | GGB | 138268.76 | GGB | 0 | 0 | 3128 | 3600 | 3112.41 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276300.22 | GGB | 276302.89 | 2805.5971 | 2733.2855 |  |  |  | 1 | 1 |  |  |  |  | 138268.76 | 2733.2855 | 138268.76 | 2733.2855 | 9.7079 |  | 3128 | -307 | 2821 | 2805.5971 | 107.7573 | 2733.2855 |  | 104.98
03.07.2008 04:00 | 3600 | 2 | 765.18 | GGB | 764.469 | 776.18 | 768.132 | 264.96 | GGB | 10821.9 | GGB | 9.79 | GGB | 1011.23 | GGB | 62.77 | GGB | 171360 | GGB | 139080.4 | GGB | 0 | 0 | 3179 | 3600 | 3163.45 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276339.16 | GGB | 276341.82 | 2856.5555 | 2717.3347 |  |  |  | 1 | 1 |  |  |  |  | 139080.4 | 2717.3347 | 139080.4 | 2717.3347 | 9.7079 |  | 3179 | -307 | 2872 | 2856.5555 | 110.3586 | 2717.3347 |  | 104.98
03.07.2008 05:00 | 3600 | 2 | 765.64 | GGB | 764.469 | 776.344 | 768.498 | 266.38 | GGB | 10847.5 | GGB | 9.8 | GGB | 1011.48 | GGB | 62.36 | GGB | 172964.29 | GGB | 140588.88 | GGB | 0 | 0 | 3171 | 3600 | 3155.67 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276378.09 | GGB | 276380.75 | 2848.562 | 2688.1785 |  |  |  | 1 | 1 |  |  |  |  | 140588.88 | 2688.1785 | 140588.88 | 2688.1785 | 9.7079 |  | 3171 | -307 | 2864 | 2848.562 | 111.2434 | 2688.1785 |  | 104.98
03.07.2008 06:00 | 3600 | 2 | 765.85 | GGB | 764.835 | 776.531 | 769.597 | 265.76 | GGB | 10909.7 | GGB | 9.82 | GGB | 1011.26 | GGB | 62.65 | GGB | 171967.39 | GGB | 139627.37 | GGB | 0 | 0 | 3180 | 3600 | 3164 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276417.03 | GGB | 276419.68 | 2857.5547 | 2706.69 |  |  |  | 1 | 1 |  |  |  |  | 139627.37 | 2706.69 | 139627.37 | 2706.69 | 9.7079 |  | 3180 | -307 | 2873 | 2857.5547 | 110.8313 | 2706.69 |  | 104.98
03.07.2008 07:00 | 3600 | 2 | 766.23 | GGB | 763.37 | 776.648 | 768.498 | 264.68 | GGB | 10872.5 | GGB | 9.82 | GGB | 1011.12 | GGB | 62.86 | GGB | 171044.2 | GGB | 138774.81 | GGB | 0 | 0 | 3160 | 3600 | 3144.16 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276455.96 | GGB | 276458.61 | 2837.571 | 2723.3184 |  |  |  | 0 | 1 | [10 empty] | 3160 | -307 | 2853 | 2837.571 | 109.3843 | 2723.3184 |  | 104.98
03.07.2008 08:00 | 3600 | 2 | 766.56 | GGB | 765.934 | 777.75 | 769.597 | 264.93 | GGB | 10831.2 | GGB | 9.82 | GGB | 1011.08 | GGB | 62.28 | GGB | 171203.75 | GGB | 139137.23 | GGB | 0 | 0 | 3116 | 3600 | 3099.87 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276494.89 | GGB | 276497.54 | 2793.6069 | 2716.2248 |  |  |  | 1 | 1 |  |  |  |  | 139137.23 | 2716.2248 | 139137.23 | 2716.2248 | 9.7079 |  | 3116 | -307 | 2809 | 2793.6069 | 107.9708 | 2716.2248 |  | 104.98
03.07.2008 09:00 | 3600 | 2 | 767.18 | GGB | 765.934 | 777.891 | 770.696 | 262.67 | GGB | 10803.8 | GGB | 9.83 | GGB | 1010.86 | GGB | 63.29 | GGB | 168367.08 | GGB | 136390.4 | GGB | 0 | 0 | 3072 | 3600 | 3056.6 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276533.83 | GGB | 276536.47 | 2749.6429 | 2749.6429 |  |  |  | 1 | 1 |  |  |  |  | 136390.4 | 2749.6429 | 136390.4 | 2749.6429 | 9.6333 |  | 3072 | -307 | 2765 | 2749.6429 | 104.1736 |  |  | #VALUE!
03.07.2008 10:00 | 3600 | 2 | 766.82 | GGB | 765.934 | 779.086 | 770.696 | 261.35 | GGB | 10687.6 | GGB | 9.81 | GGB | 1010.37 | GGB | 64.14 | GGB | 166921.24 | GGB | 134812.09 | GGB | 0 | 0 | 3042 | 3600 | 3026.07 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276572.76 | GGB | 276575.4 | 2719.6673 | 2719.6673 |  |  |  | 0 | 1 | [10 empty] | 3042 | -307 | 2735 | 2719.6673 | 101.8456 |  |  | #VALUE!
03.07.2008 11:00 | 3600 | 2 | 767.87 | GGB | 765.934 | 779.016 | 770.696 | 259.67 | GGB | 10645.4 | GGB | 9.82 | GGB | 1009.41 | GGB | 64.6 | GGB | 165322.45 | GGB | 133216.73 | GGB | 0 | 0 | 2962 | 3600 | 2946.35 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276611.7 | GGB | 276614.33 | 2639.7327 | 2639.7327 |  |  |  | 0 | 1 | [10 empty] | 2962 | -307 | 2655 | 2639.7327 | 97.6824 |  |  | #VALUE!
03.07.2008 12:00 | 3600 | 2 | 768.25 | GGB | 768.498 | 781.477 | 772.161 | 259.7 | GGB | 10573.8 | GGB | 9.81 | GGB | 1008.28 | GGB | 64.51 | GGB | 166067.37 | GGB | 133700.05 | GGB | 0 | 0 | 2910 | 3600 | 2894.77 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276650.63 | GGB | 276653.26 | 2587.7751 | 2587.7751 |  |  |  | 0 | 1 | [10 empty] | 2910 | -307 | 2603 | 2587.7751 | 96.1071 |  |  | #VALUE!
03.07.2008 13:00 | 3600 | 2 | 768.53 | GGB | 765.934 | 778.523 | 770.696 | 258.46 | GGB | 10541.5 | GGB | 9.81 | GGB | 1007.3 | GGB | 64.8 | GGB | 165006.65 | GGB | 132601.97 | GGB | 0 | 0 | 2869 | 3600 | 2853.3 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276689.57 | GGB | 276692.19 | 2546.8086 | 2546.8086 |  |  |  | 1 | 1 |  |  |  |  | 132601.97 | 2546.8086 | 132601.97 | 2546.8086 | 8.6748 |  | 2869 | -307 | 2562 | 2546.8086 | 93.8088 |  |  | #VALUE!
03.07.2008 14:00 | 3600 | 2 | 768.46 | GGB | 765.934 | 778.594 | 769.597 | 256.21 | GGB | 10540.9 | GGB | 9.81 | GGB | 1006.32 | GGB | 65.53 | GGB | 162593.61 | GGB | 130254.66 | GGB | 0 | 0 | 2875 | 3600 | 2859.48 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276728.5 | GGB | 276731.12 | 2552.8037 | 2552.8037 |  |  |  | 1 | 1 |  |  |  |  | 130254.66 | 2552.8037 | 130254.66 | 2552.8037 | 8.5413 |  | 2875 | -307 | 2568 | 2552.8037 | 92.3652 |  |  | #VALUE!
03.07.2008 15:00 | 3600 | 2 | 768.59 | GGB | 768.132 | 780.773 | 773.26 | 257.01 | GGB | 10490 | GGB | 9.8 | GGB | 1006.27 | GGB | 65.36 | GGB | 163576.21 | GGB | 131103.47 | GGB | 0 | 0 | 2850 | 3600 | 2834.72 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276767.44 | GGB | 276770.05 | 2527.8241 | 2527.8241 |  |  |  | 0 | 1 | [10 empty] | 2850 | -307 | 2543 | 2527.8241 | 92.0574 |  |  | #VALUE!
03.07.2008 16:00 | 3600 | 2 | 768.99 | GGB | 768.132 | 780.703 | 773.26 | 256.39 | GGB | 10470 | GGB | 9.81 | GGB | 1005.54 | GGB | 65.39 | GGB | 163231.8 | GGB | 130720.55 | GGB | 0 | 0 | 2810 | 3600 | 2794.66 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276806.37 | GGB | 276808.98 | 2487.8567 | 2487.8567 |  |  |  | 0 | 1 | [10 empty] | 2810 | -307 | 2503 | 2487.8567 | 90.3372 |  |  | #VALUE!
03.07.2008 17:00 | 3600 | 2 | 768.38 | GGB | 768.132 | 780.656 | 773.26 | 255.46 | GGB | 10493.4 | GGB | 9.8 | GGB | 1004.73 | GGB | 65.74 | GGB | 162044.54 | GGB | 129531.75 | GGB | 0 | 0 | 2845 | 3600 | 2829.72 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276845.3 | GGB | 276847.91 | 2522.8282 | 2522.8282 |  |  |  | 0 | 1 | [10 empty] | 2845 | -307 | 2538 | 2522.8282 | 90.774 |  |  | #VALUE!
03.07.2008 18:00 | 3600 | 2 | 768.24 | GGB | 768.132 | 780.633 | 772.527 | 256.32 | GGB | 10491.5 | GGB | 9.8 | GGB | 1004.45 | GGB | 65.53 | GGB | 162535.29 | GGB | 129967.5 | GGB | 0 | 0 | 2861 | 3600 | 2845.1 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276884.24 | GGB | 276886.84 | 2538.8151 | 2538.8151 |  |  |  | 0 | 1 | [10 empty] | 2861 | -307 | 2554 | 2538.8151 | 91.6565 |  |  | #VALUE!
03.07.2008 19:00 | 3600 | 2 | 768.52 | GGB | 765.934 | 779.367 | 771.429 | 257.87 | GGB | 10479.4 | GGB | 9.8 | GGB | 1004.08 | GGB | 65.26 | GGB | 164273.82 | GGB | 131414.24 | GGB | 0 | 0 | 2868 | 3600 | 2852.84 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276923.17 | GGB | 276925.77 | 2545.8094 | 2545.8094 |  |  |  | 0 | 1 | [10 empty] | 2868 | -307 | 2561 | 2545.8094 | 92.9321 |  |  | #VALUE!
03.07.2008 20:00 | 3600 | 2 | 768.24 | GGB | 765.934 | 779.555 | 770.33 | 256.51 | GGB | 10534.7 | GGB | 9.81 | GGB | 1003.71 | GGB | 65.59 | GGB | 162567.2 | GGB | 129874.62 | GGB | 0 | 0 | 2883 | 3600 | 2867.71 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 276962.11 | GGB | 276964.7 | 2560.7971 | 2560.7971 |  |  |  | 0 | 1 | [10 empty] | 2883 | -307 | 2576 | 2560.7971 | 92.384 |  |  | #VALUE!
03.07.2008 21:00 | 3600 | 2 | 767.57 | GGB | 767.033 | 780.656 | 772.527 | 258.66 | GGB | 10518.6 | GGB | 9.79 | GGB | 1003.53 | GGB | 64.77 | GGB | 164810.79 | GGB | 131960.37 | GGB | 0 | 0 | 2916 | 3600 | 2900.12 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 277001.04 | GGB | 277003.63 | 2593.7702 | 2593.7702 |  |  |  | 0 | 1 | [10 empty] | 2916 | -307 | 2609 | 2593.7702 | 95.0764 |  |  | #VALUE!
03.07.2008 22:00 | 3600 | 2 | 767.16 | GGB | 765.934 | 779.297 | 770.33 | 259.26 | GGB | 10562 | GGB | 9.79 | GGB | 1003.5 | GGB | 64.7 | GGB | 165320.25 | GGB | 132393.86 | GGB | 0 | 0 | 2955 | 3600 | 2939.52 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 277039.98 | GGB | 277042.56 | 2632.7384 | 2632.7384 |  |  |  | 0 | 1 | [10 empty] | 2955 | -307 | 2648 | 2632.7384 | 96.8218 |  |  | #VALUE!
03.07.2008 23:00 | 3600 | 2 | 767.05 | GGB | 763.37 | 776.063 | 767.766 | 258.38 | GGB | 10571.5 | GGB | 9.8 | GGB | 1003.68 | GGB | 64.78 | GGB | 165257.53 | GGB | 132336.11 | GGB | 0 | 0 | 2957 | 3600 | 2941.08 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 277078.91 | GGB | 277081.49 | 2634.7367 | 2634.7367 |  |  |  | 0 | 1 | [10 empty] | 2957 | -307 | 2650 | 2634.7367 | 96.853 |  |  | #VALUE!
03.07.2008 24:00 | 3600 | 2 | 766.74 | GGB | 764.835 | 777.516 | 768.864 | 260.69 | GGB | 10513.2 | GGB | 9.8 | GGB | 1004.17 | GGB | 63.47 | GGB | 167457.1 | GGB | 134684.95 | GGB | 0 | 0 | 2968 | 3600 | 2952.44 | GGB | 100 | GGB | 38.93 | GGB | 38.93 | GGB | 277117.85 | GGB | 277120.42 | 2645.7278 | 2645.7278 |  |  |  | 1 | 1 |  |  |  |  | 134684.95 | 2645.7278 | 134684.95 | 2645.7278 | 9.1533 |  | 2968 | -307 | 2661 | 2645.7278 | 98.9833 |  |  | #VALUE!
04.07.2008 01:00 | 3600 | 2 | 766.89 | GGB | 764.835 | 778.57 | 770.33 | 261.4 | GGB | 10544.8 | GGB | 9.8 | GGB | 1004.52 | GGB | 63.3 | GGB | 168582.75 | GGB | 135705.91 | GGB | 0 | 0 | 2986 | 3600 | 2970.3 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277156.09 | GGB | 277158.66 | 2663.7131 | 2663.7131 |  |  |  | 1 | 1 |  |  |  |  | 135705.91 | 2663.7131 | 135705.91 | 2663.7131 | 9.453 |  | 2986 | -307 | 2679 | 2663.7131 | 100.4116 |  |  | #VALUE!
04.07.2008 02:00 | 3600 | 2 | 766.76 | GGB | 765.934 | 778.383 | 769.963 | 260.33 | GGB | 10510.3 | GGB | 9.81 | GGB | 1004.57 | GGB | 62.88 | GGB | 167780.6 | GGB | 135234.38 | GGB | 0 | 0 | 2937 | 3600 | 2921.03 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277194.33 | GGB | 277196.9 | 2614.7531 | 2614.7531 |  |  |  | 1 | 1 |  |  |  |  | 135234.38 | 2614.7531 | 135234.38 | 2614.7531 | 9.247 |  | 2937 | -307 | 2630 | 2614.7531 | 98.2235 |  |  | #VALUE!
04.07.2008 03:00 | 3600 | 2 | 765.42 | GGB | 763.37 | 775.383 | 766.667 | 260.7 | GGB | 10528.9 | GGB | 9.79 | GGB | 1004.05 | GGB | 62.84 | GGB | 168033.68 | GGB | 135385.67 | GGB | 0 | 0 | 3016 | 3600 | 3000.05 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277232.57 | GGB | 277235.14 | 2693.6886 | 2693.6886 |  |  |  | 0 | 1 | [10 empty] | 3016 | -307 | 2709 | 2693.6886 | 101.3019 |  |  | #VALUE!
04.07.2008 04:00 | 3600 | 2 | 765.62 | GGB | 764.835 | 777.563 | 768.864 | 263.13 | GGB | 10556.5 | GGB | 9.8 | GGB | 1003.93 | GGB | 61.97 | GGB | 170868.15 | GGB | 138011.68 | GGB | 0 | 0 | 3032 | 3600 | 3016.37 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277270.81 | GGB | 277273.38 | 2709.6755 | 2709.6755 |  |  |  | 1 | 1 |  |  |  |  | 138011.68 | 2709.6755 | 138011.68 | 2709.6755 | 9.7795 |  | 3032 | -307 | 2725 | 2709.6755 | 103.8797 |  |  | #VALUE!
04.07.2008 05:00 | 3600 | 2 | 765.67 | GGB | 765.934 | 777.68 | 769.963 | 262.09 | GGB | 10580.9 | GGB | 9.81 | GGB | 1003.09 | GGB | 62.13 | GGB | 169899.85 | GGB | 137050.09 | GGB | 0 | 0 | 3035 | 3600 | 3019.01 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277309.05 | GGB | 277311.62 | 2712.6731 | 2712.6731 |  |  |  | 1 | 1 |  |  |  |  | 137050.09 | 2712.6731 | 137050.09 | 2712.6731 | 9.7221 |  | 3035 | -307 | 2728 | 2712.6731 | 103.27 |  |  | #VALUE!
04.07.2008 06:00 | 3600 | 2 | 764.86 | GGB | 763.37 | 776.508 | 768.132 | 262.3 | GGB | 10588.5 | GGB | 9.79 | GGB | 1003.19 | GGB | 62.22 | GGB | 169732.6 | GGB | 136891.02 | GGB | 0 | 0 | 3079 | 3600 | 3063.32 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277347.29 | GGB | 277349.86 | 2756.6371 | 2756.6371 |  |  |  | 0 | 1 | [10 empty] | 3079 | -307 | 2772 | 2756.6371 | 104.8219 |  |  | #VALUE!
04.07.2008 07:00 | 3600 | 2 | 765.63 | GGB | 764.835 | 777.586 | 769.597 | 264.17 | GGB | 10600.3 | GGB | 9.81 | GGB | 1003.44 | GGB | 61.56 | GGB | 171938.78 | GGB | 138979.56 | GGB | 0 | 0 | 3050 | 3600 | 3034.37 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277385.53 | GGB | 277388.1 | 2727.6608 | 2719.3063 |  |  |  | 1 | 1 |  |  |  |  | 138979.56 | 2719.3063 | 138979.56 | 2719.3063 | 9.8831 |  | 3050 | -307 | 2743 | 2727.6608 | 105.3025 | 2719.3063 |  | 104.98
04.07.2008 08:00 | 3600 | 2 | 765.85 | GGB | 764.835 | 777.539 | 769.597 | 263.54 | GGB | 10573.9 | GGB | 9.81 | GGB | 1003.25 | GGB | 61.85 | GGB | 171198.25 | GGB | 138232.81 | GGB | 0 | 0 | 3028 | 3600 | 3012.65 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277423.78 | GGB | 277426.34 | 2705.6788 | 2705.6788 |  |  |  | 1 | 1 |  |  |  |  | 138232.81 | 2705.6788 | 138232.81 | 2705.6788 | 9.7807 |  | 3028 | -307 | 2721 | 2705.6788 | 103.8927 |  |  | #VALUE!
04.07.2008 09:00 | 3600 | 2 | 767.45 | GGB | 767.033 | 779.719 | 771.795 | 260.58 | GGB | 10540 | GGB | 9.83 | GGB | 1002.82 | GGB | 62.69 | GGB | 167967.66 | GGB | 135224.94 | GGB | 0 | 0 | 2826 | 3207 | 2810.46 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277462.02 | GGB | 277464.58 | 2471.8698 | 2471.8698 |  |  |  | 0 | 1 | [10 empty] | 2826 | -339 | 2487 | 2471.8698 | 92.8496 |  |  | #VALUE!
04.07.2008 10:00 | 3600 | 2 | 767.38 | GGB | 765.934 | 778.664 | 770.696 | 256.96 | GGB | 10465.8 | GGB | 9.82 | GGB | 1002.08 | GGB | 64.03 | GGB | 164419.07 | GGB | 131748.85 | GGB | 0 | 0 | 2621 | 3600 | 2605.55 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277500.26 | GGB | 277502.82 | 2267.0371 | 2267.0371 |  |  |  | 1 | 1 |  |  |  |  | 131748.85 | 2267.0371 | 131748.85 |  | 7.8107 |  | 2621 | -339 | 2282 | 2267.0371 | 82.9665 |  |  | #VALUE!
04.07.2008 11:00 | 3600 | 2 | 767.55 | GGB | 765.934 | 778.711 | 770.696 | 257.14 | GGB | 10386.1 | GGB | 9.81 | GGB | 1001.51 | GGB | 63.87 | GGB | 164971.44 | GGB | 132175.77 | GGB | 0 | 0 | 2576 | 3600 | 2560.55 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277538.5 | GGB | 277541.06 | 2222.0739 | 2222.0739 |  |  |  | 0 | 1 | [10 empty] | 2576 | -339 | 2237 | 2222.0739 | 81.5845 |  |  | #VALUE!
04.07.2008 12:00 | 3600 | 2 | 768 | GGB | 767.033 | 779.719 | 772.161 | 255.47 | GGB | 10472.1 | GGB | 9.81 | GGB | 1001.01 | GGB | 65.14 | GGB | 161933.41 | GGB | 129190.83 | GGB | 0 | 0 | 2569 | 3600 | 2554.09 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277576.74 | GGB | 277579.3 | 2215.0796 | 2215.0796 |  |  |  | 0 | 1 | [10 empty] | 2569 | -339 | 2230 | 2215.0796 | 79.4911 |  |  | #VALUE!
04.07.2008 13:00 | 3600 | 2 | 767.85 | GGB | 767.033 | 779.719 | 770.696 | 255.53 | GGB | 10460 | GGB | 9.8 | GGB | 1000.58 | GGB | 65.6 | GGB | 161553.79 | GGB | 128656.53 | GGB | 0 | 0 | 2579 | 3600 | 2563.78 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277614.98 | GGB | 277617.54 | 2225.0714 | 2225.0714 |  |  |  | 0 | 1 | [10 empty] | 2579 | -339 | 2240 | 2225.0714 | 79.5194 |  |  | #VALUE!
04.07.2008 14:00 | 3600 | 2 | 767.94 | GGB | 768.132 | 781.711 | 773.26 | 257.45 | GGB | 10474.8 | GGB | 9.8 | GGB | 1000.58 | GGB | 65.35 | GGB | 163081.06 | GGB | 129968.24 | GGB | 0 | 0 | 2599 | 3600 | 2583.67 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277653.22 | GGB | 277655.78 | 2245.0551 | 2245.0551 |  |  |  | 0 | 1 | [10 empty] | 2599 | -339 | 2260 | 2245.0551 | 81.0516 |  |  | #VALUE!
04.07.2008 15:00 | 3600 | 2 | 768.77 | GGB | 768.498 | 781.43 | 773.26 | 255.58 | GGB | 10564.5 | GGB | 9.81 | GGB | 1000.41 | GGB | 66.28 | GGB | 161364.53 | GGB | 128227.28 | GGB | 0 | 0 | 2596 | 3600 | 2580.91 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277691.46 | GGB | 277694.02 | 2242.0576 | 2242.0576 |  |  |  | 0 | 1 | [10 empty] | 2596 | -339 | 2257 | 2242.0576 | 79.8592 |  |  | #VALUE!
04.07.2008 16:00 | 3600 | 2 | 768.12 | GGB | 767.033 | 779.766 | 771.795 | 255.42 | GGB | 10535.2 | GGB | 9.8 | GGB | 1000.23 | GGB | 66.36 | GGB | 161473.46 | GGB | 128262.48 | GGB | 0 | 0 | 2614 | 3600 | 2598.4 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277729.71 | GGB | 277732.26 | 2260.0429 | 2260.0429 |  |  |  | 0 | 1 | [10 empty] | 2614 | -339 | 2275 | 2260.0429 | 80.5219 |  |  | #VALUE!
04.07.2008 17:00 | 3600 | 2 | 768.1 | GGB | 765.934 | 778.805 | 770.696 | 256.22 | GGB | 10509.1 | GGB | 9.8 | GGB | 1000.13 | GGB | 66.24 | GGB | 162078.65 | GGB | 128772.93 | GGB | 0 | 0 | 2612 | 3600 | 2597.1 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277767.95 | GGB | 277770.5 | 2258.0445 | 2258.0445 |  |  |  | 0 | 1 | [10 empty] | 2612 | -339 | 2273 | 2258.0445 | 80.7708 |  |  | #VALUE!
04.07.2008 18:00 | 3600 | 2 | 769.31 | GGB | 767.033 | 780.773 | 772.161 | 253.91 | GGB | 10494.4 | GGB | 9.82 | GGB | 999.27 | GGB | 67.29 | GGB | 159550.07 | GGB | 126263.63 | GGB | 0 | 0 | 2543 | 3600 | 2528.15 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277806.19 | GGB | 277808.74 | 2189.1008 | 2189.1008 |  |  |  | 0 | 1 | [10 empty] | 2543 | -339 | 2204 | 2189.1008 | 76.7788 |  |  | #VALUE!
04.07.2008 19:00 | 3600 | 2 | 767.76 | GGB | 765.934 | 778.594 | 770.696 | 255.66 | GGB | 10495.2 | GGB | 9.78 | GGB | 999.07 | GGB | 66.91 | GGB | 161179.67 | GGB | 127672.56 | GGB | 0 | 0 | 2634 | 3600 | 2618.2 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277844.43 | GGB | 277846.98 | 2280.0265 | 2280.0265 |  |  |  | 1 | 1 |  |  |  |  | 127672.56 | 2280.0265 | 127672.56 |  | 7.6124 |  | 2634 | -339 | 2295 | 2280.0265 | 80.8602 |  |  | #VALUE!
04.07.2008 20:00 | 3600 | 2 | 768.52 | GGB | 769.597 | 781.805 | 773.26 | 257.48 | GGB | 10534.6 | GGB | 9.81 | GGB | 999.95 | GGB | 65.94 | GGB | 162596.91 | GGB | 129275.73 | GGB | 0 | 0 | 2610 | 3600 | 2594.37 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277882.67 | GGB | 277885.22 | 2256.0461 | 2256.0461 |  |  |  | 0 | 1 | [10 empty] | 2610 | -339 | 2271 | 2256.0461 | 81.0144 |  |  | #VALUE!
04.07.2008 21:00 | 3600 | 2 | 767.71 | GGB | 767.033 | 779.742 | 771.795 | 257.01 | GGB | 10551.5 | GGB | 9.8 | GGB | 999.69 | GGB | 66.48 | GGB | 161673.73 | GGB | 128304.55 | GGB | 0 | 0 | 2662 | 3600 | 2646.97 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277920.91 | GGB | 277923.46 | 2308.0037 | 2308.0037 |  |  |  | 0 | 1 | [10 empty] | 2662 | -339 | 2323 | 2308.0037 | 82.2576 |  |  | #VALUE!
04.07.2008 22:00 | 3600 | 2 | 767.18 | GGB | 767.033 | 779.672 | 770.696 | 258.14 | GGB | 10596.9 | GGB | 9.8 | GGB | 999.84 | GGB | 66.88 | GGB | 162014.83 | GGB | 128444.18 | GGB | 0 | 0 | 2701 | 3600 | 2685.44 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277959.15 | GGB | 277961.7 | 2346.9718 | 2346.9718 |  |  |  | 0 | 1 | [10 empty] | 2701 | -339 | 2362 | 2346.9718 | 83.7375 |  |  | #VALUE!
04.07.2008 23:00 | 3600 | 2 | 767.02 | GGB | 767.033 | 779.742 | 770.696 | 260.13 | GGB | 10581.7 | GGB | 9.8 | GGB | 1000.23 | GGB | 65.76 | GGB | 164235.31 | GGB | 130686.44 | GGB | 0 | 0 | 2693 | 3600 | 2677.13 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 277997.39 | GGB | 277999.94 | 2338.9784 | 2338.9784 |  |  |  | 0 | 1 | [10 empty] | 2693 | -339 | 2354 | 2338.9784 | 84.9091 |  |  | #VALUE!
04.07.2008 24:00 | 3600 | 2 | 767.1 | GGB | 764.835 | 777.68 | 769.597 | 260.36 | GGB | 10594 | GGB | 9.8 | GGB | 999.77 | GGB | 65.82 | GGB | 164658.94 | GGB | 130938.34 | GGB | 0 | 0 | 2696 | 3600 | 2680.36 | GGB | 100 | GGB | 38.24 | GGB | 38.24 | GGB | 278035.64 | GGB | 278038.18 | 2341.9759 | 2341.9759 |  |  |  | 1 | 1 |  |  |  |  | 130938.34 | 2341.9759 | 130938.34 | 2341.9759 | 8.0192 |  | 2696 | -339 | 2357 | 2341.9759 | 85.1818 |  |  | #VALUE!
05.07.2008 01:00 | 3600 | 2 | 766.07 | GGB | 759.707 | 771.867 | 764.469 | 260.24 | GGB | 10654.5 | GGB | 9.79 | GGB | 999.56 | GGB | 65.74 | GGB | 164359.65 | GGB | 130705.49 | GGB | 0 | 0 | 2777 | 3600 | 2761.59 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278074.13 | GGB | 278076.67 | 2422.9098 | 2422.9098 |  |  |  | 0 | 1 | [10 empty] | 2777 | -339 | 2438 | 2422.9098 | 87.9688 |  |  | #VALUE!
05.07.2008 02:00 | 3600 | 2 | 766.89 | GGB | 767.033 | 779.109 | 770.696 | 259.93 | GGB | 10683.1 | GGB | 9.82 | GGB | 999.15 | GGB | 66.4 | GGB | 163812.78 | GGB | 129964.37 | GGB | 0 | 0 | 2775 | 3600 | 2759.85 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278112.62 | GGB | 278115.16 | 2420.9114 | 2420.9114 |  |  |  | 0 | 1 | [10 empty] | 2775 | -339 | 2436 | 2420.9114 | 87.3978 |  |  | #VALUE!
05.07.2008 03:00 | 3600 | 2 | 763.98 | GGB | 765.934 | 778.406 | 770.696 | 261.51 | GGB | 10704.7 | GGB | 9.79 | GGB | 998.87 | GGB | 65.07 | GGB | 165552.42 | GGB | 131822.04 | GGB | 0 | 0 | 2904 | 3600 | 2888.14 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278151.11 | GGB | 278153.65 | 2549.8061 | 2549.8061 |  |  |  | 1 | 1 |  |  |  |  | 131822.04 | 2549.8061 | 131822.04 | 2549.8061 | 8.7327 |  | 2904 | -339 | 2565 | 2549.8061 | 93.3668 |  |  | #VALUE!
05.07.2008 04:00 | 3600 | 2 | 764.38 | GGB | 763.37 | 776.531 | 768.498 | 263.06 | GGB | 10728.5 | GGB | 9.79 | GGB | 999.23 | GGB | 64.86 | GGB | 167405.39 | GGB | 133429.95 | GGB | 0 | 0 | 2893 | 3600 | 2877.4 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278189.6 | GGB | 278192.14 | 2538.8151 | 2538.8151 |  |  |  | 0 | 1 | [10 empty] | 2893 | -339 | 2554 | 2538.8151 | 94.0983 |  |  | #VALUE!
05.07.2008 05:00 | 3600 | 2 | 764.96 | GGB | 761.172 | 774.422 | 765.934 | 263.79 | GGB | 10740.2 | GGB | 9.8 | GGB | 999.05 | GGB | 64.07 | GGB | 168626.76 | GGB | 134693.83 | GGB | 0 | 0 | 2853 | 3600 | 2837.93 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278228.09 | GGB | 278230.63 | 2498.8478 | 2498.8478 |  |  |  | 0 | 1 | [10 empty] | 2853 | -339 | 2514 | 2498.8478 | 93.4943 |  |  | #VALUE!
05.07.2008 06:00 | 3600 | 2 | 766.17 | GGB | 768.132 | 779.859 | 773.26 | 262.39 | GGB | 10791.6 | GGB | 9.82 | GGB | 999.12 | GGB | 64.77 | GGB | 166790.3 | GGB | 132961.79 | GGB | 0 | 0 | 2831 | 3600 | 2815.84 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278266.58 | GGB | 278269.12 | 2476.8657 | 2476.8657 |  |  |  | 0 | 1 | [10 empty] | 2831 | -339 | 2492 | 2476.8657 | 91.4801 |  |  | #VALUE!
05.07.2008 07:00 | 3600 | 2 | 766.56 | GGB | 768.498 | 781.547 | 772.527 | 262.51 | GGB | 10741.9 | GGB | 9.83 | GGB | 998.89 | GGB | 64.58 | GGB | 167233.73 | GGB | 133359.29 | GGB | 0 | 0 | 2768 | 3600 | 2752.46 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278305.07 | GGB | 278307.61 | 2413.9171 | 2413.9171 |  |  |  | 0 | 1 | [10 empty] | 2768 | -339 | 2429 | 2413.9171 | 89.4217 |  |  | #VALUE!
05.07.2008 08:00 | 3600 | 2 | 765.22 | GGB | 763.37 | 775.852 | 767.766 | 263.26 | GGB | 10656.9 | GGB | 9.8 | GGB | 998.61 | GGB | 64.02 | GGB | 168711.49 | GGB | 134721.3 | GGB | 0 | 0 | 2828 | 3600 | 2812.8 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278343.56 | GGB | 278346.1 | 2473.8682 | 2473.8682 |  |  |  | 0 | 1 | [10 empty] | 2828 | -339 | 2489 | 2473.8682 | 92.5785 |  |  | #VALUE!
05.07.2008 09:00 | 3600 | 2 | 766.47 | GGB | 764.469 | 777.609 | 769.963 | 261.19 | GGB | 10677.9 | GGB | 9.82 | GGB | 997.68 | GGB | 64.54 | GGB | 166179.61 | GGB | 132374.37 | GGB | 0 | 0 | 2756 | 3600 | 2741.01 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278382.05 | GGB | 278384.59 | 2401.9269 | 2401.9269 |  |  |  | 1 | 1 |  |  |  |  | 132374.37 | 2401.9269 | 132374.37 | 2401.9269 | 8.2607 |  | 2756 | -339 | 2417 | 2401.9269 | 88.3204 |  |  | #VALUE!
05.07.2008 10:00 | 3600 | 2 | 766.07 | GGB | 764.469 | 777.539 | 768.864 | 261.01 | GGB | 10615.8 | GGB | 9.81 | GGB | 997.83 | GGB | 64.92 | GGB | 165718.57 | GGB | 131877.69 | GGB | 0 | 0 | 2743 | 3600 | 2727.9 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278420.54 | GGB | 278423.08 | 2388.9376 | 2388.9376 |  |  |  | 1 | 1 |  |  |  |  | 131877.69 | 2388.9376 | 131877.69 | 2388.9376 | 8.1852 |  | 2743 | -339 | 2404 | 2388.9376 | 87.5132 |  |  | #VALUE!
05.07.2008 11:00 | 3600 | 2 | 766.54 | GGB | 765.934 | 778.781 | 770.33 | 260.77 | GGB | 10594.5 | GGB | 9.82 | GGB | 997.69 | GGB | 64.99 | GGB | 165621.74 | GGB | 131753.56 | GGB | 0 | 0 | 2702 | 3600 | 2686.63 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278459.03 | GGB | 278461.57 | 2347.971 | 2347.971 |  |  |  | 0 | 1 | [10 empty] | 2702 | -339 | 2363 | 2347.971 | 85.9315 |  |  | #VALUE!
05.07.2008 12:00 | 3600 | 2 | 766.09 | GGB | 765.934 | 777.539 | 769.963 | 258.11 | GGB | 10559.6 | GGB | 9.81 | GGB | 997.03 | GGB | 66.03 | GGB | 162692.64 | GGB | 128942.07 | GGB | 0 | 0 | 2711 | 3600 | 2695.31 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278497.52 | GGB | 278500.06 | 2356.9637 | 2356.9637 |  |  |  | 1 | 1 |  |  |  |  | 128942.07 | 2356.9637 | 128942.07 | 2356.9637 | 7.8959 |  | 2711 | -339 | 2372 | 2356.9637 | 84.4199 |  |  | #VALUE!
05.07.2008 13:00 | 3600 | 2 | 766.2 | GGB | 763.37 | 776.742 | 767.766 | 257.11 | GGB | 10536.5 | GGB | 9.81 | GGB | 996.8 | GGB | 66.29 | GGB | 162024.73 | GGB | 128282.36 | GGB | 0 | 0 | 2699 | 3600 | 2683.42 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278536.01 | GGB | 278538.55 | 2344.9735 | 2344.9735 |  |  |  | 0 | 1 | [10 empty] | 2699 | -339 | 2360 | 2344.9735 | 83.5608 |  |  | #VALUE!
05.07.2008 14:00 | 3600 | 2 | 766.33 | GGB | 765.934 | 779.109 | 770.33 | 256.25 | GGB | 10523.2 | GGB | 9.81 | GGB | 996.22 | GGB | 66.52 | GGB | 161003.62 | GGB | 127315.87 | GGB | 0 | 0 | 2711 | 3600 | 2695.66 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278574.5 | GGB | 278577.04 | 2356.9637 | 2356.9637 |  |  |  | 0 | 1 | [10 empty] | 2711 | -339 | 2372 | 2356.9637 | 83.3552 |  |  | #VALUE!
05.07.2008 15:00 | 3600 | 2 | 766.98 | GGB | 769.597 | 782.602 | 773.993 | 255.78 | GGB | 10484.6 | GGB | 9.81 | GGB | 996.02 | GGB | 67 | GGB | 160173.97 | GGB | 126454.18 | GGB | 0 | 0 | 2669 | 3600 | 2653.41 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278613 | GGB | 278615.53 | 2314.998 | 2314.998 |  |  |  | 0 | 1 | [10 empty] | 2669 | -339 | 2330 | 2314.998 | 81.317 |  |  | #VALUE!
05.07.2008 16:00 | 3600 | 2 | 767 | GGB | 762.271 | 775.617 | 767.766 | 254.33 | GGB | 10394.8 | GGB | 9.79 | GGB | 994.77 | GGB | 67.68 | GGB | 158961.39 | GGB | 125089.38 | GGB | 0 | 0 | 2614 | 3600 | 2598.99 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278651.49 | GGB | 278654.02 | 2260.0429 | 2260.0429 |  |  |  | 0 | 1 | [10 empty] | 2614 | -339 | 2275 | 2260.0429 | 78.5298 |  |  | #VALUE!
05.07.2008 17:00 | 3600 | 2 | 768.3 | GGB | 768.132 | 781.078 | 773.626 | 253.34 | GGB | 10385.7 | GGB | 9.82 | GGB | 993.72 | GGB | 67.99 | GGB | 158179.05 | GGB | 124229.76 | GGB | 0 | 0 | 2556 | 3600 | 2540.72 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278689.98 | GGB | 278692.51 | 2202.0902 | 2202.0902 |  |  |  | 0 | 1 | [10 empty] | 2556 | -339 | 2217 | 2202.0902 | 75.9903 |  |  | #VALUE!
05.07.2008 18:00 | 3600 | 2 | 767.37 | GGB | 762.271 | 776.203 | 767.766 | 254.38 | GGB | 10362.4 | GGB | 9.78 | GGB | 993.63 | GGB | 68 | GGB | 158886.57 | GGB | 124770.34 | GGB | 0 | 0 | 2587 | 3600 | 2572.01 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278728.47 | GGB | 278731 | 2233.0649 | 2233.0649 |  |  |  | 0 | 1 | [10 empty] | 2587 | -339 | 2248 | 2233.0649 | 77.3945 |  |  | #VALUE!
05.07.2008 19:00 | 3600 | 2 | 767.32 | GGB | 762.271 | 776.461 | 767.766 | 255.93 | GGB | 10386.2 | GGB | 9.79 | GGB | 994.51 | GGB | 67.7 | GGB | 160231.18 | GGB | 126049.1 | GGB | 0 | 0 | 2618 | 3600 | 2602.17 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278766.96 | GGB | 278769.49 | 2264.0396 | 2264.0396 |  |  |  | 0 | 1 | [10 empty] | 2618 | -339 | 2279 | 2264.0396 | 79.2723 |  |  | #VALUE!
05.07.2008 20:00 | 3600 | 2 | 767.72 | GGB | 769.597 | 782.789 | 775.091 | 258.2 | GGB | 10503.1 | GGB | 9.82 | GGB | 994.43 | GGB | 66.92 | GGB | 162035.74 | GGB | 127750.51 | GGB | 0 | 0 | 2647 | 3600 | 2631.87 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278805.45 | GGB | 278807.98 | 2293.0159 | 2293.0159 |  |  |  | 0 | 1 | [10 empty] | 2647 | -339 | 2308 | 2293.0159 | 81.3705 |  |  | #VALUE!
05.07.2008 21:00 | 3600 | 2 | 767.56 | GGB | 771.795 | 785.742 | 777.289 | 258.95 | GGB | 10486.3 | GGB | 9.8 | GGB | 994.72 | GGB | 66.9 | GGB | 162980.93 | GGB | 128542.6 | GGB | 0 | 0 | 2656 | 3600 | 2640.63 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278843.94 | GGB | 278846.47 | 2302.0086 | 2302.0086 |  |  |  | 0 | 1 | [10 empty] | 2656 | -339 | 2317 | 2302.0086 | 82.1962 |  |  | #VALUE!
05.07.2008 22:00 | 3600 | 2 | 766.06 | GGB | 765.934 | 779.297 | 771.429 | 258.86 | GGB | 10445.5 | GGB | 9.78 | GGB | 995 | GGB | 66.27 | GGB | 163106.37 | GGB | 128914.91 | GGB | 0 | 0 | 2690 | 3600 | 2674.87 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278882.43 | GGB | 278884.96 | 2335.9808 | 2335.9808 |  |  |  | 0 | 1 | [10 empty] | 2690 | -339 | 2351 | 2335.9808 | 83.6508 |  |  | #VALUE!
05.07.2008 23:00 | 3600 | 2 | 767.55 | GGB | 770.696 | 783.82 | 776.923 | 258.43 | GGB | 10534.6 | GGB | 9.81 | GGB | 995.79 | GGB | 66.54 | GGB | 162320.72 | GGB | 128292.18 | GGB | 0 | 0 | 2646 | 3600 | 2630.89 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278920.92 | GGB | 278923.45 | 2292.0167 | 2292.0167 |  |  |  | 0 | 1 | [10 empty] | 2646 | -339 | 2307 | 2292.0167 | 81.68 |  |  | #VALUE!
05.07.2008 24:00 | 3600 | 2 | 766.6 | GGB | 763.37 | 775.898 | 767.033 | 257.44 | GGB | 10560.7 | GGB | 9.8 | GGB | 996.72 | GGB | 66.57 | GGB | 162046.74 | GGB | 128186.39 | GGB | 0 | 0 | 2691 | 3600 | 2675.77 | GGB | 100 | GGB | 38.49 | GGB | 38.49 | GGB | 278959.41 | GGB | 278961.94 | 2336.98 | 2336.98 |  |  |  | 0 | 1 | [10 empty] | 2691 | -339 | 2352 | 2336.98 | 83.2136 |  |  | #VALUE!
06.07.2008 01:00 | 3600 | 2 | 765.87 | GGB | 764.469 | 777.914 | 769.597 | 259.8 | GGB | 10614 | GGB | 9.79 | GGB | 997.09 | GGB | 65.79 | GGB | 163954.73 | GGB | 130039.45 | GGB | 0 | 0 | 2774 | 3600 | 2758.45 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 278997.58 | GGB | 279000.11 | 2419.9122 | 2419.9122 |  |  |  | 1 | 1 |  |  |  |  | 130039.45 | 2419.9122 | 130039.45 | 2419.9122 | 8.2443 |  | 2774 | -339 | 2435 | 2419.9122 | 87.4122 |  |  | #VALUE!
06.07.2008 02:00 | 3600 | 2 | 766.52 | GGB | 765.934 | 779.18 | 770.696 | 260.75 | GGB | 10665.5 | GGB | 9.81 | GGB | 997.72 | GGB | 65.64 | GGB | 164693.05 | GGB | 130768.47 | GGB | 0 | 0 | 2733 | 3600 | 2717.96 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279035.75 | GGB | 279038.28 | 2378.9457 | 2378.9457 |  |  |  | 0 | 1 | [10 empty] | 2733 | -339 | 2394 | 2378.9457 | 86.4142 |  |  | #VALUE!
06.07.2008 03:00 | 3600 | 2 | 765.75 | GGB | 764.835 | 778.195 | 769.597 | 261.5 | GGB | 10687.7 | GGB | 9.79 | GGB | 998.26 | GGB | 65.39 | GGB | 165787.89 | GGB | 131803.18 | GGB | 0 | 0 | 2806 | 3600 | 2790.09 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279073.92 | GGB | 279076.45 | 2451.8861 | 2451.8861 |  |  |  | 1 | 1 |  |  |  |  | 131803.18 | 2451.8861 | 131803.18 | 2451.8861 | 8.4665 |  | 2806 | -339 | 2467 | 2451.8861 | 89.7684 |  |  | #VALUE!
06.07.2008 04:00 | 3600 | 2 | 765.92 | GGB | 767.033 | 779.227 | 770.696 | 261.72 | GGB | 10719.9 | GGB | 9.8 | GGB | 998.61 | GGB | 65 | GGB | 166060.77 | GGB | 132219.3 | GGB | 0 | 0 | 2792 | 3600 | 2776.78 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279112.09 | GGB | 279114.62 | 2437.8976 | 2437.8976 |  |  |  | 0 | 1 | [10 empty] | 2792 | -339 | 2453 | 2437.8976 | 89.5381 |  |  | #VALUE!
06.07.2008 05:00 | 3600 | 2 | 765.95 | GGB | 764.835 | 777.023 | 768.498 | 261.82 | GGB | 10725.9 | GGB | 9.8 | GGB | 998.8 | GGB | 64.99 | GGB | 166277.54 | GGB | 132421.3 | GGB | 0 | 0 | 2792 | 3600 | 2776.05 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279150.25 | GGB | 279152.79 | 2437.8976 | 2437.8976 |  |  |  | 1 | 1 |  |  |  |  | 132421.3 | 2437.8976 | 132421.3 | 2437.8976 | 8.4577 |  | 2792 | -339 | 2453 | 2437.8976 | 89.6749 |  |  | #VALUE!
06.07.2008 06:00 | 3600 | 2 | 765.98 | GGB | 763.37 | 776.953 | 768.498 | 261.81 | GGB | 10739.4 | GGB | 9.81 | GGB | 998.72 | GGB | 64.91 | GGB | 166497.61 | GGB | 132619.3 | GGB | 0 | 0 | 2803 | 3600 | 2787.88 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279188.42 | GGB | 279190.96 | 2448.8886 | 2448.8886 |  |  |  | 0 | 1 | [10 empty] | 2803 | -339 | 2464 | 2448.8886 | 90.2139 |  |  | #VALUE!
06.07.2008 07:00 | 3600 | 2 | 766.35 | GGB | 765.934 | 777.797 | 770.696 | 261.91 | GGB | 10742.4 | GGB | 9.81 | GGB | 999.07 | GGB | 64.88 | GGB | 166449.19 | GGB | 132639.27 | GGB | 0 | 0 | 2792 | 3600 | 2776.39 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279226.59 | GGB | 279229.13 | 2437.8976 | 2437.8976 |  |  |  | 1 | 1 |  |  |  |  | 132639.27 | 2437.8976 | 132639.27 | 2437.8976 | 8.4716 |  | 2792 | -339 | 2453 | 2437.8976 | 89.8225 |  |  | #VALUE!
06.07.2008 08:00 | 3600 | 2 | 766.51 | GGB | 764.835 | 777.82 | 768.498 | 262.01 | GGB | 10727.6 | GGB | 9.81 | GGB | 999.29 | GGB | 64.68 | GGB | 166711.07 | GGB | 132954.6 | GGB | 0 | 0 | 2774 | 3600 | 2758.73 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279264.76 | GGB | 279267.3 | 2419.9122 | 2419.9122 |  |  |  | 1 | 1 |  |  |  |  | 132954.6 | 2419.9122 | 132954.6 | 2419.9122 | 8.4291 |  | 2774 | -339 | 2435 | 2419.9122 | 89.3718 |  |  | #VALUE!
06.07.2008 09:00 | 3600 | 2 | 765.74 | GGB | 765.934 | 777.797 | 770.696 | 263.02 | GGB | 10706.3 | GGB | 9.8 | GGB | 1000.06 | GGB | 64.47 | GGB | 167884.03 | GGB | 134078.78 | GGB | 0 | 0 | 2816 | 3600 | 2800.78 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279302.93 | GGB | 279305.47 | 2461.878 | 2461.878 |  |  |  | 1 | 1 |  |  |  |  | 134078.78 | 2461.878 | 134078.78 | 2461.878 | 8.6478 |  | 2816 | -339 | 2477 | 2461.878 | 91.6904 |  |  | #VALUE!
06.07.2008 10:00 | 3600 | 2 | 766.34 | GGB | 764.835 | 776.672 | 768.498 | 261.86 | GGB | 10740.4 | GGB | 9.81 | GGB | 1000.3 | GGB | 64.69 | GGB | 166328.15 | GGB | 132778.58 | GGB | 0 | 0 | 2791 | 3600 | 2775.07 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279341.1 | GGB | 279343.64 | 2436.8984 | 2436.8984 |  |  |  | 1 | 1 |  |  |  |  | 132778.58 | 2436.8984 | 132778.58 | 2436.8984 | 8.477 |  | 2791 | -339 | 2452 | 2436.8984 | 89.88 |  |  | #VALUE!
06.07.2008 11:00 | 3600 | 2 | 765.74 | GGB | 764.835 | 776.695 | 768.498 | 262.43 | GGB | 10725.7 | GGB | 9.8 | GGB | 1000.73 | GGB | 64.89 | GGB | 166673.66 | GGB | 133032.28 | GGB | 0 | 0 | 2824 | 3600 | 2808.84 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279379.26 | GGB | 279381.81 | 2469.8714 | 2469.8714 |  |  |  | 1 | 1 |  |  |  |  | 133032.28 | 2469.8714 | 133032.28 | 2469.8714 | 8.6081 |  | 2824 | -339 | 2485 | 2469.8714 | 91.2702 |  |  | #VALUE!
06.07.2008 12:00 | 3600 | 2 | 766.32 | GGB | 764.835 | 777.445 | 769.597 | 263.12 | GGB | 10688.4 | GGB | 9.81 | GGB | 1000.74 | GGB | 64.79 | GGB | 167386.68 | GGB | 133644.87 | GGB | 0 | 0 | 2783 | 3600 | 2767.32 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279417.43 | GGB | 279419.98 | 2428.9049 | 2428.9049 |  |  |  | 1 | 1 |  |  |  |  | 133644.87 | 2428.9049 | 133644.87 | 2428.9049 | 8.5043 |  | 2783 | -339 | 2444 | 2428.9049 | 90.1696 |  |  | #VALUE!
06.07.2008 13:00 | 3600 | 2 | 767.01 | GGB | 765.934 | 778.336 | 770.696 | 260.38 | GGB | 10681.7 | GGB | 9.83 | GGB | 1000.46 | GGB | 65.72 | GGB | 164050.46 | GGB | 130584.52 | GGB | 0 | 0 | 2723 | 3600 | 2707.63 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279455.6 | GGB | 279458.15 | 2368.9539 | 2368.9539 |  |  |  | 1 | 1 |  |  |  |  | 130584.52 | 2368.9539 | 130584.52 | 2368.9539 | 8.1045 |  | 2723 | -339 | 2384 | 2368.9539 | 85.9302 |  |  | #VALUE!
06.07.2008 14:00 | 3600 | 2 | 767.14 | GGB | 765.934 | 778.43 | 770.696 | 259.48 | GGB | 10578.4 | GGB | 9.81 | GGB | 1000.12 | GGB | 66.22 | GGB | 163489.28 | GGB | 129901.24 | GGB | 0 | 0 | 2672 | 3600 | 2656.41 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279493.77 | GGB | 279496.32 | 2317.9955 | 2317.9955 |  |  |  | 1 | 1 |  |  |  |  | 129901.24 | 2317.9955 | 129901.24 | 2317.9955 | 7.8887 |  | 2672 | -339 | 2333 | 2317.9955 | 83.6418 |  |  | #VALUE!
06.07.2008 15:00 | 3600 | 2 | 767.89 | GGB | 768.132 | 780.891 | 773.26 | 259.39 | GGB | 10531.8 | GGB | 9.82 | GGB | 999.57 | GGB | 66.17 | GGB | 163773.17 | GGB | 130075.95 | GGB | 0 | 0 | 2625 | 3600 | 2609.33 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279531.94 | GGB | 279534.49 | 2271.0339 | 2271.0339 |  |  |  | 0 | 1 | [10 empty] | 2625 | -339 | 2286 | 2271.0339 | 82.0575 |  |  | #VALUE!
06.07.2008 16:00 | 3600 | 2 | 767.82 | GGB | 764.835 | 777.82 | 769.597 | 256.41 | GGB | 10479.2 | GGB | 9.8 | GGB | 998.65 | GGB | 67.26 | GGB | 160958.51 | GGB | 127313.31 | GGB | 0 | 0 | 2585 | 3600 | 2569.7 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279570.11 | GGB | 279572.66 | 2231.0665 | 2231.0665 |  |  |  | 1 | 1 |  |  |  |  | 127313.31 | 2231.0665 | 127313.31 |  | 7.4416 |  | 2585 | -339 | 2246 | 2231.0665 | 78.9012 |  |  | #VALUE!
06.07.2008 17:00 | 3600 | 2 | 768.72 | GGB | 765.934 | 780.141 | 771.429 | 256.19 | GGB | 10494.8 | GGB | 9.82 | GGB | 998.84 | GGB | 67.33 | GGB | 160969.51 | GGB | 127320.55 | GGB | 0 | 0 | 2559 | 3600 | 2544.13 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279608.27 | GGB | 279610.83 | 2205.0878 | 2205.0878 |  |  |  | 0 | 1 | [10 empty] | 2559 | -339 | 2220 | 2205.0878 | 77.9869 |  |  | #VALUE!
06.07.2008 18:00 | 3600 | 2 | 768.44 | GGB | 767.033 | 780.211 | 771.429 | 257 | GGB | 10427.4 | GGB | 9.8 | GGB | 998.8 | GGB | 66.86 | GGB | 162664.03 | GGB | 128830.64 | GGB | 0 | 0 | 2540 | 3600 | 2524.26 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279646.44 | GGB | 279649 | 2186.1033 | 2186.1033 |  |  |  | 0 | 1 | [10 empty] | 2540 | -339 | 2201 | 2186.1033 | 78.2325 |  |  | #VALUE!
06.07.2008 19:00 | 3600 | 2 | 769.01 | GGB | 768.132 | 780.281 | 772.527 | 255.96 | GGB | 10472.2 | GGB | 9.81 | GGB | 998.68 | GGB | 67.07 | GGB | 161297.41 | GGB | 127654.85 | GGB | 0 | 0 | 2522 | 3600 | 2506.5 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279684.61 | GGB | 279687.17 | 2168.118 | 2168.118 |  |  |  | 0 | 1 | [10 empty] | 2522 | -339 | 2183 | 2168.118 | 76.8808 |  |  | #VALUE!
06.07.2008 20:00 | 3600 | 2 | 768.13 | GGB | 765.934 | 779.344 | 771.429 | 255.88 | GGB | 10469.6 | GGB | 9.8 | GGB | 999.05 | GGB | 67.32 | GGB | 160587.69 | GGB | 127048.52 | GGB | 0 | 0 | 2556 | 3600 | 2540.57 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279722.78 | GGB | 279725.34 | 2202.0902 | 2202.0902 |  |  |  | 0 | 1 | [10 empty] | 2556 | -339 | 2217 | 2202.0902 | 77.7145 |  |  | #VALUE!
06.07.2008 21:00 | 3600 | 2 | 767.77 | GGB | 764.835 | 778.195 | 769.963 | 257.5 | GGB | 10471.2 | GGB | 9.79 | GGB | 999.56 | GGB | 66.69 | GGB | 162269.01 | GGB | 128680.39 | GGB | 0 | 0 | 2574 | 3600 | 2559.2 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279760.95 | GGB | 279763.51 | 2220.0755 | 2220.0755 |  |  |  | 1 | 1 |  |  |  |  | 128680.39 | 2220.0755 | 128680.39 |  | 7.4844 |  | 2574 | -339 | 2235 | 2220.0755 | 79.3556 |  |  | #VALUE!
06.07.2008 22:00 | 3600 | 2 | 768.29 | GGB | 765.934 | 779.32 | 770.33 | 258.55 | GGB | 10535.1 | GGB | 9.81 | GGB | 999.75 | GGB | 66.38 | GGB | 162896.2 | GGB | 129322.12 | GGB | 0 | 0 | 2596 | 3600 | 2580.35 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279799.12 | GGB | 279801.68 | 2242.0576 | 2242.0576 |  |  |  | 0 | 1 | [10 empty] | 2596 | -339 | 2257 | 2242.0576 | 80.541 |  |  | #VALUE!
06.07.2008 23:00 | 3600 | 2 | 767.2 | GGB | 764.835 | 778.219 | 768.864 | 259.09 | GGB | 10567.4 | GGB | 9.8 | GGB | 1000.54 | GGB | 66.61 | GGB | 162635.42 | GGB | 129127.65 | GGB | 0 | 0 | 2661 | 3600 | 2645.19 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279837.28 | GGB | 279839.85 | 2307.0045 | 2307.0045 |  |  |  | 1 | 1 |  |  |  |  | 129127.65 | 2307.0045 | 129127.65 | 2307.0045 | 7.8045 |  | 2661 | -339 | 2322 | 2307.0045 | 82.7495 |  |  | #VALUE!
06.07.2008 24:00 | 3600 | 2 | 766.17 | GGB | 764.469 | 777.07 | 769.963 | 261.11 | GGB | 10618 | GGB | 9.79 | GGB | 1001.06 | GGB | 66.19 | GGB | 164229.81 | GGB | 130626.14 | GGB | 0 | 0 | 2752 | 3600 | 2736.42 | GGB | 100 | GGB | 38.17 | GGB | 38.17 | GGB | 279875.45 | GGB | 279878.02 | 2397.9302 | 2397.9302 |  |  |  | 1 | 1 |  |  |  |  | 130626.14 | 2397.9302 | 130626.14 | 2397.9302 | 8.2062 |  | 2752 | -339 | 2413 | 2397.9302 | 87.009 |  |  | #VALUE!
07.07.2008 01:00 | 3600 | 2 | 766.34 | GGB | 764.835 | 777.914 | 769.963 | 263.26 | GGB | 10639.5 | GGB | 9.79 | GGB | 1001.6 | GGB | 65.58 | GGB | 166481.1 | GGB | 132723.94 | GGB | 0 | 0 | 2755 | 3600 | 2739.73 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 279913.45 | GGB | 279916.02 | 2400.9278 | 2400.9278 |  |  |  | 1 | 1 |  |  |  |  | 132723.94 | 2400.9278 | 132723.94 | 2400.9278 | 8.3858 |  | 2755 | -339 | 2416 | 2400.9278 | 88.5168 |  |  | #VALUE!
07.07.2008 02:00 | 3600 | 2 | 766.62 | GGB | 763.37 | 775.664 | 767.766 | 263.46 | GGB | 10701.1 | GGB | 9.8 | GGB | 1001.72 | GGB | 65.43 | GGB | 166421.68 | GGB | 132752.37 | GGB | 0 | 0 | 2761 | 3600 | 2745.91 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 279951.45 | GGB | 279954.02 | 2406.9229 | 2406.9229 |  |  |  | 0 | 1 | [10 empty] | 2761 | -339 | 2422 | 2406.9229 | 88.7569 |  |  | #VALUE!
07.07.2008 03:00 | 3600 | 2 | 766.2 | GGB | 765.934 | 778.102 | 769.963 | 263.35 | GGB | 10761.2 | GGB | 9.81 | GGB | 1002.23 | GGB | 65.44 | GGB | 167087.39 | GGB | 133346.4 | GGB | 0 | 0 | 2817 | 3600 | 2801.51 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 279989.45 | GGB | 279992.02 | 2462.8771 | 2462.8771 |  |  |  | 1 | 1 |  |  |  |  | 133346.4 | 2462.8771 | 133346.4 | 2462.8771 | 8.6425 |  | 2817 | -339 | 2478 | 2462.8771 | 91.2266 |  |  | #VALUE!
07.07.2008 04:00 | 3600 | 2 | 765.85 | GGB | 765.934 | 778.008 | 769.963 | 264.03 | GGB | 10713.8 | GGB | 9.79 | GGB | 1001.93 | GGB | 65.04 | GGB | 167493.41 | GGB | 133789.31 | GGB | 0 | 0 | 2824 | 3600 | 2808.65 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280027.46 | GGB | 280030.02 | 2469.8714 | 2469.8714 |  |  |  | 1 | 1 |  |  |  |  | 133789.31 | 2469.8714 | 133789.31 | 2469.8714 | 8.6959 |  | 2824 | -339 | 2485 | 2469.8714 | 91.7896 |  |  | #VALUE!
07.07.2008 05:00 | 3600 | 2 | 766.25 | GGB | 764.835 | 777 | 768.864 | 265.35 | GGB | 10740.9 | GGB | 9.81 | GGB | 1002.04 | GGB | 64.66 | GGB | 168952.46 | GGB | 135121.36 | GGB | 0 | 0 | 2822 | 3600 | 2806.76 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280065.46 | GGB | 280068.02 | 2467.8731 | 2467.8731 |  |  |  | 1 | 1 |  |  |  |  | 135121.36 | 2467.8731 | 135121.36 | 2467.8731 | 8.7753 |  | 2822 | -339 | 2483 | 2467.8731 | 92.6284 |  |  | #VALUE!
07.07.2008 06:00 | 3600 | 2 | 766.32 | GGB | 763.37 | 776.133 | 768.864 | 263.83 | GGB | 10771.6 | GGB | 9.81 | GGB | 1001.47 | GGB | 65.11 | GGB | 167292.05 | GGB | 133537.68 | GGB | 0 | 0 | 2824 | 3600 | 2808.09 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280103.46 | GGB | 280106.02 | 2469.8714 | 2469.8714 |  |  |  | 0 | 1 | [10 empty] | 2824 | -339 | 2485 | 2469.8714 | 91.6169 |  |  | #VALUE!
07.07.2008 07:00 | 3600 | 2 | 766.28 | GGB | 764.835 | 777.117 | 768.864 | 263.66 | GGB | 10774 | GGB | 9.81 | GGB | 1001.35 | GGB | 65.22 | GGB | 167048.88 | GGB | 133284.55 | GGB | 0 | 0 | 2826 | 3600 | 2810.99 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280141.46 | GGB | 280144.02 | 2471.8698 | 2471.8698 |  |  |  | 1 | 1 |  |  |  |  | 133284.55 | 2471.8698 | 133284.55 | 2471.8698 | 8.6701 |  | 2826 | -339 | 2487 | 2471.8698 | 91.5172 |  |  | #VALUE!
07.07.2008 08:00 | 3600 | 2 | 767.29 | GGB | 765.934 | 778.336 | 770.33 | 261.49 | GGB | 10722.9 | GGB | 9.83 | GGB | 1000.97 | GGB | 65.89 | GGB | 164786.58 | GGB | 131172.21 | GGB | 0 | 0 | 2766 | 3600 | 2750.28 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280179.46 | GGB | 280182.02 | 2411.9188 | 2411.9188 |  |  |  | 1 | 1 |  |  |  |  | 131172.21 | 2411.9188 | 131172.21 | 2411.9188 | 8.3257 |  | 2766 | -339 | 2427 | 2411.9188 | 87.8824 |  |  | #VALUE!
07.07.2008 09:00 | 3600 | 2 | 767.28 | GGB | 765.934 | 778.383 | 770.33 | 259.93 | GGB | 10634.2 | GGB | 9.82 | GGB | 1000.07 | GGB | 66.68 | GGB | 163037.04 | GGB | 129361.39 | GGB | 0 | 0 | 2738 | 3600 | 2723.05 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280217.46 | GGB | 280220.02 | 2383.9416 | 2383.9416 |  |  |  | 1 | 1 |  |  |  |  | 129361.39 | 2383.9416 | 129361.39 | 2383.9416 | 8.1155 |  | 2738 | -339 | 2399 | 2383.9416 | 85.6639 |  |  | #VALUE!
07.07.2008 10:00 | 3600 | 2 | 768.17 | GGB | 765.934 | 779.297 | 771.429 | 257.06 | GGB | 10528.6 | GGB | 9.83 | GGB | 999.24 | GGB | 67.79 | GGB | 159923.09 | GGB | 126370.95 | GGB | 0 | 0 | 2642 | 3600 | 2626.47 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280255.46 | GGB | 280258.02 | 2288.02 | 2288.02 |  |  |  | 0 | 1 | [10 empty] | 2642 | -339 | 2303 | 2288.02 | 80.3165 |  |  | #VALUE!
07.07.2008 11:00 | 3600 | 2 | 767.74 | GGB | 767.033 | 780.328 | 771.429 | 255.62 | GGB | 10431.1 | GGB | 9.81 | GGB | 998.15 | GGB | 68.41 | GGB | 158443.13 | GGB | 124839.67 | GGB | 0 | 0 | 2635 | 3600 | 2619.68 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280293.46 | GGB | 280296.02 | 2281.0257 | 2281.0257 |  |  |  | 0 | 1 | [10 empty] | 2635 | -339 | 2296 | 2281.0257 | 79.1007 |  |  | #VALUE!
07.07.2008 12:00 | 3600 | 2 | 767.99 | GGB | 767.033 | 780.281 | 771.429 | 254.89 | GGB | 10396.5 | GGB | 9.81 | GGB | 997.55 | GGB | 68.86 | GGB | 157555.16 | GGB | 123899.08 | GNB | 0 | 0 | 2608 | 3600 | 2592.77 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280331.46 | GGB | 280334.02 | 2254.0478 | 2254.0478 |  |  |  | 0 | 1 | [10 empty] | 2608 | -339 | 2269 | 2254.0478 | 77.5762 |  |  | #VALUE!
07.07.2008 13:00 | 3600 | 2 | 768.07 | GGB | 765.934 | 779.227 | 771.429 | 254.55 | GGB | 10371.8 | GGB | 9.8 | GGB | 997.35 | GGB | 69.23 | GGB | 157134.83 | GGB | 123409.86 | GNB | 0 | 0 | 2598 | 3600 | 2582.71 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280369.46 | GGB | 280372.02 | 2244.0559 | 2244.0559 |  |  |  | 0 | 1 | [10 empty] | 2598 | -339 | 2259 | 2244.0559 | 76.9274 |  |  | #VALUE!
07.07.2008 14:00 | 3600 | 2 | 768.83 | GGB | 767.033 | 780.375 | 772.527 | 254.14 | GGB | 10338.6 | GGB | 9.81 | GGB | 997.04 | GGB | 69.39 | GGB | 156909.26 | GGB | 123138.3 | GNB | 0 | 0 | 2560 | 3600 | 2544.47 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280407.46 | GGB | 280410.02 | 2206.0869 | 2206.0869 |  |  |  | 0 | 1 | [10 empty] | 2560 | -339 | 2221 | 2206.0869 | 75.4594 |  |  | #VALUE!
07.07.2008 15:00 | 3600 | 2 | 770.05 | GGB | 767.033 | 780.352 | 772.527 | 253.73 | GGB | 10260.4 | GGB | 9.8 | GGB | 996.49 | GGB | 69.01 | GGB | 157401.11 | GGB | 123591.51 | GNB | 0 | 0 | 2496 | 3600 | 2480.71 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280445.46 | GGB | 280448.02 | 2142.1392 | 2142.1392 |  |  |  | 0 | 1 | [10 empty] | 2496 | -339 | 2157 | 2142.1392 | 73.5417 |  |  | #VALUE!
07.07.2008 16:00 | 3600 | 2 | 769.7 | GGB | 767.033 | 780.422 | 772.527 | 252.4 | GGB | 10300.9 | GGB | 9.81 | GGB | 995.7 | GGB | 69.36 | GGB | 156004.79 | GGB | 122273.84 | GNB | 0 | 0 | 2499 | 3600 | 2483.78 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280483.46 | GGB | 280486.02 | 2145.1367 | 2145.1367 |  |  |  | 0 | 1 | [10 empty] | 2499 | -339 | 2160 | 2145.1367 | 72.8595 |  |  | #VALUE!
07.07.2008 17:00 | 3600 | 2 | 769 | GGB | 767.033 | 780.398 | 772.527 | 252.57 | GGB | 10307 | GGB | 9.79 | GGB | 995.39 | GGB | 69.14 | GGB | 156441.62 | GGB | 122658.58 | GNB | 0 | 0 | 2513 | 3600 | 2497.92 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280521.46 | GGB | 280524.02 | 2159.1253 | 2159.1253 |  |  |  | 0 | 1 | [10 empty] | 2513 | -339 | 2174 | 2159.1253 | 73.5653 |  |  | #VALUE!
07.07.2008 18:00 | 3600 | 2 | 768.03 | GGB | 765.934 | 779.156 | 771.429 | 254.48 | GGB | 10376.4 | GGB | 9.79 | GGB | 995.64 | GGB | 68.81 | GGB | 157755.42 | GGB | 123837.26 | GNB | 0 | 0 | 2601 | 3600 | 2585.55 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280559.46 | GGB | 280562.02 | 2247.0535 | 2247.0535 |  |  |  | 0 | 1 | [10 empty] | 2601 | -339 | 2262 | 2247.0535 | 77.2969 |  |  | #VALUE!
07.07.2008 19:00 | 3600 | 2 | 768.03 | GGB | 767.033 | 780.141 | 772.527 | 255.67 | GGB | 10416.4 | GGB | 9.8 | GGB | 996.19 | GGB | 68.83 | GGB | 158413.43 | GGB | 124416.84 | GGB | 0 | 0 | 2630 | 3600 | 2614.22 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280597.46 | GGB | 280600.02 | 2276.0298 | 2276.0298 |  |  |  | 0 | 1 | [10 empty] | 2630 | -339 | 2291 | 2276.0298 | 78.6601 |  |  | #VALUE!
07.07.2008 20:00 | 3600 | 2 | 768 | GGB | 767.033 | 781.148 | 772.527 | 257.14 | GGB | 10388.7 | GGB | 9.8 | GGB | 996.72 | GGB | 68.28 | GGB | 159997.91 | GGB | 125931.62 | GGB | 0 | 0 | 2626 | 3600 | 2610.6 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280635.46 | GGB | 280638.02 | 2272.0331 | 2272.0331 |  |  |  | 0 | 1 | [10 empty] | 2626 | -339 | 2287 | 2272.0331 | 79.478 |  |  | #VALUE!
07.07.2008 21:00 | 3600 | 2 | 767.23 | GGB | 764.835 | 777.961 | 770.33 | 256.61 | GGB | 10447.6 | GGB | 9.8 | GGB | 997.09 | GGB | 68.55 | GGB | 158895.37 | GGB | 125009.4 | GGB | 0 | 0 | 2687 | 3600 | 2671.44 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280673.46 | GGB | 280676.02 | 2332.9833 | 2332.9833 |  |  |  | 1 | 1 |  |  |  |  | 125009.4 | 2332.9833 |  | 2332.9833 | 7.6749 |  | 2687 | -339 | 2348 | 2332.9833 | 81.0125 |  |  | #VALUE!
07.07.2008 22:00 | 3600 | 2 | 767.11 | GGB | 765.934 | 780.07 | 771.429 | 257.6 | GGB | 10476.3 | GGB | 9.8 | GGB | 997.29 | GGB | 68.57 | GGB | 159498.36 | GGB | 125503.83 | GGB | 0 | 0 | 2720 | 3600 | 2704.79 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280711.46 | GGB | 280714.02 | 2365.9563 | 2365.9563 |  |  |  | 0 | 1 | [10 empty] | 2720 | -339 | 2381 | 2365.9563 | 82.4824 |  |  | #VALUE!
07.07.2008 23:00 | 3600 | 2 | 766.39 | GGB | 764.469 | 778.008 | 768.864 | 259.43 | GGB | 10451.3 | GGB | 9.78 | GGB | 997.53 | GGB | 67.91 | GGB | 161267.7 | GGB | 127171.09 | GGB | 0 | 0 | 2754 | 3600 | 2738.91 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280749.46 | GGB | 280752.02 | 2399.9286 | 2399.9286 |  |  |  | 1 | 1 |  |  |  |  | 127171.09 | 2399.9286 | 127171.09 | 2399.9286 | 8.0316 |  | 2754 | -339 | 2415 | 2399.9286 | 84.7782 |  |  | #VALUE!
07.07.2008 24:00 | 3600 | 2 | 767.64 | GGB | 764.835 | 777.914 | 768.864 | 259.6 | GGB | 10512.1 | GGB | 9.81 | GGB | 997.7 | GGB | 67.77 | GGB | 161921.3 | GGB | 127760.47 | GGB | 0 | 0 | 2714 | 3600 | 2698.37 | GGB | 100 | GGB | 38 | GGB | 38 | GGB | 280787.47 | GGB | 280790.02 | 2359.9612 | 2359.9612 |  |  |  | 1 | 1 |  |  |  |  | 127760.47 | 2359.9612 | 127760.47 | 2359.9612 | 7.9345 |  | 2714 | -339 | 2375 | 2359.9612 | 83.7527 |  |  | #VALUE!
08.07.2008 01:00 | 3600 | 2 | 767.12 | GGB | 765.934 | 779.156 | 769.963 | 258.8 | GGB | 10539.4 | GGB | 9.8 | GGB | 997.49 | GGB | 67.89 | GGB | 161035.53 | GGB | 126988.92 | GGB | 0 | 0 | 2740 | 3600 | 2725.05 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 280824.66 | GGB | 280827.21 | 2385.94 | 2385.94 |  |  |  | 0 | 1 | [10 empty] | 2740 | -339 | 2401 | 2385.94 | 84.1633 |  |  | #VALUE!
08.07.2008 02:00 | 3600 | 2 | 766.92 | GGB | 765.934 | 778.969 | 771.429 | 260.2 | GGB | 10523.2 | GGB | 9.8 | GGB | 997.39 | GGB | 67.53 | GGB | 162611.21 | GGB | 128353.79 | GGB | 0 | 0 | 2760 | 3600 | 2744.97 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 280861.85 | GGB | 280864.4 | 2405.9237 | 2405.9237 |  |  |  | 0 | 1 | [10 empty] | 2760 | -339 | 2421 | 2405.9237 | 85.7804 |  |  | #VALUE!
08.07.2008 03:00 | 3600 | 2 | 767 | GGB | 765.934 | 778.922 | 770.33 | 261.21 | GGB | 10521.4 | GGB | 9.8 | GGB | 997.53 | GGB | 67.06 | GGB | 163648.83 | GGB | 129370.75 | GGB | 0 | 0 | 2749 | 3600 | 2733.89 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 280899.04 | GGB | 280901.59 | 2394.9327 | 2394.9327 |  |  |  | 0 | 1 | [10 empty] | 2749 | -339 | 2410 | 2394.9327 | 86.0651 |  |  | #VALUE!
08.07.2008 04:00 | 3600 | 2 | 766.78 | GGB | 764.835 | 777.914 | 768.864 | 261.32 | GGB | 10523.9 | GGB | 9.8 | GGB | 997.18 | GGB | 66.91 | GGB | 163762.17 | GGB | 129471.73 | GGB | 0 | 0 | 2749 | 3600 | 2733.95 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 280936.23 | GGB | 280938.78 | 2394.9327 | 2394.9327 |  |  |  | 1 | 1 |  |  |  |  | 129471.73 | 2394.9327 | 129471.73 | 2394.9327 | 8.3376 |  | 2749 | -339 | 2410 | 2394.9327 | 86.1322 |  |  | #VALUE!
08.07.2008 05:00 | 3600 | 2 | 767.63 | GGB | 764.835 | 778.336 | 770.33 | 260.31 | GGB | 10584.7 | GGB | 9.81 | GGB | 996.88 | GGB | 67.43 | GGB | 162391.15 | GGB | 128154.56 | GGB | 0 | 0 | 2740 | 3600 | 2725 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 280973.42 | GGB | 280975.97 | 2385.94 | 2385.94 |  |  |  | 1 | 1 |  |  |  |  | 128154.56 | 2385.94 | 128154.56 | 2385.94 | 8.2218 |  | 2740 | -339 | 2401 | 2385.94 | 84.9359 |  |  | #VALUE!
08.07.2008 06:00 | 3600 | 2 | 766.5 | GGB | 764.835 | 778.289 | 769.963 | 260.55 | GGB | 10576.8 | GGB | 9.8 | GGB | 996.79 | GGB | 67.39 | GGB | 162518.79 | GGB | 128258.6 | GGB | 0 | 0 | 2796 | 3600 | 2780.07 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281010.61 | GGB | 281013.16 | 2441.8943 | 2441.8943 |  |  |  | 1 | 1 |  |  |  |  | 128258.6 | 2441.8943 | 128258.6 | 2441.8943 | 8.4215 |  | 2796 | -339 | 2457 | 2441.8943 | 86.9983 |  |  | #VALUE!
08.07.2008 07:00 | 3600 | 2 | 767.33 | GGB | 764.835 | 778.289 | 769.963 | 259.9 | GGB | 10585.3 | GGB | 9.81 | GGB | 996.79 | GGB | 67.51 | GGB | 162153.47 | GGB | 127925.97 | GGB | 0 | 0 | 2773 | 3600 | 2757.87 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281047.8 | GGB | 281050.35 | 2418.9131 | 2418.9131 |  |  |  | 1 | 1 |  |  |  |  | 127925.97 | 2418.9131 | 127925.97 | 2418.9131 | 8.3206 |  | 2773 | -339 | 2434 | 2418.9131 | 85.9561 |  |  | #VALUE!
08.07.2008 08:00 | 3600 | 2 | 766.72 | GGB | 765.934 | 779.18 | 770.33 | 259.33 | GGB | 10564.8 | GGB | 9.81 | GGB | 996.21 | GGB | 67.55 | GGB | 161635.21 | GGB | 127425.33 | GGB | 0 | 0 | 2810 | 3600 | 2794.18 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281084.99 | GGB | 281087.54 | 2455.8829 | 2455.8829 |  |  |  | 0 | 1 | [10 empty] | 2810 | -339 | 2471 | 2455.8829 | 86.9282 |  |  | #VALUE!
08.07.2008 09:00 | 3600 | 2 | 766.4 | GGB | 764.835 | 778.313 | 768.864 | 259.64 | GGB | 10563.2 | GGB | 9.8 | GGB | 996.31 | GGB | 67.17 | GGB | 161779.36 | GGB | 127696.63 | GGB | 0 | 0 | 2829 | 3600 | 2813.48 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281122.18 | GGB | 281124.73 | 2474.8673 | 2474.8673 |  |  |  | 1 | 1 |  |  |  |  | 127696.63 | 2474.8673 | 127696.63 | 2474.8673 | 8.4978 |  | 2829 | -339 | 2490 | 2474.8673 | 87.7867 |  |  | #VALUE!
08.07.2008 10:00 | 3600 | 2 | 765.35 | GGB | 768.132 | 780.797 | 772.527 | 261.48 | GGB | 10612.3 | GGB | 9.78 | GGB | 996.55 | GGB | 65.08 | GGB | 164202.3 | GGB | 130440.94 | GGB | 0 | 0 | 2909 | 3600 | 2893.3 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281159.37 | GGB | 281161.92 | 2554.802 | 2554.802 |  |  |  | 0 | 1 | [10 empty] | 2909 | -339 | 2570 | 2554.802 | 92.5697 |  |  | #VALUE!
08.07.2008 11:00 | 3600 | 2 | 767.43 | GGB | 765.934 | 778.688 | 771.429 | 260.68 | GGB | 10663.9 | GGB | 9.82 | GGB | 996.78 | GGB | 66.47 | GGB | 163643.33 | GGB | 129493.97 | GGB | 0 | 0 | 2788 | 3600 | 2772.45 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281196.56 | GGB | 281199.11 | 2433.9008 | 2433.9008 |  |  |  | 1 | 1 |  |  |  |  | 129493.97 | 2433.9008 | 129493.97 | 2433.9008 | 8.4747 |  | 2788 | -339 | 2449 | 2433.9008 | 87.5487 |  |  | #VALUE!
08.07.2008 12:00 | 3600 | 2 | 766.47 | GGB | 768.132 | 780.867 | 773.626 | 262.3 | GGB | 10612.1 | GGB | 9.8 | GGB | 996.92 | GGB | 66.18 | GGB | 165682.26 | GGB | 131236.56 | GGB | 0 | 0 | 2825 | 3600 | 2809.47 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281233.75 | GGB | 281236.3 | 2470.8706 | 2470.8706 |  |  |  | 0 | 1 | [10 empty] | 2825 | -339 | 2486 | 2470.8706 | 90.0746 |  |  | #VALUE!
08.07.2008 13:00 | 3600 | 2 | 768.24 | GGB | 765.934 | 778.758 | 771.429 | 259.1 | GGB | 10578.3 | GGB | 9.82 | GGB | 996.35 | GGB | 66.97 | GGB | 162976.53 | GGB | 128720.01 | GGB | 0 | 0 | 2866 | 2832 | 2850.31 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281270.94 | GGB | 281273.49 | 2511.8371 | 2511.8371 |  |  |  | 0 | 1 | [10 empty] | 2866 | -339 | 2527 | 2511.8371 | 89.8121 |  |  | #VALUE!
08.07.2008 14:00 | 3600 | 2 | 768.33 | GGB | 767.033 | 779.766 | 771.429 | 256.56 | GGB | 10507 | GGB | 9.82 | GGB | 995.69 | GGB | 67.55 | GGB | 161059.74 | GGB | 126908.07 | GGB | 0 | 0 | 2844 | 3600 | 2828.04 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281308.13 | GGB | 281310.68 | 2489.8551 | 2489.8551 |  |  |  | 0 | 1 | [10 empty] | 2844 | -339 | 2505 | 2489.8551 | 87.773 |  |  | #VALUE!
08.07.2008 15:00 | 3600 | 2 | 767.77 | GGB | 765.934 | 778.734 | 771.429 | 256.45 | GGB | 10465.3 | GGB | 9.8 | GGB | 995.52 | GGB | 67.42 | GGB | 161033.33 | GGB | 126912.68 | GGB | 0 | 0 | 2862 | 3600 | 2846.92 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281345.32 | GGB | 281347.87 | 2507.8404 | 2507.8404 |  |  |  | 0 | 1 | [10 empty] | 2862 | -339 | 2523 | 2507.8404 | 88.4102 |  |  | #VALUE!
08.07.2008 16:00 | 3600 | 2 | 767.18 | GGB | 767.033 | 779.977 | 771.795 | 259.22 | GGB | 10527.8 | GGB | 9.8 | GGB | 996.85 | GGB | 66.03 | GGB | 163657.64 | GGB | 129683.45 | GGB | 0 | 0 | 2924 | 3600 | 2908.09 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281382.51 | GGB | 281385.06 | 2569.7898 | 2569.7898 |  |  |  | 0 | 1 | [10 empty] | 2924 | -339 | 2585 | 2569.7898 | 92.572 |  |  | #VALUE!
08.07.2008 17:00 | 3600 | 2 | 767.9 | GGB | 768.498 | 782.109 | 773.26 | 258.36 | GGB | 10561.1 | GGB | 9.82 | GGB | 996.8 | GGB | 67.51 | GGB | 161999.43 | GGB | 127802.9 | GGB | 0 | 0 | 2917 | 3600 | 2901.45 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281419.7 | GGB | 281422.25 | 2562.7955 | 2562.7955 |  |  |  | 0 | 1 | [10 empty] | 2917 | -339 | 2578 | 2562.7955 | 90.9813 |  |  | #VALUE!
08.07.2008 18:00 | 3600 | 2 | 768.31 | GGB | 765.934 | 778.945 | 770.696 | 256.88 | GGB | 10448.2 | GGB | 9.8 | GGB | 996.75 | GGB | 67.94 | GGB | 160873.78 | GGB | 126751.43 | GGB | 0 | 0 | 2848 | 3600 | 2832.41 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281456.89 | GGB | 281459.44 | 2493.8518 | 2493.8518 |  |  |  | 0 | 1 | [10 empty] | 2848 | -339 | 2509 | 2493.8518 | 87.8054 |  |  | #VALUE!
08.07.2008 19:00 | 3600 | 2 | 767.15 | GGB | 763.37 | 776.742 | 767.033 | 257.04 | GGB | 10479.3 | GGB | 9.79 | GGB | 997.14 | GGB | 66.84 | GGB | 160793.46 | GGB | 127147.94 | GGB | 0 | 0 | 2902 | 3600 | 2886.63 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281494.08 | GGB | 281496.63 | 2547.8078 | 2547.8078 |  |  |  | 0 | 1 | [10 empty] | 2902 | -339 | 2563 | 2547.8078 | 89.9857 |  |  | #VALUE!
08.07.2008 20:00 | 3600 | 2 | 768.34 | GGB | 765.934 | 778.875 | 770.696 | 258.27 | GGB | 10483.7 | GGB | 9.82 | GGB | 997.42 | GGB | 67.87 | GGB | 161434.95 | GGB | 127304.26 | GGB | 0 | 0 | 2880 | 3600 | 2863.99 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281531.27 | GGB | 281533.82 | 2525.8257 | 2525.8257 |  |  |  | 0 | 1 | [10 empty] | 2880 | -339 | 2541 | 2525.8257 | 89.319 |  |  | #VALUE!
08.07.2008 21:00 | 3600 | 2 | 767.12 | GGB | 767.033 | 779.648 | 771.795 | 257.94 | GGB | 10472.8 | GGB | 9.79 | GGB | 997.29 | GGB | 68.54 | GGB | 160487.56 | GGB | 126291.77 | GGB | 0 | 0 | 2946 | 3600 | 2930.16 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281568.46 | GGB | 281571.01 | 2591.7718 | 2591.7718 |  |  |  | 0 | 1 | [10 empty] | 2946 | -339 | 2607 | 2591.7718 | 90.9221 |  |  | #VALUE!
08.07.2008 22:00 | 3600 | 2 | 767.33 | GGB | 764.835 | 777.516 | 768.498 | 258.67 | GGB | 10514.9 | GGB | 9.8 | GGB | 997.81 | GGB | 68.2 | GGB | 161212.68 | GGB | 127057.13 | GGB | 0 | 0 | 2938 | 3600 | 2922.54 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281605.65 | GGB | 281608.2 | 2583.7784 | 2583.7784 |  |  |  | 1 | 1 |  |  |  |  | 127057.13 | 2583.7784 | 127057.13 | 2583.7784 | 8.8273 |  | 2938 | -339 | 2599 | 2583.7784 | 91.191 |  |  | #VALUE!
08.07.2008 23:00 | 3600 | 2 | 766.41 | GGB | 764.835 | 778.758 | 769.597 | 260.72 | GGB | 10566.9 | GGB | 9.79 | GGB | 998.37 | GGB | 67.41 | GGB | 163055.75 | GGB | 128877.03 | GGB | 0 | 0 | 3018 | 3600 | 3002.23 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281642.84 | GGB | 281645.39 | 2663.7131 | 2663.7131 |  |  |  | 0 | 1 | [10 empty] | 3018 | -339 | 2679 | 2663.7131 | 95.3587 |  |  | #VALUE!
08.07.2008 24:00 | 3600 | 2 | 767.04 | GGB | 763.37 | 776.555 | 768.498 | 260.84 | GGB | 10624.8 | GGB | 9.8 | GGB | 999.36 | GGB | 66.94 | GGB | 164160.49 | GGB | 130058.21 | GGB | 0 | 0 | 2993 | 3600 | 2976.87 | GGB | 100 | GGB | 37.19 | GGB | 37.19 | GGB | 281680.03 | GGB | 281682.58 | 2638.7335 | 2638.7335 |  |  |  | 0 | 1 | [10 empty] | 2993 | -339 | 2654 | 2638.7335 | 95.3303 |  |  | #VALUE!
09.07.2008 01:00 | 3600 | 2 | 766.82 | GGB | 764.835 | 777.75 | 769.597 | 262.16 | GGB | 10657 | GGB | 9.8 | GGB | 999.42 | GGB | 66.52 | GGB | 164891.11 | GGB | 130805.94 | GGB | 0 | 0 | 3004 | 3600 | 2988.36 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281718.31 | GGB | 281720.86 | 2649.7245 | 2649.7245 |  |  |  | 1 | 1 |  |  |  |  | 130805.94 | 2649.7245 | 130805.94 | 2649.7245 | 9.0543 |  | 3004 | -339 | 2665 | 2649.7245 | 96.2777 |  |  | #VALUE!
09.07.2008 02:00 | 3600 | 2 | 766.27 | GGB | 764.835 | 777.563 | 769.597 | 263.45 | GGB | 10705 | GGB | 9.8 | GGB | 1000.31 | GGB | 65.93 | GGB | 166374.37 | GGB | 132332.21 | GGB | 0 | 0 | 3055 | 3600 | 3039.36 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281756.59 | GGB | 281759.14 | 2700.6829 | 2700.6829 |  |  |  | 1 | 1 |  |  |  |  | 132332.21 | 2700.6829 | 132332.21 | 2700.6829 | 9.3361 |  | 3055 | -339 | 2716 | 2700.6829 | 99.2743 |  |  | #VALUE!
09.07.2008 03:00 | 3600 | 2 | 765.99 | GGB | 765.934 | 777.727 | 769.597 | 265.09 | GGB | 10710.7 | GGB | 9.8 | GGB | 1000.98 | GGB | 64.92 | GGB | 168495.82 | GGB | 134511.72 | GGB | 0 | 0 | 3050 | 3600 | 3033.95 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281794.87 | GGB | 281797.42 | 2695.6869 | 2695.6869 |  |  |  | 1 | 1 |  |  |  |  | 134511.72 | 2695.6869 | 134511.72 | 2695.6869 | 9.4723 |  | 3050 | -339 | 2711 | 2695.6869 | 100.7226 |  |  | #VALUE!
09.07.2008 04:00 | 3600 | 2 | 766.54 | GGB | 765.934 | 778.781 | 770.696 | 264.71 | GGB | 10775 | GGB | 9.81 | GGB | 1001.3 | GGB | 65.23 | GGB | 167701.38 | GGB | 133796.99 | GGB | 0 | 0 | 3051 | 3600 | 3034.94 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281833.15 | GGB | 281835.7 | 2696.6861 | 2696.6861 |  |  |  | 0 | 1 | [10 empty] | 3051 | -339 | 2712 | 2696.6861 | 100.2246 |  |  | #VALUE!
09.07.2008 05:00 | 3600 | 2 | 766.08 | GGB | 764.469 | 777.609 | 769.597 | 265.23 | GGB | 10790.7 | GGB | 9.8 | GGB | 1001.48 | GGB | 65.13 | GGB | 168504.62 | GGB | 134502.29 | GGB | 0 | 0 | 3096 | 3600 | 3080.66 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281871.43 | GGB | 281873.98 | 2741.6494 | 2741.6494 |  |  |  | 1 | 1 |  |  |  |  | 134502.29 | 2741.6494 | 134502.29 | 2741.6494 | 9.6332 |  | 3096 | -339 | 2757 | 2741.6494 | 102.4328 |  |  | #VALUE!
09.07.2008 06:00 | 3600 | 2 | 765.75 | GGB | 765.934 | 777.844 | 769.597 | 266.64 | GGB | 10790.4 | GGB | 9.8 | GGB | 1001.84 | GGB | 64.53 | GGB | 170092.41 | GGB | 136057.38 | GGB | 0 | 0 | 3107 | 3600 | 3090.9 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281909.71 | GGB | 281912.26 | 2752.6404 | 2752.6404 |  |  |  | 1 | 1 |  |  |  |  | 136057.38 | 2752.6404 | 136057.38 | 2752.6404 | 9.7836 |  | 3107 | -339 | 2768 | 2752.6404 | 104.0325 |  |  | #VALUE!
09.07.2008 07:00 | 3600 | 2 | 767.12 | GGB | 765.934 | 778.078 | 770.696 | 266.08 | GGB | 10818.1 | GGB | 9.82 | GGB | 1001.95 | GGB | 64.58 | GGB | 169431.11 | GGB | 135524.46 | GGB | 0 | 0 | 3044 | 3600 | 3027.85 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281947.99 | GGB | 281950.54 | 2689.6918 | 2689.6918 |  |  |  | 1 | 1 |  |  |  |  | 135524.46 | 2689.6918 | 135524.46 | 2689.6918 | 9.5224 |  | 3044 | -339 | 2705 | 2689.6918 | 101.2553 |  |  | #VALUE!
09.07.2008 08:00 | 3600 | 2 | 767.2 | GGB | 765.934 | 778.148 | 770.696 | 264.18 | GGB | 10785.2 | GGB | 9.82 | GGB | 1001.86 | GGB | 65.34 | GGB | 167227.13 | GGB | 133449.52 | GGB | 0 | 0 | 3034 | 3600 | 3018.69 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 281986.27 | GGB | 281988.82 | 2679.7 | 2679.7 |  |  |  | 1 | 1 |  |  |  |  | 133449.52 | 2679.7 | 133449.52 | 2679.7 | 9.3418 |  | 3034 | -339 | 2695 | 2679.7 | 99.3346 |  |  | #VALUE!
09.07.2008 09:00 | 3600 | 2 | 767.61 | GGB | 765.934 | 779.273 | 770.696 | 262.73 | GGB | 10724.8 | GGB | 9.82 | GGB | 1001.75 | GGB | 66.02 | GGB | 165483.1 | GGB | 131777.79 | GGB | 0 | 0 | 2989 | 3600 | 2973.81 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282024.55 | GGB | 282027.1 | 2634.7367 | 2634.7367 |  |  |  | 0 | 1 | [10 empty] | 2989 | -339 | 2650 | 2634.7367 | 96.4444 |  |  | #VALUE!
09.07.2008 10:00 | 3600 | 2 | 768.02 | GGB | 767.033 | 779.18 | 771.795 | 260.78 | GGB | 10642.4 | GGB | 9.82 | GGB | 1001.31 | GGB | 66.91 | GGB | 163534.4 | GGB | 129827.76 | GGB | 0 | 0 | 2930 | 3600 | 2914.76 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282062.83 | GGB | 282065.38 | 2575.7849 | 2575.7849 |  |  |  | 0 | 1 | [10 empty] | 2930 | -339 | 2591 | 2575.7849 | 92.8912 |  |  | #VALUE!
09.07.2008 11:00 | 3600 | 2 | 768.69 | GGB | 768.132 | 781.664 | 773.26 | 260.93 | GGB | 10542 | GGB | 9.81 | GGB | 1000.63 | GGB | 66.74 | GGB | 164357.45 | GGB | 130457.6 | GGB | 0 | 0 | 2879 | 3600 | 2863.03 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282101.11 | GGB | 282103.66 | 2524.8265 | 2524.8265 |  |  |  | 0 | 1 | [10 empty] | 2879 | -339 | 2540 | 2524.8265 | 91.4952 |  |  | #VALUE!
09.07.2008 12:00 | 3600 | 2 | 768.67 | GGB | 764.835 | 778.828 | 768.498 | 259.61 | GGB | 10486 | GGB | 9.8 | GGB | 999.83 | GGB | 66.98 | GGB | 163462.88 | GGB | 129554.88 | GGB | 0 | 0 | 2862 | 3600 | 2846.1 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282139.39 | GGB | 282141.94 | 2507.8404 | 2507.8404 |  |  |  | 0 | 1 | [10 empty] | 2862 | -339 | 2523 | 2507.8404 | 90.2508 |  |  | #VALUE!
09.07.2008 13:00 | 3600 | 2 | 768.93 | GGB | 765.934 | 779.016 | 770.696 | 257.9 | GGB | 10517.8 | GGB | 9.82 | GGB | 999.47 | GGB | 67.33 | GGB | 161539.48 | GGB | 127848.56 | GGB | 0 | 0 | 2847 | 3600 | 2831.06 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282177.67 | GGB | 282180.22 | 2492.8527 | 2492.8527 |  |  |  | 0 | 1 | [10 empty] | 2847 | -339 | 2508 | 2492.8527 | 88.5299 |  |  | #VALUE!
09.07.2008 14:00 | 3600 | 2 | 769.36 | GGB | 767.033 | 781.219 | 772.161 | 257.01 | GGB | 10463.5 | GGB | 9.82 | GGB | 998.73 | GGB | 67.7 | GGB | 160869.38 | GGB | 127089.25 | GGB | 0 | 0 | 2800 | 3600 | 2784.68 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282215.95 | GGB | 282218.5 | 2445.891 | 2445.891 |  |  |  | 0 | 1 | [10 empty] | 2800 | -339 | 2461 | 2445.891 | 86.3462 |  |  | #VALUE!
09.07.2008 15:00 | 3600 | 2 | 769.36 | GGB | 768.132 | 781.453 | 773.26 | 256.72 | GGB | 10395.1 | GGB | 9.81 | GGB | 997.82 | GGB | 67.33 | GGB | 161337.02 | GGB | 127478.68 | GGB | 0 | 0 | 2765 | 3600 | 2749.56 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282254.23 | GGB | 282256.78 | 2410.9196 | 2410.9196 |  |  |  | 0 | 1 | [10 empty] | 2765 | -339 | 2426 | 2410.9196 | 85.3725 |  |  | #VALUE!
09.07.2008 16:00 | 3600 | 2 | 768.58 | GGB | 764.835 | 779.086 | 769.597 | 255.11 | GGB | 10395.7 | GGB | 9.8 | GGB | 997.16 | GGB | 67.92 | GGB | 159567.68 | GGB | 125779.38 | GGB | 0 | 0 | 2787 | 3600 | 2771.54 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282292.51 | GGB | 282295.06 | 2432.9016 | 2432.9016 |  |  |  | 0 | 1 | [10 empty] | 2787 | -339 | 2448 | 2432.9016 | 85.0025 |  |  | #VALUE!
09.07.2008 17:00 | 3600 | 2 | 768.05 | GGB | 768.498 | 782.297 | 774.359 | 258.52 | GGB | 10474.3 | GGB | 9.8 | GGB | 998.06 | GGB | 66.57 | GGB | 162738.85 | GGB | 128907.47 | GGB | 0 | 0 | 2880 | 3600 | 2864.13 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282330.79 | GGB | 282333.34 | 2525.8257 | 2525.8257 |  |  |  | 0 | 1 | [10 empty] | 2880 | -339 | 2541 | 2525.8257 | 90.4438 |  |  | #VALUE!
09.07.2008 18:00 | 3600 | 2 | 768.31 | GGB | 767.033 | 780.469 | 772.161 | 258.89 | GGB | 10507.7 | GGB | 9.8 | GGB | 998.35 | GGB | 66.65 | GGB | 162775.16 | GGB | 128941.35 | GGB | 0 | 0 | 2870 | 3600 | 2853.95 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282369.07 | GGB | 282371.62 | 2515.8339 | 2515.8339 |  |  |  | 0 | 1 | [10 empty] | 2870 | -339 | 2531 | 2515.8339 | 90.1097 |  |  | #VALUE!
09.07.2008 19:00 | 3600 | 2 | 767.09 | GGB | 764.835 | 778.406 | 769.597 | 259.54 | GGB | 10529.8 | GGB | 9.79 | GGB | 998.84 | GGB | 66.82 | GGB | 162760.86 | GGB | 128930.29 | GGB | 0 | 0 | 2933 | 3600 | 2917.67 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282407.35 | GGB | 282409.9 | 2578.7824 | 2578.7824 |  |  |  | 1 | 1 |  |  |  |  | 128930.29 | 2578.7824 | 128930.29 | 2578.7824 | 8.6856 |  | 2933 | -339 | 2594 | 2578.7824 | 92.3564 |  |  | #VALUE!
09.07.2008 20:00 | 3600 | 2 | 768.44 | GGB | 765.934 | 779.742 | 770.696 | 258.73 | GGB | 10557.4 | GGB | 9.82 | GGB | 999.27 | GGB | 67.42 | GGB | 161420.65 | GGB | 127697.91 | GGB | 0 | 0 | 2890 | 3600 | 2874.92 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282445.63 | GGB | 282448.18 | 2535.8176 | 2535.8176 |  |  |  | 0 | 1 | [10 empty] | 2890 | -339 | 2551 | 2535.8176 | 89.9496 |  |  | #VALUE!
09.07.2008 21:00 | 3600 | 2 | 767.28 | GGB | 768.498 | 781.734 | 773.26 | 258.6 | GGB | 10521.7 | GGB | 9.8 | GGB | 999.31 | GGB | 67.26 | GGB | 161193.98 | GGB | 127583.4 | GGB | 0 | 0 | 2916 | 3600 | 2900.38 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282483.91 | GGB | 282486.46 | 2561.7963 | 2561.7963 |  |  |  | 0 | 1 | [10 empty] | 2916 | -339 | 2577 | 2561.7963 | 90.7896 |  |  | #VALUE!
09.07.2008 22:00 | 3600 | 2 | 766.93 | GGB | 765.934 | 778.805 | 770.696 | 261.14 | GGB | 10519.5 | GGB | 9.78 | GGB | 999.64 | GGB | 66.24 | GGB | 164184.7 | GGB | 130383.35 | GGB | 0 | 0 | 2944 | 3600 | 2927.96 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282522.19 | GGB | 282524.74 | 2589.7735 | 2589.7735 |  |  |  | 0 | 1 | [10 empty] | 2944 | -339 | 2605 | 2589.7735 | 93.7954 |  |  | #VALUE!
09.07.2008 23:00 | 3600 | 2 | 767.67 | GGB | 764.835 | 777.867 | 768.498 | 260.73 | GGB | 10621.8 | GGB | 9.81 | GGB | 1000.11 | GGB | 66.56 | GGB | 163399.06 | GGB | 129698.81 | GGB | 0 | 0 | 2939 | 3600 | 2922.93 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282560.47 | GGB | 282563.02 | 2584.7776 | 2584.7776 |  |  |  | 1 | 1 |  |  |  |  | 129698.81 | 2584.7776 | 129698.81 | 2584.7776 | 8.7576 |  | 2939 | -339 | 2600 | 2584.7776 | 93.1229 |  |  | #VALUE!
09.07.2008 24:00 | 3600 | 2 | 766.63 | GGB | 763.37 | 776.555 | 768.498 | 261.41 | GGB | 10665.5 | GGB | 9.8 | GGB | 1000.9 | GGB | 65.83 | GGB | 164850.4 | GGB | 131234.6 | GGB | 0 | 0 | 3002 | 3600 | 2986.1 | GGB | 100 | GGB | 38.28 | GGB | 38.28 | GGB | 282598.75 | GGB | 282601.3 | 2647.7261 | 2647.7261 |  |  |  | 0 | 1 | [10 empty] | 3002 | -339 | 2663 | 2647.7261 | 96.5204 |  |  | #VALUE!
10.07.2008 01:00 | 3600 | 2 | 766.38 | GGB | 763.37 | 776.602 | 768.498 | 263 | GGB | 10685.1 | GGB | 9.79 | GGB | 1001.43 | GGB | 65.97 | GGB | 165424.78 | GGB | 131706.99 | GGB | 0 | 0 | 3041 | 3600 | 3025.12 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282637.89 | GGB | 282640.44 | 2686.6943 | 2686.6943 |  |  |  | 0 | 1 | [10 empty] | 3041 | -339 | 2702 | 2686.6943 | 98.2934 |  |  | #VALUE!
10.07.2008 02:00 | 3600 | 2 | 767.1 | GGB | 765.934 | 778.594 | 770.696 | 263.32 | GGB | 10731 | GGB | 9.81 | GGB | 1001.7 | GGB | 65.53 | GGB | 166045.37 | GGB | 132408.21 | GGB | 0 | 0 | 3004 | 3600 | 2987.92 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282677.03 | GGB | 282679.58 | 2649.7245 | 2649.7245 |  |  |  | 1 | 1 |  |  |  |  | 132408.21 | 2649.7245 | 132408.21 | 2649.7245 | 8.9639 |  | 3004 | -339 | 2665 | 2649.7245 | 97.457 |  |  | #VALUE!
10.07.2008 03:00 | 3600 | 2 | 767 | GGB | 767.033 | 779.602 | 771.795 | 264.4 | GGB | 10725.7 | GGB | 9.81 | GGB | 1002.14 | GGB | 64.65 | GGB | 167679.37 | GGB | 134120.19 | GGB | 0 | 0 | 2998 | 3600 | 2982.69 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282716.17 | GGB | 282718.72 | 2643.7294 | 2643.7294 |  |  |  | 0 | 1 | [10 empty] | 2998 | -339 | 2659 | 2643.7294 | 98.4937 |  |  | #VALUE!
10.07.2008 04:00 | 3600 | 2 | 766.12 | GGB | 762.271 | 775.688 | 767.766 | 264 | GGB | 10745.4 | GGB | 9.79 | GGB | 1002.9 | GGB | 64.83 | GGB | 167104.99 | GGB | 133689.93 | GGB | 0 | 0 | 3040 | 3600 | 3023.93 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282755.31 | GGB | 282757.86 | 2685.6951 | 2685.6951 |  |  |  | 0 | 1 | [10 empty] | 3040 | -339 | 2701 | 2685.6951 | 99.7362 |  |  | #VALUE!
10.07.2008 05:00 | 3600 | 2 | 766.6 | GGB | 763.37 | 776.602 | 767.766 | 264.67 | GGB | 10785.2 | GGB | 9.8 | GGB | 1003.19 | GGB | 64.77 | GGB | 167803.71 | GGB | 134311.72 | GGB | 0 | 0 | 3042 | 3600 | 3025.82 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282794.45 | GGB | 282797 | 2687.6935 | 2687.6935 |  |  |  | 0 | 1 | [10 empty] | 3042 | -339 | 2703 | 2687.6935 | 100.2746 |  |  | #VALUE!
10.07.2008 06:00 | 3600 | 2 | 766.59 | GGB | 765.934 | 777.727 | 769.963 | 266.14 | GGB | 10784.7 | GGB | 9.81 | GGB | 1003.64 | GGB | 64.38 | GGB | 169523.54 | GGB | 135906.72 | GGB | 0 | 0 | 3062 | 3600 | 3046.41 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282833.59 | GGB | 282836.14 | 2707.6771 | 2707.6771 |  |  |  | 1 | 1 |  |  |  |  | 135906.72 | 2707.6771 | 135906.72 | 2707.6771 | 9.4019 |  | 3062 | -339 | 2723 | 2707.6771 | 102.2199 |  |  | #VALUE!
10.07.2008 07:00 | 3600 | 2 | 766.58 | GGB | 764.835 | 776.813 | 769.963 | 264.92 | GGB | 10806 | GGB | 9.81 | GGB | 1003.78 | GGB | 64.69 | GGB | 167962.16 | GGB | 134549.43 | GGB | 0 | 0 | 3042 | 3600 | 3026.22 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282872.74 | GGB | 282875.28 | 2687.6935 | 2687.6935 |  |  |  | 1 | 1 |  |  |  |  | 134549.43 | 2687.6935 | 134549.43 | 2687.6935 | 9.2393 |  | 3042 | -339 | 2703 | 2687.6935 | 100.4521 |  |  | #VALUE!
10.07.2008 08:00 | 3600 | 2 | 766.86 | GGB | 765.934 | 777.984 | 769.963 | 264.08 | GGB | 10786.3 | GGB | 9.81 | GGB | 1004.05 | GGB | 64.94 | GGB | 167109.39 | GGB | 133802.34 | GGB | 0 | 0 | 3024 | 3600 | 3008.2 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282911.88 | GGB | 282914.42 | 2669.7082 | 2669.7082 |  |  |  | 1 | 1 |  |  |  |  | 133802.34 | 2669.7082 | 133802.34 | 2669.7082 | 9.1266 |  | 3024 | -339 | 2685 | 2669.7082 | 99.2259 |  |  | #VALUE!
10.07.2008 09:00 | 3600 | 2 | 767.17 | GGB | 764.835 | 777.727 | 768.864 | 263.38 | GGB | 10742.1 | GGB | 9.82 | GGB | 1004.05 | GGB | 64.97 | GGB | 166342.46 | GGB | 133178.06 | GGB | 0 | 0 | 2984 | 3600 | 2968.81 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282951.02 | GGB | 282953.56 | 2629.7408 | 2629.7408 |  |  |  | 1 | 1 |  |  |  |  | 133178.06 | 2629.7408 | 133178.06 | 2629.7408 | 8.948 |  | 2984 | -339 | 2645 | 2629.7408 | 97.2844 |  |  | #VALUE!
10.07.2008 10:00 | 3600 | 2 | 767.89 | GGB | 768.132 | 781.148 | 772.527 | 262.81 | GGB | 10665.2 | GGB | 9.82 | GGB | 1004.09 | GGB | 64.9 | GGB | 166284.14 | GGB | 133165.36 | GGB | 0 | 0 | 2914 | 3600 | 2897.99 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 282990.16 | GGB | 282992.7 | 2559.798 | 2559.798 |  |  |  | 0 | 1 | [10 empty] | 2914 | -339 | 2575 | 2559.798 | 94.6879 |  |  | #VALUE!
10.07.2008 11:00 | 3600 | 2 | 767.58 | GGB | 764.835 | 777.469 | 769.963 | 260.43 | GGB | 10631.3 | GGB | 9.81 | GGB | 1003.55 | GGB | 66.31 | GGB | 163509.09 | GGB | 130328.21 | GGB | 0 | 0 | 2931 | 3600 | 2915.43 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283029.3 | GGB | 283031.84 | 2576.7841 | 2576.7841 |  |  |  | 1 | 1 |  |  |  |  | 130328.21 | 2576.7841 | 130328.21 | 2576.7841 | 8.5802 |  | 2931 | -339 | 2592 | 2576.7841 | 93.2855 |  |  | #VALUE!
10.07.2008 12:00 | 3600 | 2 | 768.42 | GGB | 765.934 | 778.781 | 771.429 | 259.26 | GGB | 10597.8 | GGB | 9.82 | GGB | 1003.22 | GGB | 66.71 | GGB | 162585.91 | GGB | 129395.84 | GGB | 0 | 0 | 2876 | 3600 | 2860.8 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283068.44 | GGB | 283070.98 | 2521.829 | 2521.829 |  |  |  | 0 | 1 | [10 empty] | 2876 | -339 | 2537 | 2521.829 | 90.6428 |  |  | #VALUE!
10.07.2008 13:00 | 3600 | 2 | 768.24 | GGB | 765.934 | 778.594 | 770.33 | 258.26 | GGB | 10548.5 | GGB | 9.81 | GGB | 1003.53 | GGB | 67.05 | GGB | 161949.91 | GGB | 128801.6 | GGB | 0 | 0 | 2871 | 3600 | 2855.06 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283107.58 | GGB | 283110.12 | 2516.8331 | 2516.8331 |  |  |  | 1 | 1 |  |  |  |  | 128801.6 | 2516.8331 | 128801.6 | 2516.8331 | 8.2824 |  | 2871 | -339 | 2532 | 2516.8331 | 90.0478 |  |  | #VALUE!
10.07.2008 14:00 | 3600 | 2 | 768.74 | GGB | 767.033 | 780.258 | 771.429 | 257.53 | GGB | 10519.5 | GGB | 9.81 | GGB | 1003.06 | GGB | 67.45 | GGB | 161478.97 | GGB | 128215.77 | GGB | 0 | 0 | 2840 | 3600 | 2824.74 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283146.73 | GGB | 283149.26 | 2485.8584 | 2485.8584 |  |  |  | 0 | 1 | [10 empty] | 2840 | -339 | 2501 | 2485.8584 | 88.5351 |  |  | #VALUE!
10.07.2008 15:00 | 3600 | 2 | 768.7 | GGB | 767.033 | 780.352 | 772.527 | 256.72 | GGB | 10493.6 | GGB | 9.81 | GGB | 1002.58 | GGB | 67.37 | GGB | 160757.14 | GGB | 127610.82 | GGB | 0 | 0 | 2799 | 3600 | 2783.39 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283185.87 | GGB | 283188.4 | 2444.8918 | 2444.8918 |  |  |  | 0 | 1 | [10 empty] | 2799 | -339 | 2460 | 2444.8918 | 86.6652 |  |  | #VALUE!
10.07.2008 16:00 | 3600 | 2 | 768.78 | GGB | 765.934 | 779.297 | 771.429 | 256.26 | GGB | 10465.9 | GGB | 9.81 | GGB | 1002.26 | GGB | 67.65 | GGB | 160190.47 | GGB | 127017.15 | GGB | 0 | 0 | 2791 | 3600 | 2775.25 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283225.01 | GGB | 283227.54 | 2436.8984 | 2436.8984 |  |  |  | 0 | 1 | [10 empty] | 2791 | -339 | 2452 | 2436.8984 | 85.98 |  |  | #VALUE!
10.07.2008 17:00 | 3600 | 2 | 769.22 | GGB | 767.033 | 780.141 | 771.429 | 255.59 | GGB | 10442 | GGB | 9.81 | GGB | 1002.01 | GGB | 68.24 | GGB | 159456.55 | GGB | 126185.47 | GGB | 0 | 0 | 2777 | 3600 | 2761.59 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283264.15 | GGB | 283266.68 | 2422.9098 | 2422.9098 |  |  |  | 0 | 1 | [10 empty] | 2777 | -339 | 2438 | 2422.9098 | 84.9267 |  |  | #VALUE!
10.07.2008 18:00 | 3600 | 2 | 769.25 | GGB | 768.132 | 782.156 | 773.626 | 254.96 | GGB | 10416.9 | GGB | 9.81 | GGB | 1001.61 | GGB | 68.5 | GGB | 159002.11 | GGB | 125678.16 | GGB | 0 | 0 | 2784 | 3600 | 2768.16 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283303.29 | GGB | 283305.82 | 2429.9041 | 2429.9041 |  |  |  | 0 | 1 | [10 empty] | 2784 | -339 | 2445 | 2429.9041 | 84.8294 |  |  | #VALUE!
10.07.2008 19:00 | 3600 | 2 | 768.73 | GGB | 767.033 | 781.031 | 771.429 | 256.14 | GGB | 10403.7 | GGB | 9.8 | GGB | 1001.55 | GGB | 67.84 | GGB | 160063.93 | GGB | 126756.14 | GGB | 0 | 0 | 2775 | 3600 | 2759.34 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283342.43 | GGB | 283344.96 | 2420.9114 | 2420.9114 |  |  |  | 0 | 1 | [10 empty] | 2775 | -339 | 2436 | 2420.9114 | 85.2404 |  |  | #VALUE!
10.07.2008 20:00 | 3600 | 2 | 769.08 | GGB | 767.033 | 780.984 | 772.527 | 256.5 | GGB | 10417.4 | GGB | 9.8 | GGB | 1001.95 | GGB | 67.66 | GGB | 160317.01 | GGB | 127075.33 | GGB | 0 | 0 | 2773 | 3600 | 2757.77 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283381.58 | GGB | 283384.1 | 2418.9131 | 2418.9131 |  |  |  | 0 | 1 | [10 empty] | 2773 | -339 | 2434 | 2418.9131 | 85.3845 |  |  | #VALUE!
10.07.2008 21:00 | 3600 | 2 | 768.27 | GGB | 765.934 | 779.953 | 771.429 | 256.84 | GGB | 10461.9 | GGB | 9.8 | GGB | 1002.49 | GGB | 67.95 | GGB | 159995.71 | GGB | 126780.5 | GGB | 0 | 0 | 2827 | 3600 | 2811.74 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283420.72 | GGB | 283423.24 | 2472.869 | 2472.869 |  |  |  | 0 | 1 | [10 empty] | 2827 | -339 | 2488 | 2472.869 | 87.0865 |  |  | #VALUE!
10.07.2008 22:00 | 3600 | 2 | 768.01 | GGB | 765.934 | 778.828 | 771.429 | 257.91 | GGB | 10497 | GGB | 9.8 | GGB | 1003.62 | GGB | 67.7 | GGB | 160682.32 | GGB | 127562.79 | GGB | 0 | 0 | 2878 | 3600 | 2862.35 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283459.86 | GGB | 283462.38 | 2523.8273 | 2523.8273 |  |  |  | 0 | 1 | [10 empty] | 2878 | -339 | 2539 | 2523.8273 | 89.4296 |  |  | #VALUE!
10.07.2008 23:00 | 3600 | 2 | 767.63 | GGB | 764.835 | 777.656 | 768.864 | 260.25 | GGB | 10496.7 | GGB | 9.79 | GGB | 1004.53 | GGB | 67.13 | GGB | 162895.1 | GGB | 129651.03 | GGB | 0 | 0 | 2920 | 3600 | 2904.35 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283499 | GGB | 283501.52 | 2565.7931 | 2565.7931 |  |  |  | 1 | 1 |  |  |  |  | 129651.03 | 2565.7931 | 129651.03 | 2565.7931 | 8.4992 |  | 2920 | -339 | 2581 | 2565.7931 | 92.4049 |  |  | #VALUE!
10.07.2008 24:00 | 3600 | 2 | 767.76 | GGB | 768.132 | 780.539 | 772.527 | 261.08 | GGB | 10577.3 | GGB | 9.8 | GGB | 1004.95 | GGB | 66.86 | GGB | 163564.11 | GGB | 130343.96 | GGB | 0 | 0 | 2953 | 3600 | 2937.47 | GGB | 100 | GGB | 39.14 | GGB | 39.14 | GGB | 283538.14 | GGB | 283540.66 | 2598.7661 | 2598.7661 |  |  |  | 0 | 1 | [10 empty] | 2953 | -339 | 2614 | 2598.7661 | 94.0926 |  |  | #VALUE!
11.07.2008 01:00 | 3600 | 2 | 766.99 | GGB | 763.37 | 777.516 | 768.864 | 261.86 | GGB | 10620.7 | GGB | 9.79 | GGB | 1005.69 | GGB | 66.71 | GGB | 163984.44 | GGB | 130829.98 | GGB | 0 | 0 | 2979 | 3600 | 2963.14 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283576.62 | GGB | 283579.14 | 2624.7449 | 2624.7449 |  |  |  | 0 | 1 | [10 empty] | 2979 | -339 | 2640 | 2624.7449 | 95.3876 |  |  | #VALUE!
11.07.2008 02:00 | 3600 | 2 | 767.16 | GGB | 764.835 | 776.883 | 768.864 | 262.69 | GGB | 10682.2 | GGB | 9.8 | GGB | 1006.37 | GGB | 66.05 | GGB | 164909.82 | GGB | 131915.66 | GGB | 0 | 0 | 2973 | 3600 | 2957.62 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283615.11 | GGB | 283617.62 | 2618.7498 | 2618.7498 |  |  |  | 1 | 1 |  |  |  |  | 131915.66 | 2618.7498 | 131915.66 | 2618.7498 | 8.9775 |  | 2973 | -339 | 2634 | 2618.7498 | 95.9595 |  |  | #VALUE!
11.07.2008 03:00 | 3600 | 2 | 766.62 | GGB | 762.271 | 775.102 | 766.667 | 263.2 | GGB | 10705 | GGB | 9.79 | GGB | 1007.01 | GGB | 65.68 | GGB | 165538.11 | GGB | 132644.23 | GGB | 0 | 0 | 3010 | 3600 | 2994.02 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283653.59 | GGB | 283656.1 | 2655.7196 | 2655.7196 |  |  |  | 0 | 1 | [10 empty] | 3010 | -339 | 2671 | 2655.7196 | 97.8516 |  |  | #VALUE!
11.07.2008 04:00 | 3600 | 2 | 766.74 | GGB | 764.835 | 777.727 | 768.864 | 264.19 | GGB | 10752 | GGB | 9.8 | GGB | 1007.45 | GGB | 65.45 | GGB | 166474.5 | GGB | 133544.59 | GGB | 0 | 0 | 3037 | 3600 | 3021.21 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283692.07 | GGB | 283694.58 | 2682.6976 | 2682.6976 |  |  |  | 1 | 1 |  |  |  |  | 133544.59 | 2682.6976 | 133544.59 | 2682.6976 | 9.3103 |  | 3037 | -339 | 2698 | 2682.6976 | 99.5166 |  |  | #VALUE!
11.07.2008 05:00 | 3600 | 2 | 766.18 | GGB | 762.271 | 775.102 | 766.667 | 265.63 | GGB | 10785.8 | GGB | 9.79 | GGB | 1007.61 | GGB | 65.03 | GGB | 167857.62 | GGB | 134844.82 | GGB | 0 | 0 | 3082 | 3600 | 3065.79 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283730.55 | GGB | 283733.06 | 2727.6608 | 2727.6608 |  |  |  | 0 | 1 | [10 empty] | 3082 | -339 | 2743 | 2727.6608 | 102.1697 |  |  | #VALUE!
11.07.2008 06:00 | 3600 | 2 | 766.21 | GGB | 768.132 | 780.586 | 772.527 | 267.43 | GGB | 10857.4 | GGB | 9.8 | GGB | 1007.95 | GGB | 64.63 | GGB | 169631.37 | GGB | 136474.28 | GGB | 0 | 0 | 3119 | 3600 | 3103.5 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283769.03 | GGB | 283771.54 | 2764.6306 | 2764.6306 |  |  |  | 0 | 1 | [10 empty] | 3119 | -339 | 2780 | 2764.6306 | 104.8058 |  |  | #VALUE!
11.07.2008 07:00 | 3600 | 2 | 766.4 | GGB | 764.835 | 777.75 | 769.963 | 267.17 | GGB | 10870.1 | GGB | 9.81 | GGB | 1008.35 | GGB | 64.71 | GGB | 169581.85 | GGB | 136457.86 | GGB | 0 | 0 | 3099 | 3600 | 3083.1 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283807.52 | GGB | 283810.02 | 2744.6469 | 2744.6469 |  |  |  | 1 | 1 |  |  |  |  | 136457.86 | 2744.6469 | 136457.86 | 2744.6469 | 9.7331 |  | 3099 | -339 | 2760 | 2744.6469 | 104.0357 |  |  | #VALUE!
11.07.2008 08:00 | 3600 | 2 | 767.57 | GGB | 767.033 | 779.016 | 771.429 | 265.02 | GGB | 10841.6 | GGB | 9.84 | GGB | 1007.97 | GGB | 65.17 | GGB | 167403.18 | GGB | 134472.51 | GGB | 0 | 0 | 3016 | 3600 | 2999.94 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283846 | GGB | 283848.5 | 2661.7147 | 2661.7147 |  |  |  | 0 | 1 | [10 empty] | 3016 | -339 | 2677 | 2661.7147 | 99.4243 |  |  | #VALUE!
11.07.2008 09:00 | 3600 | 2 | 767.88 | GGB | 767.033 | 779.039 | 770.33 | 262.43 | GGB | 10726 | GGB | 9.83 | GGB | 1007.76 | GGB | 66.06 | GGB | 164616.03 | GGB | 131859.89 | GGB | 0 | 0 | 2957 | 2836 | 2941.79 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283884.48 | GGB | 283886.98 | 2636.7351 | 2636.7351 |  |  |  | 0 | 1 | [10 empty] | 2957 | -305 | 2652 | 2636.7351 | 96.5777 |  |  | #VALUE!
11.07.2008 10:00 | 3600 | 2 | 768.82 | GGB | 767.033 | 779.953 | 771.429 | 260.19 | GGB | 10609.4 | GGB | 9.82 | GGB | 1007.37 | GGB | 67.27 | GGB | 162102.86 | GGB | 129335.12 | GGB | 0 | 0 | 3043 | 3600 | 3027.18 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283922.96 | GGB | 283925.46 | 2722.6649 | 2722.6649 |  |  |  | 0 | 1 | [10 empty] | 3043 | -305 | 2738 | 2722.6649 | 97.8156 |  |  | #VALUE!
11.07.2008 11:00 | 3600 | 2 | 769.38 | GGB | 768.132 | 780.867 | 773.626 | 258.27 | GGB | 10526.6 | GGB | 9.82 | GGB | 1006.53 | GGB | 68.3 | GGB | 160611.9 | GGB | 127650.53 | GGB | 0 | 0 | 3012 | 3600 | 2995.88 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283961.45 | GGB | 283963.94 | 2691.6902 | 2691.6902 |  |  |  | 0 | 1 | [10 empty] | 3012 | -305 | 2707 | 2691.6902 | 95.4432 |  |  | #VALUE!
11.07.2008 12:00 | 3600 | 2 | 769.88 | GGB | 768.132 | 781.852 | 773.626 | 256.48 | GGB | 10451.3 | GGB | 9.81 | GGB | 1005.52 | GGB | 68.51 | GGB | 159157.25 | GGB | 126290.5 | GGB | 0 | 0 | 2922 | 3600 | 2906.08 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 283999.93 | GGB | 284002.42 | 2601.7637 | 2601.7637 |  |  |  | 0 | 1 | [10 empty] | 2922 | -305 | 2617 | 2601.7637 | 91.2717 |  |  | #VALUE!
11.07.2008 13:00 | 3600 | 2 | 770.01 | GGB | 767.033 | 781.969 | 772.527 | 255.21 | GGB | 10401.9 | GGB | 9.81 | GGB | 1004.39 | GGB | 69 | GGB | 158539.96 | GGB | 125477.33 | GGB | 0 | 0 | 2910 | 3600 | 2894.43 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284038.41 | GGB | 284040.9 | 2589.7735 | 2589.7735 |  |  |  | 0 | 1 | [10 empty] | 2910 | -305 | 2605 | 2589.7735 | 90.2661 |  |  | #VALUE!
11.07.2008 14:00 | 3600 | 2 | 770.03 | GGB | 767.033 | 780.914 | 772.527 | 254.66 | GGB | 10382.3 | GGB | 9.8 | GGB | 1003.63 | GGB | 69.05 | GGB | 158114.13 | GGB | 125029.21 | GGB | 0 | 0 | 2892 | 3600 | 2876.66 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284076.89 | GGB | 284079.38 | 2571.7882 | 2571.7882 |  |  |  | 0 | 1 | [10 empty] | 2892 | -305 | 2587 | 2571.7882 | 89.3191 |  |  | #VALUE!
11.07.2008 15:00 | 3600 | 2 | 770.41 | GGB | 767.033 | 780.984 | 772.527 | 254.29 | GGB | 10377.9 | GGB | 9.81 | GGB | 1003.27 | GGB | 69.03 | GGB | 157905.07 | GGB | 124824.03 | GGB | 0 | 0 | 2871 | 3600 | 2855.22 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284115.37 | GGB | 284117.86 | 2550.8053 | 2550.8053 |  |  |  | 0 | 1 | [10 empty] | 2871 | -305 | 2566 | 2550.8053 | 88.4449 |  |  | #VALUE!
11.07.2008 16:00 | 3600 | 2 | 770.33 | GGB | 769.597 | 783.023 | 775.091 | 253.62 | GGB | 10342.2 | GGB | 9.81 | GGB | 1002.92 | GGB | 69.49 | GGB | 157265.77 | GGB | 124108.08 | GGB | 0 | 0 | 2871 | 3600 | 2855.38 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284153.86 | GGB | 284156.34 | 2550.8053 | 2550.8053 |  |  |  | 0 | 1 | [10 empty] | 2871 | -305 | 2566 | 2550.8053 | 87.9377 |  |  | #VALUE!
11.07.2008 17:00 | 3600 | 2 | 770.67 | GGB | 768.498 | 782.883 | 773.993 | 253.06 | GGB | 10315.4 | GGB | 9.8 | GGB | 1002.5 | GGB | 69.52 | GGB | 156893.86 | GGB | 123754.55 | GNB | 0 | 0 | 2823 | 3600 | 2807.89 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284192.34 | GGB | 284194.82 | 2502.8445 | 2502.8445 |  |  |  | 0 | 1 | [10 empty] | 2823 | -305 | 2518 | 2502.8445 | 86.0384 |  |  | #VALUE!
11.07.2008 18:00 | 3600 | 2 | 770.59 | GGB | 768.132 | 781.875 | 773.626 | 252.53 | GGB | 10295.9 | GGB | 9.8 | GGB | 1001.94 | GGB | 69.73 | GGB | 156460.33 | GGB | 123267.36 | GNB | 0 | 0 | 2842 | 3600 | 2826.22 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284230.82 | GGB | 284233.3 | 2521.829 | 2521.829 |  |  |  | 0 | 1 | [10 empty] | 2842 | -305 | 2537 | 2521.829 | 86.3498 |  |  | #VALUE!
11.07.2008 19:00 | 3600 | 2 | 770.7 | GGB | 767.033 | 780.844 | 772.527 | 252.69 | GGB | 10301.5 | GGB | 9.8 | GGB | 1001.75 | GGB | 69.62 | GGB | 156616.57 | GGB | 123406.35 | GNB | 0 | 0 | 2843 | 3600 | 2827.74 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284269.3 | GGB | 284271.78 | 2522.8282 | 2522.8282 |  |  |  | 0 | 1 | [10 empty] | 2843 | -305 | 2538 | 2522.8282 | 86.4814 |  |  | #VALUE!
11.07.2008 20:00 | 3600 | 2 | 770.71 | GGB | 767.033 | 781.57 | 772.527 | 253.44 | GGB | 10303 | GGB | 9.8 | GGB | 1001.85 | GGB | 69.56 | GGB | 156998.39 | GGB | 123740.59 | GNB | 0 | 0 | 2825 | 3600 | 2809.42 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284307.79 | GGB | 284310.26 | 2504.8429 | 2504.8429 |  |  |  | 0 | 1 | [10 empty] | 2825 | -305 | 2520 | 2504.8429 | 86.0974 |  |  | #VALUE!
11.07.2008 21:00 | 3600 | 2 | 769.65 | GGB | 767.033 | 780.539 | 771.429 | 255.45 | GGB | 10300.9 | GGB | 9.79 | GGB | 1001.97 | GGB | 68.73 | GGB | 158743.53 | GGB | 125437.35 | GGB | 0 | 0 | 2887 | 3600 | 2871.4 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284346.27 | GGB | 284348.74 | 2566.7922 | 2566.7922 |  |  |  | 0 | 1 | [10 empty] | 2887 | -305 | 2582 | 2566.7922 | 89.4366 |  |  | #VALUE!
11.07.2008 22:00 | 3600 | 2 | 769.37 | GGB | 765.934 | 779.414 | 771.429 | 254.89 | GGB | 10383.2 | GGB | 9.8 | GGB | 1001.87 | GGB | 69.14 | GGB | 157692.7 | GGB | 124441.5 | GGB | 0 | 0 | 2920 | 3600 | 2904.25 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284384.75 | GGB | 284387.22 | 2599.7653 | 2599.7653 |  |  |  | 0 | 1 | [10 empty] | 2920 | -305 | 2615 | 2599.7653 | 89.8663 |  |  | #VALUE!
11.07.2008 23:00 | 3600 | 2 | 768.57 | GGB | 764.469 | 778.922 | 769.963 | 255.35 | GGB | 10416.8 | GGB | 9.79 | GGB | 1002 | GGB | 68.75 | GGB | 158666.5 | GGB | 125371.49 | GGB | 0 | 0 | 2964 | 3600 | 2948.44 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284423.23 | GGB | 284425.7 | 2643.7294 | 2643.7294 |  |  |  | 0 | 1 | [10 empty] | 2964 | -305 | 2659 | 2643.7294 | 92.069 |  |  | #VALUE!
11.07.2008 24:00 | 3600 | 2 | 768.54 | GGB | 764.835 | 778.547 | 769.963 | 256.78 | GGB | 10438.3 | GGB | 9.79 | GGB | 1001.62 | GGB | 68.6 | GGB | 159091.23 | GGB | 125712.8 | GGB | 0 | 0 | 2996 | 3600 | 2980.71 | GGB | 100 | GGB | 38.48 | GGB | 38.48 | GGB | 284461.71 | GGB | 284464.18 | 2675.7033 | 2675.7033 |  |  |  | 1 | 1 |  |  |  |  | 125712.8 | 2675.7033 | 125712.8 | 2675.7033 | 8.7414 |  | 2996 | -305 | 2691 | 2675.7033 | 93.4362 |  |  | #VALUE!
12.07.2008 01:00 | 3600 | 2 | 768.06 | GGB | 765.934 | 779.297 | 769.597 | 257.37 | GGB | 10461.2 | GGB | 9.79 | GGB | 1001.78 | GGB | 68.47 | GGB | 159758.04 | GGB | 126309.95 | GGB | 0 | 0 | 3030 | 3600 | 3014.22 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284499.26 | GGB | 284501.73 | 2709.6755 | 2709.6755 |  |  |  | 0 | 1 | [10 empty] | 3030 | -305 | 2725 | 2709.6755 | 95.0719 |  |  | #VALUE!
12.07.2008 02:00 | 3600 | 2 | 768.57 | GGB | 767.033 | 780.352 | 772.527 | 258.48 | GGB | 10509.8 | GGB | 9.81 | GGB | 1001.92 | GGB | 68.09 | GGB | 160527.17 | GGB | 127076.16 | GGB | 0 | 0 | 3015 | 3600 | 2998.9 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284536.81 | GGB | 284539.28 | 2694.6878 | 2694.6878 |  |  |  | 0 | 1 | [10 empty] | 3015 | -305 | 2710 | 2694.6878 | 95.1196 |  |  | #VALUE!
12.07.2008 03:00 | 3600 | 2 | 768.18 | GGB | 768.132 | 781.523 | 772.161 | 258.54 | GGB | 10505.2 | GGB | 9.8 | GGB | 1002.12 | GGB | 67.98 | GGB | 160485.36 | GGB | 127109.52 | GGB | 0 | 0 | 3032 | 3600 | 3016.25 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284574.37 | GGB | 284576.83 | 2711.6739 | 2711.6739 |  |  |  | 0 | 1 | [10 empty] | 3032 | -305 | 2727 | 2711.6739 | 95.7443 |  |  | #VALUE!
12.07.2008 04:00 | 3600 | 2 | 768.05 | GGB | 768.132 | 781.383 | 773.26 | 258.95 | GGB | 10529.7 | GGB | 9.8 | GGB | 1001.9 | GGB | 67.83 | GGB | 160884.78 | GGB | 127453.35 | GGB | 0 | 0 | 3049 | 3600 | 3032.99 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284611.92 | GGB | 284614.38 | 2728.66 | 2728.66 |  |  |  | 0 | 1 | [10 empty] | 3049 | -305 | 2744 | 2728.66 | 96.6047 |  |  | #VALUE!
12.07.2008 05:00 | 3600 | 2 | 767.26 | GGB | 767.033 | 779.461 | 770.696 | 260.36 | GGB | 10556.9 | GGB | 9.79 | GGB | 1002.15 | GGB | 67.57 | GGB | 162023.63 | GGB | 128485.45 | GGB | 0 | 0 | 3103 | 3600 | 3087.68 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284649.47 | GGB | 284651.93 | 2782.6159 | 2782.6159 |  |  |  | 0 | 1 | [10 empty] | 3103 | -305 | 2798 | 2782.6159 | 99.3127 |  |  | #VALUE!
12.07.2008 06:00 | 3600 | 2 | 767.49 | GGB | 768.132 | 781.5 | 772.161 | 261.37 | GGB | 10577.1 | GGB | 9.8 | GGB | 1002.25 | GGB | 67.18 | GGB | 163049.15 | GGB | 129459.75 | GGB | 0 | 0 | 3113 | 3600 | 3096.82 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284687.02 | GGB | 284689.48 | 2792.6078 | 2792.6078 |  |  |  | 0 | 1 | [10 empty] | 3113 | -305 | 2808 | 2792.6078 | 100.4251 |  |  | #VALUE!
12.07.2008 07:00 | 3600 | 2 | 768.12 | GGB | 767.033 | 780.492 | 771.429 | 260.27 | GGB | 10576.7 | GGB | 9.82 | GGB | 1002.07 | GGB | 67.64 | GGB | 161843.18 | GGB | 128305.79 | GGB | 0 | 0 | 3080 | 3600 | 3064.67 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284724.57 | GGB | 284727.03 | 2759.6347 | 2759.6347 |  |  |  | 0 | 1 | [10 empty] | 3080 | -305 | 2775 | 2759.6347 | 98.3548 |  |  | #VALUE!
12.07.2008 08:00 | 3600 | 2 | 768.58 | GGB | 765.934 | 780.469 | 771.429 | 258.52 | GGB | 10497.3 | GGB | 9.82 | GGB | 1001.71 | GGB | 68.14 | GGB | 160288.4 | GGB | 126843.57 | GGB | 0 | 0 | 3023 | 3600 | 3007.49 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284762.12 | GGB | 284764.58 | 2702.6812 | 2702.6812 |  |  |  | 0 | 1 | [10 empty] | 3023 | -305 | 2718 | 2702.6812 | 95.2271 |  |  | #VALUE!
12.07.2008 09:00 | 3600 | 2 | 767.42 | GGB | 763.37 | 777.117 | 768.864 | 257.23 | GGB | 10462.3 | GGB | 9.79 | GGB | 1001.28 | GGB | 68.43 | GGB | 158712.72 | GGB | 125435.08 | GGB | 0 | 0 | 3076 | 3600 | 3060.25 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284799.67 | GGB | 284802.13 | 2755.638 | 2755.638 |  |  |  | 0 | 1 | [10 empty] | 3076 | -305 | 2771 | 2755.638 | 96.0149 |  |  | #VALUE!
12.07.2008 10:00 | 3600 | 2 | 768.31 | GGB | 765.934 | 779.273 | 770.33 | 257.04 | GGB | 10470.7 | GGB | 9.82 | GGB | 1000.69 | GGB | 69.19 | GGB | 158039.31 | GGB | 124552.87 | GGB | 0 | 0 | 3040 | 3600 | 3024.02 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284837.22 | GGB | 284839.68 | 2719.6673 | 2719.6673 |  |  |  | 0 | 1 | [10 empty] | 3040 | -305 | 2735 | 2719.6673 | 94.0951 |  |  | #VALUE!
12.07.2008 11:00 | 3600 | 2 | 768.59 | GGB | 765.934 | 780.352 | 770.33 | 255.44 | GGB | 10345.5 | GGB | 9.81 | GGB | 1000.28 | GGB | 69.85 | GGB | 156644.08 | GGB | 123163.29 | GNB | 0 | 0 | 2995 | 3600 | 2978.99 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284874.77 | GGB | 284877.23 | 2674.7041 | 2674.7041 |  |  |  | 0 | 1 | [10 empty] | 2995 | -305 | 2690 | 2674.7041 | 91.507 |  |  | #VALUE!
12.07.2008 12:00 | 3600 | 2 | 768.9 | GGB | 765.934 | 779.203 | 770.33 | 254.85 | GGB | 10276.9 | GGB | 9.8 | GGB | 999.98 | GGB | 69.84 | GGB | 156421.81 | GGB | 122957.57 | GNB | 0 | 0 | 2968 | 3600 | 2952.83 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284912.32 | GGB | 284914.78 | 2647.7261 | 2647.7261 |  |  |  | 0 | 1 | [10 empty] | 2968 | -305 | 2663 | 2647.7261 | 90.4328 |  |  | #VALUE!
12.07.2008 13:00 | 3600 | 2 | 769.58 | GGB | 765.934 | 780.281 | 770.33 | 252.82 | GGB | 10277.1 | GGB | 9.81 | GGB | 999.66 | GGB | 71.15 | GGB | 154080.3 | GGB | 120617.24 | GNB | 0 | 0 | 2932 | 3600 | 2915.98 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284949.87 | GGB | 284952.33 | 2611.7555 | 2611.7555 |  |  |  | 0 | 1 | [10 empty] | 2932 | -305 | 2627 | 2611.7555 | 87.5063 |  |  | #VALUE!
12.07.2008 14:00 | 3600 | 2 | 770.35 | GGB | 768.132 | 782.25 | 772.527 | 251.39 | GGB | 10229.9 | GGB | 9.81 | GGB | 999.13 | GGB | 71.87 | GGB | 152756.59 | GGB | 119268.21 | GNB | 0 | 0 | 2908 | 3600 | 2891.98 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 284987.42 | GGB | 284989.88 | 2587.7751 | 2587.7751 |  |  |  | 0 | 1 | [10 empty] | 2908 | -305 | 2603 | 2587.7751 | 85.7331 |  |  | #VALUE!
12.07.2008 15:00 | 3600 | 2 | 770.52 | GGB | 768.132 | 781.242 | 773.626 | 250.02 | GGB | 10169.1 | GGB | 9.8 | GGB | 998.19 | GGB | 71.79 | GGB | 152254.84 | GGB | 118792.42 | GNB | 0 | 0 | 2863 | 3600 | 2847.64 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285024.97 | GGB | 285027.43 | 2542.8118 | 2542.8118 |  |  |  | 0 | 1 | [10 empty] | 2863 | -305 | 2558 | 2542.8118 | 83.9074 |  |  | #VALUE!
12.07.2008 16:00 | 3600 | 2 | 770.66 | GGB | 770.696 | 784.617 | 776.19 | 249.69 | GGB | 10169.5 | GGB | 9.81 | GGB | 998.5 | GGB | 71.97 | GGB | 151722.27 | GGB | 118351.55 | GNB | 0 | 0 | 2852 | 3600 | 2836.73 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285062.52 | GGB | 285064.98 | 2531.8208 | 2531.8208 |  |  |  | 0 | 1 | [10 empty] | 2852 | -305 | 2547 | 2531.8208 | 83.2347 |  |  | #VALUE!
12.07.2008 17:00 | 3600 | 2 | 770.5 | GGB | 767.033 | 782.25 | 772.527 | 248.7 | GGB | 10115.8 | GGB | 9.79 | GGB | 998.12 | GGB | 72.25 | GGB | 150925.63 | GGB | 117587.77 | GNB | 0 | 0 | 2821 | 3600 | 2805.87 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285100.07 | GGB | 285102.53 | 2500.8461 | 2500.8461 |  |  |  | 0 | 1 | [10 empty] | 2821 | -305 | 2516 | 2500.8461 | 81.6858 |  |  | #VALUE!
12.07.2008 18:00 | 3600 | 2 | 770.8 | GGB | 767.033 | 781.195 | 772.527 | 249.03 | GGB | 10101.5 | GGB | 9.79 | GGB | 997.97 | GGB | 72.2 | GGB | 151371.26 | GGB | 117936.9 | GNB | 0 | 0 | 2802 | 3600 | 2786.82 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285137.62 | GGB | 285140.08 | 2481.8616 | 2481.8616 |  |  |  | 0 | 1 | [10 empty] | 2802 | -305 | 2497 | 2481.8616 | 81.3064 |  |  | #VALUE!
12.07.2008 19:00 | 3600 | 2 | 770.85 | GGB | 768.132 | 782.133 | 772.527 | 250.64 | GGB | 10097.4 | GGB | 9.79 | GGB | 998.66 | GGB | 71.52 | GGB | 152791.8 | GGB | 119358.94 | GNB | 0 | 0 | 2814 | 3600 | 2798.55 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285175.17 | GGB | 285177.63 | 2493.8518 | 2493.8518 |  |  |  | 0 | 1 | [10 empty] | 2814 | -305 | 2509 | 2493.8518 | 82.6843 |  |  | #VALUE!
12.07.2008 20:00 | 3600 | 2 | 770.9 | GGB | 768.132 | 782.133 | 772.527 | 249.48 | GGB | 10135.1 | GGB | 9.8 | GGB | 998.25 | GGB | 72.22 | GGB | 151431.78 | GGB | 118008.89 | GNB | 0 | 0 | 2795 | 3600 | 2779.53 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285212.72 | GGB | 285215.18 | 2474.8673 | 2474.8673 |  |  |  | 0 | 1 | [10 empty] | 2795 | -305 | 2490 | 2474.8673 | 81.1268 |  |  | #VALUE!
12.07.2008 21:00 | 3600 | 2 | 770.88 | GGB | 769.597 | 783.398 | 775.091 | 249.97 | GGB | 10150.3 | GGB | 9.79 | GGB | 998.56 | GGB | 72.32 | GGB | 151815.8 | GGB | 118308.74 | GNB | 0 | 0 | 2822 | 3600 | 2806.64 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285250.27 | GGB | 285252.73 | 2501.8453 | 2501.8453 |  |  |  | 0 | 1 | [10 empty] | 2822 | -305 | 2517 | 2501.8453 | 82.2195 |  |  | #VALUE!
12.07.2008 22:00 | 3600 | 2 | 770.16 | GGB | 767.033 | 782.086 | 772.527 | 251.26 | GGB | 10193 | GGB | 9.78 | GGB | 999.27 | GGB | 71.69 | GGB | 152766.49 | GGB | 119354.67 | GNB | 0 | 0 | 2846 | 3600 | 2830.53 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285287.82 | GGB | 285290.28 | 2525.8257 | 2525.8257 |  |  |  | 0 | 1 | [10 empty] | 2846 | -305 | 2541 | 2525.8257 | 83.7414 |  |  | #VALUE!
12.07.2008 23:00 | 3600 | 2 | 769.39 | GGB | 767.033 | 782.039 | 772.161 | 254.83 | GGB | 10238.7 | GGB | 9.78 | GGB | 1000.56 | GGB | 70.45 | GGB | 155899.15 | GGB | 122397.52 | GNB | 0 | 0 | 2909 | 3600 | 2893.37 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285325.37 | GGB | 285327.83 | 2588.7743 | 2588.7743 |  |  |  | 0 | 1 | [10 empty] | 2909 | -305 | 2604 | 2588.7743 | 88.0165 |  |  | #VALUE!
12.07.2008 24:00 | 3600 | 2 | 768.93 | GGB | 767.033 | 781.313 | 772.161 | 255.84 | GGB | 10367.1 | GGB | 9.79 | GGB | 1001.19 | GGB | 69.73 | GGB | 157403.32 | GGB | 123915.9 | GNB | 0 | 0 | 2955 | 3600 | 2939.48 | GGB | 100 | GGB | 37.55 | GGB | 37.55 | GGB | 285362.92 | GGB | 285365.38 | 2634.7367 | 2634.7367 |  |  |  | 0 | 1 | [10 empty] | 2955 | -305 | 2650 | 2634.7367 | 90.6905 |  |  | #VALUE!
13.07.2008 01:00 | 3600 | 2 | 768.14 | GGB | 767.033 | 781.289 | 772.161 | 256.76 | GGB | 10412.6 | GGB | 9.79 | GGB | 1001.53 | GGB | 70.03 | GGB | 157227.26 | GGB | 123712.58 | GNB | 0 | 0 | 3051 | 3600 | 3035.56 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285399.89 | GGB | 285402.35 | 2730.6584 | 2730.6584 |  |  |  | 0 | 1 | [10 empty] | 3051 | -305 | 2746 | 2730.6584 | 93.838 |  |  | #VALUE!
13.07.2008 02:00 | 3600 | 2 | 767.86 | GGB | 765.934 | 779.227 | 770.696 | 257.59 | GGB | 10427.6 | GGB | 9.79 | GGB | 1001.78 | GGB | 69.85 | GGB | 157683.9 | GGB | 124167.3 | GGB | 0 | 0 | 3066 | 3600 | 3050.03 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285436.87 | GGB | 285439.32 | 2745.6461 | 2745.6461 |  |  |  | 0 | 1 | [10 empty] | 3066 | -305 | 2761 | 2745.6461 | 94.6999 |  |  | #VALUE!
13.07.2008 03:00 | 3600 | 2 | 768.35 | GGB | 767.033 | 780.328 | 771.795 | 257.61 | GGB | 10445.9 | GGB | 9.8 | GGB | 1002.25 | GGB | 69.82 | GGB | 157450.63 | GGB | 124052.13 | GGB | 0 | 0 | 3059 | 3600 | 3043.24 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285473.84 | GGB | 285476.29 | 2738.6518 | 2738.6518 |  |  |  | 0 | 1 | [10 empty] | 3059 | -305 | 2754 | 2738.6518 | 94.371 |  |  | #VALUE!
13.07.2008 04:00 | 3600 | 2 | 767.88 | GGB | 767.033 | 780.375 | 771.795 | 258.47 | GGB | 10459.1 | GGB | 9.79 | GGB | 1002.22 | GGB | 69.6 | GGB | 158232.97 | GGB | 124746.21 | GGB | 0 | 0 | 3076 | 3600 | 3060.62 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285510.81 | GGB | 285513.26 | 2755.638 | 2755.638 |  |  |  | 0 | 1 | [10 empty] | 3076 | -305 | 2771 | 2755.638 | 95.4876 |  |  | #VALUE!
13.07.2008 05:00 | 3600 | 2 | 767.79 | GGB | 765.934 | 779.297 | 770.696 | 258.99 | GGB | 10483.2 | GGB | 9.8 | GGB | 1002.44 | GGB | 69.42 | GGB | 158929.48 | GGB | 125388.91 | GGB | 0 | 0 | 3091 | 3600 | 3075.46 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285547.78 | GGB | 285550.23 | 2770.6257 | 2770.6257 |  |  |  | 0 | 1 | [10 empty] | 3091 | -305 | 2786 | 2770.6257 | 96.5016 |  |  | #VALUE!
13.07.2008 06:00 | 3600 | 2 | 767.64 | GGB | 764.835 | 778.125 | 769.597 | 259.13 | GGB | 10502.8 | GGB | 9.8 | GGB | 1002.61 | GGB | 69.01 | GGB | 159125.34 | GGB | 125713.2 | GGB | 0 | 0 | 3086 | 3600 | 3070.52 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285584.75 | GGB | 285587.2 | 2765.6298 | 2765.6298 |  |  |  | 1 | 1 |  |  |  |  | 125713.2 | 2765.6298 | 125713.2 | 2765.6298 | 9.4043 |  | 3086 | -305 | 2781 | 2765.6298 | 96.5767 |  |  | #VALUE!
13.07.2008 07:00 | 3600 | 2 | 767.81 | GGB | 764.835 | 778.148 | 769.597 | 259.1 | GGB | 10517.9 | GGB | 9.81 | GGB | 1002.38 | GGB | 69.18 | GGB | 159279.39 | GGB | 125744.23 | GGB | 0 | 0 | 3107 | 3600 | 3090.88 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285621.72 | GGB | 285624.17 | 2786.6127 | 2786.6127 |  |  |  | 1 | 1 |  |  |  |  | 125744.23 | 2786.6127 | 125744.23 | 2786.6127 | 9.478 |  | 3107 | -305 | 2802 | 2786.6127 | 97.3335 |  |  | #VALUE!
13.07.2008 08:00 | 3600 | 2 | 768.09 | GGB | 765.934 | 779.133 | 770.696 | 259.5 | GGB | 10470.7 | GGB | 9.8 | GGB | 1002.92 | GGB | 68.87 | GGB | 159861.47 | GGB | 126387.73 | GGB | 0 | 0 | 3084 | 3600 | 3068.66 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285658.69 | GGB | 285661.14 | 2763.6314 | 2763.6314 |  |  |  | 0 | 1 | [10 empty] | 3084 | -305 | 2779 | 2763.6314 | 97.0248 |  |  | #VALUE!
13.07.2008 09:00 | 3600 | 2 | 768.3 | GGB | 765.934 | 780.141 | 770.696 | 259.45 | GGB | 10445.4 | GGB | 9.81 | GGB | 1003.37 | GGB | 68.76 | GGB | 159744.83 | GGB | 126391.12 | GGB | 0 | 0 | 3060 | 3600 | 3044.73 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285695.67 | GGB | 285698.11 | 2739.651 | 2739.651 |  |  |  | 0 | 1 | [10 empty] | 3060 | -305 | 2755 | 2739.651 | 96.1854 |  |  | #VALUE!
13.07.2008 10:00 | 3600 | 2 | 768.15 | GGB | 762.271 | 775.359 | 767.033 | 258.79 | GGB | 10449.7 | GGB | 9.8 | GGB | 1003.37 | GGB | 68.1 | GGB | 159251.88 | GGB | 126247.96 | GGB | 0 | 0 | 3072 | 3600 | 3056.66 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285732.64 | GGB | 285735.08 | 2751.6412 | 2751.6412 |  |  |  | 0 | 1 | [10 empty] | 3072 | -305 | 2767 | 2751.6412 | 96.497 |  |  | #VALUE!
13.07.2008 11:00 | 3600 | 2 | 768.53 | GGB | 764.835 | 778.594 | 769.597 | 257.25 | GGB | 10476.5 | GGB | 9.81 | GGB | 1003.48 | GGB | 69.48 | GGB | 156966.48 | GGB | 123945.22 | GNB | 0 | 0 | 3059 | 3600 | 3043.56 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285769.61 | GGB | 285772.05 | 2738.6518 | 2738.6518 |  |  |  | 1 | 1 |  |  |  |  | 123945.22 | 2738.6518 |  | 2738.6518 | 9.1816 |  | 3059 | -305 | 2754 | 2738.6518 | 94.2897 |  |  | #VALUE!
13.07.2008 12:00 | 3600 | 2 | 767.58 | GGB | 764.835 | 777.844 | 769.597 | 257.91 | GGB | 10466.3 | GGB | 9.8 | GGB | 1003.82 | GGB | 69.19 | GGB | 157276.78 | GGB | 124339.68 | GGB | 0 | 0 | 3113 | 3600 | 3097.07 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285806.58 | GGB | 285809.02 | 2792.6078 | 2792.6078 |  |  |  | 1 | 1 |  |  |  |  | 124339.68 | 2792.6078 |  | 2792.6078 | 9.3923 |  | 3113 | -305 | 2808 | 2792.6078 | 96.4533 |  |  | #VALUE!
13.07.2008 13:00 | 3600 | 2 | 767.77 | GGB | 765.934 | 780.023 | 770.696 | 258.66 | GGB | 10490.4 | GGB | 9.8 | GGB | 1003.9 | GGB | 69.29 | GGB | 157766.43 | GGB | 124699.52 | GGB | 0 | 0 | 3118 | 3600 | 3102.12 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285843.55 | GGB | 285845.99 | 2797.6037 | 2797.6037 |  |  |  | 0 | 1 | [10 empty] | 3118 | -305 | 2813 | 2797.6037 | 96.9055 |  |  | #VALUE!
13.07.2008 14:00 | 3600 | 2 | 768.04 | GGB | 765.934 | 780.117 | 770.696 | 258.25 | GGB | 10484.6 | GGB | 9.81 | GGB | 1004.33 | GGB | 69.7 | GGB | 157632.19 | GGB | 124496.88 | GGB | 0 | 0 | 3092 | 3600 | 3076.59 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285880.52 | GGB | 285882.96 | 2771.6249 | 2771.6249 |  |  |  | 0 | 1 | [10 empty] | 3092 | -305 | 2787 | 2771.6249 | 95.8496 |  |  | #VALUE!
13.07.2008 15:00 | 3600 | 2 | 768.1 | GGB | 765.934 | 780.141 | 771.795 | 258.11 | GGB | 10435.6 | GGB | 9.8 | GGB | 1004.53 | GGB | 69.85 | GGB | 157566.17 | GGB | 124415.78 | GGB | 0 | 0 | 3059 | 3600 | 3043.25 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285917.49 | GGB | 285919.93 | 2738.6518 | 2738.6518 |  |  |  | 0 | 1 | [10 empty] | 3059 | -305 | 2754 | 2738.6518 | 94.6476 |  |  | #VALUE!
13.07.2008 16:00 | 3600 | 2 | 768.74 | GGB | 765.934 | 780.141 | 770.696 | 257.98 | GGB | 10382.2 | GGB | 9.8 | GGB | 1004.51 | GGB | 69.47 | GGB | 157856.65 | GGB | 124782.53 | GGB | 0 | 0 | 3008 | 3600 | 2992.39 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285954.46 | GGB | 285956.9 | 2687.6935 | 2687.6935 |  |  |  | 0 | 1 | [10 empty] | 3008 | -305 | 2703 | 2687.6935 | 93.1603 |  |  | #VALUE!
13.07.2008 17:00 | 3600 | 2 | 769.69 | GGB | 765.934 | 779.953 | 771.795 | 256.41 | GGB | 10396.2 | GGB | 9.81 | GGB | 1004.18 | GGB | 70.01 | GGB | 156419.61 | GGB | 123409.81 | GNB | 0 | 0 | 2979 | 3600 | 2962.94 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 285991.44 | GGB | 285993.87 | 2658.7171 | 2658.7171 |  |  |  | 0 | 1 | [10 empty] | 2979 | -305 | 2674 | 2658.7171 | 91.1422 |  |  | #VALUE!
13.07.2008 18:00 | 3600 | 2 | 768.9 | GGB | 767.033 | 781.195 | 772.161 | 255.98 | GGB | 10396.4 | GGB | 9.8 | GGB | 1003.99 | GGB | 70.23 | GGB | 156101.62 | GGB | 123057.43 | GNB | 0 | 0 | 3007 | 3600 | 2991.69 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 286028.41 | GGB | 286030.84 | 2686.6943 | 2686.6943 |  |  |  | 0 | 1 | [10 empty] | 3007 | -305 | 2702 | 2686.6943 | 91.8382 |  |  | #VALUE!
13.07.2008 19:00 | 3600 | 2 | 769.21 | GGB | 767.033 | 780.352 | 772.161 | 256.42 | GGB | 10393.6 | GGB | 9.8 | GGB | 1004.51 | GGB | 70.53 | GGB | 156366.8 | GGB | 123223 | GNB | 0 | 0 | 2991 | 3600 | 2975.62 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 286065.38 | GGB | 286067.81 | 2670.7073 | 2670.7073 |  |  |  | 0 | 1 | [10 empty] | 2991 | -305 | 2686 | 2670.7073 | 91.4146 |  |  | #VALUE!
13.07.2008 20:00 | 3600 | 2 | 770.15 | GGB | 767.033 | 781.477 | 772.161 | 255.07 | GGB | 10375.2 | GGB | 9.81 | GGB | 1003.76 | GGB | 71.18 | GGB | 155736.3 | GGB | 122401.71 | GNB | 0 | 0 | 2968 | 3600 | 2952.33 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 286102.35 | GGB | 286104.78 | 2647.7261 | 2647.7261 |  |  |  | 0 | 1 | [10 empty] | 2968 | -305 | 2663 | 2647.7261 | 90.0239 |  |  | #VALUE!
13.07.2008 21:00 | 3600 | 2 | 768.51 | GGB | 767.033 | 780.469 | 771.795 | 255.51 | GGB | 10361 | GGB | 9.79 | GGB | 1003.11 | GGB | 70.87 | GGB | 156152.23 | GGB | 122761.33 | GNB | 0 | 0 | 3003 | 3600 | 2987.32 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 286139.32 | GGB | 286141.75 | 2682.6976 | 2682.6976 |  |  |  | 0 | 1 | [10 empty] | 3003 | -305 | 2698 | 2682.6976 | 91.481 |  |  | #VALUE!
13.07.2008 22:00 | 3600 | 2 | 768.71 | GGB | 765.934 | 779.367 | 770.696 | 256.18 | GGB | 10403 | GGB | 9.8 | GGB | 1003.63 | GGB | 70.77 | GGB | 156448.22 | GGB | 123093.01 | GNB | 0 | 0 | 3019 | 3600 | 3003.65 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 286176.29 | GGB | 286178.72 | 2698.6845 | 2698.6845 |  |  |  | 0 | 1 | [10 empty] | 3019 | -305 | 2714 | 2698.6845 | 92.2748 |  |  | #VALUE!
13.07.2008 23:00 | 3600 | 2 | 767.95 | GGB | 765.934 | 779.391 | 770.696 | 257.41 | GGB | 10435.3 | GGB | 9.79 | GGB | 1004.08 | GGB | 70.54 | GGB | 157282.28 | GGB | 123887.5 | GNB | 0 | 0 | 3072 | 3600 | 3056.77 | GGB | 100 | GGB | 36.97 | GGB | 36.97 | GGB | 286213.26 | GGB | 286215.69 | 2751.6412 | 2751.6412 |  |  |  | 0 | 1 | [10 empty] | 3072 | -305 | 2767 | 2751.6412 | 94.6928 |  |  | #VALUE!
13.07.2008 24:00 | 3600 | 2 | 768.12 | GGB | 765.934 | 779.32 | 770.696 | 258.6 | GGB | 10505.5 | GGB | 9.8 | GGB | 1004.56 | GGB | 70.13 | GGB | 158824.95 | GGB | 125310.54 | GGB | 0 | 0 | 3124 | 3600 | 3108.31 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286250.5 | GGB | 286252.93 | 2803.5988 | 2803.5988 |  |  |  | 0 | 1 | [10 empty] | 3124 | -305 | 2819 | 2803.5988 | 97.589 |  |  | #VALUE!
14.07.2008 01:00 | 3600 | 2 | 767.34 | GGB | 764.835 | 779.297 | 769.597 | 260.65 | GGB | 10482.6 | GGB | 9.79 | GGB | 1004.83 | GGB | 69.97 | GGB | 160244.39 | GGB | 126525.03 | GGB | 0 | 0 | 3193 | 3600 | 3176.74 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286287.74 | GGB | 286290.17 | 2872.5424 | 2872.5424 |  |  |  | 0 | 1 | [10 empty] | 3193 | -305 | 2888 | 2872.5424 | 100.9579 |  |  | #VALUE!
14.07.2008 02:00 | 3600 | 2 | 768.33 | GGB | 767.033 | 781.383 | 772.161 | 260.58 | GGB | 10541.6 | GGB | 9.81 | GGB | 1004.96 | GGB | 69.7 | GGB | 160093.64 | GGB | 126519.05 | GGB | 0 | 0 | 3119 | 3600 | 3103.35 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286324.98 | GGB | 286327.41 | 2798.6029 | 2798.6029 |  |  |  | 0 | 1 | [10 empty] | 3119 | -305 | 2814 | 2798.6029 | 98.3546 |  |  | #VALUE!
14.07.2008 03:00 | 3600 | 2 | 767.47 | GGB | 768.132 | 781.289 | 773.26 | 260.52 | GGB | 10544.1 | GGB | 9.8 | GGB | 1005.26 | GGB | 69.94 | GGB | 160049.63 | GGB | 126434.02 | GGB | 0 | 0 | 3180 | 3600 | 3164.59 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286362.21 | GGB | 286364.65 | 2859.5531 | 2859.5531 |  |  |  | 0 | 1 | [10 empty] | 3180 | -305 | 2875 | 2859.5531 | 100.4291 |  |  | #VALUE!
14.07.2008 04:00 | 3600 | 2 | 767.15 | GGB | 764.469 | 777.07 | 768.132 | 260.62 | GGB | 10532.1 | GGB | 9.79 | GGB | 1004.94 | GGB | 70.16 | GGB | 160222.38 | GGB | 126451.52 | GGB | 0 | 0 | 3216 | 3600 | 3199.7 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286399.45 | GGB | 286401.89 | 2895.5237 | 2895.5237 |  |  |  | 1 | 1 |  |  |  |  | 126451.52 | 2895.5237 | 126451.52 | 2895.5237 | 9.832 |  | 3216 | -305 | 2911 | 2895.5237 | 101.7065 |  |  | #VALUE!
14.07.2008 05:00 | 3600 | 2 | 768.73 | GGB | 763.37 | 776.789 | 767.033 | 259.81 | GGB | 10569.4 | GGB | 9.83 | GGB | 1004.09 | GGB | 69.87 | GGB | 159580.88 | GGB | 125945.81 | GGB | 0 | 0 | 3148 | 3600 | 3132.62 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286436.69 | GGB | 286439.13 | 2827.5792 | 2827.5792 |  |  |  | 0 | 1 | [10 empty] | 3148 | -305 | 2843 | 2827.5792 | 98.9227 |  |  | #VALUE!
14.07.2008 06:00 | 3600 | 2 | 767.17 | GGB | 763.37 | 776.602 | 767.033 | 258.44 | GGB | 10506 | GGB | 9.8 | GGB | 1002.45 | GGB | 70.16 | GGB | 158801.84 | GGB | 125020.12 | GGB | 0 | 0 | 3205 | 3600 | 3189.35 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286473.93 | GGB | 286476.37 | 2884.5327 | 2884.5327 |  |  |  | 0 | 1 | [10 empty] | 3205 | -305 | 2900 | 2884.5327 | 100.1735 |  |  | #VALUE!
14.07.2008 07:00 | 3600 | 2 | 767.45 | GGB | 767.033 | 779.695 | 771.795 | 258.98 | GGB | 10508.5 | GGB | 9.81 | GGB | 1002.99 | GGB | 70.47 | GGB | 158921.78 | GGB | 125068.3 | GGB | 0 | 0 | 3207 | 3600 | 3191.18 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286511.16 | GGB | 286513.61 | 2886.531 | 2886.531 |  |  |  | 0 | 1 | [10 empty] | 3207 | -305 | 2902 | 2886.531 | 100.2815 |  |  | #VALUE!
14.07.2008 08:00 | 3600 | 2 | 768.09 | GGB | 763.37 | 777.117 | 768.498 | 257.36 | GGB | 10468.1 | GGB | 9.81 | GGB | 1001.78 | GGB | 71.23 | GGB | 157627.78 | GGB | 123625.61 | GNB | 0 | 0 | 3166 | 3600 | 3149.71 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286548.4 | GGB | 286550.85 | 2845.5645 | 2845.5645 |  |  |  | 0 | 1 | [10 empty] | 3166 | -305 | 2861 | 2845.5645 | 97.718 |  |  | #VALUE!
14.07.2008 09:00 | 3600 | 2 | 767.5 | GGB | 762.271 | 775.828 | 767.033 | 257.61 | GGB | 10379.2 | GGB | 9.8 | GGB | 1001.3 | GGB | 71.15 | GGB | 157906.17 | GGB | 123812.92 | GNB | 0 | 0 | 3170 | 3600 | 3154.48 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286585.64 | GGB | 286588.09 | 2849.5612 | 2849.5612 |  |  |  | 0 | 1 | [10 empty] | 3170 | -305 | 2865 | 2849.5612 | 98.0035 |  |  | #VALUE!
14.07.2008 10:00 | 3600 | 2 | 768.43 | GGB | 764.835 | 777.914 | 769.597 | 257.31 | GGB | 10366.9 | GGB | 9.82 | GGB | 1001.23 | GGB | 71.39 | GGB | 157495.74 | GGB | 123395.83 | GNB | 0 | 0 | 3144 | 3600 | 3127.74 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286622.88 | GGB | 286625.33 | 2823.5824 | 2823.5824 |  |  |  | 1 | 1 |  |  |  |  | 123395.83 | 2823.5824 |  | 2823.5824 | 9.356 |  | 3144 | -305 | 2839 | 2823.5824 | 96.7829 |  |  | #VALUE!
14.07.2008 11:00 | 3600 | 2 | 768.26 | GGB | 765.934 | 779.109 | 770.696 | 255.06 | GGB | 10378.9 | GGB | 9.81 | GGB | 1000.24 | GGB | 71.25 | GGB | 155553.65 | GGB | 121804.9 | GNB | 0 | 0 | 3154 | 3600 | 3138.63 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286660.11 | GGB | 286662.57 | 2833.5743 | 2833.5743 |  |  |  | 0 | 1 | [10 empty] | 3154 | -305 | 2849 | 2833.5743 | 95.8731 |  |  | #VALUE!
14.07.2008 12:00 | 3600 | 2 | 767.97 | GGB | 767.033 | 781.289 | 772.161 | 257.66 | GGB | 10363.2 | GGB | 9.8 | GGB | 1000.07 | GGB | 71.9 | GGB | 157438.53 | GGB | 123029.28 | GNB | 0 | 0 | 3211 | 3600 | 3194.88 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286697.35 | GGB | 286699.81 | 2890.5278 | 2890.5278 |  |  |  | 0 | 1 | [10 empty] | 3211 | -305 | 2906 | 2890.5278 | 98.7832 |  |  | #VALUE!
14.07.2008 13:00 | 3600 | 2 | 768 | GGB | 765.934 | 779.414 | 770.696 | 257.45 | GGB | 10337.9 | GGB | 9.8 | GGB | 1000.44 | GGB | 71.75 | GGB | 157464.93 | GGB | 123148.55 | GNB | 0 | 0 | 3168 | 3600 | 3151.83 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286734.59 | GGB | 286737.05 | 2847.5629 | 2847.5629 |  |  |  | 0 | 1 | [10 empty] | 3168 | -305 | 2863 | 2847.5629 | 97.4092 |  |  | #VALUE!
14.07.2008 14:00 | 3600 | 2 | 767.67 | GGB | 763.37 | 777.211 | 768.498 | 255.57 | GGB | 10403 | GGB | 9.8 | GGB | 1000.64 | GGB | 69.26 | GGB | 156722.21 | GGB | 123481.75 | GNB | 0 | 0 | 3181 | 3600 | 3164.69 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286771.83 | GGB | 286774.29 | 2860.5522 | 2860.5522 |  |  |  | 0 | 1 | [10 empty] | 3181 | -305 | 2876 | 2860.5522 | 98.1183 |  |  | #VALUE!
14.07.2008 15:00 | 3600 | 2 | 767.51 | GGB | 767.033 | 780.398 | 772.161 | 257.2 | GGB | 10456.3 | GGB | 9.81 | GGB | 1002.64 | GGB | 70.87 | GGB | 157342.8 | GGB | 123637.33 | GNB | 0 | 0 | 3212 | 3600 | 3195.67 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286809.06 | GGB | 286811.53 | 2891.5269 | 2891.5269 |  |  |  | 0 | 1 | [10 empty] | 3212 | -305 | 2907 | 2891.5269 | 99.3057 |  |  | #VALUE!
14.07.2008 16:00 | 3600 | 2 | 767.7 | GGB | 768.132 | 780.492 | 771.795 | 256.49 | GGB | 10429.3 | GGB | 9.8 | GGB | 1002.68 | GGB | 71.34 | GGB | 156711.2 | GGB | 122979.3 | GNB | 0 | 0 | 3194 | 3600 | 3178.01 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286846.3 | GGB | 286848.77 | 2873.5416 | 2873.5416 |  |  |  | 0 | 1 | [10 empty] | 3194 | -305 | 2889 | 2873.5416 | 98.1628 |  |  | #VALUE!
14.07.2008 17:00 | 3600 | 2 | 766.1 | GGB | 763.37 | 776.203 | 767.033 | 258.77 | GGB | 10409.9 | GGB | 9.76 | GGB | 1003.05 | GGB | 70.85 | GGB | 159147.35 | GGB | 125113.25 | GGB | 0 | 0 | 3269 | 3600 | 3252.84 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286883.54 | GGB | 286886.01 | 2948.4804 | 2948.4804 |  |  |  | 0 | 1 | [10 empty] | 3269 | -305 | 2964 | 2948.4804 | 102.4705 |  |  | #VALUE!
14.07.2008 18:00 | 3600 | 2 | 766.95 | GGB | 765.934 | 779.18 | 770.696 | 260.75 | GGB | 10556.8 | GGB | 9.8 | GGB | 1004.51 | GGB | 69.4 | GGB | 161098.25 | GGB | 127370.38 | GGB | 0 | 0 | 3231 | 3600 | 3214.99 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286920.78 | GGB | 286923.25 | 2910.5114 | 2910.5114 |  |  |  | 0 | 1 | [10 empty] | 3231 | -305 | 2926 | 2910.5114 | 102.9758 |  |  | #VALUE!
14.07.2008 19:00 | 3600 | 2 | 767.79 | GGB | 765.934 | 780.305 | 770.696 | 261.04 | GGB | 10591.6 | GGB | 9.81 | GGB | 1005.76 | GGB | 68.7 | GGB | 162098.46 | GGB | 128581.54 | GGB | 0 | 0 | 3150 | 3600 | 3134.64 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286958.01 | GGB | 286960.49 | 2829.5776 | 2829.5776 |  |  |  | 0 | 1 | [10 empty] | 3150 | -305 | 2845 | 2829.5776 | 101.0643 |  |  | #VALUE!
14.07.2008 20:00 | 3600 | 2 | 767.67 | GGB | 764.835 | 778.242 | 769.597 | 261.27 | GGB | 10547.9 | GGB | 9.8 | GGB | 1006.71 | GGB | 67.93 | GGB | 162914.91 | GGB | 129643.61 | GGB | 0 | 0 | 3130 | 3600 | 3114.42 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 286995.25 | GGB | 286997.73 | 2809.5939 | 2809.5939 |  |  |  | 1 | 1 |  |  |  |  | 129643.61 | 2809.5939 | 129643.61 | 2809.5939 | 9.781 |  | 3130 | -305 | 2825 | 2809.5939 | 101.1794 |  |  | #VALUE!
14.07.2008 21:00 | 3600 | 2 | 768.1 | GGB | 764.835 | 777.586 | 768.498 | 259.74 | GGB | 10584.7 | GGB | 9.81 | GGB | 1006.95 | GGB | 68.33 | GGB | 161320.52 | GGB | 128257.23 | GGB | 0 | 0 | 3086 | 3600 | 3070.61 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 287032.49 | GGB | 287034.97 | 2765.6298 | 2765.6298 |  |  |  | 1 | 1 |  |  |  |  | 128257.23 | 2765.6298 | 128257.23 | 2765.6298 | 9.525 |  | 3086 | -305 | 2781 | 2765.6298 | 98.5311 |  |  | #VALUE!
14.07.2008 22:00 | 3600 | 2 | 767.15 | GGB | 764.835 | 778.57 | 769.597 | 260.05 | GGB | 10593.5 | GGB | 9.8 | GGB | 1007.68 | GGB | 68.33 | GGB | 161688.03 | GGB | 128640.07 | GGB | 0 | 0 | 3158 | 3600 | 3142 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 287069.73 | GGB | 287072.21 | 2837.571 | 2837.571 |  |  |  | 1 | 1 |  |  |  |  | 128640.07 | 2837.571 | 128640.07 | 2837.571 | 9.802 |  | 3158 | -305 | 2853 | 2837.571 | 101.3959 |  |  | #VALUE!
14.07.2008 23:00 | 3600 | 2 | 767.4 | GGB | 765.934 | 779.508 | 770.696 | 260.7 | GGB | 10622.1 | GGB | 9.8 | GGB | 1008.54 | GGB | 68.05 | GGB | 162031.34 | GGB | 129131.17 | GGB | 0 | 0 | 3162 | 3600 | 3146.61 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 287106.96 | GGB | 287109.45 | 2841.5678 | 2841.5678 |  |  |  | 0 | 1 | [10 empty] | 3162 | -305 | 2857 | 2841.5678 | 101.9264 |  |  | #VALUE!
14.07.2008 24:00 | 3600 | 2 | 767.29 | GGB | 764.835 | 778.5 | 769.597 | 261.18 | GGB | 10642.5 | GGB | 9.8 | GGB | 1008.71 | GGB | 67.67 | GGB | 162395.55 | GGB | 129585.64 | GGB | 0 | 0 | 3178 | 3600 | 3162.32 | GGB | 100 | GGB | 37.24 | GGB | 37.24 | GGB | 287144.2 | GGB | 287146.69 | 2857.5547 | 2857.5547 |  |  |  | 1 | 1 |  |  |  |  | 129585.64 | 2857.5547 | 129585.64 | 2857.5547 | 9.9436 |  | 3178 | -305 | 2873 | 2857.5547 | 102.8606 |  |  | #VALUE!
15.07.2008 01:00 | 3600 | 2 | 766.44 | GGB | 762.271 | 775.406 | 767.033 | 262.01 | GGB | 10682.5 | GGB | 9.79 | GGB | 1009.17 | GGB | 67.16 | GGB | 163577.31 | GGB | 130785.13 | GGB | 0 | 0 | 3226 | 3600 | 3210.65 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287182.26 | GGB | 287184.75 | 2905.5155 | 2889.6863 |  |  |  | 0 | 1 | [10 empty] | 3226 | -305 | 2921 | 2905.5155 | 105.5551 | 2889.6863 |  | 104.98
15.07.2008 02:00 | 3600 | 2 | 766.9 | GGB | 765.934 | 778.547 | 770.696 | 263.65 | GGB | 10736.5 | GGB | 9.81 | GGB | 1009.79 | GGB | 66.97 | GGB | 164181.4 | GGB | 131420.98 | GGB | 0 | 0 | 3255 | 3600 | 3239.09 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287220.32 | GGB | 287222.81 | 2934.4918 | 2875.7052 |  |  |  | 1 | 1 |  |  |  |  | 131420.98 | 2875.7052 | 131420.98 | 2875.7052 | 9.9298 |  | 3255 | -305 | 2950 | 2934.4918 | 107.1261 | 2875.7052 |  | 104.98
15.07.2008 03:00 | 3600 | 2 | 766.84 | GGB | 763.37 | 776.414 | 768.132 | 263.99 | GGB | 10750.3 | GGB | 9.8 | GGB | 1009.77 | GGB | 66.7 | GGB | 164471.89 | GGB | 131756.66 | GGB | 0 | 0 | 3232 | 3600 | 3216.26 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287258.37 | GGB | 287260.87 | 2911.5106 | 2868.3787 |  |  |  | 0 | 1 | [10 empty] | 3232 | -305 | 2927 | 2911.5106 | 106.5586 | 2868.3787 |  | 104.98
15.07.2008 04:00 | 3600 | 2 | 766.34 | GGB | 764.835 | 777.328 | 768.498 | 264.96 | GGB | 10787.3 | GGB | 9.8 | GGB | 1010.61 | GGB | 66.34 | GGB | 165387.37 | GGB | 132740.22 | GGB | 0 | 0 | 3290 | 3600 | 3274.53 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287296.43 | GGB | 287298.93 | 2969.4633 | 2847.125 |  |  |  | 1 | 1 |  |  |  |  | 132740.22 | 2847.125 | 132740.22 | 2847.125 | 9.9298 |  | 3290 | -305 | 2985 | 2969.4633 | 109.4909 | 2847.125 |  | 104.98
15.07.2008 05:00 | 3600 | 2 | 766.2 | GGB | 764.835 | 777.375 | 769.597 | 265.82 | GGB | 10807.5 | GGB | 9.8 | GGB | 1010.77 | GGB | 66.07 | GGB | 166127.89 | GGB | 133463.71 | GGB | 0 | 0 | 3297 | 3600 | 3281.32 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287334.49 | GGB | 287336.99 | 2976.4576 | 2831.6911 |  |  |  | 1 | 1 |  |  |  |  | 133463.71 | 2831.6911 | 133463.71 | 2831.6911 | 9.9298 |  | 3297 | -305 | 2992 | 2976.4576 | 110.347 | 2831.6911 |  | 104.98
15.07.2008 06:00 | 3600 | 2 | 766.61 | GGB | 764.835 | 777.445 | 768.498 | 265.91 | GGB | 10830.5 | GGB | 9.81 | GGB | 1011.41 | GGB | 65.93 | GGB | 166204.92 | GGB | 133663.42 | GGB | 0 | 0 | 3280 | 3600 | 3264.51 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287372.55 | GGB | 287375.05 | 2959.4714 | 2827.4602 |  |  |  | 1 | 1 |  |  |  |  | 133663.42 | 2827.4602 | 133663.42 | 2827.4602 | 9.9298 |  | 3280 | -305 | 2975 | 2959.4714 | 109.8814 | 2827.4602 |  | 104.98
15.07.2008 07:00 | 3600 | 2 | 766.71 | GGB | 764.469 | 777.258 | 768.498 | 265.35 | GGB | 10825.4 | GGB | 9.81 | GGB | 1011.46 | GGB | 65.87 | GGB | 165724.07 | GGB | 133306 | GGB | 0 | 0 | 3264 | 3600 | 3247.78 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287410.61 | GGB | 287413.11 | 2943.4845 | 2835.0412 |  |  |  | 1 | 1 |  |  |  |  | 133306 | 2835.0412 | 133306 | 2835.0412 | 9.9298 |  | 3264 | -305 | 2959 | 2943.4845 | 108.9956 | 2835.0412 |  | 104.98
15.07.2008 08:00 | 3600 | 2 | 766.9 | GGB | 764.835 | 778.336 | 769.597 | 264.56 | GGB | 10812.8 | GGB | 9.82 | GGB | 1011.26 | GGB | 66.07 | GGB | 164935.13 | GGB | 132569.57 | GGB | 0 | 0 | 3249 | 3600 | 3233.5 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287448.67 | GGB | 287451.17 | 2928.4967 | 2850.79 |  |  |  | 1 | 1 |  |  |  |  | 132569.57 | 2850.79 | 132569.57 | 2850.79 | 9.9298 |  | 3249 | -305 | 2944 | 2928.4967 | 107.8415 | 2850.79 |  | 104.98
15.07.2008 09:00 | 3600 | 2 | 767.37 | GGB | 764.835 | 778.5 | 769.597 | 262.98 | GGB | 10766.6 | GGB | 9.82 | GGB | 1010.83 | GGB | 66.69 | GGB | 163132.77 | GGB | 130823.36 | GGB | 0 | 0 | 3216 | 3600 | 3200.36 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287486.72 | GGB | 287489.23 | 2895.5237 | 2888.8419 |  |  |  | 1 | 1 |  |  |  |  | 130823.36 | 2888.8419 | 130823.36 | 2888.8419 | 9.9298 |  | 3216 | -305 | 2911 | 2895.5237 | 105.2228 | 2888.8419 |  | 104.98
15.07.2008 10:00 | 3600 | 2 | 767.74 | GGB | 767.033 | 780.773 | 770.696 | 261.19 | GGB | 10691.4 | GGB | 9.82 | GGB | 1010.82 | GGB | 67.44 | GGB | 161057.54 | GGB | 128875.86 | GGB | 0 | 0 | 3163 | 3600 | 3147.31 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287524.78 | GGB | 287527.29 | 2842.5669 | 2842.5669 |  |  |  | 0 | 1 | [10 empty] | 3163 | -305 | 2858 | 2842.5669 | 101.7606 |  |  | #VALUE!
15.07.2008 11:00 | 3600 | 2 | 766.77 | GGB | 764.469 | 777.633 | 768.132 | 261.19 | GGB | 10584.5 | GGB | 9.79 | GGB | 1010.49 | GGB | 67.46 | GGB | 161421.75 | GGB | 129118 | GGB | 0 | 0 | 3176 | 3600 | 3160.1 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287562.84 | GGB | 287565.35 | 2855.5563 | 2855.5563 |  |  |  | 1 | 1 |  |  |  |  | 129118 | 2855.5563 | 129118 | 2855.5563 | 9.6874 |  | 3176 | -305 | 2871 | 2855.5563 | 102.4177 |  |  | #VALUE!
15.07.2008 12:00 | 3600 | 2 | 768.66 | GGB | 765.934 | 778.969 | 769.597 | 260.57 | GGB | 10619.5 | GGB | 9.82 | GGB | 1010.3 | GGB | 67.9 | GGB | 160548.08 | GGB | 128226.69 | GGB | 0 | 0 | 3110 | 3600 | 3093.76 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287600.9 | GGB | 287603.41 | 2789.6102 | 2789.6102 |  |  |  | 0 | 1 | [10 empty] | 3110 | -305 | 2805 | 2789.6102 | 99.3618 |  |  | #VALUE!
15.07.2008 13:00 | 3600 | 2 | 768.54 | GGB | 767.033 | 780.258 | 771.795 | 258.78 | GGB | 10556.8 | GGB | 9.81 | GGB | 1010.02 | GGB | 68.68 | GGB | 159194.67 | GGB | 126821.25 | GGB | 0 | 0 | 3090 | 3600 | 3073.92 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287638.96 | GGB | 287641.47 | 2769.6265 | 2769.6265 |  |  |  | 0 | 1 | [10 empty] | 3090 | -305 | 2785 | 2769.6265 | 97.5687 |  |  | #VALUE!
15.07.2008 14:00 | 3600 | 2 | 769.08 | GGB | 767.033 | 780.445 | 771.795 | 257.51 | GGB | 10511.7 | GGB | 9.82 | GGB | 1009.7 | GGB | 69.04 | GGB | 158138.34 | GGB | 125806.4 | GGB | 0 | 0 | 3028 | 3600 | 3012.17 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287677.01 | GGB | 287679.53 | 2707.6771 | 2707.6771 |  |  |  | 0 | 1 | [10 empty] | 3028 | -305 | 2723 | 2707.6771 | 94.6231 |  |  | #VALUE!
15.07.2008 15:00 | 3600 | 2 | 768.93 | GGB | 768.132 | 781.641 | 773.26 | 256.5 | GGB | 10478.6 | GGB | 9.81 | GGB | 1008.78 | GGB | 69.23 | GGB | 157528.75 | GGB | 125137.92 | GGB | 0 | 0 | 3024 | 3600 | 3008.79 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287715.07 | GGB | 287717.59 | 2703.6804 | 2703.6804 |  |  |  | 0 | 1 | [10 empty] | 3024 | -305 | 2719 | 2703.6804 | 93.9814 |  |  | #VALUE!
15.07.2008 16:00 | 3600 | 2 | 768.79 | GGB | 765.934 | 779.273 | 770.696 | 255.54 | GGB | 10422.9 | GGB | 9.8 | GGB | 1008.04 | GGB | 69.56 | GGB | 156875.15 | GGB | 124407.96 | GGB | 0 | 0 | 3013 | 3600 | 2997.12 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287753.13 | GGB | 287755.65 | 2692.6894 | 2692.6894 |  |  |  | 0 | 1 | [10 empty] | 3013 | -305 | 2708 | 2692.6894 | 93.0533 |  |  | #VALUE!
15.07.2008 17:00 | 3600 | 2 | 768.93 | GGB | 767.033 | 781.43 | 773.26 | 256.14 | GGB | 10444.4 | GGB | 9.8 | GGB | 1007.91 | GGB | 69.31 | GGB | 157112.83 | GGB | 124673.05 | GGB | 0 | 0 | 3003 | 3600 | 2987.37 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287791.19 | GGB | 287793.71 | 2682.6976 | 2682.6976 |  |  |  | 0 | 1 | [10 empty] | 3003 | -305 | 2698 | 2682.6976 | 92.9056 |  |  | #VALUE!
15.07.2008 18:00 | 3600 | 2 | 769.81 | GGB | 768.132 | 781.43 | 773.26 | 255.33 | GGB | 10422.2 | GGB | 9.81 | GGB | 1007.44 | GGB | 69.77 | GGB | 156604.47 | GGB | 124042.33 | GGB | 0 | 0 | 2945 | 3600 | 2929.76 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287829.25 | GGB | 287831.77 | 2624.7449 | 2624.7449 |  |  |  | 0 | 1 | [10 empty] | 2945 | -305 | 2640 | 2624.7449 | 90.4387 |  |  | #VALUE!
15.07.2008 19:00 | 3600 | 2 | 769.63 | GGB | 768.132 | 781.664 | 773.26 | 254.65 | GGB | 10387.4 | GGB | 9.8 | GGB | 1006.85 | GGB | 69.85 | GGB | 156324.98 | GGB | 123719.53 | GNB | 0 | 0 | 2941 | 3600 | 2925.02 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287867.3 | GGB | 287869.83 | 2620.7482 | 2620.7482 |  |  |  | 0 | 1 | [10 empty] | 2941 | -305 | 2636 | 2620.7482 | 90.066 |  |  | #VALUE!
15.07.2008 20:00 | 3600 | 2 | 769.82 | GGB | 768.498 | 781.781 | 772.161 | 254.76 | GGB | 10401.1 | GGB | 9.8 | GGB | 1006.78 | GGB | 69.66 | GGB | 156786.03 | GGB | 124145.57 | GGB | 0 | 0 | 2933 | 3600 | 2917.5 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287905.36 | GGB | 287907.89 | 2612.7547 | 2612.7547 |  |  |  | 0 | 1 | [10 empty] | 2933 | -305 | 2628 | 2612.7547 | 90.1005 |  |  | #VALUE!
15.07.2008 21:00 | 3600 | 2 | 768.94 | GGB | 767.033 | 780.867 | 771.795 | 255.48 | GGB | 10430.4 | GGB | 9.8 | GGB | 1007.1 | GGB | 69.13 | GGB | 157305.39 | GGB | 124789.74 | GGB | 0 | 0 | 2981 | 3600 | 2965.17 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287943.42 | GGB | 287945.95 | 2660.7155 | 2660.7155 |  |  |  | 0 | 1 | [10 empty] | 2981 | -305 | 2676 | 2660.7155 | 92.2306 |  |  | #VALUE!
15.07.2008 22:00 | 3600 | 2 | 768.28 | GGB | 765.934 | 779.766 | 770.696 | 256.87 | GGB | 10485.1 | GGB | 9.79 | GGB | 1007.93 | GGB | 68.45 | GGB | 158448.64 | GGB | 126048.94 | GGB | 0 | 0 | 3013 | 3600 | 2997.15 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 287981.48 | GGB | 287984.01 | 2692.6894 | 2692.6894 |  |  |  | 0 | 1 | [10 empty] | 3013 | -305 | 2708 | 2692.6894 | 94.2807 |  |  | #VALUE!
15.07.2008 23:00 | 3600 | 2 | 767.52 | GGB | 764.835 | 778.758 | 769.597 | 258.48 | GGB | 10537.3 | GGB | 9.79 | GGB | 1008.92 | GGB | 68.03 | GGB | 159495.06 | GGB | 127165.17 | GGB | 0 | 0 | 3086 | 3600 | 3069.77 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 288019.54 | GGB | 288022.07 | 2765.6298 | 2765.6298 |  |  |  | 0 | 1 | [10 empty] | 3086 | -305 | 2781 | 2765.6298 | 97.6922 |  |  | #VALUE!
15.07.2008 24:00 | 3600 | 2 | 767.29 | GGB | 764.835 | 778.922 | 769.597 | 260.15 | GGB | 10597.8 | GGB | 9.8 | GGB | 1009.46 | GGB | 67.73 | GGB | 160808.86 | GGB | 128393.46 | GGB | 0 | 0 | 3137 | 3600 | 3121.09 | GGB | 100 | GGB | 38.06 | GGB | 38.06 | GGB | 288057.6 | GGB | 288060.13 | 2816.5882 | 2816.5882 |  |  |  | 0 | 1 | [10 empty] | 3137 | -305 | 2832 | 2816.5882 | 100.4532 |  |  | #VALUE!
16.07.2008 01:00 | 3600 | 2 | 766.97 | GGB | 765.934 | 779.086 | 769.597 | 261.18 | GGB | 10641.3 | GGB | 9.8 | GGB | 1009.8 | GGB | 67.26 | GGB | 161604.4 | GGB | 129251.32 | GGB | 0 | 0 | 3182 | 3600 | 3166.12 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288096.05 | GGB | 288098.59 | 2861.5514 | 2861.5514 |  |  |  | 0 | 1 | [10 empty] | 3182 | -305 | 2877 | 2861.5514 | 102.7387 |  |  | #VALUE!
16.07.2008 02:00 | 3600 | 2 | 766.81 | GGB | 764.469 | 777 | 768.498 | 261.7 | GGB | 10659 | GGB | 9.8 | GGB | 1009.94 | GGB | 67.14 | GGB | 161963.12 | GGB | 129601.78 | GGB | 0 | 0 | 3209 | 3600 | 3193.18 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288134.51 | GGB | 288137.05 | 2888.5294 | 2888.5294 |  |  |  | 1 | 1 |  |  |  |  | 129601.78 | 2888.5294 | 129601.78 | 2888.5294 | 9.7337 |  | 3209 | -305 | 2904 | 2888.5294 | 103.9885 |  |  | #VALUE!
16.07.2008 03:00 | 3600 | 2 | 766.56 | GGB | 764.835 | 778.172 | 769.597 | 262.73 | GGB | 10700.6 | GGB | 9.8 | GGB | 1010.13 | GGB | 66.75 | GGB | 162765.26 | GGB | 130414.66 | GGB | 0 | 0 | 3226 | 3600 | 3209.82 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288172.97 | GGB | 288175.51 | 2905.5155 | 2897.8951 |  |  |  | 1 | 1 |  |  |  |  | 130414.66 | 2897.8951 | 130414.66 | 2897.8951 | 9.8265 |  | 3226 | -305 | 2921 | 2905.5155 | 105.2561 | 2897.8951 |  | 104.98
16.07.2008 04:00 | 3600 | 2 | 766.72 | GGB | 765.934 | 779.344 | 770.696 | 263.45 | GGB | 10726.1 | GGB | 9.81 | GGB | 1010.24 | GGB | 66.72 | GGB | 163259.31 | GGB | 130836.43 | GGB | 0 | 0 | 3235 | 3600 | 3218.88 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288211.43 | GGB | 288213.97 | 2914.5082 | 2888.5533 |  |  |  | 0 | 1 | [10 empty] | 3235 | -305 | 2930 | 2914.5082 | 105.9233 | 2888.5533 |  | 104.98
16.07.2008 05:00 | 3600 | 2 | 766.58 | GGB | 764.469 | 777.305 | 768.498 | 263.12 | GGB | 10717.9 | GGB | 9.81 | GGB | 1009.74 | GGB | 66.74 | GGB | 162941.32 | GGB | 130512.35 | GGB | 0 | 0 | 3236 | 3600 | 3220.57 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288249.89 | GGB | 288252.43 | 2915.5073 | 2895.726 |  |  |  | 1 | 1 |  |  |  |  | 130512.35 | 2895.726 | 130512.35 | 2895.726 | 9.8265 |  | 3236 | -305 | 2931 | 2915.5073 | 105.6971 | 2895.726 |  | 104.98
16.07.2008 06:00 | 3600 | 2 | 766.43 | GGB | 764.835 | 778.664 | 769.597 | 263.61 | GGB | 10726.1 | GGB | 9.8 | GGB | 1009.59 | GGB | 66.58 | GGB | 163390.25 | GGB | 130913.65 | GGB | 0 | 0 | 3246 | 3600 | 3229.95 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288288.35 | GGB | 288290.89 | 2925.4992 | 2886.8495 |  |  |  | 1 | 1 |  |  |  |  | 130913.65 | 2886.8495 | 130913.65 | 2886.8495 | 9.8265 |  | 3246 | -305 | 2941 | 2925.4992 | 106.3855 | 2886.8495 |  | 104.98
16.07.2008 07:00 | 3600 | 2 | 766.96 | GGB | 764.835 | 778.5 | 769.597 | 262.96 | GGB | 10724.8 | GGB | 9.82 | GGB | 1009.13 | GGB | 66.72 | GGB | 162625.52 | GGB | 130188.07 | GGB | 0 | 0 | 3211 | 3600 | 3195.04 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288326.81 | GGB | 288329.35 | 2890.5278 | 2890.5278 |  |  |  | 1 | 1 |  |  |  |  | 130188.07 | 2890.5278 | 130188.07 | 2890.5278 | 9.7845 |  | 3211 | -305 | 2906 | 2890.5278 | 104.5312 |  |  | #VALUE!
16.07.2008 08:00 | 3600 | 2 | 766.8 | GGB | 763.37 | 777.586 | 768.498 | 262.41 | GGB | 10696.5 | GGB | 9.81 | GGB | 1008.86 | GGB | 66.9 | GGB | 162206.29 | GGB | 129746.26 | GGB | 0 | 0 | 3211 | 3600 | 3195.51 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288365.26 | GGB | 288367.81 | 2890.5278 | 2890.5278 |  |  |  | 0 | 1 | [10 empty] | 3211 | -305 | 2906 | 2890.5278 | 104.1764 |  |  | #VALUE!
16.07.2008 09:00 | 3600 | 2 | 767.47 | GGB | 765.934 | 779.789 | 770.33 | 261.32 | GGB | 10673.2 | GGB | 9.82 | GGB | 1008.26 | GGB | 67.21 | GGB | 160906.79 | GGB | 128514.63 | GGB | 0 | 0 | 3174 | 3600 | 3157.97 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288403.72 | GGB | 288406.27 | 2853.558 | 2853.558 |  |  |  | 0 | 1 | [10 empty] | 3174 | -305 | 2869 | 2853.558 | 101.8678 |  |  | #VALUE!
16.07.2008 10:00 | 3600 | 2 | 767.51 | GGB | 767.033 | 779.93 | 771.429 | 260.52 | GGB | 10629.7 | GGB | 9.82 | GGB | 1007.85 | GGB | 67.58 | GGB | 160138.76 | GGB | 127711.83 | GGB | 0 | 0 | 3154 | 3600 | 3138.18 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288442.18 | GGB | 288444.73 | 2833.5743 | 2833.5743 |  |  |  | 0 | 1 | [10 empty] | 3154 | -305 | 2849 | 2833.5743 | 100.5225 |  |  | #VALUE!
16.07.2008 11:00 | 3600 | 2 | 767.99 | GGB | 765.934 | 779.93 | 770.33 | 258.68 | GGB | 10555.5 | GGB | 9.82 | GGB | 1007.06 | GGB | 68.47 | GGB | 158378.21 | GGB | 125878.13 | GGB | 0 | 0 | 3111 | 3600 | 3095.42 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288480.64 | GGB | 288483.19 | 2790.6094 | 2790.6094 |  |  |  | 0 | 1 | [10 empty] | 3111 | -305 | 2806 | 2790.6094 | 97.5769 |  |  | #VALUE!
16.07.2008 12:00 | 3600 | 2 | 768.39 | GGB | 767.033 | 780.117 | 771.429 | 257.15 | GGB | 10484.4 | GGB | 9.81 | GGB | 1006.02 | GGB | 69.02 | GGB | 156920.27 | GGB | 124392.01 | GGB | 0 | 0 | 3053 | 3600 | 3036.9 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288519.1 | GGB | 288521.65 | 2732.6567 | 2732.6567 |  |  |  | 0 | 1 | [10 empty] | 3053 | -305 | 2748 | 2732.6567 | 94.4224 |  |  | #VALUE!
16.07.2008 13:00 | 3600 | 2 | 767.99 | GGB | 764.835 | 778.055 | 768.864 | 255.96 | GGB | 10423 | GGB | 9.8 | GGB | 1005.31 | GGB | 69.51 | GGB | 156256.76 | GGB | 123600.49 | GNB | 0 | 0 | 3061 | 3335 | 3045.26 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288557.56 | GGB | 288560.11 | 2740.6502 | 2740.6502 |  |  |  | 1 | 1 |  |  |  |  | 123600.49 | 2740.6502 |  | 2740.6502 | 8.8077 |  | 3061 | -305 | 2756 | 2740.6502 | 94.096 |  |  | #VALUE!
16.07.2008 14:00 | 3600 | 2 | 768.32 | GGB | 765.934 | 779.016 | 770.33 | 256.18 | GGB | 10437.1 | GGB | 9.81 | GGB | 1005.76 | GGB | 69.72 | GGB | 156077.41 | GGB | 123437.5 | GNB | 0 | 0 | 3074 | 3600 | 3058.15 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288596.02 | GGB | 288598.57 | 2753.6396 | 2753.6396 |  |  |  | 0 | 1 | [10 empty] | 3074 | -305 | 2769 | 2753.6396 | 94.4173 |  |  | #VALUE!
16.07.2008 15:00 | 3600 | 2 | 767.6 | GGB | 764.835 | 778.102 | 768.864 | 256.5 | GGB | 10443.9 | GGB | 9.8 | GGB | 1004.84 | GGB | 69.54 | GGB | 156249.06 | GGB | 123524.15 | GNB | 0 | 0 | 3096 | 3600 | 3080.44 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288634.47 | GGB | 288637.03 | 2775.6216 | 2775.6216 |  |  |  | 1 | 1 |  |  |  |  | 123524.15 | 2775.6216 |  | 2775.6216 | 8.9146 |  | 3096 | -305 | 2791 | 2775.6216 | 95.2379 |  |  | #VALUE!
16.07.2008 16:00 | 3600 | 2 | 767.38 | GGB | 764.835 | 777.914 | 768.864 | 258.12 | GGB | 10502.3 | GGB | 9.8 | GGB | 1004.87 | GGB | 69.11 | GGB | 157672.9 | GGB | 124812.92 | GGB | 0 | 0 | 3157 | 3600 | 3141.05 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288672.93 | GGB | 288675.49 | 2836.5718 | 2836.5718 |  |  |  | 1 | 1 |  |  |  |  | 124812.92 | 2836.5718 |  | 2836.5718 | 9.2054 |  | 3157 | -305 | 2852 | 2836.5718 | 98.3447 |  |  | #VALUE!
16.07.2008 17:00 | 3600 | 2 | 768.78 | GGB | 765.934 | 779.766 | 770.33 | 256.47 | GGB | 10470 | GGB | 9.82 | GGB | 1004.08 | GGB | 69.69 | GGB | 156280.97 | GGB | 123402.1 | GNB | 0 | 0 | 3081 | 3600 | 3065.59 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288711.39 | GGB | 288713.95 | 2760.6339 | 2760.6339 |  |  |  | 0 | 1 | [10 empty] | 3081 | -305 | 2776 | 2760.6339 | 94.63 |  |  | #VALUE!
16.07.2008 18:00 | 3600 | 2 | 768.31 | GGB | 767.033 | 780.938 | 771.429 | 255.52 | GGB | 10413.6 | GGB | 9.8 | GGB | 1003.45 | GGB | 69.72 | GGB | 155515.14 | GGB | 122711.36 | GNB | 0 | 0 | 3044 | 3600 | 3028.02 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288749.85 | GGB | 288752.41 | 2723.6641 | 2723.6641 |  |  |  | 0 | 1 | [10 empty] | 3044 | -305 | 2739 | 2723.6641 | 92.8401 |  |  | #VALUE!
16.07.2008 19:00 | 3600 | 2 | 768.41 | GGB | 765.934 | 780.188 | 771.429 | 255.19 | GGB | 10391.9 | GGB | 9.8 | GGB | 1003.17 | GGB | 70.06 | GGB | 155422.71 | GGB | 122481 | GNB | 0 | 0 | 3059 | 3600 | 3042.87 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288788.31 | GGB | 288790.87 | 2738.6518 | 2738.6518 |  |  |  | 0 | 1 | [10 empty] | 3059 | -305 | 2754 | 2738.6518 | 93.1758 |  |  | #VALUE!
16.07.2008 20:00 | 3600 | 2 | 768.78 | GGB | 767.033 | 780.188 | 771.429 | 255 | GGB | 10389.1 | GGB | 9.81 | GGB | 1002.73 | GGB | 70.31 | GGB | 155121.21 | GGB | 122100.4 | GNB | 0 | 0 | 3037 | 3600 | 3021.16 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288826.77 | GGB | 288829.33 | 2716.6698 | 2716.6698 |  |  |  | 0 | 1 | [10 empty] | 3037 | -305 | 2732 | 2716.6698 | 92.1407 |  |  | #VALUE!
16.07.2008 21:00 | 3600 | 2 | 768.11 | GGB | 764.835 | 779.086 | 768.864 | 254.88 | GGB | 10365 | GGB | 9.79 | GGB | 1002.13 | GGB | 70.33 | GGB | 154975.97 | GGB | 121908.66 | GNB | 0 | 0 | 3046 | 3600 | 3029.88 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288865.23 | GGB | 288867.79 | 2725.6624 | 2725.6624 |  |  |  | 0 | 1 | [10 empty] | 3046 | -305 | 2741 | 2725.6624 | 92.3005 |  |  | #VALUE!
16.07.2008 22:00 | 3600 | 2 | 768.13 | GGB | 764.835 | 778.992 | 769.963 | 255.81 | GGB | 10400.6 | GGB | 9.8 | GGB | 1002.34 | GGB | 70.08 | GGB | 155461.22 | GGB | 122405.02 | GNB | 0 | 0 | 3068 | 3600 | 3052.07 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288903.68 | GGB | 288906.25 | 2747.6445 | 2747.6445 |  |  |  | 0 | 1 | [10 empty] | 3068 | -305 | 2763 | 2747.6445 | 93.4237 |  |  | #VALUE!
16.07.2008 23:00 | 3600 | 2 | 767.23 | GGB | 763.37 | 778.031 | 768.864 | 256.61 | GGB | 10447.4 | GGB | 9.79 | GGB | 1002.65 | GGB | 69.72 | GGB | 156875.15 | GGB | 123684.34 | GNB | 0 | 0 | 3137 | 3600 | 3121.63 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288942.14 | GGB | 288944.71 | 2816.5882 | 2816.5882 |  |  |  | 0 | 1 | [10 empty] | 3137 | -305 | 2832 | 2816.5882 | 96.7688 |  |  | #VALUE!
16.07.2008 24:00 | 3600 | 2 | 767.18 | GGB | 764.469 | 778.008 | 769.963 | 258.22 | GGB | 10478.2 | GGB | 9.8 | GGB | 1002.5 | GGB | 69.24 | GGB | 157281.18 | GGB | 124159.32 | GGB | 0 | 0 | 3167 | 3600 | 3151.6 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 288980.6 | GGB | 288983.17 | 2846.5637 | 2846.5637 |  |  |  | 1 | 1 |  |  |  |  | 124159.32 | 2846.5637 |  | 2846.5637 | 9.1895 |  | 3167 | -305 | 2862 | 2846.5637 | 98.1743 |  |  | #VALUE!
17.07.2008 01:00 | 3600 | 2 | 767.54 | GGB | 765.934 | 778.313 | 769.963 | 259.01 | GGB | 10511.4 | GGB | 9.81 | GGB | 1002.64 | GGB | 69.09 | GGB | 158006.3 | GGB | 124805.55 | GGB | 0 | 0 | 3145 | 3600 | 3129.67 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289018.34 | GGB | 289020.91 | 2824.5816 | 2824.5816 |  |  |  | 1 | 1 |  |  |  |  | 124805.55 | 2824.5816 |  | 2824.5816 | 9.3408 |  | 3145 | -305 | 2840 | 2824.5816 | 97.9232 |  |  | #VALUE!
17.07.2008 02:00 | 3600 | 2 | 767.13 | GGB | 764.835 | 778.289 | 769.963 | 259.56 | GGB | 10530.6 | GGB | 9.8 | GGB | 1002.62 | GGB | 68.63 | GGB | 158456.34 | GGB | 125327.03 | GGB | 0 | 0 | 3167 | 3600 | 3151.24 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289056.08 | GGB | 289058.65 | 2846.5637 | 2846.5637 |  |  |  | 1 | 1 |  |  |  |  | 125327.03 | 2846.5637 |  | 2846.5637 | 9.4529 |  | 3167 | -305 | 2862 | 2846.5637 | 99.0976 |  |  | #VALUE!
17.07.2008 03:00 | 3600 | 2 | 767.07 | GGB | 764.835 | 779.203 | 769.963 | 260.23 | GGB | 10559.2 | GGB | 9.8 | GGB | 1002.5 | GGB | 68.34 | GGB | 159195.77 | GGB | 126004.42 | GGB | 0 | 0 | 3182 | 3600 | 3166.4 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289093.82 | GGB | 289096.39 | 2861.5514 | 2861.5514 |  |  |  | 0 | 1 | [10 empty] | 3182 | -305 | 2877 | 2861.5514 | 100.1578 |  |  | #VALUE!
17.07.2008 04:00 | 3600 | 2 | 767.04 | GGB | 764.835 | 777.844 | 769.597 | 260.45 | GGB | 10580.7 | GGB | 9.81 | GGB | 1001.99 | GGB | 68.08 | GGB | 159660.11 | GGB | 126404.5 | GGB | 0 | 0 | 3189 | 3600 | 3173.08 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289131.56 | GGB | 289134.13 | 2868.5457 | 2868.5457 |  |  |  | 1 | 1 |  |  |  |  | 126404.5 | 2868.5457 | 126404.5 | 2868.5457 | 9.6078 |  | 3189 | -305 | 2884 | 2868.5457 | 100.7214 |  |  | #VALUE!
17.07.2008 05:00 | 3600 | 2 | 766.89 | GGB | 764.835 | 777.984 | 769.597 | 259.58 | GGB | 10566.2 | GGB | 9.81 | GGB | 1001.48 | GGB | 67.82 | GGB | 158964.69 | GGB | 125885.97 | GGB | 0 | 0 | 3158 | 3600 | 3141.99 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289169.3 | GGB | 289171.87 | 2837.571 | 2837.571 |  |  |  | 1 | 1 |  |  |  |  | 125885.97 | 2837.571 | 125885.97 | 2837.571 | 9.465 |  | 3158 | -305 | 2853 | 2837.571 | 99.2251 |  |  | #VALUE!
17.07.2008 06:00 | 3600 | 2 | 766.87 | GGB | 764.835 | 778.125 | 769.597 | 259.52 | GGB | 10569.7 | GGB | 9.81 | GGB | 1000.51 | GGB | 67.59 | GGB | 159070.33 | GGB | 125929.43 | GGB | 0 | 0 | 3167 | 3600 | 3151.48 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289207.04 | GGB | 289209.61 | 2846.5637 | 2846.5637 |  |  |  | 1 | 1 |  |  |  |  | 125929.43 | 2846.5637 | 125929.43 | 2846.5637 | 9.4983 |  | 3167 | -305 | 2862 | 2846.5637 | 99.5739 |  |  | #VALUE!
17.07.2008 07:00 | 3600 | 2 | 767.01 | GGB | 764.835 | 778.289 | 769.597 | 258.95 | GGB | 10556.4 | GGB | 9.81 | GGB | 999.88 | GGB | 67.71 | GGB | 158590.58 | GGB | 125428.7 | GGB | 0 | 0 | 3143 | 3600 | 3127.01 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289244.78 | GGB | 289247.35 | 2822.5833 | 2822.5833 |  |  |  | 1 | 1 |  |  |  |  | 125428.7 | 2822.5833 | 125428.7 | 2822.5833 | 9.3808 |  | 3143 | -305 | 2838 | 2822.5833 | 98.3425 |  |  | #VALUE!
17.07.2008 08:00 | 3600 | 2 | 766.53 | GGB | 763.37 | 777 | 768.132 | 258.52 | GGB | 10520.8 | GGB | 9.8 | GGB | 1000 | GGB | 67.86 | GGB | 158110.83 | GGB | 125009.91 | GGB | 0 | 0 | 3178 | 3600 | 3162.15 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289282.52 | GGB | 289285.09 | 2857.5547 | 2857.5547 |  |  |  | 0 | 1 | [10 empty] | 3178 | -305 | 2873 | 2857.5547 | 99.2285 |  |  | #VALUE!
17.07.2008 09:00 | 3600 | 2 | 765.83 | GGB | 764.469 | 777.188 | 768.132 | 259.11 | GGB | 10534.6 | GGB | 9.79 | GGB | 1000.14 | GGB | 67.35 | GGB | 158752.33 | GGB | 125721.48 | GGB | 0 | 0 | 3229 | 3600 | 3213.39 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289320.26 | GGB | 289322.83 | 2908.5131 | 2908.5131 |  |  |  | 1 | 1 |  |  |  |  | 125721.48 | 2908.5131 | 125721.48 | 2908.5131 | 9.689 |  | 3229 | -305 | 2924 | 2908.5131 | 101.5729 |  |  | #VALUE!
17.07.2008 10:00 | 3600 | 2 | 766.9 | GGB | 764.469 | 778.148 | 769.597 | 260.1 | GGB | 10614.2 | GGB | 9.82 | GGB | 1001.09 | GGB | 66.71 | GGB | 159928.59 | GGB | 127013.47 | GGB | 0 | 0 | 3176 | 3600 | 3160.3 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289358 | GGB | 289360.57 | 2855.5563 | 2855.5563 |  |  |  | 1 | 1 |  |  |  |  | 127013.47 | 2855.5563 | 127013.47 | 2855.5563 | 9.6103 |  | 3176 | -305 | 2871 | 2855.5563 | 100.7484 |  |  | #VALUE!
17.07.2008 11:00 | 3600 | 2 | 767.03 | GGB | 764.835 | 777.891 | 768.498 | 259.34 | GGB | 10591.5 | GGB | 9.81 | GGB | 1001.44 | GGB | 66.87 | GGB | 159371.82 | GGB | 126555.85 | GGB | 0 | 0 | 3146 | 3600 | 3129.98 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289395.74 | GGB | 289398.31 | 2825.5808 | 2825.5808 |  |  |  | 1 | 1 |  |  |  |  | 126555.85 | 2825.5808 | 126555.85 | 2825.5808 | 9.4752 |  | 3146 | -305 | 2841 | 2825.5808 | 99.3316 |  |  | #VALUE!
17.07.2008 12:00 | 3600 | 2 | 767.07 | GGB | 764.835 | 777.82 | 769.597 | 259.09 | GGB | 10576.4 | GGB | 9.81 | GGB | 1002.22 | GGB | 66.85 | GGB | 159278.29 | GGB | 126587.7 | GGB | 0 | 0 | 3143 | 3600 | 3127.61 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289433.48 | GGB | 289436.05 | 2822.5833 | 2822.5833 |  |  |  | 1 | 1 |  |  |  |  | 126587.7 | 2822.5833 | 126587.7 | 2822.5833 | 9.4675 |  | 3143 | -305 | 2838 | 2822.5833 | 99.2512 |  |  | #VALUE!
17.07.2008 13:00 | 3600 | 2 | 767.62 | GGB | 764.835 | 778.969 | 769.597 | 258.35 | GGB | 10545.3 | GGB | 9.81 | GGB | 1001.75 | GGB | 66.97 | GGB | 159053.82 | GGB | 126304.95 | GGB | 0 | 0 | 3073 | 3600 | 3057.63 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289471.22 | GGB | 289473.79 | 2752.6404 | 2752.6404 |  |  |  | 0 | 1 | [10 empty] | 3073 | -305 | 2768 | 2752.6404 | 96.5756 |  |  | #VALUE!
17.07.2008 14:00 | 3600 | 2 | 767.98 | GGB | 767.033 | 779.813 | 770.696 | 257.23 | GGB | 10510.5 | GGB | 9.81 | GGB | 1001.74 | GGB | 67.31 | GGB | 158254.98 | GGB | 125542.3 | GGB | 0 | 0 | 3041 | 3600 | 3024.81 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289508.96 | GGB | 289511.53 | 2720.6665 | 2720.6665 |  |  |  | 0 | 1 | [10 empty] | 3041 | -305 | 2736 | 2720.6665 | 94.8774 |  |  | #VALUE!
17.07.2008 15:00 | 3600 | 2 | 768.07 | GGB | 765.934 | 780.07 | 770.696 | 256.37 | GGB | 10476.6 | GGB | 9.81 | GGB | 1001.19 | GGB | 67.44 | GGB | 157656.39 | GGB | 124950.28 | GGB | 0 | 0 | 3014 | 3600 | 2998.27 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289546.7 | GGB | 289549.27 | 2693.6886 | 2693.6886 |  |  |  | 0 | 1 | [10 empty] | 3014 | -305 | 2709 | 2693.6886 | 93.4937 |  |  | #VALUE!
17.07.2008 16:00 | 3600 | 2 | 768 | GGB | 767.033 | 780.891 | 771.795 | 256.69 | GGB | 10485.1 | GGB | 9.81 | GGB | 1001.34 | GGB | 67.52 | GGB | 157837.95 | GGB | 125083.49 | GGB | 0 | 0 | 3028 | 3600 | 3012.16 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289584.44 | GGB | 289587.01 | 2707.6771 | 2707.6771 |  |  |  | 0 | 1 | [10 empty] | 3028 | -305 | 2723 | 2707.6771 | 94.0794 |  |  | #VALUE!
17.07.2008 17:00 | 3600 | 2 | 768.07 | GGB | 767.033 | 780.938 | 771.795 | 256.05 | GGB | 10466.8 | GGB | 9.81 | GGB | 1001.36 | GGB | 67.51 | GGB | 157493.54 | GGB | 124816.65 | GGB | 0 | 0 | 2992 | 3600 | 2976.69 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289622.18 | GGB | 289624.75 | 2671.7065 | 2671.7065 |  |  |  | 0 | 1 | [10 empty] | 2992 | -305 | 2687 | 2671.7065 | 92.6315 |  |  | #VALUE!
17.07.2008 18:00 | 3600 | 2 | 767.67 | GGB | 765.934 | 778.875 | 770.696 | 256.55 | GGB | 10477.4 | GGB | 9.8 | GGB | 1001.43 | GGB | 67.28 | GGB | 157957.89 | GGB | 125278.63 | GGB | 0 | 0 | 3024 | 3600 | 3008.36 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289659.92 | GGB | 289662.49 | 2703.6804 | 2703.6804 |  |  |  | 0 | 1 | [10 empty] | 3024 | -305 | 2719 | 2703.6804 | 94.087 |  |  | #VALUE!
17.07.2008 19:00 | 3600 | 2 | 767.4 | GGB | 765.934 | 778.945 | 769.597 | 257.3 | GGB | 10498.7 | GGB | 9.8 | GGB | 1002.13 | GGB | 67.52 | GGB | 157942.48 | GGB | 125267.55 | GGB | 0 | 0 | 3055 | 3600 | 3039.21 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289697.66 | GGB | 289700.23 | 2734.6551 | 2734.6551 |  |  |  | 0 | 1 | [10 empty] | 3055 | -305 | 2750 | 2734.6551 | 95.1565 |  |  | #VALUE!
17.07.2008 20:00 | 3600 | 2 | 767.99 | GGB | 767.033 | 781.055 | 771.795 | 257.8 | GGB | 10509.7 | GGB | 9.81 | GGB | 1002.25 | GGB | 67.7 | GGB | 158282.49 | GGB | 125483.74 | GGB | 0 | 0 | 3043 | 3600 | 3027.05 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289735.4 | GGB | 289737.97 | 2722.6649 | 2722.6649 |  |  |  | 0 | 1 | [10 empty] | 3043 | -305 | 2738 | 2722.6649 | 94.9028 |  |  | #VALUE!
17.07.2008 21:00 | 3600 | 2 | 767.89 | GGB | 765.934 | 778.992 | 770.696 | 257.35 | GGB | 10494.6 | GGB | 9.8 | GGB | 1002.31 | GGB | 67.85 | GGB | 158049.21 | GGB | 125250.64 | GGB | 0 | 0 | 3045 | 3600 | 3029.29 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289773.14 | GGB | 289775.71 | 2724.6633 | 2724.6633 |  |  |  | 0 | 1 | [10 empty] | 3045 | -305 | 2740 | 2724.6633 | 94.7961 |  |  | #VALUE!
17.07.2008 22:00 | 3600 | 2 | 767.72 | GGB | 765.934 | 779.063 | 769.597 | 257.88 | GGB | 10520.9 | GGB | 9.8 | GGB | 1002.7 | GGB | 67.72 | GGB | 158524.56 | GGB | 125725.43 | GGB | 0 | 0 | 3075 | 3600 | 3058.81 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289810.88 | GGB | 289813.45 | 2754.6388 | 2754.6388 |  |  |  | 0 | 1 | [10 empty] | 3075 | -305 | 2770 | 2754.6388 | 96.2023 |  |  | #VALUE!
17.07.2008 23:00 | 3600 | 2 | 767.38 | GGB | 764.835 | 778.734 | 769.597 | 259.01 | GGB | 10549.2 | GGB | 9.8 | GGB | 1003.55 | GGB | 67.59 | GGB | 159232.08 | GGB | 126441.62 | GGB | 0 | 0 | 3109 | 3600 | 3093.59 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289848.62 | GGB | 289851.19 | 2788.611 | 2788.611 |  |  |  | 0 | 1 | [10 empty] | 3109 | -305 | 2804 | 2788.611 | 97.9435 |  |  | #VALUE!
17.07.2008 24:00 | 3600 | 2 | 766.93 | GGB | 764.835 | 778.688 | 769.597 | 259.88 | GGB | 10611 | GGB | 9.8 | GGB | 1004.39 | GGB | 67.03 | GGB | 160850.67 | GGB | 128044.13 | GGB | 0 | 0 | 3166 | 3600 | 3150.41 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 289886.36 | GGB | 289888.93 | 2845.5645 | 2845.5645 |  |  |  | 1 | 1 |  |  |  |  | 128044.13 | 2845.5645 | 128044.13 | 2845.5645 | 9.6544 |  | 3166 | -305 | 2861 | 2845.5645 | 101.2105 |  |  | #VALUE!
18.07.2008 01:00 | 3600 | 2 | 766.7 | GGB | 764.835 | 778.547 | 768.498 | 262.03 | GGB | 10642.8 | GGB | 9.8 | GGB | 1005.43 | GGB | 67.03 | GGB | 161566.99 | GGB | 128749.62 | GGB | 0 | 0 | 3215 | 3600 | 3199.22 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 289924.47 | GGB | 289927.04 | 2894.5245 | 2894.5245 |  |  |  | 1 | 1 |  |  |  |  | 128749.62 | 2894.5245 | 128749.62 | 2894.5245 | 9.7788 |  | 3215 | -305 | 2910 | 2894.5245 | 103.5191 |  |  | #VALUE!
18.07.2008 02:00 | 3600 | 2 | 766.49 | GGB | 764.469 | 777.539 | 768.498 | 263.31 | GGB | 10697.5 | GGB | 9.8 | GGB | 1005.79 | GGB | 66.59 | GGB | 162772.96 | GGB | 129925.25 | GGB | 0 | 0 | 3241 | 3600 | 3225.4 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 289962.58 | GGB | 289965.15 | 2920.5033 | 2908.811 |  |  |  | 1 | 1 |  |  |  |  | 129925.25 | 2908.811 | 129925.25 | 2908.811 | 9.9168 |  | 3241 | -305 | 2936 | 2920.5033 | 105.402 | 2908.811 |  | 104.98
18.07.2008 03:00 | 3600 | 2 | 766.44 | GGB | 762.271 | 775.523 | 767.033 | 263.98 | GGB | 10733.6 | GGB | 9.8 | GGB | 1006.39 | GGB | 66.11 | GGB | 163686.24 | GGB | 130916.66 | GGB | 0 | 0 | 3245 | 3600 | 3229.54 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290000.7 | GGB | 290003.26 | 2924.5 | 2886.7831 |  |  |  | 0 | 1 | [10 empty] | 3245 | -305 | 2940 | 2924.5 | 106.3516 | 2886.7831 |  | 104.98
18.07.2008 04:00 | 3600 | 2 | 766.2 | GGB | 764.835 | 777.914 | 769.597 | 264.98 | GGB | 10780.6 | GGB | 9.81 | GGB | 1006.49 | GGB | 65.47 | GGB | 164705.16 | GGB | 131993.68 | GGB | 0 | 0 | 3265 | 3600 | 3249.07 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290038.81 | GGB | 290041.37 | 2944.4837 | 2863.228 |  |  |  | 1 | 1 |  |  |  |  | 131993.68 | 2863.228 | 131993.68 | 2863.228 | 9.9168 |  | 3265 | -305 | 2960 | 2944.4837 | 107.9592 | 2863.228 |  | 104.98
18.07.2008 05:00 | 3600 | 2 | 765.87 | GGB | 765.934 | 777.727 | 769.597 | 265.38 | GGB | 10791.4 | GGB | 9.8 | GGB | 1007.11 | GGB | 65.21 | GGB | 165186 | GGB | 132562.19 | GGB | 0 | 0 | 3274 | 3600 | 3257.89 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290076.92 | GGB | 290079.48 | 2953.4763 | 2850.9487 |  |  |  | 1 | 1 |  |  |  |  | 132562.19 | 2850.9487 | 132562.19 | 2850.9487 | 9.9168 |  | 3274 | -305 | 2969 | 2953.4763 | 108.7554 | 2850.9487 |  | 104.98
18.07.2008 06:00 | 3600 | 2 | 766.28 | GGB | 765.934 | 778.547 | 769.597 | 265.73 | GGB | 10831.1 | GGB | 9.81 | GGB | 1007.23 | GGB | 65.07 | GGB | 165934.23 | GGB | 133231.21 | GGB | 0 | 0 | 3270 | 3600 | 3254.01 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290115.03 | GGB | 290117.59 | 2949.4796 | 2836.6326 |  |  |  | 1 | 1 |  |  |  |  | 133231.21 | 2836.6326 | 133231.21 | 2836.6326 | 9.9168 |  | 3270 | -305 | 2965 | 2949.4796 | 109.1563 | 2836.6326 |  | 104.98
18.07.2008 07:00 | 3600 | 2 | 766.12 | GGB | 765.934 | 778.547 | 769.597 | 265 | GGB | 10822.5 | GGB | 9.81 | GGB | 1007.26 | GGB | 65.06 | GGB | 165653.65 | GGB | 133016.89 | GGB | 0 | 0 | 3267 | 3600 | 3251.09 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290153.15 | GGB | 290155.7 | 2946.482 | 2841.2031 |  |  |  | 1 | 1 |  |  |  |  | 133016.89 | 2841.2031 | 133016.89 | 2841.2031 | 9.9168 |  | 3267 | -305 | 2962 | 2946.482 | 108.87 | 2841.2031 |  | 104.98
18.07.2008 08:00 | 3600 | 2 | 766.86 | GGB | 763.37 | 777.539 | 768.498 | 263.49 | GGB | 10791.2 | GGB | 9.82 | GGB | 1007.41 | GGB | 65.45 | GGB | 163871.1 | GGB | 131451.42 | GGB | 0 | 0 | 3219 | 3600 | 3203.13 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290191.26 | GGB | 290193.81 | 2898.5212 | 2875.0393 |  |  |  | 0 | 1 | [10 empty] | 3219 | -305 | 2914 | 2898.5212 | 105.8374 | 2875.0393 |  | 104.98
18.07.2008 09:00 | 3600 | 2 | 767.19 | GGB | 765.934 | 779.625 | 770.696 | 262.1 | GGB | 10738.8 | GGB | 9.82 | GGB | 1007.48 | GGB | 66.18 | GGB | 162506.68 | GGB | 130087.09 | GGB | 0 | 0 | 3104 | 3208 | 3088.16 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290229.37 | GGB | 290231.92 | 3088.16 | 2905.1922 |  |  |  | 0 | 1 | [14 empty] | 111.5916 | 2905.1922 |  | 104.98
18.07.2008 10:00 | 3600 | 2 | 767.49 | GGB | 765.934 | 779.93 | 770.696 | 260.32 | GGB | 10642.4 | GGB | 9.81 | GGB | 1007.09 | GGB | 67.02 | GGB | 160504.07 | GGB | 128114.36 | GGB | 0 | 0 | 2860 | 3153 | 2844.39 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290267.48 | GGB | 290270.03 | 2844.39 | 2844.39 |  |  |  | 0 | 1 | [14 empty] | 101.2242 |  |  | #VALUE!
18.07.2008 11:00 | 3600 | 2 | 767.85 | GGB | 767.033 | 779.93 | 771.795 | 259.34 | GGB | 10590 | GGB | 9.82 | GGB | 1007.09 | GGB | 67.51 | GGB | 159499.46 | GGB | 127131.42 | GGB | 0 | 0 | 2812 | 3600 | 2796.86 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290305.6 | GGB | 290308.14 | 2796.86 | 2796.86 |  |  |  | 0 | 1 | [14 empty] | 98.7691 |  |  | #VALUE!
18.07.2008 12:00 | 3600 | 2 | 768.05 | GGB | 767.033 | 780.891 | 771.795 | 258.74 | GGB | 10546.7 | GGB | 9.81 | GGB | 1006.59 | GGB | 68.06 | GGB | 159153.95 | GGB | 126586.46 | GGB | 0 | 0 | 2807 | 3600 | 2791.88 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290343.71 | GGB | 290346.25 | 2791.88 | 2791.88 |  |  |  | 0 | 1 | [14 empty] | 98.1706 |  |  | #VALUE!
18.07.2008 13:00 | 3600 | 2 | 768.83 | GGB | 767.033 | 779.883 | 771.795 | 257.45 | GGB | 10498.1 | GGB | 9.81 | GGB | 1006.74 | GGB | 68.57 | GGB | 158072.32 | GGB | 125559.45 | GGB | 0 | 0 | 2748 | 3600 | 2732.34 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290381.82 | GGB | 290384.36 | 2732.34 | 2732.34 |  |  |  | 0 | 1 | [14 empty] | 95.2975 |  |  | #VALUE!
18.07.2008 14:00 | 3600 | 2 | 769.32 | GGB | 767.033 | 781.008 | 772.161 | 255.75 | GGB | 10452.7 | GGB | 9.81 | GGB | 1005.51 | GGB | 68.75 | GGB | 157047.91 | GGB | 124526.03 | GGB | 0 | 0 | 2685 | 3600 | 2669.13 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290419.93 | GGB | 290422.47 | 2669.13 | 2669.13 |  |  |  | 0 | 1 | [14 empty] | 92.3267 |  |  | #VALUE!
18.07.2008 15:00 | 3600 | 2 | 769.06 | GGB | 767.033 | 780.797 | 772.161 | 256.23 | GGB | 10457.9 | GGB | 9.8 | GGB | 1005.22 | GGB | 68.68 | GGB | 157622.28 | GGB | 124972.64 | GGB | 0 | 0 | 2722 | 3600 | 2706.36 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290458.04 | GGB | 290460.58 | 2706.36 | 2706.36 |  |  |  | 0 | 1 | [14 empty] | 93.9503 |  |  | #VALUE!
18.07.2008 16:00 | 3600 | 2 | 769.17 | GGB | 765.934 | 780.563 | 770.696 | 256.13 | GGB | 10452.8 | GGB | 9.8 | GGB | 1005.28 | GGB | 68.7 | GGB | 157308.69 | GGB | 124723.51 | GGB | 0 | 0 | 2702 | 3600 | 2686.23 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290496.16 | GGB | 290498.69 | 2686.23 | 2686.23 |  |  |  | 0 | 1 | [14 empty] | 93.0656 |  |  | #VALUE!
18.07.2008 17:00 | 3600 | 2 | 769.22 | GGB | 767.033 | 780.844 | 771.795 | 255.88 | GGB | 10448 | GGB | 9.81 | GGB | 1005.27 | GGB | 68.79 | GGB | 156830.04 | GGB | 124312.28 | GGB | 0 | 0 | 2708 | 3600 | 2692.89 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290534.27 | GGB | 290536.8 | 2692.89 | 2692.89 |  |  |  | 0 | 1 | [14 empty] | 92.9887 |  |  | #VALUE!
18.07.2008 18:00 | 3600 | 2 | 769.25 | GGB | 765.934 | 779.766 | 770.696 | 255.64 | GGB | 10438.6 | GGB | 9.81 | GGB | 1005.39 | GGB | 68.88 | GGB | 156475.73 | GGB | 124010.76 | GNB | 0 | 0 | 2694 | 3600 | 2678.62 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290572.38 | GGB | 290574.91 | 2678.62 | 2678.62 |  |  |  | 0 | 1 | [14 empty] | 92.2716 |  |  | #VALUE!
18.07.2008 19:00 | 3600 | 2 | 769.14 | GGB | 767.033 | 780.633 | 770.696 | 255.8 | GGB | 10435.6 | GGB | 9.81 | GGB | 1005.11 | GGB | 69.49 | GGB | 156254.56 | GGB | 123582.08 | GNB | 0 | 0 | 2746 | 3600 | 2730.81 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290610.49 | GGB | 290613.02 | 2730.81 | 2730.81 |  |  |  | 0 | 1 | [14 empty] | 93.7442 |  |  | #VALUE!
18.07.2008 20:00 | 3600 | 2 | 768.28 | GGB | 765.934 | 780.539 | 770.696 | 256.26 | GGB | 10442.8 | GGB | 9.8 | GGB | 1004.99 | GGB | 69.3 | GGB | 156446.02 | GGB | 123784.31 | GNB | 0 | 0 | 2762 | 3600 | 2746.47 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290648.61 | GGB | 290651.13 | 2746.47 | 2746.47 |  |  |  | 0 | 1 | [14 empty] | 94.4361 |  |  | #VALUE!
18.07.2008 21:00 | 3600 | 2 | 768.55 | GGB | 767.033 | 781.641 | 773.26 | 256.69 | GGB | 10469 | GGB | 9.81 | GGB | 1005.22 | GGB | 69.14 | GGB | 156688.1 | GGB | 124065.46 | GGB | 0 | 0 | 2763 | 3600 | 2747.51 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290686.72 | GGB | 290689.24 | 2747.51 | 2747.51 |  |  |  | 0 | 1 | [14 empty] | 94.6864 |  |  | #VALUE!
18.07.2008 22:00 | 3600 | 2 | 767.75 | GGB | 768.132 | 781.641 | 771.795 | 257.22 | GGB | 10473.1 | GGB | 9.8 | GGB | 1005.33 | GGB | 68.95 | GGB | 156945.57 | GGB | 124349.5 | GGB | 0 | 0 | 2794 | 3600 | 2778.73 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290724.83 | GGB | 290727.35 | 2778.73 | 2778.73 |  |  |  | 0 | 1 | [14 empty] | 95.9816 |  |  | #VALUE!
18.07.2008 23:00 | 3600 | 2 | 767.21 | GGB | 764.469 | 778.383 | 768.132 | 258.4 | GGB | 10497.5 | GGB | 9.79 | GGB | 1006.01 | GGB | 68.74 | GGB | 157427.52 | GGB | 124893.15 | GGB | 0 | 0 | 2828 | 3600 | 2812.72 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290762.94 | GGB | 290765.46 | 2812.72 | 2812.72 |  |  |  | 1 | 1 |  |  |  |  | 124893.15 | 2812.72 |  | 2812.72 | 9.2178 | [5 empty] | 97.5804 |  |  | #VALUE!
18.07.2008 24:00 | 3600 | 2 | 767.38 | GGB | 764.469 | 777.492 | 769.597 | 259.53 | GGB | 10541.2 | GGB | 9.8 | GGB | 1006.54 | GGB | 68.55 | GGB | 158295.69 | GGB | 125719.46 | GGB | 0 | 0 | 2854 | 3600 | 2838.23 | GGB | 100 | GGB | 38.11 | GGB | 38.11 | GGB | 290801.06 | GGB | 290803.57 | 2838.23 | 2838.23 |  |  |  | 1 | 1 |  |  |  |  | 125719.46 | 2838.23 | 125719.46 | 2838.23 | 9.3629 | [5 empty] | 99.1169 |  |  | #VALUE!
19.07.2008 01:00 | 3600 | 2 | 767.38 | GGB | 765.934 | 779.602 | 770.696 | 260.64 | GGB | 10592.5 | GGB | 9.81 | GGB | 1007.14 | GGB | 68.43 | GGB | 159093.43 | GGB | 126472.38 | GGB | 0 | 0 | 2887 | 3600 | 2871.42 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 290838.79 | GGB | 290841.31 | 2871.42 | 2871.42 |  |  |  | 0 | 1 | [14 empty] | 100.8765 |  |  | #VALUE!
19.07.2008 02:00 | 3600 | 2 | 766.65 | GGB | 765.934 | 779.367 | 770.696 | 261.65 | GGB | 10609.5 | GGB | 9.8 | GGB | 1007.43 | GGB | 68.12 | GGB | 159929.69 | GGB | 127288.2 | GGB | 0 | 0 | 2920 | 3600 | 2904.79 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 290876.53 | GGB | 290879.05 | 2904.79 | 2904.79 |  |  |  | 0 | 1 | [14 empty] | 102.7071 |  |  | #VALUE!
19.07.2008 03:00 | 3600 | 2 | 766.7 | GGB | 764.469 | 778.289 | 769.597 | 261.5 | GGB | 10631.1 | GGB | 9.8 | GGB | 1007.69 | GGB | 67.94 | GGB | 160070.53 | GGB | 127501.84 | GGB | 0 | 0 | 2929 | 3600 | 2913.57 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 290914.27 | GGB | 290916.79 | 2913.57 | 2913.57 |  |  |  | 1 | 1 |  |  |  |  | 127501.84 | 2913.57 | 127501.84 | 2913.57 | 9.8433 | [5 empty] | 103.1904 |  |  | #VALUE!
19.07.2008 04:00 | 3600 | 2 | 766.73 | GGB | 767.033 | 780.727 | 771.795 | 262.6 | GGB | 10673.7 | GGB | 9.81 | GGB | 1007.46 | GGB | 67.63 | GGB | 161103.75 | GGB | 128413.36 | GGB | 0 | 0 | 2951 | 3600 | 2935.17 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 290952.01 | GGB | 290954.53 | 2935.17 | 2935.17 |  |  |  | 0 | 1 | [14 empty] | 104.6986 |  |  | #VALUE!
19.07.2008 05:00 | 3600 | 2 | 766.44 | GGB | 764.469 | 777.469 | 769.597 | 262.61 | GGB | 10667.5 | GGB | 9.8 | GGB | 1007.56 | GGB | 67.56 | GGB | 161346.93 | GGB | 128644.6 | GGB | 0 | 0 | 2961 | 3600 | 2945.31 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 290989.75 | GGB | 290992.27 | 2945.31 | 2937.7681 |  |  |  | 1 | 1 |  |  |  |  | 128644.6 | 2937.7681 | 128644.6 | 2937.7681 | 10.014 | [5 empty] | 105.2495 | 2937.7681 |  | 104.98
19.07.2008 06:00 | 3600 | 2 | 767.18 | GGB | 768.132 | 780.773 | 772.161 | 262.94 | GGB | 10709.2 | GGB | 9.82 | GGB | 1007.7 | GGB | 67.36 | GGB | 161861.88 | GGB | 129149.13 | GGB | 0 | 0 | 2946 | 3600 | 2930.16 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291027.49 | GGB | 291030.01 | 2930.16 | 2926.2915 |  |  |  | 0 | 1 | [14 empty] | 105.1188 | 2926.2915 |  | 104.98
19.07.2008 07:00 | 3600 | 2 | 766.58 | GGB | 767.033 | 779.977 | 770.696 | 262.66 | GGB | 10677.8 | GGB | 9.8 | GGB | 1007.98 | GGB | 67.39 | GGB | 161553.79 | GGB | 128925.95 | GGB | 0 | 0 | 2955 | 3600 | 2939.68 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291065.23 | GGB | 291067.75 | 2939.68 | 2931.3571 |  |  |  | 0 | 1 | [14 empty] | 105.2781 | 2931.3571 |  | 104.98
19.07.2008 08:00 | 3600 | 2 | 766.74 | GGB | 764.835 | 779.555 | 769.597 | 262.68 | GGB | 10690 | GGB | 9.81 | GGB | 1008.49 | GGB | 67.19 | GGB | 161440.45 | GGB | 128978.17 | GGB | 0 | 0 | 2925 | 3600 | 2909.65 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291102.96 | GGB | 291105.49 | 2909.65 | 2909.65 |  |  |  | 0 | 1 | [14 empty] | 104.2448 |  |  | #VALUE!
19.07.2008 09:00 | 3600 | 2 | 767.25 | GGB | 767.033 | 780.844 | 771.795 | 261.78 | GGB | 10660.2 | GGB | 9.82 | GGB | 1007.7 | GGB | 67.62 | GGB | 160613 | GGB | 128053.47 | GGB | 0 | 0 | 2911 | 3600 | 2895.21 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291140.7 | GGB | 291143.23 | 2895.21 | 2895.21 |  |  |  | 0 | 1 | [14 empty] | 102.9838 |  |  | #VALUE!
19.07.2008 10:00 | 3600 | 2 | 768.41 | GGB | 767.033 | 780.984 | 772.161 | 259.92 | GGB | 10526.5 | GGB | 9.82 | GGB | 1006.97 | GGB | 68.51 | GGB | 159130.85 | GGB | 126451.85 | GGB | 0 | 0 | 2819 | 3600 | 2803.64 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291178.44 | GGB | 291180.97 | 2803.64 | 2803.64 |  |  |  | 0 | 1 | [14 empty] | 98.4793 |  |  | #VALUE!
19.07.2008 11:00 | 3600 | 2 | 769.52 | GGB | 768.132 | 782.086 | 772.161 | 258.17 | GGB | 10410.1 | GGB | 9.81 | GGB | 1006.21 | GGB | 68.79 | GGB | 157881.96 | GGB | 125261.55 | GGB | 0 | 0 | 2728 | 3600 | 2712.33 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291216.18 | GGB | 291218.71 | 2712.33 | 2712.33 |  |  |  | 0 | 1 | [14 empty] | 94.3752 |  |  | #VALUE!
19.07.2008 12:00 | 3600 | 2 | 769.54 | GGB | 767.033 | 781.102 | 771.795 | 255.68 | GGB | 10403.7 | GGB | 9.81 | GGB | 1005.22 | GGB | 69.78 | GGB | 155671.38 | GGB | 123031.03 | GNB | 0 | 0 | 2707 | 3600 | 2691.1 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291253.92 | GGB | 291256.45 | 2691.1 | 2691.1 |  |  |  | 0 | 1 | [14 empty] | 91.9691 |  |  | #VALUE!
19.07.2008 13:00 | 3600 | 2 | 768.9 | GGB | 767.033 | 781.102 | 771.795 | 255.8 | GGB | 10389.8 | GGB | 9.8 | GGB | 1004.89 | GGB | 69.87 | GGB | 155695.59 | GGB | 122976.45 | GNB | 0 | 0 | 2725 | 3600 | 2710.04 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291291.66 | GGB | 291294.19 | 2710.04 | 2710.04 |  |  |  | 0 | 1 | [14 empty] | 92.5753 |  |  | #VALUE!
19.07.2008 14:00 | 3600 | 2 | 769.13 | GGB | 767.033 | 781.102 | 770.696 | 255.82 | GGB | 10396.2 | GGB | 9.81 | GGB | 1004.76 | GGB | 69.74 | GGB | 155543.74 | GGB | 122884.49 | GNB | 0 | 0 | 2702 | 3600 | 2686.65 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291329.39 | GGB | 291331.93 | 2686.65 | 2686.65 |  |  |  | 0 | 1 | [14 empty] | 91.7077 |  |  | #VALUE!
19.07.2008 15:00 | 3600 | 2 | 769.09 | GGB | 767.033 | 781.102 | 771.795 | 256.92 | GGB | 10370.5 | GGB | 9.8 | GGB | 1004.67 | GGB | 69.72 | GGB | 156916.97 | GGB | 123966.83 | GNB | 0 | 0 | 2722 | 3600 | 2706.5 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291367.13 | GGB | 291369.67 | 2706.5 | 2706.5 |  |  |  | 0 | 1 | [14 empty] | 93.199 |  |  | #VALUE!
19.07.2008 16:00 | 3600 | 2 | 769.93 | GGB | 768.132 | 782.109 | 773.26 | 256.25 | GGB | 10384 | GGB | 9.81 | GGB | 1004.54 | GGB | 69.94 | GGB | 156249.06 | GGB | 123342.97 | GNB | 0 | 0 | 2698 | 3600 | 2682.78 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291404.87 | GGB | 291407.41 | 2682.78 | 2682.78 |  |  |  | 0 | 1 | [14 empty] | 91.9172 |  |  | #VALUE!
19.07.2008 17:00 | 3600 | 2 | 768.79 | GGB | 767.033 | 781.031 | 771.795 | 255.64 | GGB | 10374.5 | GGB | 9.8 | GGB | 1004.22 | GGB | 70.58 | GGB | 155577.86 | GGB | 122548.61 | GNB | 0 | 0 | 2729 | 3600 | 2713.31 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291442.61 | GGB | 291445.15 | 2713.31 | 2713.31 |  |  |  | 0 | 1 | [14 empty] | 92.3645 |  |  | #VALUE!
19.07.2008 18:00 | 3600 | 2 | 769.03 | GGB | 767.033 | 781.102 | 770.696 | 255.59 | GGB | 10370.5 | GGB | 9.8 | GGB | 1003.75 | GGB | 71.21 | GGB | 155619.67 | GGB | 122296.4 | GNB | 0 | 0 | 2771 | 3600 | 2755.6 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291480.35 | GGB | 291482.89 | 2755.6 | 2755.6 |  |  |  | 0 | 1 | [14 empty] | 93.6111 |  |  | #VALUE!
19.07.2008 19:00 | 3600 | 2 | 768.75 | GGB | 765.934 | 780.258 | 769.597 | 256.73 | GGB | 10358.4 | GGB | 9.8 | GGB | 1003.56 | GGB | 71.04 | GGB | 156558.26 | GGB | 123072.45 | GNB | 0 | 0 | 2787 | 3600 | 2772 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291518.09 | GGB | 291520.63 | 2772 | 2772 |  |  |  | 0 | 1 | [14 empty] | 94.7658 |  |  | #VALUE!
19.07.2008 20:00 | 3600 | 2 | 769.25 | GGB | 767.033 | 781.43 | 771.429 | 256.8 | GGB | 10388.3 | GGB | 9.81 | GGB | 1003.54 | GGB | 71.06 | GGB | 156539.55 | GGB | 123049.89 | GNB | 0 | 0 | 2804 | 3600 | 2788.38 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291555.82 | GGB | 291558.37 | 2788.38 | 2788.38 |  |  |  | 0 | 1 | [14 empty] | 95.3083 |  |  | #VALUE!
19.07.2008 21:00 | 3600 | 2 | 768.61 | GGB | 767.033 | 781.195 | 771.429 | 258.34 | GGB | 10362.5 | GGB | 9.8 | GGB | 1003.72 | GGB | 70.39 | GGB | 157993.1 | GGB | 124455.5 | GGB | 0 | 0 | 2829 | 3600 | 2813.38 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291593.56 | GGB | 291596.11 | 2813.38 | 2813.38 |  |  |  | 0 | 1 | [14 empty] | 97.2613 |  |  | #VALUE!
19.07.2008 22:00 | 3600 | 2 | 768.3 | GGB | 764.835 | 778.102 | 768.864 | 257.3 | GGB | 10422.4 | GGB | 9.8 | GGB | 1003.85 | GGB | 71.13 | GGB | 156570.36 | GGB | 123086.77 | GNB | 0 | 0 | 2849 | 3600 | 2833.54 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291631.3 | GGB | 291633.85 | 2833.54 | 2833.54 |  |  |  | 1 | 1 |  |  |  |  | 123086.77 | 2833.54 |  | 2833.54 | 9.2414 | [5 empty] | 96.8809 |  |  | #VALUE!
19.07.2008 23:00 | 3600 | 2 | 767.6 | GGB | 765.934 | 780.117 | 770.33 | 258.69 | GGB | 10455.6 | GGB | 9.8 | GGB | 1003.88 | GGB | 70.79 | GGB | 157445.13 | GGB | 123899.74 | GNB | 0 | 0 | 2893 | 3600 | 2877.17 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291669.04 | GGB | 291671.59 | 2877.17 | 2877.17 |  |  |  | 0 | 1 | [14 empty] | 99.0224 |  |  | #VALUE!
19.07.2008 24:00 | 3600 | 2 | 767.66 | GGB | 767.033 | 780.914 | 772.527 | 259.35 | GGB | 10505.9 | GGB | 9.8 | GGB | 1003.87 | GGB | 70.25 | GGB | 158511.36 | GGB | 124933.21 | GGB | 0 | 0 | 2917 | 3600 | 2901.48 | GGB | 100 | GGB | 37.74 | GGB | 37.74 | GGB | 291706.78 | GGB | 291709.33 | 2901.48 | 2901.48 |  |  |  | 0 | 1 | [14 empty] | 100.692 |  |  | #VALUE!
20.07.2008 01:00 | 3600 | 2 | 766.93 | GGB | 765.934 | 779.766 | 770.33 | 260.8 | GGB | 10506.1 | GGB | 9.79 | GGB | 1003.51 | GGB | 70.03 | GGB | 159226.58 | GGB | 125533.21 | GGB | 0 | 0 | 2961 | 3600 | 2945.39 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291744.85 | GGB | 291747.41 | 2945.39 | 2945.39 |  |  |  | 0 | 1 | [14 empty] | 102.7067 |  |  | #VALUE!
20.07.2008 02:00 | 3600 | 2 | 767.11 | GGB | 764.835 | 778.664 | 769.963 | 261.33 | GGB | 10546.1 | GGB | 9.8 | GGB | 1003.37 | GGB | 69.54 | GGB | 159743.73 | GGB | 126103.55 | GGB | 0 | 0 | 2946 | 3600 | 2930.08 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291782.93 | GGB | 291785.49 | 2930.08 | 2930.08 |  |  |  | 1 | 1 | STOP OF baseline or calculation of NCSG |  |  |  | 126103.55 | 2930.08 | 126103.55 | 2930.08 | 9.7031 | [5 empty] | 102.6371 |  |  | #VALUE!
20.07.2008 03:00 | 3600 | 2 | 767.74 | GGB | 764.835 | 778.664 | 769.963 | 261.59 | GGB | 10575.7 | GGB | 9.81 | GGB | 1003.16 | GGB | 69.33 | GGB | 159872.47 | GGB | 126254.74 | GGB | 0 | 0 | 2928 | 3600 | 2912.22 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291821 | GGB | 291823.57 | 2912.22 | 2912.22 |  |  |  | 1 | 1 |  |  |  |  | 126254.74 | 2912.22 | 126254.74 | 2912.22 | 9.6555 | [5 empty] | 102.1338 |  |  | #VALUE!
20.07.2008 04:00 | 3600 | 2 | 767.05 | GGB | 763.37 | 776.531 | 767.766 | 262.03 | GGB | 10556.2 | GGB | 9.8 | GGB | 1003.29 | GGB | 68.45 | GGB | 160388.53 | GGB | 127008.48 | GGB | 0 | 0 | 2883 | 3600 | 2867.06 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291859.08 | GGB | 291861.65 | 2867.06 | 2867.06 |  |  |  | 0 | 1 | [14 empty] | 101.1503 |  |  | #VALUE!
20.07.2008 05:00 | 3600 | 2 | 767.64 | GGB | 767.033 | 780.375 | 771.429 | 261.44 | GGB | 10603.1 | GGB | 9.82 | GGB | 1002.68 | GGB | 68.63 | GGB | 159841.66 | GGB | 126430.44 | GGB | 0 | 0 | 2881 | 3600 | 2865.82 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291897.16 | GGB | 291899.73 | 2865.82 | 2865.82 |  |  |  | 0 | 1 | [14 empty] | 100.6464 |  |  | #VALUE!
20.07.2008 06:00 | 3600 | 2 | 766.55 | GGB | 764.835 | 778.266 | 768.864 | 262.1 | GGB | 10589.5 | GGB | 9.8 | GGB | 1002.71 | GGB | 68.46 | GGB | 160570.09 | GGB | 127074.44 | GGB | 0 | 0 | 2934 | 3600 | 2918.66 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291935.23 | GGB | 291937.81 | 2918.66 | 2918.66 |  |  |  | 1 | 1 |  |  |  |  | 127074.44 | 2918.66 | 127074.44 | 2918.66 | 9.7397 | [5 empty] | 103.0242 |  |  | #VALUE!
20.07.2008 07:00 | 3600 | 2 | 766.83 | GGB | 767.033 | 779.531 | 771.429 | 262.45 | GGB | 10615.2 | GGB | 9.81 | GGB | 1002.55 | GGB | 68.23 | GGB | 160992.62 | GGB | 127471.7 | GGB | 0 | 0 | 2934 | 3600 | 2918.84 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 291973.31 | GGB | 291975.89 | 2918.84 | 2918.84 |  |  |  | 0 | 1 | [14 empty] | 103.3526 |  |  | #VALUE!
20.07.2008 08:00 | 3600 | 2 | 767.71 | GGB | 767.033 | 779.531 | 771.429 | 261.51 | GGB | 10584.2 | GGB | 9.82 | GGB | 1002.54 | GGB | 68.35 | GGB | 160275.2 | GGB | 126859.75 | GGB | 0 | 0 | 2885 | 3600 | 2869.65 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292011.38 | GGB | 292013.97 | 2869.65 | 2869.65 |  |  |  | 0 | 1 | [14 empty] | 101.1231 |  |  | #VALUE!
20.07.2008 09:00 | 3600 | 2 | 768.15 | GGB | 767.033 | 780.492 | 771.429 | 259.52 | GGB | 10509.3 | GGB | 9.82 | GGB | 1002.14 | GGB | 68.86 | GGB | 158247.27 | GGB | 125015.95 | GGB | 0 | 0 | 2844 | 3600 | 2828.94 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292049.46 | GGB | 292052.05 | 2828.94 | 2828.94 |  |  |  | 0 | 1 | [14 empty] | 98.2396 |  |  | #VALUE!
20.07.2008 10:00 | 3600 | 2 | 768.48 | GGB | 767.033 | 780.469 | 771.429 | 256.95 | GGB | 10433.6 | GGB | 9.82 | GGB | 1000.55 | GGB | 69.84 | GGB | 155942.07 | GGB | 122649.86 | GNB | 0 | 0 | 2784 | 3600 | 2768.25 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292087.53 | GGB | 292090.13 | 2768.25 | 2768.25 |  |  |  | 0 | 1 | [14 empty] | 94.3126 |  |  | #VALUE!
20.07.2008 11:00 | 3600 | 2 | 769.07 | GGB | 768.132 | 782.719 | 773.626 | 255.16 | GGB | 10360.2 | GGB | 9.82 | GGB | 999.33 | GGB | 70.44 | GGB | 154331.17 | GGB | 121021.5 | GNB | 0 | 0 | 2730 | 3600 | 2714.89 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292125.61 | GGB | 292128.21 | 2714.89 | 2714.89 |  |  |  | 0 | 1 | [14 empty] | 91.2667 |  |  | #VALUE!
20.07.2008 12:00 | 3600 | 2 | 769.45 | GGB | 768.132 | 782.742 | 772.527 | 253.66 | GGB | 10296.1 | GGB | 9.81 | GGB | 998.38 | GGB | 70.79 | GGB | 153674.27 | GGB | 120270.36 | GNB | 0 | 0 | 2703 | 3600 | 2688.03 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292163.69 | GGB | 292166.29 | 2688.03 | 2688.03 |  |  |  | 0 | 1 | [14 empty] | 89.8029 |  |  | #VALUE!
20.07.2008 13:00 | 3600 | 2 | 769.51 | GGB | 768.132 | 782.602 | 773.626 | 252.88 | GGB | 10276.8 | GGB | 9.81 | GGB | 997.68 | GGB | 70.93 | GGB | 153151.61 | GGB | 119730.25 | GNB | 0 | 0 | 2683 | 3600 | 2668.08 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292201.76 | GGB | 292204.37 | 2668.08 | 2668.08 |  |  |  | 0 | 1 | [14 empty] | 88.7361 |  |  | #VALUE!
20.07.2008 14:00 | 3600 | 2 | 769.13 | GGB | 765.934 | 780.656 | 770.33 | 252.56 | GGB | 10266.5 | GGB | 9.79 | GGB | 997.23 | GGB | 70.62 | GGB | 153307.86 | GGB | 119905.71 | GNB | 0 | 0 | 2680 | 3600 | 2664.99 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292239.84 | GGB | 292242.45 | 2664.99 | 2664.99 |  |  |  | 0 | 1 | [14 empty] | 88.7632 |  |  | #VALUE!
20.07.2008 15:00 | 3600 | 2 | 768.54 | GGB | 765.934 | 779.461 | 768.864 | 254.22 | GGB | 10343.8 | GGB | 9.8 | GGB | 997.39 | GGB | 70.11 | GGB | 154469.81 | GGB | 121010.27 | GNB | 0 | 0 | 2751 | 3600 | 2736.02 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292277.91 | GGB | 292280.53 | 2736.02 | 2736.02 |  |  |  | 0 | 1 | [14 empty] | 91.9685 |  |  | #VALUE!
20.07.2008 16:00 | 3600 | 2 | 767.09 | GGB | 767.033 | 780.492 | 771.429 | 256.93 | GGB | 10422.9 | GGB | 9.79 | GGB | 998.55 | GGB | 69.44 | GGB | 156446.02 | GGB | 122942.47 | GNB | 0 | 0 | 2875 | 3600 | 2859.62 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292315.99 | GGB | 292318.61 | 2859.62 | 2859.62 |  |  |  | 0 | 1 | [14 empty] | 97.658 |  |  | #VALUE!
20.07.2008 17:00 | 3600 | 2 | 767.69 | GGB | 765.934 | 780.469 | 770.33 | 256.41 | GGB | 10411.8 | GGB | 9.81 | GGB | 998.75 | GGB | 69.66 | GGB | 155638.37 | GGB | 122253.88 | GNB | 0 | 0 | 2828 | 3600 | 2812.71 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292354.06 | GGB | 292356.69 | 2812.71 | 2812.71 |  |  |  | 0 | 1 | [14 empty] | 95.518 |  |  | #VALUE!
20.07.2008 18:00 | 3600 | 2 | 767.72 | GGB | 765.934 | 779.484 | 770.33 | 255.94 | GGB | 10394.5 | GGB | 9.8 | GGB | 998.62 | GGB | 69.69 | GGB | 155309.37 | GGB | 121970.41 | GNB | 0 | 0 | 2805 | 3600 | 2789.7 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292392.14 | GGB | 292394.77 | 2789.7 | 2789.7 |  |  |  | 0 | 1 | [14 empty] | 94.5169 |  |  | #VALUE!
20.07.2008 19:00 | 3600 | 2 | 767.94 | GGB | 767.033 | 780.445 | 770.33 | 256.02 | GGB | 10393.8 | GGB | 9.8 | GGB | 998.66 | GGB | 69.71 | GGB | 155460.12 | GGB | 122086.14 | GNB | 0 | 0 | 2790 | 3600 | 2774.9 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292430.21 | GGB | 292432.85 | 2774.9 | 2774.9 |  |  |  | 0 | 1 | [14 empty] | 94.1047 |  |  | #VALUE!
20.07.2008 20:00 | 3600 | 2 | 768.12 | GGB | 765.934 | 779.367 | 770.33 | 256.11 | GGB | 10395.4 | GGB | 9.8 | GGB | 998.86 | GGB | 69.7 | GGB | 155896.95 | GGB | 122455.35 | GNB | 0 | 0 | 2782 | 3600 | 2766.48 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292468.29 | GGB | 292470.93 | 2766.48 | 2766.48 |  |  |  | 0 | 1 | [14 empty] | 94.1029 |  |  | #VALUE!
20.07.2008 21:00 | 3600 | 2 | 767.94 | GGB | 765.934 | 779.438 | 769.963 | 256.82 | GGB | 10426.9 | GGB | 9.8 | GGB | 999.82 | GGB | 69.54 | GGB | 156396.51 | GGB | 123025.67 | GNB | 0 | 0 | 2815 | 3600 | 2799.49 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292506.37 | GGB | 292509.01 | 2799.49 | 2799.49 |  |  |  | 0 | 1 | [14 empty] | 95.6692 |  |  | #VALUE!
20.07.2008 22:00 | 3600 | 2 | 767.55 | GGB | 764.835 | 778.359 | 768.864 | 257.65 | GGB | 10457.2 | GGB | 9.8 | GGB | 1000.78 | GGB | 69.35 | GGB | 156971.98 | GGB | 123664.08 | GNB | 0 | 0 | 2854 | 3600 | 2838.69 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292544.44 | GGB | 292547.09 | 2838.69 | 2838.69 |  |  |  | 1 | 1 |  |  |  |  | 123664.08 | 2838.69 |  | 2838.69 | 9.2186 | [5 empty] | 97.5122 |  |  | #VALUE!
20.07.2008 23:00 | 3600 | 2 | 767.47 | GGB | 764.835 | 778.125 | 768.864 | 258.75 | GGB | 10489.3 | GGB | 9.8 | GGB | 1001.99 | GGB | 69.26 | GGB | 157602.48 | GGB | 124345.14 | GGB | 0 | 0 | 2872 | 3600 | 2856.2 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292582.52 | GGB | 292585.17 | 2856.2 | 2856.2 |  |  |  | 1 | 1 |  |  |  |  | 124345.14 | 2856.2 |  | 2856.2 | 9.3265 | [5 empty] | 98.6541 |  |  | #VALUE!
20.07.2008 24:00 | 3600 | 2 | 767.01 | GGB | 764.469 | 778.055 | 768.864 | 259.16 | GGB | 10537.5 | GGB | 9.79 | GGB | 1002.64 | GGB | 68.56 | GGB | 158751.23 | GGB | 125589.6 | GGB | 0 | 0 | 2908 | 3600 | 2892.19 | GGB | 100 | GGB | 38.08 | GGB | 38.08 | GGB | 292620.59 | GGB | 292623.25 | 2892.19 | 2892.19 |  |  |  | 1 | 1 |  |  |  |  | 125589.6 | 2892.19 | 125589.6 | 2892.19 | 9.5386 | [5 empty] | 100.8969 |  |  | #VALUE!
21.07.2008 01:00 | 3600 | 2 | 767.04 | GGB | 764.835 | 778.102 | 768.864 | 260.77 | GGB | 10571.2 | GGB | 9.8 | GGB | 1003.04 | GGB | 68.58 | GGB | 159446.64 | GGB | 126180.72 | GGB | 0 | 0 | 2940 | 3600 | 2924.15 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292657.75 | GGB | 292660.41 | 2924.15 | 2924.15 |  |  |  | 1 | 1 |  |  |  |  | 126180.72 | 2924.15 | 126180.72 | 2924.15 | 9.9293 | [5 empty] | 102.492 |  |  | #VALUE!
21.07.2008 02:00 | 3600 | 2 | 766.58 | GGB | 764.469 | 778.5 | 768.864 | 261.41 | GGB | 10602.7 | GGB | 9.8 | GGB | 1003.21 | GGB | 67.83 | GGB | 159984.71 | GGB | 126908.42 | GGB | 0 | 0 | 2927 | 3600 | 2911.72 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292694.91 | GGB | 292697.57 | 2911.72 | 2911.72 |  |  |  | 1 | 1 |  |  |  |  | 126908.42 | 2911.72 | 126908.42 | 2911.72 | 9.9441 | [5 empty] | 102.6449 |  |  | #VALUE!
21.07.2008 03:00 | 3600 | 2 | 766.81 | GGB | 764.835 | 777.305 | 768.498 | 262.02 | GGB | 10628.7 | GGB | 9.81 | GGB | 1003.84 | GGB | 67.99 | GGB | 160456.75 | GGB | 127301.76 | GGB | 0 | 0 | 2958 | 3600 | 2942.36 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292732.07 | GGB | 292734.73 | 2942.36 | 2942.36 |  |  |  | 1 | 1 |  |  |  |  | 127301.76 | 2942.36 | 127301.76 | 2942.36 | 10.0799 | [5 empty] | 104.0466 |  |  | #VALUE!
21.07.2008 04:00 | 3600 | 2 | 766.32 | GGB | 764.469 | 777.258 | 769.597 | 262.49 | GGB | 10645.3 | GGB | 9.8 | GGB | 1004.18 | GGB | 67.74 | GGB | 161189.58 | GGB | 128022.09 | GGB | 0 | 0 | 2984 | 3600 | 2968.69 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292769.23 | GGB | 292771.89 | 2968.69 | 2952.053 |  |  |  | 1 | 1 |  |  |  |  | 128022.09 | 2952.053 | 128022.09 | 2952.053 | 10.1703 | [5 empty] | 105.5716 | 2952.053 |  | 104.98
21.07.2008 05:00 | 3600 | 2 | 766.49 | GGB | 764.835 | 778.313 | 769.597 | 263.27 | GGB | 10666.7 | GGB | 9.8 | GGB | 1004.19 | GGB | 67.56 | GGB | 161915.8 | GGB | 128667.92 | GGB | 0 | 0 | 2974 | 3600 | 2958.28 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292806.39 | GGB | 292809.05 | 2958.28 | 2937.2356 |  |  |  | 1 | 1 |  |  |  |  | 128667.92 | 2937.2356 | 128667.92 | 2937.2356 | 10.1703 | [5 empty] | 105.7321 | 2937.2356 |  | 104.98
21.07.2008 06:00 | 3600 | 2 | 766.04 | GGB | 764.469 | 777.305 | 768.132 | 263.7 | GGB | 10687.4 | GGB | 9.8 | GGB | 1004.39 | GGB | 67.45 | GGB | 162633.22 | GGB | 129304.81 | GGB | 0 | 0 | 2997 | 3600 | 2981.55 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292843.54 | GGB | 292846.21 | 2981.55 | 2922.7683 |  |  |  | 1 | 1 |  |  |  |  | 129304.81 | 2922.7683 | 129304.81 | 2922.7683 | 10.1703 | [5 empty] | 107.0913 | 2922.7683 |  | 104.98
21.07.2008 07:00 | 3600 | 2 | 767.32 | GGB | 764.835 | 778.242 | 769.963 | 263.26 | GGB | 10714.6 | GGB | 9.82 | GGB | 1004.89 | GGB | 67.69 | GGB | 162555.1 | GGB | 129215.02 | GGB | 0 | 0 | 2973 | 3600 | 2957.39 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292880.7 | GGB | 292883.37 | 2957.39 | 2924.7993 |  |  |  | 1 | 1 |  |  |  |  | 129215.02 | 2924.7993 | 129215.02 | 2924.7993 | 10.1703 | [5 empty] | 106.1498 | 2924.7993 |  | 104.98
21.07.2008 08:00 | 3600 | 2 | 767.5 | GGB | 764.835 | 778.172 | 769.597 | 262.18 | GGB | 10674.6 | GGB | 9.82 | GGB | 1005.24 | GGB | 67.89 | GGB | 161488.87 | GGB | 128338.62 | GGB | 0 | 0 | 2946 | 3600 | 2929.92 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292917.86 | GGB | 292920.53 | 2929.92 | 2929.92 |  |  |  | 1 | 1 |  |  |  |  | 128338.62 | 2929.92 | 128338.62 | 2929.92 | 10.119 | [5 empty] | 104.4505 |  |  | #VALUE!
21.07.2008 09:00 | 3600 | 2 | 767.76 | GGB | 765.934 | 779.742 | 769.597 | 260.54 | GGB | 10608.5 | GGB | 9.82 | GGB | 1005.19 | GGB | 68.34 | GGB | 159712.92 | GGB | 126752.13 | GGB | 0 | 0 | 2896 | 3600 | 2880.04 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292955.02 | GGB | 292957.69 | 2880.04 | 2880.04 |  |  |  | 0 | 1 | [14 empty] | 101.4031 |  |  | #VALUE!
21.07.2008 10:00 | 3600 | 2 | 767.8 | GGB | 765.934 | 779.719 | 770.696 | 259.47 | GGB | 10552.5 | GGB | 9.81 | GGB | 1004.35 | GGB | 68.86 | GGB | 158543.27 | GGB | 125526.2 | GGB | 0 | 0 | 2882 | 3600 | 2866.68 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 292992.18 | GGB | 292994.85 | 2866.68 | 2866.68 |  |  |  | 0 | 1 | [14 empty] | 99.9565 |  |  | #VALUE!
21.07.2008 11:00 | 3600 | 2 | 768.43 | GGB | 768.132 | 781.617 | 771.795 | 258.52 | GGB | 10507.8 | GGB | 9.81 | GGB | 1004.06 | GGB | 69.25 | GGB | 157811.54 | GGB | 124769.78 | GGB | 0 | 0 | 2840 | 3600 | 2824.09 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293029.34 | GGB | 293032.01 | 2824.09 | 2824.09 |  |  |  | 0 | 1 | [14 empty] | 97.8781 |  |  | #VALUE!
21.07.2008 12:00 | 3600 | 2 | 768.69 | GGB | 767.033 | 780.539 | 771.795 | 257.51 | GGB | 10460.9 | GGB | 9.81 | GGB | 1003.69 | GGB | 69.49 | GGB | 157352.7 | GGB | 124273.6 | GGB | 0 | 0 | 2798 | 3600 | 2782.32 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293066.5 | GGB | 293069.17 | 2782.32 | 2782.32 |  |  |  | 0 | 1 | [14 empty] | 96.0469 |  |  | #VALUE!
21.07.2008 13:00 | 3600 | 2 | 767.43 | GGB | 764.835 | 779.297 | 769.597 | 256.59 | GGB | 10361.3 | GGB | 9.79 | GGB | 1003.67 | GGB | 69.26 | GGB | 156898.26 | GGB | 123993.74 | GNB | 0 | 0 | 2819 | 3600 | 2803.07 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293103.66 | GGB | 293106.33 | 2803.07 | 2803.07 |  |  |  | 0 | 1 | [14 empty] | 96.5453 |  |  | #VALUE!
21.07.2008 14:00 | 3600 | 2 | 767.64 | GGB | 764.835 | 779.297 | 769.597 | 255.84 | GGB | 10336.8 | GGB | 9.79 | GGB | 1003.36 | GGB | 69.48 | GGB | 156064.2 | GGB | 123218.05 | GNB | 0 | 0 | 2789 | 3600 | 2773.67 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293140.81 | GGB | 293143.49 | 2773.67 | 2773.67 |  |  |  | 0 | 1 | [14 empty] | 94.9351 |  |  | #VALUE!
21.07.2008 15:00 | 3600 | 2 | 767.57 | GGB | 764.835 | 779.297 | 769.597 | 255.32 | GGB | 10309.3 | GGB | 9.79 | GGB | 1002.77 | GGB | 69.62 | GGB | 155581.16 | GGB | 122714.2 | GNB | 0 | 0 | 2776 | 3600 | 2760.64 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293177.97 | GGB | 293180.65 | 2760.64 | 2760.64 |  |  |  | 0 | 1 | [14 empty] | 94.1027 |  |  | #VALUE!
21.07.2008 16:00 | 3600 | 2 | 767.53 | GGB | 764.835 | 779.297 | 769.597 | 255.32 | GGB | 10310.8 | GGB | 9.79 | GGB | 1002.49 | GGB | 69.61 | GGB | 155449.12 | GGB | 122580.52 | GNB | 0 | 0 | 2771 | 3600 | 2755.23 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293215.13 | GGB | 293217.81 | 2755.23 | 2755.23 |  |  |  | 0 | 1 | [14 empty] | 93.816 |  |  | #VALUE!
21.07.2008 17:00 | 3600 | 2 | 767.6 | GGB | 764.835 | 779.414 | 769.597 | 255.38 | GGB | 10318.3 | GGB | 9.79 | GGB | 1002.5 | GGB | 69.63 | GGB | 155405.1 | GGB | 122540.76 | GNB | 0 | 0 | 2775 | 3600 | 2759.32 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293252.29 | GGB | 293254.97 | 2759.32 | 2759.32 |  |  |  | 0 | 1 | [14 empty] | 93.9248 |  |  | #VALUE!
21.07.2008 18:00 | 3600 | 2 | 767.53 | GGB | 765.934 | 779.32 | 770.696 | 255.59 | GGB | 10320.2 | GGB | 9.79 | GGB | 1002.34 | GGB | 69.55 | GGB | 155517.34 | GGB | 122636.85 | GNB | 0 | 0 | 2777 | 3600 | 2761.82 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293289.45 | GGB | 293292.13 | 2761.82 | 2761.82 |  |  |  | 0 | 1 | [14 empty] | 94.0836 |  |  | #VALUE!
21.07.2008 19:00 | 3600 | 2 | 767.06 | GGB | 763.37 | 778.313 | 768.498 | 257.36 | GGB | 10285.7 | GGB | 9.77 | GGB | 1002.23 | GGB | 68.64 | GGB | 157666.3 | GGB | 124651.19 | GGB | 0 | 0 | 2811 | 3600 | 2795.68 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293326.61 | GGB | 293329.29 | 2795.68 | 2795.68 |  |  |  | 0 | 1 | [14 empty] | 96.8013 |  |  | #VALUE!
21.07.2008 20:00 | 3600 | 2 | 766.78 | GGB | 764.469 | 778.313 | 769.597 | 259.46 | GGB | 10363.8 | GGB | 9.78 | GGB | 1002.61 | GGB | 67.91 | GGB | 159228.78 | GGB | 126200.33 | GGB | 0 | 0 | 2843 | 3600 | 2827.62 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293363.77 | GGB | 293366.45 | 2827.62 | 2827.62 |  |  |  | 1 | 1 |  |  |  |  | 126200.33 | 2827.62 | 126200.33 | 2827.62 | 9.603 | [5 empty] | 99.124 |  |  | #VALUE!
21.07.2008 21:00 | 3600 | 2 | 766.82 | GGB | 764.469 | 777.563 | 768.864 | 260.07 | GGB | 10381.6 | GGB | 9.78 | GGB | 1003.26 | GGB | 67.74 | GGB | 159722.83 | GGB | 126739.1 | GGB | 0 | 0 | 2850 | 3600 | 2834.46 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293400.92 | GGB | 293403.61 | 2834.46 | 2834.46 |  |  |  | 1 | 1 |  |  |  |  | 126739.1 | 2834.46 | 126739.1 | 2834.46 | 9.6673 | [5 empty] | 99.788 |  |  | #VALUE!
21.07.2008 22:00 | 3600 | 2 | 766.51 | GGB | 764.469 | 777.703 | 768.864 | 261.2 | GGB | 10440.8 | GGB | 9.78 | GGB | 1004.18 | GGB | 67.18 | GGB | 160879.28 | GGB | 127985.13 | GGB | 0 | 0 | 2896 | 3600 | 2880.88 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293438.08 | GGB | 293440.77 | 2880.88 | 2880.88 |  |  |  | 1 | 1 |  |  |  |  | 127985.13 | 2880.88 | 127985.13 | 2880.88 | 9.9222 | [5 empty] | 102.4194 |  |  | #VALUE!
21.07.2008 23:00 | 3600 | 2 | 766.06 | GGB | 764.469 | 777.773 | 768.864 | 262.47 | GGB | 10496.7 | GGB | 9.78 | GGB | 1005.21 | GGB | 66.36 | GGB | 162028.03 | GGB | 129341.76 | GGB | 0 | 0 | 2933 | 3600 | 2917.1 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293475.24 | GGB | 293477.93 | 2917.1 | 2917.1 |  |  |  | 1 | 1 |  |  |  |  | 129341.76 | 2917.1 | 129341.76 | 2917.1 | 10.1535 | [5 empty] | 104.8063 |  |  | #VALUE!
21.07.2008 24:00 | 3600 | 2 | 765.9 | GGB | 765.934 | 778.594 | 769.963 | 263.19 | GGB | 10527.4 | GGB | 9.78 | GGB | 1005.6 | GGB | 66.1 | GGB | 163024.94 | GGB | 130287.32 | GGB | 0 | 0 | 2937 | 3600 | 2921.75 | GGB | 100 | GGB | 37.16 | GGB | 37.16 | GGB | 293512.4 | GGB | 293515.09 | 2921.75 | 2900.7274 |  |  |  | 1 | 1 |  |  |  |  | 130287.32 | 2900.7274 | 130287.32 | 2900.7274 | 10.1703 | [5 empty] | 105.7408 | 2900.7274 |  | 104.98
22.07.2008 01:00 | 3600 | 2 | 765.8 | GGB | 764.469 | 777.469 | 767.766 | 263.29 | GGB | 10538.7 | GGB | 9.79 | GGB | 1005.67 | GGB | 66.14 | GGB | 163134.97 | GGB | 130369.31 | GGB | 0 | 0 | 2953 | 3600 | 2937.19 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293549.67 | GGB | 293552.36 | 2937.19 | 2898.9031 |  |  |  | 1 | 1 |  |  |  |  | 130369.31 | 2898.9031 | 130369.31 | 2898.9031 | 10.1403 | [5 empty] | 106.3665 | 2898.9031 |  | 104.98
22.07.2008 02:00 | 3600 | 2 | 765.43 | GGB | 764.469 | 777.539 | 768.864 | 263.65 | GGB | 10550.4 | GGB | 9.78 | GGB | 1006.03 | GGB | 65.95 | GGB | 163623.52 | GGB | 130878.1 | GGB | 0 | 0 | 2989 | 3600 | 2973.65 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293586.94 | GGB | 293589.63 | 2973.65 | 2887.6336 |  |  |  | 1 | 1 |  |  |  |  | 130878.1 | 2887.6336 | 130878.1 | 2887.6336 | 10.1403 | [5 empty] | 108.1071 | 2887.6336 |  | 104.98
22.07.2008 03:00 | 3600 | 2 | 765.17 | GGB | 763.37 | 776.484 | 767.766 | 264.54 | GGB | 10576.3 | GGB | 9.78 | GGB | 1006.59 | GGB | 65.46 | GGB | 164433.37 | GGB | 131791.05 | GGB | 0 | 0 | 3011 | 3600 | 2994.93 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293624.2 | GGB | 293626.9 | 2994.93 | 2867.6302 |  |  |  | 0 | 1 | [14 empty] | 109.6403 | 2867.6302 |  | 104.98
22.07.2008 04:00 | 3600 | 2 | 765.84 | GGB | 762.271 | 775.852 | 766.667 | 264.46 | GGB | 10600.8 | GGB | 9.79 | GGB | 1006.7 | GGB | 65.39 | GGB | 164544.51 | GGB | 131920.94 | GGB | 0 | 0 | 2986 | 3600 | 2970.63 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293661.47 | GGB | 293664.17 | 2970.63 | 2864.8068 |  |  |  | 0 | 1 | [14 empty] | 108.8579 | 2864.8068 |  | 104.98
22.07.2008 05:00 | 3600 | 2 | 766.17 | GGB | 764.469 | 778.031 | 768.864 | 263.97 | GGB | 10603.8 | GGB | 9.79 | GGB | 1006.9 | GGB | 65.64 | GGB | 164380.56 | GGB | 131721.05 | GGB | 0 | 0 | 2976 | 3600 | 2960.34 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293698.74 | GGB | 293701.44 | 2960.34 | 2869.1542 |  |  |  | 1 | 1 |  |  |  |  | 131721.05 | 2869.1542 | 131721.05 | 2869.1542 | 10.1403 | [5 empty] | 108.3164 | 2869.1542 |  | 104.98
22.07.2008 06:00 | 3600 | 2 | 765.6 | GGB | 764.469 | 776.93 | 768.864 | 264.14 | GGB | 10600.5 | GGB | 9.78 | GGB | 1007.35 | GGB | 65.43 | GGB | 164570.92 | GGB | 132014.94 | GGB | 0 | 0 | 2992 | 3600 | 2976.41 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293736 | GGB | 293738.71 | 2976.41 | 2862.7669 |  |  |  | 1 | 1 |  |  |  |  | 132014.94 | 2862.7669 | 132014.94 | 2862.7669 | 10.1403 | [5 empty] | 109.1474 | 2862.7669 |  | 104.98
22.07.2008 07:00 | 3600 | 2 | 766.19 | GGB | 763.37 | 776.742 | 767.766 | 264.31 | GGB | 10617.9 | GGB | 9.79 | GGB | 1007.73 | GGB | 65.24 | GGB | 164581.92 | GGB | 132145.12 | GGB | 0 | 0 | 2965 | 3600 | 2949.65 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293773.27 | GGB | 293775.98 | 2949.65 | 2859.9467 |  |  |  | 0 | 1 | [14 empty] | 108.2727 | 2859.9467 |  | 104.98
22.07.2008 08:00 | 3600 | 2 | 765.81 | GGB | 763.37 | 776.836 | 766.667 | 264.48 | GGB | 10609.8 | GGB | 9.78 | GGB | 1008.61 | GGB | 65.39 | GGB | 164716.16 | GGB | 132310.69 | GGB | 0 | 0 | 2989 | 3600 | 2973 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293810.54 | GGB | 293813.25 | 2973 | 2856.3678 |  |  |  | 0 | 1 | [14 empty] | 109.2666 | 2856.3678 |  | 104.98
22.07.2008 09:00 | 3600 | 2 | 766.22 | GGB | 764.835 | 777.703 | 767.766 | 264.22 | GGB | 10608.2 | GGB | 9.79 | GGB | 1009.38 | GGB | 65.65 | GGB | 164287.03 | GGB | 131966.14 | GGB | 0 | 0 | 2970 | 3600 | 2953.97 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293847.8 | GGB | 293850.52 | 2953.97 | 2863.8255 |  |  |  | 1 | 1 |  |  |  |  | 131966.14 | 2863.8255 | 131966.14 | 2863.8255 | 10.1403 | [5 empty] | 108.2844 | 2863.8255 |  | 104.98
22.07.2008 10:00 | 3600 | 2 | 766.72 | GGB | 765.934 | 778.969 | 770.33 | 263.68 | GGB | 10613.8 | GGB | 9.8 | GGB | 1009.71 | GGB | 65.96 | GGB | 163402.36 | GGB | 131177.02 | GGB | 0 | 0 | 2944 | 3600 | 2928.38 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293885.07 | GGB | 293887.79 | 2928.38 | 2881.0534 |  |  |  | 0 | 1 | [14 empty] | 106.7045 | 2881.0534 |  | 104.98
22.07.2008 11:00 | 3600 | 2 | 767.44 | GGB | 764.835 | 778.195 | 769.963 | 260.69 | GGB | 10570.2 | GGB | 9.8 | GGB | 1009.5 | GGB | 67.4 | GGB | 160159.66 | GGB | 128002.85 | GGB | 0 | 0 | 2893 | 3600 | 2877.07 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293922.34 | GGB | 293925.06 | 2877.07 | 2877.07 |  |  |  | 1 | 1 |  |  |  |  | 128002.85 | 2877.07 | 128002.85 | 2877.07 | 9.8812 | [5 empty] | 102.2981 |  |  | #VALUE!
22.07.2008 12:00 | 3600 | 2 | 767.27 | GGB | 765.934 | 779.156 | 769.963 | 259.45 | GGB | 10506.2 | GGB | 9.79 | GGB | 1009.5 | GGB | 67.9 | GGB | 159158.35 | GGB | 127017.82 | GGB | 0 | 0 | 2889 | 3600 | 2873.58 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293959.61 | GGB | 293962.33 | 2873.58 | 2873.58 |  |  |  | 0 | 1 | [14 empty] | 101.3877 |  |  | #VALUE!
22.07.2008 13:00 | 3600 | 2 | 767.6 | GGB | 764.835 | 779.156 | 768.864 | 258.89 | GGB | 10472.1 | GGB | 9.79 | GGB | 1009.59 | GGB | 68.47 | GGB | 158666.5 | GGB | 126426.16 | GGB | 0 | 0 | 2864 | 3600 | 2848.67 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 293996.87 | GGB | 293999.6 | 2848.67 | 2848.67 |  |  |  | 0 | 1 | [14 empty] | 100.0407 |  |  | #VALUE!
22.07.2008 14:00 | 3600 | 2 | 767.32 | GGB | 764.469 | 777.938 | 768.864 | 258.12 | GGB | 10443.7 | GGB | 9.78 | GGB | 1009.68 | GGB | 68.79 | GGB | 157807.14 | GGB | 125635.09 | GGB | 0 | 0 | 2863 | 3600 | 2847.56 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294034.14 | GGB | 294036.87 | 2847.56 | 2847.56 |  |  |  | 1 | 1 |  |  |  |  | 125635.09 | 2847.56 | 125635.09 | 2847.56 | 9.599 | [5 empty] | 99.376 |  |  | #VALUE!
22.07.2008 15:00 | 3600 | 2 | 768.4 | GGB | 765.934 | 780.047 | 770.33 | 258.02 | GGB | 10412.8 | GGB | 9.8 | GGB | 1010.15 | GGB | 69.2 | GGB | 158005.2 | GGB | 125699.77 | GGB | 0 | 0 | 2823 | 3600 | 2807.95 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294071.41 | GGB | 294074.14 | 2807.95 | 2807.95 |  |  |  | 0 | 1 | [14 empty] | 98.0441 |  |  | #VALUE!
22.07.2008 16:00 | 3600 | 2 | 768.08 | GGB | 767.033 | 780.164 | 771.429 | 257.05 | GGB | 10367.4 | GGB | 9.79 | GGB | 1009.2 | GGB | 69.37 | GGB | 157678.4 | GGB | 125258.66 | GGB | 0 | 0 | 2806 | 3600 | 2790.83 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294108.67 | GGB | 294111.41 | 2790.83 | 2790.83 |  |  |  | 0 | 1 | [14 empty] | 97.1043 |  |  | #VALUE!
22.07.2008 17:00 | 3600 | 2 | 768.56 | GGB | 767.033 | 781.43 | 772.527 | 256.35 | GGB | 10354.2 | GGB | 9.79 | GGB | 1008.74 | GGB | 69.52 | GGB | 157159.04 | GGB | 124734.61 | GGB | 0 | 0 | 2770 | 3600 | 2754.25 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294145.94 | GGB | 294148.68 | 2754.25 | 2754.25 |  |  |  | 0 | 1 | [14 empty] | 95.4306 |  |  | #VALUE!
22.07.2008 18:00 | 3600 | 2 | 768.37 | GGB | 765.934 | 780.211 | 770.33 | 256.34 | GGB | 10345.7 | GGB | 9.78 | GGB | 1008.67 | GGB | 69.52 | GGB | 157138.13 | GGB | 124707.75 | GGB | 0 | 0 | 2769 | 3600 | 2753.44 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294183.21 | GGB | 294185.95 | 2753.44 | 2753.44 |  |  |  | 0 | 1 | [14 empty] | 95.382 |  |  | #VALUE!
22.07.2008 19:00 | 3600 | 2 | 768.79 | GGB | 765.934 | 779.602 | 770.33 | 256.71 | GGB | 10355 | GGB | 9.78 | GGB | 1009.11 | GGB | 69.68 | GGB | 157308.69 | GGB | 124841.86 | GGB | 0 | 0 | 2760 | 3600 | 2744.48 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294220.47 | GGB | 294223.22 | 2744.48 | 2744.48 |  |  |  | 0 | 1 | [14 empty] | 95.1739 |  |  | #VALUE!
22.07.2008 20:00 | 3600 | 2 | 768.19 | GGB | 764.835 | 778.336 | 769.597 | 256.63 | GGB | 10377.9 | GGB | 9.78 | GGB | 1009.44 | GGB | 69.54 | GGB | 157039.1 | GGB | 124717.42 | GGB | 0 | 0 | 2802 | 3600 | 2786.31 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294257.74 | GGB | 294260.49 | 2786.31 | 2786.31 |  |  |  | 1 | 1 |  |  |  |  | 124717.42 | 2786.31 |  | 2786.31 | 9.3239 | [5 empty] | 96.5282 |  |  | #VALUE!
22.07.2008 21:00 | 3600 | 2 | 767.96 | GGB | 764.835 | 779.344 | 769.597 | 257.71 | GGB | 10415.1 | GGB | 9.78 | GGB | 1010.19 | GGB | 69.36 | GGB | 157502.35 | GGB | 125245.96 | GGB | 0 | 0 | 2828 | 3600 | 2812.57 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294295.01 | GGB | 294297.76 | 2812.57 | 2812.57 |  |  |  | 0 | 1 | [14 empty] | 97.8508 |  |  | #VALUE!
22.07.2008 22:00 | 3600 | 2 | 767.01 | GGB | 765.934 | 779.273 | 769.597 | 259.47 | GGB | 10459.7 | GGB | 9.77 | GGB | 1011.07 | GGB | 68.89 | GGB | 158831.55 | GGB | 126586.6 | GGB | 0 | 0 | 2891 | 3600 | 2875.62 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294332.27 | GGB | 294335.03 | 2875.62 | 2875.62 |  |  |  | 0 | 1 | [14 empty] | 101.1153 |  |  | #VALUE!
22.07.2008 23:00 | 3600 | 2 | 766.52 | GGB | 764.835 | 778.148 | 769.597 | 261.38 | GGB | 10522.5 | GGB | 9.77 | GGB | 1012.17 | GGB | 68.34 | GGB | 160050.73 | GGB | 127900.11 | GGB | 0 | 0 | 2930 | 3600 | 2914.07 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294369.54 | GGB | 294372.3 | 2914.07 | 2914.07 |  |  |  | 1 | 1 |  |  |  |  | 127900.11 | 2914.07 | 127900.11 | 2914.07 | 10.0003 | [5 empty] | 103.5305 |  |  | #VALUE!
22.07.2008 24:00 | 3600 | 2 | 766.21 | GGB | 764.835 | 778.313 | 768.498 | 262.96 | GGB | 10569.1 | GGB | 9.77 | GGB | 1013.19 | GGB | 67.97 | GGB | 161549.39 | GGB | 129368.77 | GGB | 0 | 0 | 2972 | 3600 | 2956.39 | GGB | 100 | GGB | 37.27 | GGB | 37.27 | GGB | 294406.81 | GGB | 294409.57 | 2956.39 | 2921.3233 |  |  |  | 1 | 1 |  |  |  |  | 129368.77 | 2921.3233 | 129368.77 | 2921.3233 | 10.1403 | [5 empty] | 106.2401 | 2921.3233 |  | 104.98
23.07.2008 01:00 | 3600 | 2 | 765.64 | GGB | 767.033 | 780.164 | 771.795 | 265.15 | GGB | 10621.1 | GGB | 9.77 | GGB | 1014.53 | GGB | 66.8 | GGB | 164509.3 | GGB | 132367.21 | GGB | 0 | 0 | 3029 | 3600 | 3013.47 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294444.78 | GGB | 294447.54 | 3013.47 | 2855.1482 |  |  |  | 0 | 1 | [14 empty] | 110.8013 | 2855.1482 |  | 104.98
23.07.2008 02:00 | 3600 | 2 | 766.06 | GGB | 764.469 | 779.063 | 769.597 | 265.25 | GGB | 10667.7 | GGB | 9.78 | GGB | 1015 | GGB | 67.2 | GGB | 163399.06 | GGB | 131383.13 | GGB | 0 | 0 | 3001 | 3600 | 2985.83 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294482.74 | GGB | 294485.51 | 2985.83 | 2876.5337 |  |  |  | 0 | 1 | [14 empty] | 108.9688 | 2876.5337 |  | 104.98
23.07.2008 03:00 | 3600 | 2 | 765.63 | GGB | 764.469 | 776.93 | 768.132 | 265.87 | GGB | 10616.7 | GGB | 9.78 | GGB | 1015.82 | GGB | 66.39 | GGB | 164852.6 | GGB | 132974.95 | GGB | 0 | 0 | 3009 | 3600 | 2993.68 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294520.71 | GGB | 294523.48 | 2993.68 | 2842.0992 |  |  |  | 1 | 1 |  |  |  |  | 132974.95 | 2842.0992 | 132974.95 | 2842.0992 | 9.9533 | [5 empty] | 110.579 | 2842.0992 |  | 104.98
23.07.2008 04:00 | 3600 | 2 | 765.08 | GGB | 762.271 | 774.727 | 766.3 | 266.88 | GGB | 10652.7 | GGB | 9.78 | GGB | 1016.71 | GGB | 65.76 | GGB | 165976.05 | GGB | 134248.21 | GGB | 0 | 0 | 3047 | 3600 | 3031.36 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294558.68 | GGB | 294561.45 | 3031.36 | 2815.1437 |  |  |  | 0 | 1 | [14 empty] | 113.043 | 2815.1437 |  | 104.98
23.07.2008 05:00 | 3600 | 2 | 765.48 | GGB | 764.469 | 776.859 | 767.766 | 267.05 | GGB | 10693.4 | GGB | 9.79 | GGB | 1016.87 | GGB | 65.56 | GGB | 166280.84 | GGB | 134593.75 | GGB | 0 | 0 | 3037 | 3600 | 3021.59 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294596.64 | GGB | 294599.42 | 3021.59 | 2807.9164 |  |  |  | 1 | 1 |  |  |  |  | 134593.75 | 2807.9164 | 134593.75 | 2807.9164 | 9.9533 | [5 empty] | 112.9686 | 2807.9164 |  | 104.98
23.07.2008 06:00 | 3600 | 2 | 765.17 | GGB | 762.271 | 775.992 | 767.766 | 267.65 | GGB | 10670.8 | GGB | 9.78 | GGB | 1017.32 | GGB | 65.27 | GGB | 167113.8 | GGB | 135442.94 | GGB | 0 | 0 | 3033 | 3600 | 3017.29 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294634.61 | GGB | 294637.39 | 3017.29 | 2790.3116 |  |  |  | 0 | 1 | [14 empty] | 113.5196 | 2790.3116 |  | 104.98
23.07.2008 07:00 | 3600 | 2 | 765.89 | GGB | 763.37 | 776.039 | 767.766 | 267.59 | GGB | 10686.5 | GGB | 9.8 | GGB | 1017.68 | GGB | 65.07 | GGB | 167219.43 | GGB | 135658.54 | GGB | 0 | 0 | 3009 | 3600 | 2993.14 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294672.58 | GGB | 294675.36 | 2993.14 | 2785.877 |  |  |  | 0 | 1 | [14 empty] | 112.7903 | 2785.877 |  | 104.98
23.07.2008 08:00 | 3600 | 2 | 766.2 | GGB | 765.934 | 779.484 | 770.696 | 266.98 | GGB | 10641.1 | GGB | 9.8 | GGB | 1017.79 | GGB | 64.85 | GGB | 167084.09 | GGB | 135651.38 | GGB | 0 | 0 | 2973 | 3600 | 2957.81 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294710.54 | GGB | 294713.33 | 2957.81 | 2786.024 |  |  |  | 0 | 1 | [14 empty] | 111.4531 | 2786.024 |  | 104.98
23.07.2008 09:00 | 3600 | 2 | 766.64 | GGB | 764.835 | 778.523 | 769.597 | 265.51 | GGB | 10582.7 | GGB | 9.8 | GGB | 1017.47 | GGB | 65.41 | GGB | 165463.29 | GGB | 134072.14 | GGB | 0 | 0 | 2918 | 3600 | 2902.28 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294748.51 | GGB | 294751.3 | 2902.28 | 2818.8407 |  |  |  | 1 | 1 |  |  |  |  | 134072.14 | 2818.8407 | 134072.14 | 2818.8407 | 9.9533 | [5 empty] | 108.0875 | 2818.8407 |  | 104.98
23.07.2008 10:00 | 3600 | 2 | 767.56 | GGB | 765.934 | 779.203 | 769.597 | 262.47 | GGB | 10545.6 | GGB | 9.81 | GGB | 1016.96 | GGB | 66.79 | GGB | 162021.43 | GGB | 130684.08 | GGB | 0 | 0 | 2859 | 3600 | 2843.89 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294786.48 | GGB | 294789.27 | 2843.89 | 2843.89 |  |  |  | 0 | 1 | [14 empty] | 103.2364 |  |  | #VALUE!
23.07.2008 11:00 | 3600 | 2 | 767.24 | GGB | 764.835 | 778.266 | 769.597 | 261.58 | GGB | 10469.2 | GGB | 9.78 | GGB | 1016.53 | GGB | 67.31 | GGB | 161064.14 | GGB | 129655.73 | GGB | 0 | 0 | 2856 | 3600 | 2840.01 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294824.44 | GGB | 294827.24 | 2840.01 | 2840.01 |  |  |  | 1 | 1 |  |  |  |  | 129655.73 | 2840.01 | 129655.73 | 2840.01 | 9.6978 | [5 empty] | 102.2843 |  |  | #VALUE!
23.07.2008 12:00 | 3600 | 2 | 768.58 | GGB | 765.934 | 779.672 | 770.696 | 259.98 | GGB | 10422.3 | GGB | 9.8 | GGB | 1015.95 | GGB | 67.89 | GGB | 159825.16 | GGB | 128367.86 | GGB | 0 | 0 | 2762 | 3600 | 2746.54 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294862.41 | GGB | 294865.21 | 2746.54 | 2746.54 |  |  |  | 0 | 1 | [14 empty] | 97.9354 |  |  | #VALUE!
23.07.2008 13:00 | 3600 | 2 | 769.26 | GGB | 767.033 | 780.984 | 772.161 | 258.13 | GGB | 10369 | GGB | 9.8 | GGB | 1015.06 | GGB | 68.45 | GGB | 158802.94 | GGB | 127226.23 | GGB | 0 | 0 | 2718 | 3600 | 2702.14 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294900.38 | GGB | 294903.18 | 2702.14 | 2702.14 |  |  |  | 0 | 1 | [14 empty] | 95.4953 |  |  | #VALUE!
23.07.2008 14:00 | 3600 | 2 | 769.35 | GGB | 768.132 | 782.039 | 773.26 | 256.65 | GGB | 10311.3 | GGB | 9.79 | GGB | 1014.6 | GGB | 69.05 | GGB | 157832.45 | GGB | 126168.26 | GGB | 0 | 0 | 2697 | 3600 | 2681.94 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294938.35 | GGB | 294941.15 | 2681.94 | 2681.94 |  |  |  | 0 | 1 | [14 empty] | 93.9933 |  |  | #VALUE!
23.07.2008 15:00 | 3600 | 2 | 769.11 | GGB | 767.033 | 782.203 | 772.161 | 255.96 | GGB | 10267.3 | GGB | 9.78 | GGB | 1013.92 | GGB | 69.36 | GGB | 157365.9 | GGB | 125598.98 | GGB | 0 | 0 | 2695 | 3600 | 2679.79 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 294976.31 | GGB | 294979.12 | 2679.79 | 2679.79 |  |  |  | 0 | 1 | [14 empty] | 93.4941 |  |  | #VALUE!
23.07.2008 16:00 | 3600 | 2 | 769.8 | GGB | 767.033 | 781.688 | 772.161 | 255.84 | GGB | 10244.5 | GGB | 9.79 | GGB | 1013.06 | GGB | 69.67 | GGB | 157320.79 | GGB | 125343.02 | GGB | 0 | 0 | 2663 | 3600 | 2647.58 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295014.28 | GGB | 295017.09 | 2647.58 | 2647.58 |  |  |  | 0 | 1 | [14 empty] | 92.1821 |  |  | #VALUE!
23.07.2008 17:00 | 3600 | 2 | 769.3 | GGB | 765.934 | 780.82 | 772.161 | 255.41 | GGB | 10222.7 | GGB | 9.78 | GGB | 1012.4 | GGB | 69.54 | GGB | 156945.57 | GGB | 125007.79 | GGB | 0 | 0 | 2693 | 3600 | 2677.74 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295052.25 | GGB | 295055.06 | 2677.74 | 2677.74 |  |  |  | 0 | 1 | [14 empty] | 92.9829 |  |  | #VALUE!
23.07.2008 18:00 | 3600 | 2 | 769.13 | GGB | 767.033 | 781.969 | 772.161 | 255.41 | GGB | 10235 | GGB | 9.78 | GGB | 1012.25 | GGB | 69.35 | GGB | 156663.89 | GGB | 124836.89 | GGB | 0 | 0 | 2688 | 3600 | 2672.6 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295090.21 | GGB | 295093.03 | 2672.6 | 2672.6 |  |  |  | 0 | 1 | [14 empty] | 92.6775 |  |  | #VALUE!
23.07.2008 19:00 | 3600 | 2 | 768.8 | GGB | 765.934 | 779.859 | 770.696 | 255.57 | GGB | 10241.3 | GGB | 9.78 | GGB | 1012.26 | GGB | 69.05 | GGB | 156433.92 | GGB | 124762.73 | GGB | 0 | 0 | 2698 | 3600 | 2683.05 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295128.18 | GGB | 295131 | 2683.05 | 2683.05 |  |  |  | 0 | 1 | [14 empty] | 92.9846 |  |  | #VALUE!
23.07.2008 20:00 | 3600 | 2 | 768.77 | GGB | 764.835 | 779.836 | 770.696 | 256.9 | GGB | 10252.4 | GGB | 9.78 | GGB | 1012.78 | GGB | 68.9 | GGB | 157124.93 | GGB | 125433.45 | GGB | 0 | 0 | 2722 | 3600 | 2706.56 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295166.15 | GGB | 295168.97 | 2706.56 | 2706.56 |  |  |  | 0 | 1 | [14 empty] | 94.3037 |  |  | #VALUE!
23.07.2008 21:00 | 3600 | 2 | 768.4 | GGB | 765.934 | 778.945 | 770.696 | 258.34 | GGB | 10256.9 | GGB | 9.78 | GGB | 1013.14 | GGB | 68.34 | GGB | 158236.27 | GGB | 126572.36 | GGB | 0 | 0 | 2725 | 3600 | 2709.82 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295204.11 | GGB | 295206.94 | 2709.82 | 2709.82 |  |  |  | 0 | 1 | [14 empty] | 95.2745 |  |  | #VALUE!
23.07.2008 22:00 | 3600 | 2 | 768.44 | GGB | 764.469 | 777.891 | 768.498 | 258.2 | GGB | 10286.7 | GGB | 9.78 | GGB | 1012.97 | GGB | 68.48 | GGB | 157743.32 | GGB | 126107.71 | GGB | 0 | 0 | 2715 | 3600 | 2699.91 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295242.08 | GGB | 295244.91 | 2699.91 | 2699.91 |  |  |  | 1 | 1 |  |  |  |  | 126107.71 | 2699.91 | 126107.71 | 2699.91 | 8.9671 | [5 empty] | 94.5776 |  |  | #VALUE!
23.07.2008 23:00 | 3600 | 2 | 767.68 | GGB | 764.469 | 778.102 | 768.864 | 259.68 | GGB | 10288.5 | GGB | 9.77 | GGB | 1014.05 | GGB | 67.92 | GGB | 159076.93 | GGB | 127515.95 | GGB | 0 | 0 | 2773 | 3600 | 2757.95 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295280.05 | GGB | 295282.88 | 2757.95 | 2757.95 |  |  |  | 1 | 1 |  |  |  |  | 127515.95 | 2757.95 | 127515.95 | 2757.95 | 9.2621 | [5 empty] | 97.6896 |  |  | #VALUE!
23.07.2008 24:00 | 3600 | 2 | 768.12 | GGB | 764.469 | 777.984 | 768.864 | 259.29 | GGB | 10363.9 | GGB | 9.78 | GGB | 1014.42 | GGB | 68.41 | GGB | 157850.05 | GGB | 126398.5 | GGB | 0 | 0 | 2788 | 3600 | 2772.94 | GGB | 100 | GGB | 37.97 | GGB | 37.97 | GGB | 295318.01 | GGB | 295320.85 | 2772.94 | 2772.94 |  |  |  | 1 | 1 |  |  |  |  | 126398.5 | 2772.94 | 126398.5 | 2772.94 | 9.2309 | [5 empty] | 97.3598 |  |  | #VALUE!
24.07.2008 01:00 | 3600 | 2 | 767.01 | GGB | 763.37 | 776.906 | 767.766 | 261.57 | GGB | 10344.9 | GGB | 9.77 | GGB | 1015 | GGB | 67.71 | GGB | 160004.51 | GGB | 128459.96 | GGB | 0 | 0 | 2830 | 3600 | 2814.14 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295355.96 | GGB | 295358.8 | 2814.14 | 2814.14 |  |  |  | 0 | 1 | [14 empty] | 100.4179 |  |  | #VALUE!
24.07.2008 02:00 | 3600 | 2 | 767.65 | GGB | 763.37 | 776.766 | 767.766 | 261.22 | GGB | 10407.6 | GGB | 9.79 | GGB | 1014.6 | GGB | 67.65 | GGB | 159298.1 | GGB | 127864.75 | GGB | 0 | 0 | 2813 | 3600 | 2797.19 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295393.91 | GGB | 295396.75 | 2797.19 | 2797.19 |  |  |  | 0 | 1 | [14 empty] | 99.3506 |  |  | #VALUE!
24.07.2008 03:00 | 3600 | 2 | 767.51 | GGB | 764.835 | 777.727 | 768.864 | 261.11 | GGB | 10428.3 | GGB | 9.79 | GGB | 1014.49 | GGB | 68.01 | GGB | 159282.69 | GGB | 127704.4 | GGB | 0 | 0 | 2834 | 3600 | 2818.76 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295431.86 | GGB | 295434.7 | 2818.76 | 2818.76 |  |  |  | 1 | 1 |  |  |  |  | 127704.4 | 2818.76 | 127704.4 | 2818.76 | 9.4853 | [5 empty] | 99.9911 |  |  | #VALUE!
24.07.2008 04:00 | 3600 | 2 | 766.79 | GGB | 764.835 | 778.852 | 768.864 | 261.82 | GGB | 10441.9 | GGB | 9.78 | GGB | 1015.04 | GGB | 67.78 | GGB | 160021.02 | GGB | 128451.99 | GGB | 0 | 0 | 2888 | 3600 | 2872.58 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295469.81 | GGB | 295472.65 | 2872.58 | 2872.58 |  |  |  | 0 | 1 | [14 empty] | 102.4968 |  |  | #VALUE!
24.07.2008 05:00 | 3600 | 2 | 767.29 | GGB | 765.934 | 779.719 | 770.33 | 262.22 | GGB | 10473.1 | GGB | 9.79 | GGB | 1015.18 | GGB | 67.64 | GGB | 160259.79 | GGB | 128713.01 | GGB | 0 | 0 | 2882 | 3600 | 2866.35 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295507.76 | GGB | 295510.6 | 2866.35 | 2866.35 |  |  |  | 0 | 1 | [14 empty] | 102.4824 |  |  | #VALUE!
24.07.2008 06:00 | 3600 | 2 | 766.22 | GGB | 764.835 | 778.805 | 769.963 | 263.01 | GGB | 10477.5 | GGB | 9.77 | GGB | 1014.99 | GGB | 67.29 | GGB | 160847.37 | GGB | 129295.28 | GGB | 0 | 0 | 2931 | 3600 | 2915.68 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295545.71 | GGB | 295548.55 | 2915.68 | 2915.68 |  |  |  | 0 | 1 | [14 empty] | 104.7177 |  |  | #VALUE!
24.07.2008 07:00 | 3600 | 2 | 766.57 | GGB | 764.469 | 777.703 | 769.963 | 263.97 | GGB | 10470 | GGB | 9.78 | GGB | 1015.3 | GGB | 66.87 | GGB | 161650.62 | GGB | 130139.63 | GGB | 0 | 0 | 2907 | 3600 | 2891.2 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295583.66 | GGB | 295586.5 | 2891.2 | 2891.2 |  |  |  | 1 | 1 |  |  |  |  | 130139.63 | 2891.2 | 130139.63 | 2891.2 | 9.9146 | [5 empty] | 104.5166 |  |  | #VALUE!
24.07.2008 08:00 | 3600 | 2 | 767.72 | GGB | 764.469 | 778.031 | 769.963 | 261.99 | GGB | 10487.5 | GGB | 9.8 | GGB | 1015.22 | GGB | 67.56 | GGB | 159502.76 | GGB | 128141.81 | GGB | 0 | 0 | 2850 | 3600 | 2834.37 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295621.61 | GGB | 295624.45 | 2834.37 | 2834.37 |  |  |  | 1 | 1 |  |  |  |  | 128141.81 | 2834.37 | 128141.81 | 2834.37 | 9.5705 | [5 empty] | 100.8893 |  |  | #VALUE!
24.07.2008 09:00 | 3600 | 2 | 768.06 | GGB | 764.835 | 778.969 | 770.33 | 260.26 | GGB | 10422.7 | GGB | 9.8 | GGB | 1014.94 | GGB | 67.9 | GGB | 158108.63 | GGB | 126858.17 | GGB | 0 | 0 | 2803 | 3600 | 2787.07 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295659.55 | GGB | 295662.4 | 2787.07 | 2787.07 |  |  |  | 0 | 1 | [14 empty] | 98.2118 |  |  | #VALUE!
24.07.2008 10:00 | 3600 | 2 | 767.89 | GGB | 765.934 | 778.781 | 770.33 | 259.04 | GGB | 10356 | GGB | 9.79 | GGB | 1015.1 | GGB | 68.45 | GGB | 157361.5 | GGB | 126075.06 | GGB | 0 | 0 | 2782 | 3600 | 2766.15 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295697.5 | GGB | 295700.35 | 2766.15 | 2766.15 |  |  |  | 0 | 1 | [14 empty] | 96.8729 |  |  | #VALUE!
24.07.2008 11:00 | 3600 | 2 | 768.14 | GGB | 765.934 | 780.164 | 770.696 | 258.35 | GGB | 10322.2 | GGB | 9.79 | GGB | 1014.82 | GGB | 68.76 | GGB | 156680.39 | GGB | 125382.11 | GGB | 0 | 0 | 2753 | 3600 | 2738.03 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295735.45 | GGB | 295738.3 | 2738.03 | 2738.03 |  |  |  | 0 | 1 | [14 empty] | 95.3611 |  |  | #VALUE!
24.07.2008 12:00 | 3600 | 2 | 768.69 | GGB | 765.934 | 780.188 | 770.696 | 256.65 | GGB | 10251.9 | GGB | 9.79 | GGB | 1014.05 | GGB | 69.46 | GGB | 155346.78 | GGB | 123966.17 | GNB | 0 | 0 | 2716 | 3600 | 2700.91 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295773.4 | GGB | 295776.25 | 2700.91 | 2700.91 |  |  |  | 0 | 1 | [14 empty] | 93.006 |  |  | #VALUE!
24.07.2008 13:00 | 3600 | 2 | 769.4 | GGB | 767.033 | 780.234 | 771.795 | 255.81 | GGB | 10179.8 | GGB | 9.79 | GGB | 1013.16 | GGB | 69.53 | GGB | 155139.92 | GGB | 123668.75 | GNB | 0 | 0 | 2669 | 3600 | 2653.39 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295811.35 | GGB | 295814.2 | 2653.39 | 2653.39 |  |  |  | 0 | 1 | [14 empty] | 91.1504 |  |  | #VALUE!
24.07.2008 14:00 | 3600 | 2 | 770.16 | GGB | 767.033 | 781.336 | 772.527 | 255.39 | GGB | 10124.4 | GGB | 9.79 | GGB | 1012.56 | GGB | 69.57 | GGB | 155067.3 | GGB | 123521.41 | GNB | 0 | 0 | 2620 | 3600 | 2605.12 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295849.3 | GGB | 295852.15 | 2605.12 | 2605.12 |  |  |  | 0 | 1 | [14 empty] | 89.3856 |  |  | #VALUE!
24.07.2008 15:00 | 3600 | 2 | 770.3 | GGB | 767.033 | 782.531 | 772.527 | 254.22 | GGB | 10090.4 | GGB | 9.79 | GGB | 1011.72 | GGB | 70.21 | GGB | 154040.68 | GGB | 122372.78 | GNB | 0 | 0 | 2607 | 3600 | 2591.37 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295887.25 | GGB | 295890.1 | 2591.37 | 2591.37 |  |  |  | 0 | 1 | [14 empty] | 88.087 |  |  | #VALUE!
24.07.2008 16:00 | 3600 | 2 | 769.94 | GGB | 764.835 | 778.734 | 770.33 | 251.64 | GGB | 10072.3 | GGB | 9.77 | GGB | 1010.58 | GGB | 71.19 | GGB | 151937.94 | GGB | 120225.58 | GNB | 0 | 0 | 2602 | 3600 | 2586.51 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295925.2 | GGB | 295928.05 | 2586.51 | 2586.51 |  |  |  | 0 | 1 | [14 empty] | 86.3791 |  |  | #VALUE!
24.07.2008 17:00 | 3600 | 2 | 769.97 | GGB | 765.934 | 780.891 | 771.429 | 252.54 | GGB | 10097.7 | GGB | 9.78 | GGB | 1010.18 | GGB | 71.09 | GGB | 152591.54 | GGB | 120728.44 | GNB | 0 | 0 | 2622 | 3600 | 2606.59 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 295963.15 | GGB | 295966 | 2606.59 | 2606.59 |  |  |  | 0 | 1 | [14 empty] | 87.4138 |  |  | #VALUE!
24.07.2008 18:00 | 3600 | 2 | 770.03 | GGB | 767.033 | 780.914 | 772.527 | 253.02 | GGB | 10108 | GGB | 9.78 | GGB | 1009.91 | GGB | 70.98 | GGB | 152730.18 | GGB | 120843.72 | GNB | 0 | 0 | 2633 | 3600 | 2617.32 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296001.09 | GGB | 296003.95 | 2617.32 | 2617.32 |  |  |  | 0 | 1 | [14 empty] | 87.8574 |  |  | #VALUE!
24.07.2008 19:00 | 3600 | 2 | 770.08 | GGB | 767.033 | 781.078 | 772.527 | 253.4 | GGB | 10091.5 | GGB | 9.78 | GGB | 1009.9 | GGB | 70.96 | GGB | 153160.41 | GGB | 121191.21 | GNB | 0 | 0 | 2619 | 3600 | 2604.04 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296039.04 | GGB | 296041.9 | 2604.04 | 2604.04 |  |  |  | 0 | 1 | [14 empty] | 87.663 |  |  | #VALUE!
24.07.2008 20:00 | 3600 | 2 | 769.46 | GGB | 765.934 | 779.063 | 770.33 | 253.23 | GGB | 10101.8 | GGB | 9.77 | GGB | 1009.8 | GGB | 71.12 | GGB | 152721.38 | GGB | 120775.38 | GNB | 0 | 0 | 2647 | 3600 | 2631.65 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296076.99 | GGB | 296079.85 | 2631.65 | 2631.65 |  |  |  | 0 | 1 | [14 empty] | 88.2885 |  |  | #VALUE!
24.07.2008 21:00 | 3600 | 2 | 769.02 | GGB | 764.835 | 778.922 | 768.864 | 254.17 | GGB | 10131.7 | GGB | 9.77 | GGB | 1009.93 | GGB | 71.03 | GGB | 153252.84 | GGB | 121243.24 | GNB | 0 | 0 | 2678 | 3600 | 2663.02 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296114.94 | GGB | 296117.8 | 2663.02 | 2663.02 |  |  |  | 0 | 1 | [14 empty] | 89.687 |  |  | #VALUE!
24.07.2008 22:00 | 3600 | 2 | 768.61 | GGB | 764.835 | 778.758 | 770.33 | 255.94 | GGB | 10190.7 | GGB | 9.77 | GGB | 1010.46 | GGB | 70.42 | GGB | 154490.72 | GGB | 122503.33 | GNB | 0 | 0 | 2722 | 3600 | 2706.77 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296152.89 | GGB | 296155.75 | 2706.77 | 2706.77 |  |  |  | 0 | 1 | [14 empty] | 92.1079 |  |  | #VALUE!
24.07.2008 23:00 | 3600 | 2 | 768.54 | GGB | 767.033 | 780.82 | 771.429 | 258.01 | GGB | 10245.5 | GGB | 9.77 | GGB | 1011.31 | GGB | 69.8 | GGB | 156199.55 | GGB | 124188.62 | GGB | 0 | 0 | 2750 | 3600 | 2734.42 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296190.84 | GGB | 296193.7 | 2734.42 | 2734.42 |  |  |  | 0 | 1 | [14 empty] | 94.3288 |  |  | #VALUE!
24.07.2008 24:00 | 3600 | 2 | 767.97 | GGB | 768.132 | 781.617 | 772.527 | 260.6 | GGB | 10271.3 | GGB | 9.77 | GGB | 1011.93 | GGB | 68.73 | GGB | 158795.24 | GGB | 126724.37 | GGB | 0 | 0 | 2788 | 3600 | 2772.77 | GGB | 100 | GGB | 37.95 | GGB | 37.95 | GGB | 296228.79 | GGB | 296231.65 | 2772.77 | 2772.77 |  |  |  | 0 | 1 | [14 empty] | 97.6049 |  |  | #VALUE!
25.07.2008 01:00 | 3600 | 2 | 767.91 | GGB | 768.132 | 781.852 | 772.527 | 260.48 | GGB | 10339.3 | GGB | 9.78 | GGB | 1012.12 | GGB | 68.54 | GGB | 158380.42 | GGB | 126485.96 | GGB | 0 | 0 | 2792 | 3600 | 2776.52 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296266.11 | GGB | 296268.97 | 2776.52 | 2776.52 |  |  |  | 0 | 1 | [14 empty] | 97.553 |  |  | #VALUE!
25.07.2008 02:00 | 3600 | 2 | 766.57 | GGB | 764.469 | 778.359 | 769.963 | 261.04 | GGB | 10367.1 | GGB | 9.76 | GGB | 1012.44 | GGB | 68.57 | GGB | 158744.63 | GGB | 126806.06 | GGB | 0 | 0 | 2870 | 3600 | 2854.41 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296303.43 | GGB | 296306.29 | 2854.41 | 2854.41 |  |  |  | 1 | 1 |  |  |  |  | 126806.06 | 2854.41 | 126806.06 | 2854.41 | 9.6987 | [5 empty] | 100.5435 |  |  | #VALUE!
25.07.2008 03:00 | 3600 | 2 | 767.04 | GGB | 762.271 | 775.313 | 766.667 | 261.58 | GGB | 10408.8 | GGB | 9.78 | GGB | 1012.69 | GGB | 68.38 | GGB | 159290.39 | GGB | 127345.18 | GGB | 0 | 0 | 2869 | 3600 | 2853.2 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296340.75 | GGB | 296343.61 | 2853.2 | 2853.2 |  |  |  | 0 | 1 | [14 empty] | 100.9281 |  |  | #VALUE!
25.07.2008 04:00 | 3600 | 2 | 766.22 | GGB | 762.271 | 776.32 | 767.766 | 262.68 | GGB | 10436.3 | GGB | 9.77 | GGB | 1013.15 | GGB | 67.77 | GGB | 160289.5 | GGB | 128432.71 | GGB | 0 | 0 | 2913 | 3600 | 2896.94 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296378.08 | GGB | 296380.93 | 2896.94 | 2896.94 |  |  |  | 0 | 1 | [14 empty] | 103.3505 |  |  | #VALUE!
25.07.2008 05:00 | 3600 | 2 | 766.74 | GGB | 763.37 | 776.906 | 766.667 | 263.87 | GGB | 10494.9 | GGB | 9.78 | GGB | 1013.25 | GGB | 67.39 | GGB | 161364.53 | GGB | 129448.37 | GGB | 0 | 0 | 2902 | 3600 | 2886.66 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296415.4 | GGB | 296418.25 | 2886.66 | 2886.66 |  |  |  | 0 | 1 | [14 empty] | 103.7982 |  |  | #VALUE!
25.07.2008 06:00 | 3600 | 2 | 766.72 | GGB | 765.934 | 778.992 | 769.963 | 264.44 | GGB | 10528.3 | GGB | 9.79 | GGB | 1013.18 | GGB | 67.07 | GGB | 162098.46 | GGB | 130153.1 | GGB | 0 | 0 | 2909 | 3600 | 2893.31 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296452.72 | GGB | 296455.57 | 2893.31 | 2893.31 |  |  |  | 0 | 1 | [14 empty] | 104.6037 |  |  | #VALUE!
25.07.2008 07:00 | 3600 | 2 | 766.64 | GGB | 764.469 | 777.773 | 768.864 | 263.66 | GGB | 10510.3 | GGB | 9.79 | GGB | 1013.55 | GGB | 67.01 | GGB | 161729.84 | GGB | 129926.95 | GGB | 0 | 0 | 2901 | 3600 | 2885.64 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296490.04 | GGB | 296492.89 | 2885.64 | 2885.64 |  |  |  | 1 | 1 |  |  |  |  | 129926.95 | 2885.64 | 129926.95 | 2885.64 | 10.0462 | [5 empty] | 104.1451 |  |  | #VALUE!
25.07.2008 08:00 | 3600 | 2 | 767.8 | GGB | 764.835 | 778.477 | 768.864 | 261.97 | GGB | 10475.5 | GGB | 9.8 | GGB | 1013.13 | GGB | 67.37 | GGB | 160150.86 | GGB | 128467.7 | GGB | 0 | 0 | 2837 | 3600 | 2821.57 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296527.36 | GGB | 296530.21 | 2821.57 | 2821.57 |  |  |  | 1 | 1 |  |  |  |  | 128467.7 | 2821.57 | 128467.7 | 2821.57 | 9.7128 | [5 empty] | 100.6891 |  |  | #VALUE!
25.07.2008 09:00 | 3600 | 2 | 767.77 | GGB | 765.934 | 779.344 | 770.33 | 259.87 | GGB | 10407.4 | GGB | 9.8 | GGB | 1013.55 | GGB | 67.81 | GGB | 158380.42 | GGB | 126937.16 | GGB | 0 | 0 | 2867 | 3103 | 2851.82 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296564.69 | GGB | 296567.53 | 2851.82 | 2851.82 |  |  |  | 0 | 1 | [14 empty] | 100.5561 |  |  | #VALUE!
25.07.2008 10:00 | 3600 | 2 | 768.2 | GGB | 767.033 | 780.281 | 771.429 | 258.18 | GGB | 10329.2 | GGB | 9.8 | GGB | 1012.73 | GGB | 68.66 | GGB | 156496.64 | GGB | 125012.95 | GGB | 0 | 0 | 2945 | 3600 | 2929.18 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296602.01 | GGB | 296604.85 | 2929.18 | 2929.18 |  |  |  | 0 | 1 | [14 empty] | 101.7182 |  |  | #VALUE!
25.07.2008 11:00 | 3600 | 2 | 768.58 | GGB | 767.033 | 781.219 | 772.527 | 256.33 | GGB | 10243.3 | GGB | 9.79 | GGB | 1011.78 | GGB | 69.35 | GGB | 154907.75 | GGB | 123379.97 | GNB | 0 | 0 | 2898 | 3600 | 2882.06 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296639.33 | GGB | 296642.17 | 2882.06 | 2882.06 |  |  |  | 0 | 1 | [14 empty] | 98.7746 |  |  | #VALUE!
25.07.2008 12:00 | 3600 | 2 | 768.98 | GGB | 765.934 | 780.891 | 771.429 | 254.79 | GGB | 10167.7 | GGB | 9.78 | GGB | 1010.92 | GGB | 69.91 | GGB | 153735.89 | GGB | 122142.57 | GNB | 0 | 0 | 2843 | 3600 | 2827.78 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296676.65 | GGB | 296679.49 | 2827.78 | 2827.78 |  |  |  | 0 | 1 | [14 empty] | 95.9423 |  |  | #VALUE!
25.07.2008 13:00 | 3600 | 2 | 770.05 | GGB | 765.934 | 780.867 | 771.429 | 253.51 | GGB | 10135.5 | GGB | 9.79 | GGB | 1009.8 | GGB | 70.37 | GGB | 152988.76 | GGB | 121250.73 | GNB | 0 | 0 | 2794 | 3600 | 2778.5 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296713.97 | GGB | 296716.81 | 2778.5 | 2778.5 |  |  |  | 0 | 1 | [14 empty] | 93.582 |  |  | #VALUE!
25.07.2008 14:00 | 3600 | 2 | 769.78 | GGB | 767.033 | 782.016 | 772.527 | 252.78 | GGB | 10086.2 | GGB | 9.78 | GGB | 1008.94 | GGB | 70.77 | GGB | 152210.82 | GGB | 120391.04 | GNB | 0 | 0 | 2778 | 3600 | 2762.82 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296751.29 | GGB | 296754.13 | 2762.82 | 2762.82 |  |  |  | 0 | 1 | [14 empty] | 92.3941 |  |  | #VALUE!
25.07.2008 15:00 | 3600 | 2 | 770.06 | GGB | 767.033 | 781.008 | 772.527 | 251.92 | GGB | 10052.2 | GGB | 9.78 | GGB | 1008.18 | GGB | 71.41 | GGB | 151607.84 | GGB | 119600.11 | GNB | 0 | 0 | 2775 | 3600 | 2759.87 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296788.62 | GGB | 296791.45 | 2759.87 | 2759.87 |  |  |  | 0 | 1 | [14 empty] | 91.6891 |  |  | #VALUE!
25.07.2008 16:00 | 3600 | 2 | 770.58 | GGB | 767.033 | 782.086 | 772.527 | 251.59 | GGB | 10048.4 | GGB | 9.78 | GGB | 1007.62 | GGB | 71.54 | GGB | 151322.85 | GGB | 119265.7 | GNB | 0 | 0 | 2745 | 3600 | 2729.97 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296825.94 | GGB | 296828.77 | 2729.97 | 2729.97 |  |  |  | 0 | 1 | [14 empty] | 90.4422 |  |  | #VALUE!
25.07.2008 17:00 | 3600 | 2 | 770.37 | GGB | 767.033 | 782.109 | 773.626 | 251.02 | GGB | 10021.9 | GGB | 9.78 | GGB | 1006.95 | GGB | 71.72 | GGB | 151055.47 | GGB | 118913.81 | GNB | 0 | 0 | 2728 | 3600 | 2712.57 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296863.26 | GGB | 296866.09 | 2712.57 | 2712.57 |  |  |  | 0 | 1 | [14 empty] | 89.6006 |  |  | #VALUE!
25.07.2008 18:00 | 3600 | 2 | 770.13 | GGB | 767.033 | 781.242 | 772.527 | 251.42 | GGB | 10005.9 | GGB | 9.77 | GGB | 1006.2 | GGB | 71.54 | GGB | 151550.62 | GGB | 119278.16 | GNB | 0 | 0 | 2752 | 3600 | 2736.56 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296900.58 | GGB | 296903.41 | 2736.56 | 2736.56 |  |  |  | 0 | 1 | [14 empty] | 90.67 |  |  | #VALUE!
25.07.2008 19:00 | 3600 | 2 | 770.06 | GGB | 767.033 | 781.266 | 772.527 | 251.41 | GGB | 10019.6 | GGB | 9.77 | GGB | 1005.93 | GGB | 71.76 | GGB | 151153.4 | GGB | 118855.01 | GNB | 0 | 0 | 2763 | 3600 | 2747.56 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296937.9 | GGB | 296940.73 | 2747.56 | 2747.56 |  |  |  | 0 | 1 | [14 empty] | 90.7115 |  |  | #VALUE!
25.07.2008 20:00 | 3600 | 2 | 769.75 | GGB | 765.934 | 780.211 | 771.429 | 252 | GGB | 10036 | GGB | 9.77 | GGB | 1006.05 | GGB | 71.68 | GGB | 151386.67 | GGB | 119080.56 | GNB | 0 | 0 | 2780 | 3600 | 2764.44 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 296975.23 | GGB | 296978.05 | 2764.44 | 2764.44 |  |  |  | 0 | 1 | [14 empty] | 91.442 |  |  | #VALUE!
25.07.2008 21:00 | 3600 | 2 | 769.32 | GGB | 765.934 | 781.219 | 771.429 | 252.97 | GGB | 10064.5 | GGB | 9.77 | GGB | 1006.42 | GGB | 71.4 | GGB | 152139.3 | GGB | 119815.89 | GNB | 0 | 0 | 2805 | 3600 | 2789.6 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 297012.55 | GGB | 297015.37 | 2789.6 | 2789.6 |  |  |  | 0 | 1 | [14 empty] | 92.844 |  |  | #VALUE!
25.07.2008 22:00 | 3600 | 2 | 768.77 | GGB | 765.934 | 780.305 | 770.33 | 254.79 | GGB | 10121 | GGB | 9.77 | GGB | 1007.1 | GGB | 70.68 | GGB | 153667.67 | GGB | 121354.1 | GNB | 0 | 0 | 2851 | 3600 | 2835 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 297049.87 | GGB | 297052.69 | 2835 | 2835 |  |  |  | 0 | 1 | [14 empty] | 95.5664 |  |  | #VALUE!
25.07.2008 23:00 | 3600 | 2 | 768.11 | GGB | 765.934 | 780.211 | 770.33 | 257.6 | GGB | 10159.6 | GGB | 9.76 | GGB | 1008.14 | GGB | 69.22 | GGB | 156781.62 | GGB | 124469.44 | GGB | 0 | 0 | 2888 | 3600 | 2872.77 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 297087.19 | GGB | 297090.01 | 2872.77 | 2872.77 |  |  |  | 0 | 1 | [14 empty] | 99.3256 |  |  | #VALUE!
25.07.2008 24:00 | 3600 | 2 | 768.04 | GGB | 764.835 | 779.109 | 769.963 | 257.34 | GGB | 10250.6 | GGB | 9.78 | GGB | 1008.53 | GGB | 69.1 | GGB | 155917.86 | GGB | 123874.49 | GNB | 0 | 0 | 2902 | 3600 | 2886.16 | GGB | 100 | GGB | 37.32 | GGB | 37.32 | GGB | 297124.51 | GGB | 297127.33 | 2886.16 | 2886.16 |  |  |  | 0 | 1 | [14 empty] | 99.3116 |  |  | #VALUE!
26.07.2008 01:00 | 3600 | 2 | 767.39 | GGB | 764.835 | 778.055 | 768.864 | 258.61 | GGB | 10284.3 | GGB | 9.77 | GGB | 1009.32 | GGB | 69.42 | GGB | 156535.15 | GGB | 124348 | GGB | 0 | 0 | 2970 | 3600 | 2954.26 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297160.61 | GGB | 297163.43 | 2954.26 | 2954.26 |  |  |  | 1 | 1 |  |  |  |  | 124348 | 2954.26 |  | 2954.26 | 10.1761 | [5 empty] | 102.0434 |  |  | #VALUE!
26.07.2008 02:00 | 3600 | 2 | 767.04 | GGB | 763.37 | 777 | 766.667 | 259.87 | GGB | 10332.2 | GGB | 9.77 | GGB | 1009.7 | GGB | 68.9 | GGB | 157719.11 | GGB | 125525.05 | GGB | 0 | 0 | 3005 | 3600 | 2989.01 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297196.7 | GGB | 297199.53 | 2989.01 | 2989.01 |  |  |  | 0 | 1 | [14 empty] | 104.221 |  |  | #VALUE!
26.07.2008 03:00 | 3600 | 2 | 766.99 | GGB | 762.271 | 776.719 | 766.667 | 261.02 | GGB | 10383.3 | GGB | 9.77 | GGB | 1010.2 | GGB | 68.44 | GGB | 158787.54 | GGB | 126609.25 | GGB | 0 | 0 | 3031 | 3600 | 3015.79 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297232.8 | GGB | 297235.63 | 3015.79 | 2984.9952 |  |  |  | 0 | 1 | [14 empty] | 106.063 | 2984.9952 |  | 104.98
26.07.2008 04:00 | 3600 | 2 | 766.74 | GGB | 764.469 | 778.594 | 768.864 | 261.84 | GGB | 10423.4 | GGB | 9.78 | GGB | 1010.54 | GGB | 67.96 | GGB | 159579.78 | GGB | 127464.42 | GGB | 0 | 0 | 3050 | 3600 | 3034.55 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297268.9 | GGB | 297271.73 | 3034.55 | 2964.9686 |  |  |  | 1 | 1 |  |  |  |  | 127464.42 | 2964.9686 | 127464.42 |  | 10.4689 | [5 empty] | 107.4437 | 2964.9686 |  | 104.98
26.07.2008 05:00 | 3600 | 2 | 766.5 | GGB | 763.37 | 777.469 | 768.864 | 262.72 | GGB | 10442.4 | GGB | 9.77 | GGB | 1011.43 | GGB | 67.66 | GGB | 160418.24 | GGB | 128358.93 | GGB | 0 | 0 | 3069 | 3600 | 3053.6 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297304.99 | GGB | 297307.83 | 3053.6 | 2944.3063 |  |  |  | 0 | 1 | [14 empty] | 108.8769 | 2944.3063 |  | 104.98
26.07.2008 06:00 | 3600 | 2 | 766.57 | GGB | 764.835 | 778.852 | 768.864 | 263.65 | GGB | 10480.8 | GGB | 9.78 | GGB | 1012.06 | GGB | 67.25 | GGB | 161208.28 | GGB | 129225.06 | GGB | 0 | 0 | 3074 | 3600 | 3058.3 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297341.09 | GGB | 297343.93 | 3058.3 | 2924.5721 |  |  |  | 0 | 1 | [14 empty] | 109.7803 | 2924.5721 |  | 104.98
26.07.2008 07:00 | 3600 | 2 | 766.3 | GGB | 764.469 | 777.422 | 768.864 | 263.89 | GGB | 10490.3 | GGB | 9.78 | GGB | 1012.66 | GGB | 67.06 | GGB | 161306.21 | GGB | 129454.9 | GGB | 0 | 0 | 3085 | 3600 | 3069.33 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297377.18 | GGB | 297380.03 | 3069.33 | 2919.3796 |  |  |  | 1 | 1 |  |  |  |  | 129454.9 | 2919.3796 | 129454.9 | 2919.3796 | 10.4689 | [5 empty] | 110.3722 | 2919.3796 |  | 104.98
26.07.2008 08:00 | 3600 | 2 | 767.48 | GGB | 764.835 | 778.453 | 769.963 | 262.28 | GGB | 10468.1 | GGB | 9.8 | GGB | 1012.47 | GGB | 67.35 | GGB | 160024.32 | GGB | 128289.45 | GGB | 0 | 0 | 3024 | 3600 | 3008.57 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297413.28 | GGB | 297416.13 | 3008.57 | 2945.9009 |  |  |  | 1 | 1 |  |  |  |  | 128289.45 | 2945.9009 | 128289.45 | 2945.9009 | 10.4689 | [5 empty] | 107.2133 | 2945.9009 |  | 104.98
26.07.2008 09:00 | 3600 | 2 | 767.68 | GGB | 764.835 | 778.758 | 770.33 | 260.2 | GGB | 10381.2 | GGB | 9.8 | GGB | 1012.42 | GGB | 67.96 | GGB | 157879.76 | GGB | 126338.46 | GGB | 0 | 0 | 2954 | 3600 | 2938.82 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297449.37 | GGB | 297452.23 | 2938.82 | 2938.82 |  |  |  | 0 | 1 | [14 empty] | 103.135 |  |  | #VALUE!
26.07.2008 10:00 | 3600 | 2 | 768.06 | GGB | 764.835 | 779.578 | 770.33 | 258.41 | GGB | 10291.4 | GGB | 9.8 | GGB | 1011.87 | GGB | 68.81 | GGB | 156146.73 | GGB | 124574.86 | GGB | 0 | 0 | 2905 | 3600 | 2889.56 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297485.47 | GGB | 297488.33 | 2889.56 | 2889.56 |  |  |  | 0 | 1 | [14 empty] | 99.9907 |  |  | #VALUE!
26.07.2008 11:00 | 3600 | 2 | 768.71 | GGB | 767.033 | 781.711 | 771.795 | 256.85 | GGB | 10226.4 | GGB | 9.8 | GGB | 1011.05 | GGB | 69.38 | GGB | 154824.12 | GGB | 123213.31 | GNB | 0 | 0 | 2870 | 3600 | 2854.9 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297521.57 | GGB | 297524.43 | 2854.9 | 2854.9 |  |  |  | 0 | 1 | [14 empty] | 97.7116 |  |  | #VALUE!
26.07.2008 12:00 | 3600 | 2 | 769.07 | GGB | 767.033 | 781.477 | 771.795 | 255.39 | GGB | 10159.6 | GGB | 9.79 | GGB | 1010.23 | GGB | 69.98 | GGB | 153979.06 | GGB | 122225.17 | GNB | 0 | 0 | 2838 | 3600 | 2822.11 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297557.66 | GGB | 297560.53 | 2822.11 | 2822.11 |  |  |  | 0 | 1 | [14 empty] | 95.8147 |  |  | #VALUE!
26.07.2008 13:00 | 3600 | 2 | 769.71 | GGB | 768.132 | 782.367 | 773.626 | 254.18 | GGB | 10126.9 | GGB | 9.79 | GGB | 1010.18 | GGB | 70.38 | GGB | 153136.21 | GGB | 121408.62 | GNB | 0 | 0 | 2807 | 3600 | 2791.05 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297593.76 | GGB | 297596.63 | 2791.05 | 2791.05 |  |  |  | 0 | 1 | [14 empty] | 94.1271 |  |  | #VALUE!
26.07.2008 14:00 | 3600 | 2 | 770 | GGB | 767.033 | 781.547 | 772.527 | 253.39 | GGB | 10084.2 | GGB | 9.78 | GGB | 1008.69 | GGB | 70.74 | GGB | 152582.74 | GGB | 120668.37 | GNB | 0 | 0 | 2766 | 3600 | 2750.9 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297629.85 | GGB | 297632.73 | 2750.9 | 2750.9 |  |  |  | 0 | 1 | [14 empty] | 92.2074 |  |  | #VALUE!
26.07.2008 15:00 | 3600 | 2 | 769.97 | GGB | 765.934 | 780.492 | 771.429 | 252.92 | GGB | 10065.5 | GGB | 9.78 | GGB | 1008.07 | GGB | 70.97 | GGB | 152314.25 | GGB | 120299.72 | GNB | 0 | 0 | 2745 | 3600 | 2729.64 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297665.95 | GGB | 297668.83 | 2729.64 | 2729.64 |  |  |  | 0 | 1 | [14 empty] | 91.2153 |  |  | #VALUE!
26.07.2008 16:00 | 3600 | 2 | 770.57 | GGB | 767.033 | 781.641 | 772.527 | 252.44 | GGB | 10046.2 | GGB | 9.78 | GGB | 1007.93 | GGB | 71.37 | GGB | 151778.39 | GGB | 119719.2 | GNB | 0 | 0 | 2729 | 3600 | 2713.24 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297702.04 | GGB | 297704.93 | 2713.24 | 2713.24 |  |  |  | 0 | 1 | [14 empty] | 90.2297 |  |  | #VALUE!
26.07.2008 17:00 | 3600 | 2 | 770.43 | GGB | 767.033 | 782.766 | 772.527 | 252.18 | GGB | 10014.3 | GGB | 9.78 | GGB | 1007.2 | GGB | 71.74 | GGB | 151621.04 | GGB | 119380.41 | GNB | 0 | 0 | 2733 | 3600 | 2717.47 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297738.14 | GGB | 297741.03 | 2717.47 | 2717.47 |  |  |  | 0 | 1 | [14 empty] | 90.1146 |  |  | #VALUE!
26.07.2008 18:00 | 3600 | 2 | 770.78 | GGB | 768.132 | 781.688 | 773.626 | 252.95 | GGB | 9974.24 | GGB | 9.78 | GGB | 1007.24 | GGB | 71.55 | GGB | 152642.15 | GGB | 120255.08 | GNB | 0 | 0 | 2710 | 3600 | 2694.45 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297774.24 | GGB | 297777.13 | 2694.45 | 2694.45 |  |  |  | 0 | 1 | [14 empty] | 90.0059 |  |  | #VALUE!
26.07.2008 19:00 | 3600 | 2 | 771.23 | GGB | 768.132 | 783.703 | 773.993 | 252.76 | GGB | 10002.2 | GGB | 9.78 | GGB | 1006.73 | GGB | 71.68 | GGB | 152268.04 | GGB | 119855.16 | GNB | 0 | 0 | 2702 | 3600 | 2686.72 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297810.33 | GGB | 297813.23 | 2686.72 | 2686.72 |  |  |  | 0 | 1 | [14 empty] | 89.4492 |  |  | #VALUE!
26.07.2008 20:00 | 3600 | 2 | 770.26 | GGB | 767.033 | 781.547 | 773.626 | 252.86 | GGB | 10018.4 | GGB | 9.77 | GGB | 1006.75 | GGB | 71.9 | GGB | 151911.53 | GGB | 119500.15 | GNB | 0 | 0 | 2732 | 3600 | 2716.94 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297846.43 | GGB | 297849.33 | 2716.94 | 2716.94 |  |  |  | 0 | 1 | [14 empty] | 90.1874 |  |  | #VALUE!
26.07.2008 21:00 | 3600 | 2 | 769.84 | GGB | 765.934 | 780.492 | 771.429 | 253.89 | GGB | 10052.6 | GGB | 9.77 | GGB | 1007.13 | GGB | 71.64 | GGB | 152280.14 | GGB | 119927.64 | GNB | 0 | 0 | 2763 | 3600 | 2747.71 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297882.52 | GGB | 297885.43 | 2747.71 | 2747.71 |  |  |  | 0 | 1 | [14 empty] | 91.5351 |  |  | #VALUE!
26.07.2008 22:00 | 3600 | 2 | 769.01 | GGB | 764.835 | 779.438 | 769.963 | 256.33 | GGB | 10076 | GGB | 9.76 | GGB | 1007.69 | GGB | 70.7 | GGB | 154431.3 | GGB | 122023.17 | GNB | 0 | 0 | 2827 | 3600 | 2811.38 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297918.62 | GGB | 297921.53 | 2811.38 | 2811.38 |  |  |  | 0 | 1 | [14 empty] | 95.2926 |  |  | #VALUE!
26.07.2008 23:00 | 3600 | 2 | 768.65 | GGB | 764.835 | 777.961 | 769.963 | 258.57 | GGB | 10132.7 | GGB | 9.77 | GGB | 1008.78 | GGB | 70.03 | GGB | 156110.42 | GGB | 123722.75 | GNB | 0 | 0 | 2894 | 3600 | 2878.67 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297954.71 | GGB | 297957.63 | 2878.67 | 2878.67 |  |  |  | 1 | 1 |  |  |  |  | 123722.75 | 2878.67 |  | 2878.67 | 9.8658 | [5 empty] | 98.9325 |  |  | #VALUE!
26.07.2008 24:00 | 3600 | 2 | 768.25 | GGB | 764.469 | 777.82 | 769.597 | 259.09 | GGB | 10229.5 | GGB | 9.77 | GGB | 1009.59 | GGB | 70.36 | GGB | 156224.85 | GGB | 123795.19 | GNB | 0 | 0 | 2952 | 3600 | 2936.19 | GGB | 100 | GGB | 36.1 | GGB | 36.1 | GGB | 297990.81 | GGB | 297993.73 | 2936.19 | 2936.19 |  |  |  | 1 | 1 |  |  |  |  | 123795.19 | 2936.19 |  | 2936.19 | 10.0689 | [5 empty] | 100.9684 |  |  | #VALUE!
27.07.2008 01:00 | 3600 | 2 | 767.73 | GGB | 763.37 | 777.68 | 768.498 | 259.9 | GGB | 10276.4 | GGB | 9.77 | GGB | 1010.11 | GGB | 69.98 | GGB | 156540.65 | GGB | 124245.27 | GGB | 0 | 0 | 2995 | 3600 | 2979.03 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298029.27 | GGB | 298032.19 | 2979.03 | 2979.03 |  |  |  | 0 | 1 | [14 empty] | 102.814 |  |  | #VALUE!
27.07.2008 02:00 | 3600 | 2 | 767.44 | GGB | 764.835 | 778.781 | 768.498 | 261.39 | GGB | 10330.7 | GGB | 9.77 | GGB | 1010.26 | GGB | 69.63 | GGB | 158030.51 | GGB | 125575.7 | GGB | 0 | 0 | 3034 | 3600 | 3018.66 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298067.73 | GGB | 298070.65 | 3018.66 | 3009.5632 |  |  |  | 0 | 1 | [14 empty] | 105.2973 | 3009.5632 |  | 104.98
27.07.2008 03:00 | 3600 | 2 | 767.36 | GGB | 764.835 | 778.664 | 769.597 | 262.59 | GGB | 10364.1 | GGB | 9.78 | GGB | 1010.68 | GGB | 69.3 | GGB | 159124.24 | GGB | 126619.18 | GGB | 0 | 0 | 3041 | 3600 | 3025.48 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298106.19 | GGB | 298109.11 | 3025.48 | 2984.7611 |  |  |  | 1 | 1 |  |  |  |  | 126619.18 | 2984.7611 | 126619.18 |  | 9.8265 | [5 empty] | 106.4122 | 2984.7611 |  | 104.98
27.07.2008 04:00 | 3600 | 2 | 766.59 | GGB | 764.835 | 778.523 | 768.498 | 264.57 | GGB | 10347.9 | GGB | 9.76 | GGB | 1011.55 | GGB | 68.36 | GGB | 161218.19 | GGB | 128749.03 | GGB | 0 | 0 | 3067 | 3600 | 3051.7 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298144.64 | GGB | 298147.57 | 3051.7 | 2935.3852 |  |  |  | 1 | 1 |  |  |  |  | 128749.03 | 2935.3852 | 128749.03 | 2935.3852 | 9.8265 | [5 empty] | 109.1398 | 2935.3852 |  | 104.98
27.07.2008 05:00 | 3600 | 2 | 766.9 | GGB | 763.37 | 778.406 | 768.498 | 264.48 | GGB | 10443.1 | GGB | 9.78 | GGB | 1011.97 | GGB | 68.57 | GGB | 160322.51 | GGB | 128006.71 | GGB | 0 | 0 | 3077 | 3600 | 3060.78 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298183.1 | GGB | 298186.03 | 3060.78 | 2952.4077 |  |  |  | 0 | 1 | [14 empty] | 108.8334 | 2952.4077 |  | 104.98
27.07.2008 06:00 | 3600 | 2 | 766.57 | GGB | 763.37 | 777.422 | 768.498 | 264.88 | GGB | 10455.5 | GGB | 9.78 | GGB | 1012.03 | GGB | 68.5 | GGB | 160703.23 | GGB | 128346.84 | GGB | 0 | 0 | 3108 | 3600 | 3092.33 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298221.56 | GGB | 298224.49 | 3092.33 | 2944.5836 |  |  |  | 0 | 1 | [14 empty] | 110.2474 | 2944.5836 |  | 104.98
27.07.2008 07:00 | 3600 | 2 | 767.16 | GGB | 764.835 | 778.617 | 769.597 | 264.34 | GGB | 10465.3 | GGB | 9.8 | GGB | 1012.23 | GGB | 68.63 | GGB | 160359.92 | GGB | 128047.13 | GGB | 0 | 0 | 3097 | 3600 | 3080.8 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298260.02 | GGB | 298262.95 | 3080.8 | 2951.4758 |  |  |  | 1 | 1 |  |  |  |  | 128047.13 | 2951.4758 | 128047.13 | 2951.4758 | 9.8265 | [5 empty] | 109.5799 | 2951.4758 |  | 104.98
27.07.2008 08:00 | 3600 | 2 | 767.41 | GGB | 764.835 | 778.617 | 768.498 | 262.89 | GGB | 10425.3 | GGB | 9.8 | GGB | 1012.28 | GGB | 68.96 | GGB | 159024.11 | GGB | 126863.94 | GGB | 0 | 0 | 3072 | 3600 | 3056.57 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298298.48 | GGB | 298301.41 | 3056.57 | 2979.0025 |  |  |  | 1 | 1 |  |  |  |  | 126863.94 | 2979.0025 | 126863.94 |  | 9.8265 | [5 empty] | 107.7135 | 2979.0025 |  | 104.98
27.07.2008 09:00 | 3600 | 2 | 767.47 | GGB | 765.934 | 779.648 | 770.696 | 261.68 | GGB | 10364.5 | GGB | 9.8 | GGB | 1011.94 | GGB | 69.31 | GGB | 157639.89 | GGB | 125590.52 | GGB | 0 | 0 | 3041 | 3600 | 3025.58 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298336.94 | GGB | 298339.87 | 3025.58 | 3009.208 |  |  |  | 0 | 1 | [14 empty] | 105.5512 | 3009.208 |  | 104.98
27.07.2008 10:00 | 3600 | 2 | 768.41 | GGB | 765.934 | 779.719 | 770.696 | 260.35 | GGB | 10229.2 | GGB | 9.8 | GGB | 1011.25 | GGB | 69.79 | GGB | 156751.92 | GGB | 124621.9 | GGB | 0 | 0 | 2956 | 3600 | 2940.82 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298375.4 | GGB | 298378.33 | 2940.82 | 2940.82 |  |  |  | 0 | 1 | [14 empty] | 101.8029 |  |  | #VALUE!
27.07.2008 11:00 | 3600 | 2 | 768.77 | GGB | 767.033 | 781.031 | 771.795 | 256.97 | GGB | 10155.7 | GGB | 9.79 | GGB | 1010.26 | GGB | 70.89 | GGB | 153757.9 | GGB | 121730.86 | GNB | 0 | 0 | 2910 | 3600 | 2894.52 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298413.85 | GGB | 298416.79 | 2894.52 | 2894.52 |  |  |  | 0 | 1 | [14 empty] | 97.8757 |  |  | #VALUE!
27.07.2008 12:00 | 3600 | 2 | 769.41 | GGB | 767.033 | 782.086 | 773.26 | 255.53 | GGB | 10119.8 | GGB | 9.79 | GGB | 1009.74 | GGB | 71.91 | GGB | 152975.56 | GGB | 120693.8 | GNB | 0 | 0 | 2906 | 3600 | 2890.91 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298452.31 | GGB | 298455.25 | 2890.91 | 2890.91 |  |  |  | 0 | 1 | [14 empty] | 96.9208 |  |  | #VALUE!
27.07.2008 13:00 | 3600 | 2 | 769.06 | GGB | 765.934 | 781.031 | 770.696 | 254.91 | GGB | 10085.5 | GGB | 9.78 | GGB | 1009.25 | GGB | 71.94 | GGB | 152437.49 | GGB | 120198.18 | GNB | 0 | 0 | 2856 | 3600 | 2840.14 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298490.77 | GGB | 298493.71 | 2840.14 | 2840.14 |  |  |  | 0 | 1 | [14 empty] | 94.8277 |  |  | #VALUE!
27.07.2008 14:00 | 3600 | 2 | 769.48 | GGB | 765.934 | 781.102 | 771.795 | 254.33 | GGB | 10059.6 | GGB | 9.78 | GGB | 1008.68 | GGB | 72.19 | GGB | 152137.1 | GGB | 119806.64 | GNB | 0 | 0 | 2847 | 3600 | 2831.23 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298529.23 | GGB | 298532.17 | 2831.23 | 2831.23 |  |  |  | 0 | 1 | [14 empty] | 94.2223 |  |  | #VALUE!
27.07.2008 15:00 | 3600 | 2 | 770.14 | GGB | 767.033 | 781.031 | 772.161 | 254.84 | GGB | 10012.3 | GGB | 9.78 | GGB | 1008.31 | GGB | 72.07 | GGB | 152945.85 | GGB | 120443.03 | GNB | 0 | 0 | 2824 | 3600 | 2808.79 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298567.69 | GGB | 298570.63 | 2808.79 | 2808.79 |  |  |  | 0 | 1 | [14 empty] | 93.972 |  |  | #VALUE!
27.07.2008 16:00 | 3600 | 2 | 770.75 | GGB | 767.033 | 782.297 | 773.26 | 254.55 | GGB | 9980.19 | GGB | 9.78 | GGB | 1007.66 | GGB | 71.97 | GGB | 152949.15 | GGB | 120401.37 | GNB | 0 | 0 | 2789 | 3600 | 2774.01 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298606.15 | GGB | 298609.09 | 2774.01 | 2774.01 |  |  |  | 0 | 1 | [14 empty] | 92.7763 |  |  | #VALUE!
27.07.2008 17:00 | 3600 | 2 | 770.4 | GGB | 767.033 | 781.289 | 772.161 | 253.2 | GGB | 10003.8 | GGB | 9.78 | GGB | 1007.41 | GGB | 72.53 | GGB | 151737.68 | GGB | 119224.66 | GNB | 0 | 0 | 2798 | 3600 | 2783.01 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298644.6 | GGB | 298647.55 | 2783.01 | 2783.01 |  |  |  | 0 | 1 | [14 empty] | 92.1676 |  |  | #VALUE!
27.07.2008 18:00 | 3600 | 2 | 770.37 | GGB | 767.033 | 781.289 | 772.161 | 252.93 | GGB | 9997.41 | GGB | 9.78 | GGB | 1007.46 | GGB | 72.81 | GGB | 151487.9 | GGB | 118938.63 | GNB | 0 | 0 | 2783 | 3172 | 2767.53 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298683.06 | GGB | 298686.01 | 2767.53 | 2767.53 |  |  |  | 0 | 1 | [14 empty] | 91.4351 |  |  | #VALUE!
27.07.2008 19:00 | 3600 | 2 | 770.85 | GGB | 767.033 | 781.242 | 773.26 | 252.41 | GGB | 9986.16 | GGB | 9.78 | GGB | 1007.11 | GGB | 73.06 | GGB | 150996.05 | GGB | 118423.79 | GNB | 0 | 0 | 2754 | 3600 | 2738.18 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298721.52 | GGB | 298724.47 | 2738.18 | 2738.18 |  |  |  | 0 | 1 | [14 empty] | 90.0738 |  |  | #VALUE!
27.07.2008 20:00 | 3600 | 2 | 770.57 | GGB | 765.934 | 781.219 | 772.161 | 252.59 | GGB | 9991.01 | GGB | 9.77 | GGB | 1006.67 | GGB | 72.99 | GGB | 151309.64 | GGB | 118642.72 | GNB | 0 | 0 | 2774 | 3600 | 2758.71 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298759.98 | GGB | 298762.93 | 2758.71 | 2758.71 |  |  |  | 0 | 1 | [14 empty] | 90.9169 |  |  | #VALUE!
27.07.2008 21:00 | 3600 | 2 | 769.8 | GGB | 765.934 | 781.008 | 770.696 | 253.81 | GGB | 10041.1 | GGB | 9.77 | GGB | 1006.69 | GGB | 72.81 | GGB | 151906.03 | GGB | 119176.03 | GNB | 0 | 0 | 2824 | 3600 | 2808.97 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298798.44 | GGB | 298801.39 | 2808.97 | 2808.97 |  |  |  | 0 | 1 | [14 empty] | 92.9894 |  |  | #VALUE!
27.07.2008 22:00 | 3600 | 2 | 768.82 | GGB | 765.934 | 780.82 | 771.795 | 255.43 | GGB | 10094.7 | GGB | 9.76 | GGB | 1007.22 | GGB | 72.12 | GGB | 153006.37 | GGB | 120340.9 | GNB | 0 | 0 | 2891 | 3600 | 2875.63 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298836.9 | GGB | 298839.85 | 2875.63 | 2875.63 |  |  |  | 0 | 1 | [14 empty] | 96.1266 |  |  | #VALUE!
27.07.2008 23:00 | 3600 | 2 | 768.71 | GGB | 767.033 | 780.773 | 771.429 | 256.93 | GGB | 10160.4 | GGB | 9.77 | GGB | 1008.05 | GGB | 71.2 | GGB | 154245.35 | GGB | 121741.9 | GNB | 0 | 0 | 2919 | 3600 | 2903.47 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298875.36 | GGB | 298878.31 | 2903.47 | 2903.47 |  |  |  | 0 | 1 | [14 empty] | 98.1872 |  |  | #VALUE!
27.07.2008 24:00 | 3600 | 2 | 767.77 | GGB | 764.835 | 778.664 | 768.864 | 258.52 | GGB | 10217.5 | GGB | 9.77 | GGB | 1008.79 | GGB | 70.96 | GGB | 155483.23 | GGB | 122894.19 | GNB | 0 | 0 | 2996 | 3600 | 2980.75 | GGB | 100 | GGB | 38.46 | GGB | 38.46 | GGB | 298913.81 | GGB | 298916.77 | 2980.75 | 2980.75 |  |  |  | 1 | 1 |  |  |  |  | 122894.19 | 2980.75 |  |  | 9.5246 | [5 empty] | 101.7547 |  |  | #VALUE!
28.07.2008 01:00 | 3600 | 2 | 767.51 | GGB | 764.835 | 778.641 | 768.864 | 259.79 | GGB | 10274 | GGB | 9.77 | GGB | 1009.29 | GGB | 70.21 | GGB | 156428.42 | GGB | 123970.99 | GNB | 0 | 0 | 3044 | 3600 | 3028.22 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 298950.77 | GGB | 298953.73 | 3028.22 | 3028.22 |  |  |  | 1 | 1 |  |  |  |  | 123970.99 | 3028.22 |  |  | 10.1572 | [5 empty] | 104.281 |  |  | #VALUE!
28.07.2008 02:00 | 3600 | 2 | 767.22 | GGB | 764.469 | 777.656 | 768.498 | 262.07 | GGB | 10262.5 | GGB | 9.77 | GGB | 1009.97 | GGB | 69.26 | GGB | 158661 | GGB | 126176.38 | GGB | 0 | 0 | 3040 | 3600 | 3024.08 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 298987.73 | GGB | 298990.69 | 3024.08 | 2995.2357 |  |  |  | 1 | 1 |  |  |  |  | 126176.38 | 2995.2357 | 126176.38 |  | 10.2253 | [5 empty] | 105.991 | 2995.2357 |  | 104.98
28.07.2008 03:00 | 3600 | 2 | 767.01 | GGB | 764.469 | 778.688 | 768.498 | 262.21 | GGB | 10328.6 | GGB | 9.77 | GGB | 1009.94 | GGB | 69.11 | GGB | 157988.7 | GGB | 125691.56 | GGB | 0 | 0 | 3045 | 3600 | 3029.48 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299024.69 | GGB | 299027.65 | 3029.48 | 3006.789 |  |  |  | 1 | 1 |  |  |  |  | 125691.56 | 3006.789 | 125691.56 |  | 10.2253 | [5 empty] | 105.7722 | 3006.789 |  | 104.98
28.07.2008 04:00 | 3600 | 2 | 766.46 | GGB | 763.37 | 777.445 | 768.132 | 263.42 | GGB | 10365.4 | GGB | 9.77 | GGB | 1010.49 | GGB | 69.43 | GGB | 158956.99 | GGB | 126413.49 | GGB | 0 | 0 | 3103 | 3600 | 3087.02 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299061.65 | GGB | 299064.61 | 3087.02 | 2989.6176 |  |  |  | 0 | 1 | [14 empty] | 108.4003 | 2989.6176 |  | 104.98
28.07.2008 05:00 | 3600 | 2 | 766.7 | GGB | 763.37 | 776.461 | 768.132 | 264.26 | GGB | 10402.5 | GGB | 9.78 | GGB | 1010.91 | GGB | 69.19 | GGB | 159859.27 | GGB | 127274 | GGB | 0 | 0 | 3111 | 3600 | 3094.76 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299098.6 | GGB | 299101.57 | 3094.76 | 2969.4046 |  |  |  | 0 | 1 | [14 empty] | 109.4118 | 2969.4046 |  | 104.98
28.07.2008 06:00 | 3600 | 2 | 765.71 | GGB | 763.37 | 776.625 | 767.766 | 266.06 | GGB | 10448.2 | GGB | 9.76 | GGB | 1011.53 | GGB | 68.45 | GGB | 161605.51 | GGB | 129021.36 | GGB | 0 | 0 | 3181 | 3600 | 3164.96 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299135.56 | GGB | 299138.53 | 3164.96 | 2929.1894 |  |  |  | 0 | 1 | [14 empty] | 113.4298 | 2929.1894 |  | 104.98
28.07.2008 07:00 | 3600 | 2 | 766.7 | GGB | 765.934 | 778.805 | 769.963 | 266.7 | GGB | 10504.3 | GGB | 9.79 | GGB | 1012.04 | GGB | 67.88 | GGB | 162379.04 | GGB | 129920.7 | GGB | 0 | 0 | 3144 | 3600 | 3128.46 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299172.52 | GGB | 299175.49 | 3128.46 | 2908.9129 |  |  |  | 0 | 1 | [14 empty] | 112.9033 | 2908.9129 |  | 104.98
28.07.2008 08:00 | 3600 | 2 | 767.56 | GGB | 765.934 | 778.781 | 769.963 | 265.61 | GGB | 10504.2 | GGB | 9.81 | GGB | 1012.76 | GGB | 68.36 | GGB | 161571.39 | GGB | 129183.51 | GGB | 0 | 0 | 3097 | 3600 | 3081.7 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299209.48 | GGB | 299212.45 | 3081.7 | 2925.5127 |  |  |  | 0 | 1 | [14 empty] | 110.5847 | 2925.5127 |  | 104.98
28.07.2008 09:00 | 3600 | 2 | 767.46 | GGB | 767.033 | 780.797 | 771.429 | 264.16 | GGB | 10438.1 | GGB | 9.8 | GGB | 1012.92 | GGB | 68.84 | GGB | 159957.2 | GGB | 127736.97 | GGB | 0 | 0 | 3083 | 3600 | 3067.24 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299246.43 | GGB | 299249.41 | 3067.24 | 2958.6423 |  |  |  | 0 | 1 | [14 empty] | 108.8333 | 2958.6423 |  | 104.98
28.07.2008 10:00 | 3600 | 2 | 767.78 | GGB | 765.934 | 779.883 | 770.33 | 262.89 | GGB | 10373.1 | GGB | 9.79 | GGB | 1013.22 | GGB | 69.44 | GGB | 158690.71 | GGB | 126540.33 | GGB | 0 | 0 | 3035 | 3600 | 3019.78 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299283.39 | GGB | 299286.37 | 3019.78 | 2986.6209 |  |  |  | 0 | 1 | [14 empty] | 106.1455 | 2986.6209 |  | 104.98
28.07.2008 11:00 | 3600 | 2 | 768.29 | GGB | 765.934 | 779.813 | 771.429 | 261.57 | GGB | 10315.9 | GGB | 9.79 | GGB | 1012.41 | GGB | 69.67 | GGB | 157603.58 | GGB | 125487.91 | GGB | 0 | 0 | 2966 | 3600 | 2950.07 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299320.35 | GGB | 299323.33 | 2950.07 | 2950.07 |  |  |  | 0 | 1 | [14 empty] | 102.8328 |  |  | #VALUE!
28.07.2008 12:00 | 3600 | 2 | 768.5 | GGB | 767.033 | 781.875 | 771.429 | 261.03 | GGB | 10288 | GGB | 9.79 | GGB | 1011.8 | GGB | 69.69 | GGB | 157670.7 | GGB | 125458.48 | GGB | 0 | 0 | 2956 | 3600 | 2940.16 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299357.31 | GGB | 299360.29 | 2940.16 | 2940.16 |  |  |  | 0 | 1 | [14 empty] | 102.4633 |  |  | #VALUE!
28.07.2008 13:00 | 3600 | 2 | 769.14 | GGB | 768.132 | 781.875 | 773.626 | 260.28 | GGB | 10273.9 | GGB | 9.79 | GGB | 1011.45 | GGB | 69.74 | GGB | 157504.55 | GGB | 125264.24 | GGB | 0 | 0 | 2922 | 3600 | 2906.11 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299394.27 | GGB | 299397.25 | 2906.11 | 2906.11 |  |  |  | 0 | 1 | [14 empty] | 101.1199 |  |  | #VALUE!
28.07.2008 14:00 | 3600 | 2 | 769.27 | GGB | 767.033 | 782.344 | 772.527 | 259.42 | GGB | 10247.5 | GGB | 9.78 | GGB | 1011.29 | GGB | 69.92 | GGB | 156967.58 | GGB | 124750.83 | GGB | 0 | 0 | 2899 | 3600 | 2883.02 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299431.22 | GGB | 299434.21 | 2883.02 | 2883.02 |  |  |  | 0 | 1 | [14 empty] | 99.9053 |  |  | #VALUE!
28.07.2008 15:00 | 3600 | 2 | 769.88 | GGB | 770.696 | 784.078 | 775.091 | 259.55 | GGB | 10214.5 | GGB | 9.8 | GGB | 1010.94 | GGB | 69.8 | GGB | 157727.92 | GGB | 125354.69 | GGB | 0 | 0 | 2858 | 3600 | 2842.21 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299468.18 | GGB | 299471.17 | 2842.21 | 2842.21 |  |  |  | 0 | 1 | [14 empty] | 98.9679 |  |  | #VALUE!
28.07.2008 16:00 | 3600 | 2 | 770.74 | GGB | 765.934 | 780.703 | 771.429 | 257.45 | GGB | 10217 | GGB | 9.8 | GGB | 1010.28 | GGB | 70.4 | GGB | 156126.92 | GGB | 123785.2 | GNB | 0 | 0 | 2788 | 3600 | 2772.84 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299505.14 | GGB | 299508.13 | 2772.84 | 2772.84 |  |  |  | 0 | 1 | [14 empty] | 95.3435 |  |  | #VALUE!
28.07.2008 17:00 | 3600 | 2 | 771.08 | GGB | 768.132 | 781.922 | 772.527 | 256.81 | GGB | 10213.1 | GGB | 9.81 | GGB | 1009.9 | GGB | 70.65 | GGB | 155556.95 | GGB | 123200.17 | GNB | 0 | 0 | 2774 | 3600 | 2758.22 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299542.1 | GGB | 299545.09 | 2758.22 | 2758.22 |  |  |  | 0 | 1 | [14 empty] | 94.3925 |  |  | #VALUE!
28.07.2008 18:00 | 3600 | 2 | 770.86 | GGB | 768.132 | 782.203 | 773.26 | 256.81 | GGB | 10202.8 | GGB | 9.8 | GGB | 1009.38 | GGB | 70.55 | GGB | 155473.32 | GGB | 123102.24 | GNB | 0 | 0 | 2779 | 3600 | 2763.28 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299579.05 | GGB | 299582.05 | 2763.28 | 2763.28 |  |  |  | 0 | 1 | [14 empty] | 94.4905 |  |  | #VALUE!
28.07.2008 19:00 | 3600 | 2 | 770.82 | GGB | 767.033 | 781.078 | 772.161 | 256.86 | GGB | 10201.4 | GGB | 9.8 | GGB | 1009.27 | GGB | 70.67 | GGB | 155332.48 | GGB | 122934.62 | GNB | 0 | 0 | 2775 | 3600 | 2759.52 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299616.01 | GGB | 299619.01 | 2759.52 | 2759.52 |  |  |  | 0 | 1 | [14 empty] | 94.2335 |  |  | #VALUE!
28.07.2008 20:00 | 3600 | 2 | 770.89 | GGB | 767.033 | 782.484 | 772.161 | 256.83 | GGB | 10197.6 | GGB | 9.8 | GGB | 1009.09 | GGB | 70.85 | GGB | 155263.16 | GGB | 122795.05 | GNB | 0 | 0 | 2774 | 3600 | 2758.8 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299652.97 | GGB | 299655.97 | 2758.8 | 2758.8 |  |  |  | 0 | 1 | [14 empty] | 94.1019 |  |  | #VALUE!
28.07.2008 21:00 | 3600 | 2 | 769.8 | GGB | 767.033 | 781.453 | 771.795 | 257.05 | GGB | 10204.5 | GGB | 9.79 | GGB | 1009.11 | GGB | 70.7 | GGB | 155387.5 | GGB | 122950.63 | GNB | 0 | 0 | 2838 | 3600 | 2822.92 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299689.93 | GGB | 299692.93 | 2822.92 | 2822.92 |  |  |  | 0 | 1 | [14 empty] | 96.4111 |  |  | #VALUE!
28.07.2008 22:00 | 3600 | 2 | 768.78 | GGB | 767.033 | 781.383 | 771.795 | 260.51 | GGB | 10252.6 | GGB | 9.79 | GGB | 1009.61 | GGB | 69.81 | GGB | 158015.1 | GGB | 125416.99 | GGB | 0 | 0 | 2927 | 3600 | 2911.21 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299726.89 | GGB | 299729.89 | 2911.21 | 2911.21 |  |  |  | 0 | 1 | [14 empty] | 101.4209 |  |  | #VALUE!
28.07.2008 23:00 | 3600 | 2 | 768.45 | GGB | 765.934 | 780.07 | 769.597 | 262.06 | GGB | 10290.7 | GGB | 9.79 | GGB | 1010.32 | GGB | 69.13 | GGB | 159328.91 | GGB | 126798.97 | GGB | 0 | 0 | 2952 | 3600 | 2935.95 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299763.84 | GGB | 299766.85 | 2935.95 | 2935.95 |  |  |  | 0 | 1 | [14 empty] | 103.4098 |  |  | #VALUE!
28.07.2008 24:00 | 3600 | 2 | 769.16 | GGB | 765.934 | 780 | 770.696 | 262.47 | GGB | 10325.5 | GGB | 9.81 | GGB | 1010.99 | GGB | 68.99 | GGB | 159458.75 | GGB | 127037.48 | GGB | 0 | 0 | 2947 | 3600 | 2931.66 | GGB | 100 | GGB | 36.96 | GGB | 36.96 | GGB | 299800.8 | GGB | 299803.81 | 2931.66 | 2931.66 |  |  |  | 0 | 1 | [14 empty] | 103.453 |  |  | #VALUE!
| 27320400 |  | The end of baseline | [32 empty] | The end of baseline | [5 empty] | 5045 | 7589 |  |  |  |  | 701454676.78 | 13291994.6544 | [9 empty] | 2346
Total operation hours | 7589 | [31 empty] | CLBL | 299800.8 | [7 empty] | 66.4778
[33 empty] | Clnormal | 303129.333
ok
Note on AJ1: BASELINE"S ROW DATA
Note on A790: Shutdown of GP plant
Note on A2760: Shutdown of GP Plant
Note on A2924: Shutdown of GP Plant

## revision list
Revision list of baseline campaign calculations
version No. | date of revision | performed changes
1 | 18-12-2009 | 1. Because CLn<CLnormal therefore the values were eliminated for the parameter NCSGBC beyond the length of CLn for calculating mean values for NCSGBC. The baseline emissions (BEBC) were recalculated by using this mean value multiplied by the mean value of the volume of stack gas (VSGBC) and total operating hours (OHBC) of the baseline campaign. For recalculation of the EFBL the nitric acid production (NAPBC) corresponding to the total operating hours of the baseline campaign length (OHBC) was used. 2. Performed correction of NCSG values when the drift of span calibration was upper the limit values (±3,04% of the measurement range). 3. In the sheet "Downtime of AMS" were inputed daily events (shutdowns, downtimes, troubles).
2 | 15-01-2010 | 1. From DCS database were inputed OT data from the Burners No.2,3 and 4 for the filtering of valid VSG and NCSG values. 2. During 2008 period in case if N2O concentration in g/s was higher than ELV (104,98 g/s) as stated in Environmental IPPC, NCSG concentartion mg/m3 was recalculated and adjusted 104,98 g/s.
3 | 18-01-2010 | 1. Performed correction in calculation of NAPBC.
4 | 11-02-2010 | 1. Was written additionally explanation about collection of NCSG values in AL and AM columns.
2. Corrected measurement units of OH, and of NCSG valid counter
3. Were written definition of the parameters extracted from Afriso system
5 | 01-07-2011 | 1. Performed calculation of Efbl by using NCSG values of full baseline campaign